## ER
Project Name:- | CHANJU I HYDRO ELECTRIC PROJECT
GS Project activity reference:- | GS 7154
GS Project activity Web link:- | https://registry.goldstandard.org/projects/details/1425
Date:- | 2025-11-03
Version:- | 7
Parameter |  | Value | Unit
Start Date of Monitoring Period |  | 2019-07-01 | date
End Date of Monitoring Period |  | 2022-07-25 | date
Number of operational Days for Current Monitoring Period (days) |  | 1121 | Number
Baseline Emission Factor |  | 0.9124 | tCO2e/MWh
Annual (365 Days) estimation as per Registered PDD |  | 142582 | tCO2e
Annual (365 Days) Estimated value of electricity generation as per PDD |  | 156272 | MWh
ER Estimation for Current Monitoring Period |  | 437902 | tCO2e
Estimated value of electricity generation for current monitoring period |  | 479945.1995 | MWh
Generation achieved in this monitoring period |  | 457980.363 | MWh
Baseline Emissions |  | 417782 | tCO2e
Project Emissions |  | 0 | tCO2e
Leakage Emissions |  | 0 | tCO2e
ER for Current Monitoring Period |  | 417782 | tCO2e
Variation in Actual Vs Estimated ER |  | -4.595% | %
[8 empty] | SDG 13 |  | SDG 07
[5 empty] | Vintage |  | Days | Estimated | Actual | Estimated | Actual
During Monitoring Period | Unit | Estimated | Actual |  | 2019-07-01 | 2019-12-31 | 184 | 71876 | 80644 | 78778 | 88401
SDG 7 | MWh | 479945.1995 | 457980.363 |  | 2020-01-01 | 2020-12-31 | 366 | 142972 | 151375 | 156700 | 165939
SDG 13 | tCO2e | 437902 | 417782 |  | 2021-01-01 | 2021-12-31 | 365 | 156272 | 124889 | 156272 | 136906.456
SDG 08 (Employment) | Number | 5 | 04 (Skilled: 04, Un-Skilled: 0, Semi-Skilled: 0) |  | 2022-01-01 | 2022-07-25 | 206 | 80470 | 60874 | 88197 | 66733.907
SDG 08 (training) | Number | 1 | 6 |  | Total |  | 1121 | 451590 | 417782 | 479947 | 457980.363
Vintage Wise Data
Start Date | End Date | SDG 7 (MWh) | SDG 13 (tCO2e) | SDG 8: Training record (Number) | SDG 8 Employment generation (Number)
2019-07-01 | 2020-01-05 | 88401 | 80644 | 1 | 04 (Skilled: 04, Un-Skilled: 0, Semi-Skilled: 0)
2020-01-06 | 2021-01-03 | 165939 | 151375 | 2 | 04 (Skilled: 04, Un-Skilled: 0, Semi-Skilled: 0)
2021-01-04 | 2022-01-02 | 136906.456 | 124889 | 2 | 04 (Skilled: 04, Un-Skilled: 0, Semi-Skilled: 0)
2022-01-03 | 2022-07-25 | 66733.907 | 60874 | 1 | 04 (Skilled: 04, Un-Skilled: 0, Semi-Skilled: 0)
Billing Cycle |  | Joint Meter Reading |  | Reading As per Energy Meter at Plant Site owned by Client (in MWh) | Minimum of Plant Records and JMR (MRI) (in MWh) |  | Minimum of Plant Records and JMR (MRI) (in MWh) with error factor | BEy | PEy | LEy | ERy | Vintage
From | To | As per JMR - Meter Reading Instrument (MRI) owned by State Electricity Board (in kWh) | As per JMR - Meter Reading Instrument (MRI) owned by State Electricity Board (in MWh) |  |  |  |  | tCO1 | tCO2 | tCO2 | tCO2 | tCO2
2019-07-01 | 2019-07-07 | 5253000 | 5253 | 5288.1813 | 5253 |  | 5253 | 4792 | 0 | 0 | 4792 | 80644
2019-07-08 | 2019-07-14 | 6294000 | 6294 | 6346.2853 | 6294 |  | 6294 | 5742 | 0 | 0 | 5742
2019-07-15 | 2019-07-21 | 6538000 | 6538 | 6588.3531 | 6538 |  | 6538 | 5965 | 0 | 0 | 5965
2019-07-22 | 2019-07-28 | 4720000 | 4720 | 4756.728 | 4720 |  | 4720 | 4306 | 0 | 0 | 4306
2019-07-29 | 2019-08-04 | 4809000 | 4809 | 4849.778 | 4809 |  | 4809 | 4387 | 0 | 0 | 4387
2019-08-05 | 2019-08-11 | 6415000 | 6415 | 6466.1785 | 6415 |  | 6415 | 5853 | 0 | 0 | 5853
2019-08-12 | 2019-08-18 | 5243000 | 5243 | 5290.4162 | 5243 |  | 5243 | 4783 | 0 | 0 | 4783
2019-08-19 | 2019-08-25 | 6403000 | 6403 | 6451.5794 | 6403 |  | 6403 | 5842 | 0 | 0 | 5842
2019-08-26 | 2019-09-01 | 6520000 | 6520 | 6571.7303 | 6520 |  | 6520 | 5948 | 0 | 0 | 5948
2019-09-02 | 2019-09-08 | 6275000 | 6275 | 6318.9415 | 6275 |  | 6275 | 5725 | 0 | 0 | 5725
2019-09-09 | 2019-09-15 | 4791000 | 4791 | 4834.0324 | 4791 |  | 4791 | 4371 | 0 | 0 | 4371
2019-09-16 | 2019-09-22 | 3730000 | 3730 | 3756.1069 | 3730 |  | 3730 | 3403 | 0 | 0 | 3403
2019-09-23 | 2019-09-29 | 2955000 | 2955 | 2976.1292 | 2955 |  | 2955 | 2696 | 0 | 0 | 2696
2019-09-30 | 2019-10-06 | 2539000 | 2539 | 2559.3547 | 2539 |  | 2539 | 2316 | 0 | 0 | 2316
2019-10-07 | 2019-10-13 | 2318000 | 2318 | 2334.4888 | 2318 |  | 2318 | 2114 | 0 | 0 | 2114
2019-10-14 | 2019-10-20 | 2066000 | 2066 | 2083.7991 | 2066 |  | 2066 | 1885 | 0 | 0 | 1885
2019-10-21 | 2019-10-27 | 1721000 | 1721 | 1738.7889 | 1721 |  | 1721 | 1570 | 0 | 0 | 1570
2019-10-28 | 2019-11-03 | 1496000 | 1496 | 1511.7319 | 1496 |  | 1496 | 1364 | 0 | 0 | 1364
2019-11-04 | 2019-11-10 | 1440000 | 1440 | 1449.7347 | 1440 |  | 1440 | 1313 | 0 | 0 | 1313
2019-11-11 | 2019-11-17 | 1219000 | 1219 | 1234.1022 | 1219 |  | 1219 | 1112 | 0 | 0 | 1112
2019-11-18 | 2019-11-24 | 1137000 | 1137 | 1147.2484 | 1137 |  | 1137 | 1037 | 0 | 0 | 1037
2019-11-25 | 2019-12-01 | 1061000 | 1061 | 1071.5501 | 1061 |  | 1061 | 968 | 0 | 0 | 968
2019-12-02 | 2019-12-08 | 505000 | 505 | 514.9361 | 505 |  | 505 | 460 | 0 | 0 | 460
2019-12-09 | 2019-12-15 | 260000 | 260 | 267.3525 | 260 |  | 260 | 237 | 0 | 0 | 237
2019-12-16 | 2019-12-22 | 933000 | 933 | 943.7963 | 933 |  | 933 | 851 | 0 | 0 | 851
2019-12-23 | 2019-12-29 | 982000 | 982 | 994.738 | 982 |  | 982 | 895 | 0 | 0 | 895
2019-12-30 | 2020-01-05 | 778000 | 778 | 790.4687 | 778 |  | 778 | 709 | 0 | 0 | 709
2020-01-06 | 2020-01-12 | 881000 | 881 | 892.0172 | 881 |  | 881 | 803 | 0 | 0 | 803 | 151375
2020-01-13 | 2020-01-19 | 1056000 | 1056 | 1067.0834 | 1056 |  | 1056 | 963 | 0 | 0 | 963
2020-01-20 | 2020-01-26 | 1012000 | 1012 | 1023.4429 | 1012 |  | 1012 | 923 | 0 | 0 | 923
2020-01-27 | 2020-02-02 | 1046000 | 1046 | 1083.3905 | 1046 |  | 1046 | 954 | 0 | 0 | 954
2020-02-03 | 2020-02-09 | 1035000 | 1035 | 1049.1719 | 1035 |  | 1035 | 944 | 0 | 0 | 944
2020-02-10 | 2020-02-16 | 1313000 | 1313 | 1325.0361 | 1313 |  | 1313 | 1197 | 0 | 0 | 1197
2020-02-17 | 2020-02-23 | 1444000 | 1444 | 1454.669 | 1444 |  | 1444 | 1317 | 0 | 0 | 1317
2020-02-24 | 2020-03-01 | 1290000 | 1290 | 1304.4675 | 1290 |  | 1290 | 1176 | 0 | 0 | 1176
2020-03-02 | 2020-03-08 | 1236000 | 1236 | 1250.3618 | 1236 |  | 1236 | 1127 | 0 | 0 | 1127
2020-03-09 | 2020-03-15 | 1308000 | 1308 | 1320.9231 | 1308 |  | 1308 | 1193 | 0 | 0 | 1193
2020-03-16 | 2020-03-22 | 1989000 | 1989 | 2004.3449 | 1989 |  | 1989 | 1814 | 0 | 0 | 1814
2020-03-23 | 2020-03-29 | 2503000 | 2503 | 2520.5822 | 2503 |  | 2503 | 2283 | 0 | 0 | 2283
2020-03-30 | 2020-04-05 | 2976000 | 2976 | 2989.7007 | 2976 |  | 2976 | 2715 | 0 | 0 | 2715
2020-04-06 | 2020-04-12 | 2978000 | 2978 | 3002.8166 | 2978 |  | 2978 | 2717 | 0 | 0 | 2717
2020-04-13 | 2020-04-19 | 4681000 | 4681 | 4708.2239 | 4681 |  | 4681 | 4270 | 0 | 0 | 4270
2020-04-20 | 2020-04-26 | 4013000 | 4013 | 4026.9764 | 4013 |  | 4013 | 3661 | 0 | 0 | 3661
2020-04-27 | 2020-05-03 | 4707000 | 4707 | 4743.3793 | 4707 |  | 4707 | 4294 | 0 | 0 | 4294
2020-05-04 | 2020-05-10 | 4973000 | 4973 | 5009.5939 | 4973 |  | 4973 | 4537 | 0 | 0 | 4537
2020-05-11 | 2020-05-17 | 4937000 | 4937 | 4968.2447 | 4937 |  | 4937 | 4504 | 0 | 0 | 4504
2020-05-18 | 2020-05-24 | 4499000 | 4499 | 4525.084 | 4499 |  | 4499 | 4104 | 0 | 0 | 4104
2020-05-25 | 2020-05-31 | 4616000 | 4616 | 4648.6567 | 4616 |  | 4616 | 4211 | 0 | 0 | 4211
2020-06-01 | 2020-06-07 | 4777000 | 4777 | 4819.5326 | 4777 |  | 4777 | 4358 | 0 | 0 | 4358
2020-06-08 | 2020-06-14 | 5466000 | 5466 | 5514.1584 | 5466 |  | 5466 | 4987 | 0 | 0 | 4987
2020-06-15 | 2020-06-21 | 5616000 | 5616 | 5664.4046 | 5616 |  | 5616 | 5124 | 0 | 0 | 5124
2020-06-22 | 2020-06-28 | 5996000 | 5996 | 6049.9023 | 5996 |  | 5996 | 5470 | 0 | 0 | 5470
2020-06-29 | 2020-07-05 | 6620000 | 6620 | 6680.9521 | 6620 |  | 6620 | 6040 | 0 | 0 | 6040
2020-07-06 | 2020-07-12 | 6794000 | 6794 | 6857.7958 | 6794 |  | 6794 | 6198 | 0 | 0 | 6198
2020-07-13 | 2020-07-19 | 6513000 | 6513 | 6571.872 | 6513 |  | 6513 | 5942 | 0 | 0 | 5942
2020-07-20 | 2020-07-26 | 6372000 | 6372 | 6433.2284 | 6372 |  | 6372 | 5813 | 0 | 0 | 5813
2020-07-27 | 2020-08-02 | 5460000 | 5460 | 5507.8305 | 5460 |  | 5460 | 4981 | 0 | 0 | 4981
2020-08-03 | 2020-08-09 | 5690000 | 5690 | 5739.6509 | 5690 |  | 5690 | 5191 | 0 | 0 | 5191
2020-08-10 | 2020-08-16 | 6431000 | 6431 | 6489.4832 | 6431 |  | 6431 | 5867 | 0 | 0 | 5867
2020-08-17 | 2020-08-23 | 6053000 | 6053 | 6106.9902 | 6053 |  | 6053 | 5522 | 0 | 0 | 5522
2020-08-24 | 2020-08-30 | 6698000 | 6698 | 6760.8092 | 6698 |  | 6698 | 6111 | 0 | 0 | 6111
2020-08-31 | 2020-09-06 | 6435000 | 6435 | 6494.1051 | 6435 |  | 6435 | 5871 | 0 | 0 | 5871
2020-09-07 | 2020-09-13 | 4825000 | 4825 | 4862.7315 | 4825 |  | 4825 | 4402 | 0 | 0 | 4402
2020-09-14 | 2020-09-20 | 3662000 | 3662 | 3687.3704 | 3662 |  | 3662 | 3341 | 0 | 0 | 3341
2020-09-21 | 2020-09-27 | 2680000 | 2680 | 2701.3313 | 2680 |  | 2680 | 2445 | 0 | 0 | 2445
2020-09-28 | 2020-10-04 | 2372000 | 2372 | 2391.2767 | 2372 |  | 2372 | 2164 | 0 | 0 | 2164
2020-10-05 | 2020-10-11 | 2048000 | 2048 | 2064.0898 | 2048 |  | 2048 | 1868 | 0 | 0 | 1868
2020-10-12 | 2020-10-18 | 1793000 | 1793 | 1809.4498 | 1793 |  | 1793 | 1635 | 0 | 0 | 1635
2020-10-19 | 2020-10-25 | 1476000 | 1476 | 1491.3336 | 1476 |  | 1476 | 1346 | 0 | 0 | 1346
2020-10-26 | 2020-11-01 | 1251000 | 1251 | 1268.4429 | 1251 |  | 1251 | 1141 | 0 | 0 | 1141
2020-11-02 | 2020-11-08 | 1069000 | 1069 | 1084.6481 | 1069 |  | 1069 | 975 | 0 | 0 | 975
2020-11-09 | 2020-11-15 | 922000 | 922 | 936.577 | 922 |  | 922 | 841 | 0 | 0 | 841
2020-11-16 | 2020-11-22 | 813000 | 813 | 830.3668 | 813 |  | 813 | 741 | 0 | 0 | 741
2020-11-23 | 2020-11-29 | 829000 | 829 | 850.872 | 829 |  | 829 | 756 | 0 | 0 | 756
2020-11-30 | 2020-12-06 | 840000 | 840 | 859.0787 | 840 |  | 840 | 766 | 0 | 0 | 766
2020-12-07 | 2020-12-13 | 859000 | 859 | 879.4807 | 859 |  | 859 | 783 | 0 | 0 | 783
2020-12-14 | 2020-12-20 | 264000 | 264 | 280.8312 | 264 |  | 264 | 240 | 0 | 0 | 240
2020-12-21 | 2020-12-27 | 133000 | 133 | 149.0405 | 133 |  | 133 | 121 | 0 | 0 | 121
2020-12-28 | 2021-01-03 | 689000 | 689 | 708.7129 | 689 |  | 689 | 628 | 0 | 0 | 628
2021-01-04 | 2021-01-10 | 690000 | 690 | 711.3318 | 690 |  | 690 | 629 | 0 | 0 | 629 | 124889
2021-01-11 | 2021-01-17 | 667000 | 667 | 686.1525 | 667 |  | 667 | 608 | 0 | 0 | 608
2021-01-18 | 2021-01-24 | 669000 | 669 | 691.1547 | 669 |  | 669 | 610 | 0 | 0 | 610
2021-01-25 | 2021-01-31 | 661000 | 661 | 681.7097 | 661 |  | 659.678 | 601 | 0 | 0 | 601
2021-02-01 | 2021-02-07 | 614000 | 614 | 633.0004 | 614 |  | 612.772 | 559 | 0 | 0 | 559
2021-02-08 | 2021-02-14 | 654000 | 654 | 667.9042 | 654 |  | 652.692 | 595 | 0 | 0 | 595
2021-02-15 | 2021-02-21 | 634000 | 634 | 651.6438 | 634 |  | 632.732 | 577 | 0 | 0 | 577
2021-02-22 | 2021-02-28 | 650000 | 650 | 668.977 | 650 |  | 648.7 | 591 | 0 | 0 | 591
2021-03-01 | 2021-03-07 | 630000 | 630 | 646.6804 | 630 |  | 628.74 | 573 | 0 | 0 | 573
2021-03-08 | 2021-03-14 | 603000 | 603 | 617.055 | 603 |  | 603 | 550 | 0 | 0 | 550
2021-03-15 | 2021-03-21 | 616000 | 616 | 634.4525 | 616 |  | 616 | 562 | 0 | 0 | 562
2021-03-22 | 2021-03-28 | 832000 | 832 | 854.1786 | 832 |  | 832 | 759 | 0 | 0 | 759
2021-03-29 | 2021-04-04 | 1065000 | 1065 | 1087.5807 | 1065 |  | 1065 | 971 | 0 | 0 | 971
2021-04-05 | 2021-04-11 | 1149000 | 1149 | 1171.2908 | 1149 |  | 1149 | 1048 | 0 | 0 | 1048
2021-04-12 | 2021-04-18 | 1144000 | 1144 | 1165.4815 | 1144 |  | 1144 | 1043 | 0 | 0 | 1043
2021-04-19 | 2021-04-25 | 1874000 | 1874 | 1900.8418 | 1874 |  | 1874 | 1709 | 0 | 0 | 1709
2021-04-26 | 2021-05-02 | 2596000 | 2596 | 2625.9712 | 2596 |  | 2596 | 2368 | 0 | 0 | 2368
2021-05-03 | 2021-05-09 | 2668000 | 2668 | 2700.5143 | 2668 |  | 2668 | 2434 | 0 | 0 | 2434
2021-05-10 | 2021-05-16 | 2715000 | 2715 | 2742.1173 | 2715 |  | 2715 | 2477 | 0 | 0 | 2477
2021-05-17 | 2021-05-23 | 2854000 | 2854 | 2880.0542 | 2854 |  | 2854 | 2603 | 0 | 0 | 2603
2021-05-24 | 2021-05-30 | 3581000 | 3581 | 3611.5033 | 3581 |  | 3581 | 3267 | 0 | 0 | 3267
2021-05-31 | 2021-06-06 | 3882000 | 3882 | 3910.3087 | 3882 |  | 3882 | 3541 | 0 | 0 | 3541
2021-06-07 | 2021-06-13 | 5513000 | 5513 | 5562.7596 | 5513 |  | 5513 | 5030 | 0 | 0 | 5030
2021-06-14 | 2021-06-20 | 5555000 | 5555 | 5600.8053 | 5555 |  | 5555 | 5068 | 0 | 0 | 5068
2021-06-21 | 2021-06-27 | 5003097 | 5003.097 | 5043.2038 | 5003.097 |  | 5003.097 | 4564 | 0 | 0 | 4564
2021-06-28 | 2021-07-04 | 5099609 | 5099.609 | 5138.562 | 5099.609 |  | 5099.609 | 4652 | 0 | 0 | 4652
2021-07-05 | 2021-07-11 | 5885777 | 5885.777 | 5930.988 | 5885.777 |  | 5885.777 | 5370 | 0 | 0 | 5370
2021-07-12 | 2021-07-18 | 6235891 | 6235.891 | 6286.482 | 6235.891 |  | 6235.891 | 5689 | 0 | 0 | 5689
2021-07-19 | 2021-07-25 | 6825123 | 6825.123 | 6877.524 | 6825.123 |  | 6825.123 | 6227 | 0 | 0 | 6227
2021-07-26 | 2021-08-01 | 6139448 | 6139.448 | 6184.654 | 6139.448 |  | 6139.448 | 5601 | 0 | 0 | 5601
2021-08-02 | 2021-08-08 | 6610273 | 6610.273 | 6660.776 | 6610.273 |  | 6610.273 | 6031 | 0 | 0 | 6031
2021-08-09 | 2021-08-15 | 6544856 | 6544.856 | 6595.372 | 6544.856 |  | 6544.856 | 5971 | 0 | 0 | 5971
2021-08-16 | 2021-08-22 | 5073985 | 5073.985 | 5109.42 | 5073.985 |  | 5073.985 | 4629 | 0 | 0 | 4629
2021-08-23 | 2021-08-29 | 4760728 | 4760.728 | 4792.356 | 4760.728 |  | 4760.728 | 4343 | 0 | 0 | 4343
2021-08-30 | 2021-09-05 | 4005416 | 4005.416 | 4033.78 | 4005.416 |  | 4005.416 | 3654 | 0 | 0 | 3654
2021-09-06 | 2021-09-12 | 4870911 | 4870.911 | 4906.572 | 4870.911 |  | 4870.911 | 4444 | 0 | 0 | 4444
2021-09-13 | 2021-09-19 | 4873568 | 4873.568 | 4908.934 | 4873.568 |  | 4873.568 | 4446 | 0 | 0 | 4446
2021-09-20 | 2021-09-26 | 3718389 | 3718.389 | 3742.116 | 3718.389 |  | 3718.389 | 3392 | 0 | 0 | 3392
2021-09-27 | 2021-10-03 | 3004973 | 3004.973 | 3024.736 | 3004.973 |  | 3004.973 | 2741 | 0 | 0 | 2741
2021-10-04 | 2021-10-10 | 2588182 | 2588.182 | 2607.274 | 2588.182 |  | 2588.182 | 2361 | 0 | 0 | 2361
2021-10-11 | 2021-10-17 | 2748762 | 2748.762 | 2206.212 | 2206.212 |  | 2206.212 | 2012 | 0 | 0 | 2012
2021-10-18 | 2021-10-24 | 1856787 | 1856.787 | 1873.768 | 1856.787 |  | 1856.787 | 1694 | 0 | 0 | 1694
2021-10-25 | 2021-10-31 | 1635576 | 1635.576 | 1654.476 | 1635.576 |  | 1635.576 | 1492 | 0 | 0 | 1492
2021-11-01 | 2021-11-07 | 1376637 | 1376.637 | 1395.386 | 1376.637 |  | 1376.637 | 1256 | 0 | 0 | 1256
2021-11-08 | 2021-11-14 | 1205759 | 1205.759 | 1224.064 | 1205.759 |  | 1205.759 | 1100 | 0 | 0 | 1100
2021-11-15 | 2021-11-21 | 1139421 | 1139.421 | 1157.846 | 1139.421 |  | 1139.421 | 1039 | 0 | 0 | 1039
2021-11-22 | 2021-11-28 | 975373 | 975.373 | 993.298 | 975.373 |  | 975.373 | 889 | 0 | 0 | 889
2021-11-29 | 2021-12-05 | 892718 | 892.718 | 909.982 | 892.718 |  | 892.718 | 814 | 0 | 0 | 814
2021-12-06 | 2021-12-12 | 35359 | 35.359 | 44.424 | 35.359 |  | 35.359 | 32 | 0 | 0 | 32
2021-12-13 | 2021-12-19 | 332171 | 332.171 | 349.916 | 332.171 |  | 332.171 | 303 | 0 | 0 | 303
2021-12-20 | 2021-12-26 | 768468 | 768.468 | 783.18 | 768.468 |  | 768.468 | 701 | 0 | 0 | 701
2021-12-27 | 2022-01-02 | 733435 | 733.435 | 751.872 | 733.435 |  | 733.435 | 669 | 0 | 0 | 669
2022-01-03 | 2022-01-09 | 852718 | 852.718 | 872.728 | 852.718 |  | 852.718 | 778 | 0 | 0 | 778 | 60874
2022-01-10 | 2022-01-16 | 799471 | 799.471 | 816.57 | 799.471 |  | 799.471 | 729 | 0 | 0 | 729
2022-01-17 | 2022-01-23 | 831239 | 831.239 | 851.966 | 831.239 |  | 831.239 | 758 | 0 | 0 | 758
2022-01-24 | 2022-01-30 | 813536 | 813.536 | 833.244 | 813.536 |  | 813.536 | 742 | 0 | 0 | 742
2022-01-31 | 2022-02-06 | 825806 | 825.806 | 843.822 | 825.806 |  | 825.806 | 753 | 0 | 0 | 753
2022-02-07 | 2022-02-13 | 853772 | 853.772 | 871.858 | 853.772 |  | 853.772 | 778 | 0 | 0 | 778
2022-02-14 | 2022-02-20 | 932751 | 932.751 | 950.972 | 932.751 |  | 932.751 | 851 | 0 | 0 | 851
2022-02-21 | 2022-02-27 | 976036 | 976.036 | 993.742 | 976.036 |  | 976.036 | 890 | 0 | 0 | 890
2022-02-28 | 2022-03-06 | 1008926 | 1008.926 | 1026.872 | 1008.926 |  | 1008.926 | 920 | 0 | 0 | 920
2022-03-07 | 2022-03-13 | 1463539 | 1463.539 | 1480.812 | 1463.539 |  | 1463.539 | 1335 | 0 | 0 | 1335
2022-03-14 | 2022-03-20 | 2966621 | 2966.621 | 2991.04 | 2966.621 |  | 2966.621 | 2706 | 0 | 0 | 2706
2022-03-21 | 2022-03-27 | 2317131 | 2317.131 | 2335.882 | 2317.131 |  | 2317.131 | 2114 | 0 | 0 | 2114
2022-03-28 | 2022-03-31 | 1412834 | 1412.834 | 1424.48 | 1412.834 |  | 1412.834 | 1289 | 0 | 0 | 1289
2022-04-01 | 2022-04-03 | 1080370 | 1080.37 | 1089.954 | 1080.37 |  | 1080.37 | 985 | 0 | 0 | 985
2022-04-04 | 2022-04-10 | 2488506 | 2488.506 | 2508.598 | 2488.506 |  | 2488.506 | 2270 | 0 | 0 | 2270
2022-04-11 | 2022-04-17 | 2336966 | 2336.966 | 2355.876 | 2336.966 |  | 2336.966 | 2132 | 0 | 0 | 2132
2022-04-18 | 2022-04-24 | 2025206 | 2025.206 | 2041.758 | 2025.206 |  | 2025.206 | 1847 | 0 | 0 | 1847
2022-04-25 | 2022-05-01 | 1989660 | 1989.66 | 2006.28 | 1989.66 |  | 1989.66 | 1815 | 0 | 0 | 1815
2022-05-02 | 2022-05-08 | 2036430 | 2036.43 | 2055.05 | 2036.43 |  | 2036.43 | 1858 | 0 | 0 | 1858
2022-05-09 | 2022-05-15 | 2487425 | 2487.425 | 2511.012 | 2487.425 |  | 2487.425 | 2269 | 0 | 0 | 2269
2022-05-16 | 2022-05-22 | 2314300 | 2314.3 | 2337.112 | 2314.3 |  | 2314.3 | 2111 | 0 | 0 | 2111
2022-05-23 | 2022-05-29 | 2082500 | 2082.5 | 2104.202 | 2082.5 |  | 2082.5 | 1900 | 0 | 0 | 1900
2022-05-30 | 2022-06-05 | 2053099 | 2053.099 | 2075.5299 | 2053.099 |  | 2053.099 | 1873 | 0 | 0 | 1873
2022-06-06 | 2022-06-12 | 2224803 | 2224.803 | 2249.6021 | 2224.803 |  | 2224.803 | 2029 | 0 | 0 | 2029
2022-06-13 | 2022-06-19 | 2776783 | 2776.783 | 2804.766 | 2776.783 |  | 2776.783 | 2533 | 0 | 0 | 2533
2022-06-20 | 2022-06-26 | 3215072 | 3215.072 | 3244.194 | 3215.072 |  | 3215.072 | 2933 | 0 | 0 | 2933
2022-06-27 | 2022-07-03 | 4196163 | 4196.163 | 4235.382 | 4196.163 |  | 4196.163 | 3828 | 0 | 0 | 3828
2022-07-04 | 2022-07-10 | 4707972 | 4707.972 | 4757.802 | 4707.972 |  | 4707.972 | 4295 | 0 | 0 | 4295
2022-07-11 | 2022-07-17 | 5912614 | 5912.614 | 5978.256 | 5912.614 |  | 5912.614 | 5394 | 0 | 0 | 5394
2022-07-18 | 2022-07-24 | 6087084 | 6087.084 | 6152.844 | 6087.084 |  | 6087.084 | 5553 | 0 | 0 | 5553
2022-07-25 | 2022-07-31 | 7502342 | 7502.342 | 664.574 | 664.574 |  | 664.574 | 606 | 0 | 0 | 606
Total |  | 465368367 | 465368.367 | 462358.4694 | 457988.049 |  | 457980.363 | 417782 | 0 | 0 | 417782 | 417782
Note on I124: ThinkPad: error factor applied due to delay in calibration for period 29/01/2021 to 03/03/2021

## PE
CapPJ | W | 36000000
CapBL | W | 0
APJ | m2 | 17000
ABL | m2 | 0
Power Density (PD) |  | W/ m2 | 2117.6471
Since the PD value is greater than 10 W/ m2 the project emissions are zero.
PE | tCO2 | 0

## JMR
Billing Cycle |  | Joint Meter Reading |  | Reading As per Energy Meter at Plant Site owned by Client (in MWh) | Minimum of Plant Records and JMR (MRI) (in MWh) | Minimum of Plant Records and JMR (MRI) (in MWh) with error factor
From | To | As per JMR - Meter Reading Instrument (MRI) owned by State Electricity Board (in kWh) | As per JMR - Meter Reading Instrument (MRI) owned by State Electricity Board (in MWh)
2019-07-01 | 2019-07-07 | 5253000 | 5253 | 5288.1813 | 5253 | 5253
2019-07-08 | 2019-07-14 | 6294000 | 6294 | 6346.2853 | 6294 | 6294
2019-07-15 | 2019-07-21 | 6538000 | 6538 | 6588.3531 | 6538 | 6538
2019-07-22 | 2019-07-28 | 4720000 | 4720 | 4756.728 | 4720 | 4720
2019-07-29 | 2019-08-04 | 4809000 | 4809 | 4849.778 | 4809 | 4809
2019-08-05 | 2019-08-11 | 6415000 | 6415 | 6466.1785 | 6415 | 6415
2019-08-12 | 2019-08-18 | 5243000 | 5243 | 5290.4162 | 5243 | 5243
2019-08-19 | 2019-08-25 | 6403000 | 6403 | 6451.5794 | 6403 | 6403
2019-08-26 | 2019-09-01 | 6520000 | 6520 | 6571.7303 | 6520 | 6520
2019-09-02 | 2019-09-08 | 6275000 | 6275 | 6318.9415 | 6275 | 6275
2019-09-09 | 2019-09-15 | 4791000 | 4791 | 4834.0324 | 4791 | 4791
2019-09-16 | 2019-09-22 | 3730000 | 3730 | 3756.1069 | 3730 | 3730
2019-09-23 | 2019-09-29 | 2955000 | 2955 | 2976.1292 | 2955 | 2955
2019-09-30 | 2019-10-06 | 2539000 | 2539 | 2559.3547 | 2539 | 2539
2019-10-07 | 2019-10-13 | 2318000 | 2318 | 2334.4888 | 2318 | 2318
2019-10-14 | 2019-10-20 | 2066000 | 2066 | 2083.7991 | 2066 | 2066
2019-10-21 | 2019-10-27 | 1721000 | 1721 | 1738.7889 | 1721 | 1721
2019-10-28 | 2019-11-03 | 1496000 | 1496 | 1511.7319 | 1496 | 1496
2019-11-04 | 2019-11-10 | 1440000 | 1440 | 1449.7347 | 1440 | 1440
2019-11-11 | 2019-11-17 | 1219000 | 1219 | 1234.1022 | 1219 | 1219
2019-11-18 | 2019-11-24 | 1137000 | 1137 | 1147.2484 | 1137 | 1137
2019-11-25 | 2019-12-01 | 1061000 | 1061 | 1071.5501 | 1061 | 1061
2019-12-02 | 2019-12-08 | 505000 | 505 | 514.9361 | 505 | 505
2019-12-09 | 2019-12-15 | 260000 | 260 | 267.3525 | 260 | 260
2019-12-16 | 2019-12-22 | 933000 | 933 | 943.7963 | 933 | 933
2019-12-23 | 2019-12-29 | 982000 | 982 | 994.738 | 982 | 982
2019-12-30 | 2020-01-05 | 778000 | 778 | 790.4687 | 778 | 778
2020-01-06 | 2020-01-12 | 881000 | 881 | 892.0172 | 881 | 881
2020-01-13 | 2020-01-19 | 1056000 | 1056 | 1067.0834 | 1056 | 1056
2020-01-20 | 2020-01-26 | 1012000 | 1012 | 1023.4429 | 1012 | 1012
2020-01-27 | 2020-02-02 | 1046000 | 1046 | 1083.3905 | 1046 | 1046
2020-02-03 | 2020-02-09 | 1035000 | 1035 | 1049.1719 | 1035 | 1035
2020-02-10 | 2020-02-16 | 1313000 | 1313 | 1325.0361 | 1313 | 1313
2020-02-17 | 2020-02-23 | 1444000 | 1444 | 1454.669 | 1444 | 1444
2020-02-24 | 2020-03-01 | 1290000 | 1290 | 1304.4675 | 1290 | 1290
2020-03-02 | 2020-03-08 | 1236000 | 1236 | 1250.3618 | 1236 | 1236
2020-03-09 | 2020-03-15 | 1308000 | 1308 | 1320.9231 | 1308 | 1308
2020-03-16 | 2020-03-22 | 1989000 | 1989 | 2004.3449 | 1989 | 1989
2020-03-23 | 2020-03-29 | 2503000 | 2503 | 2520.5822 | 2503 | 2503
2020-03-30 | 2020-04-05 | 2976000 | 2976 | 2989.7007 | 2976 | 2976
2020-04-06 | 2020-04-12 | 2978000 | 2978 | 3002.8166 | 2978 | 2978
2020-04-13 | 2020-04-19 | 4681000 | 4681 | 4708.2239 | 4681 | 4681
2020-04-20 | 2020-04-26 | 4013000 | 4013 | 4026.9764 | 4013 | 4013
2020-04-27 | 2020-05-03 | 4707000 | 4707 | 4743.3793 | 4707 | 4707
2020-05-04 | 2020-05-10 | 4973000 | 4973 | 5009.5939 | 4973 | 4973
2020-05-11 | 2020-05-17 | 4937000 | 4937 | 4968.2447 | 4937 | 4937
2020-05-18 | 2020-05-24 | 4499000 | 4499 | 4525.084 | 4499 | 4499
2020-05-25 | 2020-05-31 | 4616000 | 4616 | 4648.6567 | 4616 | 4616
2020-06-01 | 2020-06-07 | 4777000 | 4777 | 4819.5326 | 4777 | 4777
2020-06-08 | 2020-06-14 | 5466000 | 5466 | 5514.1584 | 5466 | 5466
2020-06-15 | 2020-06-21 | 5616000 | 5616 | 5664.4046 | 5616 | 5616
2020-06-22 | 2020-06-28 | 5996000 | 5996 | 6049.9023 | 5996 | 5996
2020-06-29 | 2020-07-05 | 6620000 | 6620 | 6680.9521 | 6620 | 6620
2020-07-06 | 2020-07-12 | 6794000 | 6794 | 6857.7958 | 6794 | 6794
2020-07-13 | 2020-07-19 | 6513000 | 6513 | 6571.872 | 6513 | 6513
2020-07-20 | 2020-07-26 | 6372000 | 6372 | 6433.2284 | 6372 | 6372
2020-07-27 | 2020-08-02 | 5460000 | 5460 | 5507.8305 | 5460 | 5460
2020-08-03 | 2020-08-09 | 5690000 | 5690 | 5739.6509 | 5690 | 5690
2020-08-10 | 2020-08-16 | 6431000 | 6431 | 6489.4832 | 6431 | 6431
2020-08-17 | 2020-08-23 | 6053000 | 6053 | 6106.9902 | 6053 | 6053
2020-08-24 | 2020-08-30 | 6698000 | 6698 | 6760.8092 | 6698 | 6698
2020-08-31 | 2020-09-06 | 6435000 | 6435 | 6494.1051 | 6435 | 6435
2020-09-07 | 2020-09-13 | 4825000 | 4825 | 4862.7315 | 4825 | 4825
2020-09-14 | 2020-09-20 | 3662000 | 3662 | 3687.3704 | 3662 | 3662
2020-09-21 | 2020-09-27 | 2680000 | 2680 | 2701.3313 | 2680 | 2680
2020-09-28 | 2020-10-04 | 2372000 | 2372 | 2391.2767 | 2372 | 2372
2020-10-05 | 2020-10-11 | 2048000 | 2048 | 2064.0898 | 2048 | 2048
2020-10-12 | 2020-10-18 | 1793000 | 1793 | 1809.4498 | 1793 | 1793
2020-10-19 | 2020-10-25 | 1476000 | 1476 | 1491.3336 | 1476 | 1476
2020-10-26 | 2020-11-01 | 1251000 | 1251 | 1268.4429 | 1251 | 1251
2020-11-02 | 2020-11-08 | 1069000 | 1069 | 1084.6481 | 1069 | 1069
2020-11-09 | 2020-11-15 | 922000 | 922 | 936.577 | 922 | 922
2020-11-16 | 2020-11-22 | 813000 | 813 | 830.3668 | 813 | 813
2020-11-23 | 2020-11-29 | 829000 | 829 | 850.872 | 829 | 829
2020-11-30 | 2020-12-06 | 840000 | 840 | 859.0787 | 840 | 840
2020-12-07 | 2020-12-13 | 859000 | 859 | 879.4807 | 859 | 859
2020-12-14 | 2020-12-20 | 264000 | 264 | 280.8312 | 264 | 264
2020-12-21 | 2020-12-27 | 133000 | 133 | 149.0405 | 133 | 133
2020-12-28 | 2021-01-03 | 689000 | 689 | 708.7129 | 689 | 689
2021-01-04 | 2021-01-10 | 690000 | 690 | 711.3318 | 690 | 690
2021-01-11 | 2021-01-17 | 667000 | 667 | 686.1525 | 667 | 667
2021-01-18 | 2021-01-24 | 669000 | 669 | 691.1547 | 669 | 669
2021-01-25 | 2021-01-31 | 661000 | 661 | 681.7097 | 661 | 659.678
2021-02-01 | 2021-02-07 | 614000 | 614 | 633.0004 | 614 | 612.772
2021-02-08 | 2021-02-14 | 654000 | 654 | 667.9042 | 654 | 652.692
2021-02-15 | 2021-02-21 | 634000 | 634 | 651.6438 | 634 | 632.732
2021-02-22 | 2021-02-28 | 650000 | 650 | 668.977 | 650 | 648.7
2021-03-01 | 2021-03-07 | 630000 | 630 | 646.6804 | 630 | 628.74
2021-03-08 | 2021-03-14 | 603000 | 603 | 617.055 | 603 | 603
2021-03-15 | 2021-03-21 | 616000 | 616 | 634.4525 | 616 | 616
2021-03-22 | 2021-03-28 | 832000 | 832 | 854.1786 | 832 | 832
2021-03-29 | 2021-04-04 | 1065000 | 1065 | 1087.5807 | 1065 | 1065
2021-04-05 | 2021-04-11 | 1149000 | 1149 | 1171.2908 | 1149 | 1149
2021-04-12 | 2021-04-18 | 1144000 | 1144 | 1165.4815 | 1144 | 1144
2021-04-19 | 2021-04-25 | 1874000 | 1874 | 1900.8418 | 1874 | 1874
2021-04-26 | 2021-05-02 | 2596000 | 2596 | 2625.9712 | 2596 | 2596
2021-05-03 | 2021-05-09 | 2668000 | 2668 | 2700.5143 | 2668 | 2668
2021-05-10 | 2021-05-16 | 2715000 | 2715 | 2742.1173 | 2715 | 2715
2021-05-17 | 2021-05-23 | 2854000 | 2854 | 2880.0542 | 2854 | 2854
2021-05-24 | 2021-05-30 | 3581000 | 3581 | 3611.5033 | 3581 | 3581
2021-05-31 | 2021-06-06 | 3882000 | 3882 | 3910.3087 | 3882 | 3882
2021-06-07 | 2021-06-13 | 5513000 | 5513 | 5562.7596 | 5513 | 5513
2021-06-14 | 2021-06-20 | 5555000 | 5555 | 5600.8053 | 5555 | 5555
2021-06-21 | 2021-06-27 | 5003097 | 5003.097 | 5043.2038 | 5003.097 | 5003.097
2021-06-28 | 2021-07-04 | 5099609 | 5099.609 | 5138.562 | 5099.609 | 5099.609
2021-07-05 | 2021-07-11 | 5885777 | 5885.777 | 5930.988 | 5885.777 | 5885.777
2021-07-12 | 2021-07-18 | 6235891 | 6235.891 | 6286.482 | 6235.891 | 6235.891
2021-07-19 | 2021-07-25 | 6825123 | 6825.123 | 6877.524 | 6825.123 | 6825.123
2021-07-26 | 2021-08-01 | 6139448 | 6139.448 | 6184.654 | 6139.448 | 6139.448
2021-08-02 | 2021-08-08 | 6610273 | 6610.273 | 6660.776 | 6610.273 | 6610.273
2021-08-09 | 2021-08-15 | 6544856 | 6544.856 | 6595.372 | 6544.856 | 6544.856
2021-08-16 | 2021-08-22 | 5073985 | 5073.985 | 5109.42 | 5073.985 | 5073.985
2021-08-23 | 2021-08-29 | 4760728 | 4760.728 | 4792.356 | 4760.728 | 4760.728
2021-08-30 | 2021-09-05 | 4005416 | 4005.416 | 4033.78 | 4005.416 | 4005.416
2021-09-06 | 2021-09-12 | 4870911 | 4870.911 | 4906.572 | 4870.911 | 4870.911
2021-09-13 | 2021-09-19 | 4873568 | 4873.568 | 4908.934 | 4873.568 | 4873.568
2021-09-20 | 2021-09-26 | 3718389 | 3718.389 | 3742.116 | 3718.389 | 3718.389
2021-09-27 | 2021-10-03 | 3004973 | 3004.973 | 3024.736 | 3004.973 | 3004.973
2021-10-04 | 2021-10-10 | 2588182 | 2588.182 | 2607.274 | 2588.182 | 2588.182
2021-10-11 | 2021-10-17 | 2748762 | 2748.762 | 2206.212 | 2206.212 | 2206.212
2021-10-18 | 2021-10-24 | 1856787 | 1856.787 | 1873.768 | 1856.787 | 1856.787
2021-10-25 | 2021-10-31 | 1635576 | 1635.576 | 1654.476 | 1635.576 | 1635.576
2021-11-01 | 2021-11-07 | 1376637 | 1376.637 | 1395.386 | 1376.637 | 1376.637
2021-11-08 | 2021-11-14 | 1205759 | 1205.759 | 1224.064 | 1205.759 | 1205.759
2021-11-15 | 2021-11-21 | 1139421 | 1139.421 | 1157.846 | 1139.421 | 1139.421
2021-11-22 | 2021-11-28 | 975373 | 975.373 | 993.298 | 975.373 | 975.373
2021-11-29 | 2021-12-05 | 892718 | 892.718 | 909.982 | 892.718 | 892.718
2021-12-06 | 2021-12-12 | 35359 | 35.359 | 44.424 | 35.359 | 35.359
2021-12-13 | 2021-12-19 | 332171 | 332.171 | 349.916 | 332.171 | 332.171
2021-12-20 | 2021-12-26 | 768468 | 768.468 | 783.18 | 768.468 | 768.468
2021-12-27 | 2022-01-02 | 733435 | 733.435 | 751.872 | 733.435 | 733.435
2022-01-03 | 2022-01-09 | 852718 | 852.718 | 872.728 | 852.718 | 852.718
2022-01-10 | 2022-01-16 | 799471 | 799.471 | 816.57 | 799.471 | 799.471
2022-01-17 | 2022-01-23 | 831239 | 831.239 | 851.966 | 831.239 | 831.239
2022-01-24 | 2022-01-30 | 813536 | 813.536 | 833.244 | 813.536 | 813.536
2022-01-31 | 2022-02-06 | 825806 | 825.806 | 843.822 | 825.806 | 825.806
2022-02-07 | 2022-02-13 | 853772 | 853.772 | 871.858 | 853.772 | 853.772
2022-02-14 | 2022-02-20 | 932751 | 932.751 | 950.972 | 932.751 | 932.751
2022-02-21 | 2022-02-27 | 976036 | 976.036 | 993.742 | 976.036 | 976.036
2022-02-28 | 2022-03-06 | 1008926 | 1008.926 | 1026.872 | 1008.926 | 1008.926
2022-03-07 | 2022-03-13 | 1463539 | 1463.539 | 1480.812 | 1463.539 | 1463.539
2022-03-14 | 2022-03-20 | 2966621 | 2966.621 | 2991.04 | 2966.621 | 2966.621
2022-03-21 | 2022-03-27 | 2317131 | 2317.131 | 2335.882 | 2317.131 | 2317.131
2022-03-28 | 2022-03-31 | 1412834 | 1412.834 | 1424.48 | 1412.834 | 1412.834
2022-04-01 | 2022-04-03 | 1080370 | 1080.37 | 1089.954 | 1080.37 | 1080.37
2022-04-04 | 2022-04-10 | 2488506 | 2488.506 | 2508.598 | 2488.506 | 2488.506
2022-04-11 | 2022-04-17 | 2336966 | 2336.966 | 2355.876 | 2336.966 | 2336.966
2022-04-18 | 2022-04-24 | 2025206 | 2025.206 | 2041.758 | 2025.206 | 2025.206
2022-04-25 | 2022-05-01 | 1989660 | 1989.66 | 2006.28 | 1989.66 | 1989.66
2022-05-02 | 2022-05-08 | 2036430 | 2036.43 | 2055.05 | 2036.43 | 2036.43
2022-05-09 | 2022-05-15 | 2487425 | 2487.425 | 2511.012 | 2487.425 | 2487.425
2022-05-16 | 2022-05-22 | 2314300 | 2314.3 | 2337.112 | 2314.3 | 2314.3
2022-05-23 | 2022-05-29 | 2082500 | 2082.5 | 2104.202 | 2082.5 | 2082.5
2022-05-30 | 2022-06-05 | 2053099 | 2053.099 | 2075.5299 | 2053.099 | 2053.099
2022-06-06 | 2022-06-12 | 2224803 | 2224.803 | 2249.6021 | 2224.803 | 2224.803
2022-06-13 | 2022-06-19 | 2776783 | 2776.783 | 2804.766 | 2776.783 | 2776.783
2022-06-20 | 2022-06-26 | 3215072 | 3215.072 | 3244.194 | 3215.072 | 3215.072
2022-06-27 | 2022-07-03 | 4196163 | 4196.163 | 4235.382 | 4196.163 | 4196.163
2022-07-04 | 2022-07-10 | 4707972 | 4707.972 | 4757.802 | 4707.972 | 4707.972
2022-07-11 | 2022-07-17 | 5912614 | 5912.614 | 5978.256 | 5912.614 | 5912.614
2022-07-18 | 2022-07-24 | 6087084 | 6087.084 | 6152.844 | 6087.084 | 6087.084
2022-07-25 | 2022-07-31 | 7502342 | 7502.342 | 664.574 | 664.574 | 664.574
Total |  | 465368367 | 465368.367 | 462358.4694 | 457988.049 | 457980.363
Note on H86: ThinkPad: error factor applied due to delay in calibration for period 29/01/2021 to 03/03/2021

## Daily data
Reading As per Energy Meter at Plant Site owned by Client (in MWh)
From | To | Total TG generation in MWh- (EGgross) | Total Auxilary in MWh (Egaux) | Net | Note -This formula sums all values in column F that fall within the date range specified in B4 to C4. It’s commonly used in monitoring reports to calculate totals for a specific reporting period like sum of 7 days as per JMR 01/07/2019 to 07/07/2019 (F174: F180) - SUMIFS(...): A function that sums values based on multiple criteria. - F174:$F$1330: The range of values to sum—likely representing energy generation, emissions, or another metric. - B174:$B$1330: The criteria range, typically a column of dates corresponding to each value in column F. - ">=" & B4: Includes only rows where the date in column B is on or after the date in cell B4. - "<=" & C4: Includes only rows where the date in column B is on or before the date in cell C4.
2019-07-01 | 2019-07-07 | 5298.82 | 10.6387 | 5288.1813
2019-07-08 | 2019-07-14 | 6356.65 | 10.3647 | 6346.2853
2019-07-15 | 2019-07-21 | 6599.05 | 10.6969 | 6588.3531
2019-07-22 | 2019-07-28 | 4764.4 | 7.672 | 4756.728
2019-07-29 | 2019-08-04 | 4859.06 | 9.282 | 4849.778
2019-08-05 | 2019-08-11 | 6476.98 | 10.8015 | 6466.1785
2019-08-12 | 2019-08-18 | 5300.21 | 9.7938 | 5290.4162
2019-08-19 | 2019-08-25 | 6463.36 | 11.7806 | 6451.5794
2019-08-26 | 2019-09-01 | 6583.18 | 11.4497 | 6571.7303
2019-09-02 | 2019-09-08 | 6329.98 | 11.0385 | 6318.9415
2019-09-09 | 2019-09-15 | 4844.29 | 10.2576 | 4834.0324
2019-09-16 | 2019-09-22 | 3765.04 | 8.9331 | 3756.1069
2019-09-23 | 2019-09-29 | 2984.63 | 8.5008 | 2976.1292
2019-09-30 | 2019-10-06 | 2567.99 | 8.6353 | 2559.3547
2019-10-07 | 2019-10-13 | 2343.52 | 9.0312 | 2334.4888
2019-10-14 | 2019-10-20 | 2092.59 | 8.7909 | 2083.7991
2019-10-21 | 2019-10-27 | 1746.92 | 8.1311 | 1738.7889 | 5298.82
2019-10-28 | 2019-11-03 | 1520.27 | 8.5382 | 1511.7319
2019-11-04 | 2019-11-10 | 1458.69 | 8.9553 | 1449.7347
2019-11-11 | 2019-11-17 | 1242.52 | 8.4178 | 1234.1022
2019-11-18 | 2019-11-24 | 1155.86 | 8.6116 | 1147.2484
2019-11-25 | 2019-12-01 | 1080.49 | 8.9399 | 1071.5501
2019-12-02 | 2019-12-08 | 522.6 | 7.6639 | 514.9361
2019-12-09 | 2019-12-15 | 275.33 | 7.9775 | 267.3525
2019-12-16 | 2019-12-22 | 952.85 | 9.0537 | 943.7963
2019-12-23 | 2019-12-29 | 1003.77 | 9.032 | 994.738
2019-12-30 | 2020-01-05 | 799.29 | 8.8213 | 790.4687
Total |  | 89388.34 | 251.8093
2020-01-06 | 2020-01-12 | 901.55 | 9.5328 | 892.0172
2020-01-13 | 2020-01-19 | 1076.8 | 9.7166 | 1067.0834
2020-01-20 | 2020-01-26 | 1032.93 | 9.4871 | 1023.4429
2020-01-27 | 2020-02-02 | 1093.33 | 9.9395 | 1083.3905
2020-02-03 | 2020-02-09 | 1058.49 | 9.3181 | 1049.1719
2020-02-10 | 2020-02-16 | 1334.63 | 9.5939 | 1325.0361
2020-02-17 | 2020-02-23 | 1463.15 | 8.481 | 1454.669
2020-02-24 | 2020-03-01 | 1312.44 | 7.9725 | 1304.4675
2020-03-02 | 2020-03-08 | 1258.08 | 7.7182 | 1250.3618
2020-03-09 | 2020-03-15 | 1328.37 | 7.4469 | 1320.9231
2020-03-16 | 2020-03-22 | 2012.03 | 7.6851 | 2004.3449
2020-03-23 | 2020-03-29 | 2528.28 | 7.6978 | 2520.5822
2020-03-30 | 2020-04-05 | 2997.91 | 8.2093 | 2989.7007
2020-04-06 | 2020-04-12 | 3011.25 | 8.4334 | 3002.8166
2020-04-13 | 2020-04-19 | 4717.23 | 9.0061 | 4708.2239
2020-04-20 | 2020-04-26 | 4035.52 | 8.5436 | 4026.9764
2020-04-27 | 2020-05-03 | 4752.11 | 8.7307 | 4743.3793
2020-05-04 | 2020-05-10 | 5018.67 | 9.0761 | 5009.5939
2020-05-11 | 2020-05-17 | 4977.41 | 9.1653 | 4968.2447
2020-05-18 | 2020-05-24 | 4533.86 | 8.776 | 4525.084
2020-05-25 | 2020-05-31 | 4657.619 | 8.9624 | 4648.6567
2020-06-01 | 2020-06-07 | 4829.47 | 9.9374 | 4819.5326
2020-06-08 | 2020-06-14 | 5524.16 | 10.0016 | 5514.1584
2020-06-15 | 2020-06-21 | 5673.58 | 9.1754 | 5664.4046
2020-06-22 | 2020-06-28 | 6059.01 | 9.1077 | 6049.9023
2020-06-29 | 2020-07-05 | 6690.46 | 9.5079 | 6680.9521
2020-07-06 | 2020-07-12 | 6868.21 | 10.4142 | 6857.7958
2020-07-13 | 2020-07-19 | 6581.66 | 9.788 | 6571.872
2020-07-20 | 2020-07-26 | 6443.91 | 10.6816 | 6433.2284
2020-07-27 | 2020-08-02 | 5518.36 | 10.5295 | 5507.8305
2020-08-03 | 2020-08-09 | 5750.68 | 11.0291 | 5739.6509
2020-08-10 | 2020-08-16 | 6499.9 | 10.4168 | 6489.4832
2020-08-17 | 2020-08-23 | 6117.88 | 10.8898 | 6106.9902
2020-08-24 | 2020-08-30 | 6773.25 | 12.4408 | 6760.8092
2020-08-31 | 2020-09-06 | 6505.17 | 11.0649 | 6494.1051
2020-09-07 | 2020-09-13 | 4871.93 | 9.1985 | 4862.7315
2020-09-14 | 2020-09-20 | 3695.49 | 8.1196 | 3687.3704
2020-09-21 | 2020-09-27 | 2709.29 | 7.9587 | 2701.3313
2020-09-28 | 2020-10-04 | 2399.06 | 7.7833 | 2391.2767
2020-10-05 | 2020-10-11 | 2072.15 | 8.0602 | 2064.0898
2020-10-12 | 2020-10-18 | 1817.82 | 8.3702 | 1809.4498
2020-10-19 | 2020-10-25 | 1499.73 | 8.3964 | 1491.3336
2020-10-26 | 2020-11-01 | 1277.06 | 8.6171 | 1268.4429
2020-11-02 | 2020-11-08 | 1093.53 | 8.8819 | 1084.6481
2020-11-09 | 2020-11-15 | 944.98 | 8.403 | 936.577
2020-11-16 | 2020-11-22 | 838.64 | 8.2732 | 830.3668
2020-11-23 | 2020-11-29 | 859.84 | 8.968 | 850.872
2020-11-30 | 2020-12-06 | 866.9 | 7.8213 | 859.0787
2020-12-07 | 2020-12-13 | 887.76 | 8.2793 | 879.4807
2020-12-14 | 2020-12-20 | 288.26 | 7.4288 | 280.8312
2020-12-21 | 2020-12-27 | 158.99 | 9.9495 | 149.0405
2020-12-28 | 2021-01-03 | 716 | 7.2871 | 708.7129
Total |  | 167934.789 | 470.2733
2021-01-04 | 2021-01-10 | 718.37 | 7.0382 | 711.3318
2021-01-11 | 2021-01-17 | 693.07 | 6.9175 | 686.1525
2021-01-18 | 2021-01-24 | 698.49 | 7.3353 | 691.1547
2021-01-25 | 2021-01-31 | 688.64 | 6.9303 | 681.7097
2021-02-01 | 2021-02-07 | 639.49 | 6.4897 | 633.0004
2021-02-08 | 2021-02-14 | 674.65 | 6.7457 | 667.9042
2021-02-15 | 2021-02-21 | 657.8 | 6.1562 | 651.6438
2021-02-22 | 2021-02-28 | 674.98 | 6.003 | 668.977
2021-03-01 | 2021-03-07 | 652.25 | 5.5696 | 646.6804
2021-03-08 | 2021-03-14 | 622.85 | 5.795 | 617.055
2021-03-15 | 2021-03-21 | 640.4 | 5.9475 | 634.4525
2021-03-22 | 2021-03-28 | 861.12 | 6.9414 | 854.1786
2021-03-29 | 2021-04-04 | 1094.78 | 7.1993 | 1087.5807
2021-04-05 | 2021-04-11 | 1178.31 | 7.0192 | 1171.2908
2021-04-12 | 2021-04-18 | 1172.3 | 6.8185 | 1165.4815
2021-04-19 | 2021-04-25 | 1908.23 | 7.3882 | 1900.8418
2021-04-26 | 2021-05-02 | 2633.86 | 7.8889 | 2625.9712
2021-05-03 | 2021-05-09 | 2709.3 | 8.7857 | 2700.5143
2021-05-10 | 2021-05-16 | 2750.49 | 8.3727 | 2742.1173
2021-05-17 | 2021-05-23 | 2888.24 | 8.1858 | 2880.0542
2021-05-24 | 2021-05-30 | 3620.56 | 9.0568 | 3611.5033
2021-05-31 | 2021-06-06 | 3919.52 | 9.2113 | 3910.3087
2021-06-07 | 2021-06-13 | 5575.64 | 12.8804 | 5562.7596
2021-06-14 | 2021-06-20 | 5612.08 | 11.2747 | 5600.8053
2021-06-21 | 2021-06-27 | 5053.54 | 10.3362 | 5043.2038
2021-06-28 | 2021-07-04 | 5149.03 | 10.468 | 5138.562
2021-07-05 | 2021-07-11 | 5943.62 | 12.632 | 5930.988
2021-07-12 | 2021-07-18 | 6300.89 | 14.408 | 6286.482
2021-07-19 | 2021-07-25 | 6891.2 | 13.676 | 6877.524
2021-07-26 | 2021-08-01 | 6198.67 | 14.016 | 6184.654
2021-08-02 | 2021-08-08 | 6677.74 | 16.964 | 6660.776
2021-08-09 | 2021-08-15 | 6611 | 15.628 | 6595.372
2021-08-16 | 2021-08-22 | 5123.8 | 14.38 | 5109.42
2021-08-23 | 2021-08-29 | 4806.52 | 14.164 | 4792.356
2021-08-30 | 2021-09-05 | 4045.66 | 11.88 | 4033.78
2021-09-06 | 2021-09-12 | 4922.28 | 15.708 | 4906.572
2021-09-13 | 2021-09-19 | 4922.83 | 13.896 | 4908.934
2021-09-20 | 2021-09-26 | 3755.3 | 13.184 | 3742.116
2021-09-27 | 2021-10-03 | 3035.6 | 10.864 | 3024.736
2021-10-04 | 2021-10-10 | 2618.67 | 11.396 | 2607.274
2021-10-11 | 2021-10-17 | 2217.16 | 10.948 | 2206.212
2021-10-18 | 2021-10-24 | 1884.98 | 11.212 | 1873.768
2021-10-25 | 2021-10-31 | 1666.12 | 11.644 | 1654.476
2021-11-01 | 2021-11-07 | 1407.69 | 12.304 | 1395.386
2021-11-08 | 2021-11-14 | 1234.08 | 10.016 | 1224.064
2021-11-15 | 2021-11-21 | 1167.83 | 9.984 | 1157.846
2021-11-22 | 2021-11-28 | 1003.03 | 9.732 | 993.298
2021-11-29 | 2021-12-05 | 919.49 | 9.508 | 909.982
2021-12-06 | 2021-12-12 | 52.14 | 7.716 | 44.424
2021-12-13 | 2021-12-19 | 358.88 | 8.964 | 349.916
2021-12-20 | 2021-12-26 | 792.26 | 9.08 | 783.18
2021-12-27 | 2022-01-02 | 760.8 | 8.928 | 751.872
Total |  | 138806.23 | 515.587
2022-01-03 | 2022-01-09 | 881.58 | 8.852 | 872.728
2022-01-10 | 2022-01-16 | 825.11 | 8.54 | 816.57
2022-01-17 | 2022-01-23 | 861.37 | 9.404 | 851.966
2022-01-24 | 2022-01-30 | 841.54 | 8.296 | 833.244
2022-01-31 | 2022-02-06 | 852.11 | 8.288 | 843.822
2022-02-07 | 2022-02-13 | 880.17 | 8.312 | 871.858
2022-02-14 | 2022-02-20 | 959.2 | 8.228 | 950.972
2022-02-21 | 2022-02-27 | 1001.69 | 7.948 | 993.742
2022-02-28 | 2022-03-06 | 1035.42 | 8.548 | 1026.872
2022-03-07 | 2022-03-13 | 1490.42 | 9.608 | 1480.812
2022-03-14 | 2022-03-20 | 3004.62 | 13.58 | 2991.04
2022-03-21 | 2022-03-27 | 2345.23 | 9.348 | 2335.882
2022-03-28 | 2022-03-31 | 1431.68 | 7.2 | 1424.48
2022-04-01 | 2022-04-03 | 1095.47 | 5.516 | 1089.954
2022-04-04 | 2022-04-10 | 2519.21 | 10.612 | 2508.598
2022-04-11 | 2022-04-17 | 2366.58 | 10.704 | 2355.876
2022-04-18 | 2022-04-24 | 2054.19 | 12.432 | 2041.758
2022-04-25 | 2022-05-01 | 2016.26 | 9.98 | 2006.28
2022-05-02 | 2022-05-08 | 2065.11 | 10.06 | 2055.05
2022-05-09 | 2022-05-15 | 2519.96 | 8.948 | 2511.012
2022-05-16 | 2022-05-22 | 2345.82 | 8.708 | 2337.112
2022-05-23 | 2022-05-29 | 2112.51 | 8.308 | 2104.202
2022-05-30 | 2022-06-05 | 2083.7139 | 8.184 | 2075.5299
2022-06-06 | 2022-06-12 | 2257.7661 | 8.164 | 2249.6021
2022-06-13 | 2022-06-19 | 2815.71 | 10.944 | 2804.766
2022-06-20 | 2022-06-26 | 3254.15 | 9.956 | 3244.194
2022-06-27 | 2022-07-03 | 4248.77 | 13.388 | 4235.382
2022-07-04 | 2022-07-10 | 4770.85 | 13.048 | 4757.802
2022-07-11 | 2022-07-17 | 5989.88 | 11.624 | 5978.256
2022-07-18 | 2022-07-24 | 6163.3 | 10.456 | 6152.844
2022-07-25 | 2022-07-31 | 666.39 | 1.816 | 664.574
Total |  | 67755.78 | 289
Total |  | 463885.139 | 1526.6696 | 462358.4694
Date | (EGgross)(kWh) |  |  | Total TG Generation (In MWh) | (EGaux)(kWh) |  | Total Auxiliary (In MWh) | Total Auxiliary (In MWh)-after correction factor
| Gross electricity generation by the project activity in year y, from plant logbook |  |  |  | Auxiliary consumption by the project activity in year y, from Plant logbook
| TG-1 | TG-2 | TG-3 |  | Aux-1 | Aux-2
2019-07-01 | 303840 | 306020 | 96940 | 706.8 | 676.83 | 796.17 | 1.473 | 1.473 | 303840
2019-07-02 | 308980 | 309540 | 93090 | 711.61 | 677.59 | 796.33 | 1.4739 | 1.4739 | 308980
2019-07-03 | 307190 | 308690 | 117220 | 733.1 | 675.25 | 792.84 | 1.4681 | 1.4681 | 307190
2019-07-04 | 278020 | 272570 | 244660 | 795.25 | 764.01 | 876.26 | 1.6403 | 1.6403 | 278020
2019-07-05 | 268860 | 258340 | 244850 | 772.05 | 790.82 | 905.34 | 1.6962 | 1.6962 | 268860
2019-07-06 | 300990 | 292550 | 195830 | 789.37 | 660.42 | 786.36 | 1.4468 | 1.4468 | 300990
2019-07-07 | 297120 | 264690 | 228830 | 790.64 | 661.12 | 779.32 | 1.4404 | 1.4404 | 297120
2019-07-08 | 295360 | 272610 | 260600 | 828.57 | 655.84 | 779.08 | 1.4349 | 1.4349 | 295360
2019-07-09 | 318150 | 302630 | 293230 | 914.01 | 695.83 | 817.03 | 1.5129 | 1.5129 | 318150
2019-07-10 | 322110 | 300390 | 309150 | 931.65 | 696.62 | 821.69 | 1.5183 | 1.5183 | 322110
2019-07-11 | 328160 | 303400 | 313470 | 945.03 | 684.25 | 808.11 | 1.4924 | 1.4924 | 328160
2019-07-12 | 293650 | 269980 | 282210 | 845.84 | 616.79 | 728.19 | 1.345 | 1.345 | 293650
2019-07-13 | 329680 | 303480 | 312920 | 946.08 | 718.13 | 844.37 | 1.5625 | 1.5625 | 329680
2019-07-14 | 329360 | 303040 | 313070 | 945.47 | 687.57 | 811.16 | 1.4987 | 1.4987 | 329360
2019-07-15 | 329670 | 303090 | 313410 | 946.17 | 697.98 | 822.85 | 1.5208 | 1.5208 | 329670
2019-07-16 | 319690 | 298340 | 306220 | 924.25 | 695.16 | 819.82 | 1.515 | 1.515 | 319690
2019-07-17 | 329280 | 307260 | 313130 | 949.67 | 694.12 | 820.15 | 1.5143 | 1.5143 | 329280
2019-07-18 | 317670 | 312230 | 308780 | 938.68 | 705.68 | 833.52 | 1.5392 | 1.5392 | 317670
2019-07-19 | 319670 | 313840 | 312720 | 946.23 | 706.25 | 830.68 | 1.5369 | 1.5369 | 319670
2019-07-20 | 320100 | 313210 | 313250 | 946.56 | 703.46 | 831.74 | 1.5352 | 1.5352 | 320100
2019-07-21 | 321450 | 312780 | 313260 | 947.49 | 703.82 | 831.69 | 1.5355 | 1.5355 | 321450
2019-07-22 | 130310 | 127810 | 129540 | 387.66 | 310.98 | 367.62 | 0.6786 | 0.6786 | 130310
2019-07-23 | 143950 | 120580 | 142790 | 407.32 | 328.76 | 450.85 | 0.77961 | 0.77961 | 143950
2019-07-24 | 212100 | 201380 | 207630 | 621.11 | 465.02 | 490.13 | 0.95515 | 0.95515 | 212100
2019-07-25 | 174210 | 165790 | 169500 | 509.5 | 378.71 | 447.38 | 0.82609 | 0.82609 | 174210
2019-07-26 | 319820 | 310090 | 313220 | 943.13 | 681.99 | 804.88 | 1.4869 | 1.4869 | 319820
2019-07-27 | 320350 | 313230 | 313870 | 947.45 | 689.53 | 813.64 | 1.5032 | 1.5032 | 320350
2019-07-28 | 320230 | 313280 | 314720 | 948.23 | 661.19 | 781.32 | 1.4425 | 1.4425 | 320230
2019-07-29 | 320780 | 313200 | 313890 | 947.87 | 662.01 | 781.84 | 1.4438 | 1.4438 | 320780
2019-07-30 | 320810 | 313290 | 314200 | 948.3 | 683.9 | 806.48 | 1.4904 | 1.4904 | 320810
2019-07-31 | 168440 | 163720 | 166010 | 498.17 | 517.45 | 623.94 | 1.1414 | 1.1414 | 168440
| 8970000 | 8571050 | 7872210 | 25413.26 | 19947.08 | 23500.78 | 43.4479 | 43.4479 | 8970000
2019-08-01 | 40010 | 39190 | 39310 | 118.51 | 335.03 | 429.02 | 0.76405 | 0.76405 | 40010
2019-08-02 | 179100 | 173980 | 175320 | 528.4 | 555.21 | 670.56 | 1.2258 | 1.2258 | 179100
2019-08-03 | 320430 | 313260 | 314420 | 948.11 | 779.08 | 913.44 | 1.6925 | 1.6925 | 320430
2019-08-04 | 294570 | 288240 | 286890 | 869.7 | 699.23 | 824.83 | 1.5241 | 1.5241 | 294570
2019-08-05 | 307810 | 300690 | 313590 | 922.09 | 674.49 | 853.98 | 1.5285 | 1.5285 | 307810
2019-08-06 | 320550 | 314310 | 312880 | 947.74 | 709.03 | 834.87 | 1.5439 | 1.5439 | 320550
2019-08-07 | 276900 | 270640 | 264920 | 812.46 | 661.85 | 783.09 | 1.4449 | 1.4449 | 276900
2019-08-08 | 320580 | 313220 | 315060 | 948.86 | 718.11 | 845.22 | 1.5633 | 1.5633 | 320580
2019-08-09 | 320290 | 313270 | 314350 | 947.91 | 723.7 | 849.93 | 1.5736 | 1.5736 | 320290
2019-08-10 | 320760 | 313800 | 313620 | 948.18 | 729.96 | 858.03 | 1.588 | 1.588 | 320760
2019-08-11 | 321300 | 314370 | 314070 | 949.74 | 716.43 | 842.79 | 1.5592 | 1.5592 | 321300
2019-08-12 | 322270 | 314210 | 314640 | 951.12 | 726.71 | 855.39 | 1.5821 | 1.5821 | 322270
2019-08-13 | 322370 | 314160 | 314590 | 951.12 | 727.47 | 854.65 | 1.5821 | 1.5821 | 322370
2019-08-14 | 322660 | 313430 | 314650 | 950.74 | 711.7 | 836.62 | 1.5483 | 1.5483 | 322660
2019-08-15 | 320810 | 310650 | 312060 | 943.52 | 714.29 | 840.31 | 1.5546 | 1.5546 | 320810
2019-08-16 | 322320 | 313790 | 314490 | 950.6 | 705.05 | 828.93 | 1.534 | 1.534 | 322320
2019-08-17 | 119140 | 115950 | 116190 | 351.28 | 457.3 | 567.26 | 1.0246 | 1.0246 | 119140
2019-08-18 | 69400 | 65220 | 67210 | 201.83 | 427.6 | 540.51 | 0.96811 | 0.96811 | 69400
2019-08-19 | 299100 | 293340 | 270320 | 862.76 | 869.03 | 1010.85 | 1.8799 | 1.8799 | 299100
2019-08-20 | 306630 | 298490 | 300280 | 905.4 | 800.79 | 935.55 | 1.7363 | 1.7363 | 306630
2019-08-21 | 324460 | 290830 | 303420 | 918.71 | 787.2 | 920.5 | 1.7077 | 1.7077 | 324460
2019-08-22 | 323410 | 313240 | 314140 | 950.79 | 791.09 | 922.39 | 1.7135 | 1.7135 | 323410
2019-08-23 | 319500 | 310100 | 311990 | 941.59 | 744.85 | 874.31 | 1.6192 | 1.6192 | 319500
2019-08-24 | 323010 | 312950 | 315250 | 951.21 | 716.38 | 841.65 | 1.558 | 1.558 | 323010
2019-08-25 | 317790 | 306800 | 308310 | 932.9 | 720.73 | 845.25 | 1.566 | 1.566 | 317790
2019-08-26 | 297770 | 287590 | 292130 | 877.49 | 749.74 | 876.54 | 1.6263 | 1.6263 | 297770
2019-08-27 | 323060 | 313420 | 315320 | 951.8 | 775.39 | 906.05 | 1.6814 | 1.6814 | 323060
2019-08-28 | 323180 | 313200 | 315640 | 952.02 | 793.63 | 925.46 | 1.7191 | 1.7191 | 323180
2019-08-29 | 323050 | 313290 | 315720 | 952.06 | 785.87 | 917.82 | 1.7037 | 1.7037 | 323050
2019-08-30 | 324400 | 314410 | 301960 | 940.77 | 729.03 | 853.84 | 1.5829 | 1.5829 | 324400
2019-08-31 | 323650 | 316330 | 314590 | 954.57 | 719.21 | 843.55 | 1.5628 | 1.5628 | 323650
| 8950280 | 8686370 | 8697330 | 26333.98 | 21755.18 | 25703.19 | 47.4584 | 47.4584 | 8950280
2019-09-01 | 324040 | 316010 | 314420 | 954.47 | 724.95 | 848.64 | 1.5736 | 1.5736 | 324040
2019-09-02 | 324570 | 314280 | 314730 | 953.58 | 727.07 | 852.23 | 1.5793 | 1.5793 | 324570
2019-09-03 | 325010 | 315300 | 316230 | 956.54 | 716 | 840.69 | 1.5567 | 1.5567 | 325010
2019-09-04 | 299640 | 286900 | 278650 | 865.19 | 714.49 | 837.87 | 1.5524 | 1.5524 | 299640
2019-09-05 | 325530 | 316270 | 316720 | 958.52 | 740.93 | 867.94 | 1.6089 | 1.6089 | 325530
2019-09-06 | 323750 | 312780 | 307900 | 944.43 | 734.02 | 860.46 | 1.5945 | 1.5945 | 323750
2019-09-07 | 281120 | 286840 | 292750 | 860.71 | 725.19 | 850.99 | 1.5762 | 1.5762 | 281120
2019-09-08 | 277770 | 285520 | 227720 | 791.01 | 722.69 | 847.9 | 1.5706 | 1.5706 | 277770
2019-09-09 | 297640 | 290050 | 180580 | 768.27 | 719.17 | 843.54 | 1.5627 | 1.5627 | 297640
2019-09-10 | 267200 | 256870 | 208160 | 732.23 | 716.65 | 841.78 | 1.5584 | 1.5584 | 267200
2019-09-11 | 262940 | 245640 | 188670 | 697.25 | 705.16 | 826.47 | 1.5316 | 1.5316 | 262940
2019-09-12 | 289470 | 280470 | 120580 | 690.52 | 682.36 | 800.83 | 1.4832 | 1.4832 | 289470
2019-09-13 | 316190 | 132230 | 209050 | 657.47 | 654.94 | 771.68 | 1.4266 | 1.4266 | 316190
2019-09-14 | 332700 | 322380 | 0 | 655.08 | 615.42 | 724.64 | 1.3401 | 1.3401 | 332700
2019-09-15 | 329690 | 313780 | 0 | 643.47 | 622.96 | 732 | 1.355 | 1.355 | 329690
2019-09-16 | 313320 | 299830 | 0 | 613.15 | 635.93 | 744.08 | 1.38 | 1.38 | 313320
2019-09-17 | 309140 | 253400 | 0 | 562.54 | 598.02 | 704.38 | 1.3024 | 1.3024 | 309140
2019-09-18 | 292430 | 259790 | 0 | 552.22 | 582.66 | 690 | 1.2727 | 1.2727 | 292430
2019-09-19 | 268180 | 257410 | 3470 | 529.06 | 576.38 | 682.02 | 1.2584 | 1.2584 | 268180
2019-09-20 | 266210 | 266890 | 0 | 533.1 | 570.07 | 674.82 | 1.2449 | 1.2449 | 266210
2019-09-21 | 266510 | 237500 | 0 | 504.01 | 562.96 | 666.59 | 1.2296 | 1.2296 | 266510
2019-09-22 | 226080 | 244880 | 0 | 470.96 | 569.83 | 675.4 | 1.2452 | 1.2452 | 226080
2019-09-23 | 225630 | 238440 | 0 | 464.07 | 576.63 | 682.76 | 1.2594 | 1.2594 | 225630
2019-09-24 | 211200 | 178540 | 0 | 389.74 | 529.69 | 627.52 | 1.1572 | 1.1572 | 211200
2019-09-25 | 211570 | 237100 | 0 | 448.67 | 551.55 | 655.13 | 1.2067 | 1.2067 | 211570
2019-09-26 | 211630 | 226680 | 0 | 438.31 | 561.6 | 667.77 | 1.2294 | 1.2294 | 211630
2019-09-27 | 195620 | 228450 | 0 | 424.07 | 554.1 | 657.11 | 1.2112 | 1.2112 | 195620
2019-09-28 | 162230 | 230360 | 0 | 392.59 | 525.99 | 622 | 1.148 | 1.148 | 162230
2019-09-29 | 172540 | 254640 | 0 | 427.18 | 590.04 | 698.87 | 1.2889 | 1.2889 | 172540
2019-09-30 | 189310 | 221100 | 0 | 410.41 | 584.03 | 691.69 | 1.2757 | 1.2757 | 189310
| 8098860 | 7910330 | 3279630 | 19288.82 | 19091.48 | 22487.8 | 41.5793 | 41.5793 | 8098860
2019-10-01 | 189900 | 208580 | 0 | 398.48 | 587.52 | 695.91 | 1.2834 | 1.2834 | 189900
2019-10-02 | 161480 | 201750 | 0 | 363.23 | 572.55 | 679.4 | 1.2519 | 1.2519 | 161480
2019-10-03 | 156120 | 194040 | 0 | 350.16 | 560.41 | 666.75 | 1.2272 | 1.2272 | 156120
2019-10-04 | 227010 | 81140 | 42940 | 351.09 | 564.61 | 672.32 | 1.2369 | 1.2369 | 227010
2019-10-05 | 210190 | 137240 | 0 | 347.43 | 538.21 | 643.43 | 1.1816 | 1.1816 | 210190
2019-10-06 | 280560 | 66630 | 0 | 347.19 | 536.29 | 642.15 | 1.1784 | 1.1784 | 280560
2019-10-07 | 296790 | 49400 | 0 | 346.19 | 524.67 | 630.07 | 1.1547 | 1.1547 | 296790
2019-10-08 | 315180 | 24530 | 0 | 339.71 | 491.51 | 593.24 | 1.0847 | 1.0847 | 315180
2019-10-09 | 311370 | 32410 | 0 | 343.78 | 521.35 | 629.7 | 1.1511 | 1.1511 | 311370
2019-10-10 | 340330 | 50 | 0 | 340.38 | 499.34 | 610.04 | 1.1094 | 1.1094 | 340330
2019-10-11 | 339180 | 0 | 0 | 339.18 | 532.09 | 651.41 | 1.1835 | 1.1835 | 339180
2019-10-12 | 326870 | 0 | 0 | 326.87 | 610.14 | 737.26 | 1.3474 | 1.3474 | 326870
2019-10-13 | 307410 | 0 | 0 | 307.41 | 912.76 | 1087.63 | 2.0004 | 2.0004 | 307410
2019-10-14 | 138880 | 180450 | 0 | 319.33 | 828.68 | 986.79 | 1.8155 | 1.8155 | 138880
2019-10-15 | 0 | 311250 | 0 | 311.25 | 520.53 | 624.33 | 1.1449 | 1.1449 | 0
2019-10-16 | 0 | 302050 | 0 | 302.05 | 519.61 | 624.05 | 1.1437 | 1.1437 | 0
2019-10-17 | 0 | 295790 | 0 | 295.79 | 546.57 | 647.35 | 1.1939 | 1.1939 | 0
2019-10-18 | 0 | 300150 | 0 | 300.15 | 528.94 | 622.65 | 1.1516 | 1.1516 | 0
2019-10-19 | 172530 | 123230 | 0 | 295.76 | 540.71 | 633.91 | 1.1746 | 1.1746 | 172530
2019-10-20 | 268260 | 0 | 0 | 268.26 | 535.49 | 631.31 | 1.1668 | 1.1668 | 268260
2019-10-21 | 269730 | 0 | 0 | 269.73 | 555.34 | 649.1 | 1.2044 | 1.2044 | 269730
2019-10-22 | 128950 | 130510 | 0 | 259.46 | 563.74 | 656.94 | 1.2207 | 1.2207 | 128950
2019-10-23 | 0 | 257940 | 0 | 257.94 | 531.79 | 627.78 | 1.1596 | 1.1596 | 0
2019-10-24 | 0 | 247750 | 0 | 247.75 | 527.08 | 626.24 | 1.1533 | 1.1533 | 0
2019-10-25 | 0 | 244810 | 0 | 244.81 | 513.1 | 612.92 | 1.126 | 1.126 | 0
2019-10-26 | 123820 | 112330 | 0 | 236.15 | 510.13 | 610.51 | 1.1206 | 1.1206 | 123820
2019-10-27 | 231080 | 0 | 0 | 231.08 | 522.5 | 623.94 | 1.1464 | 1.1464 | 231080
2019-10-28 | 231800 | 0 | 0 | 231.8 | 518.74 | 617.49 | 1.1362 | 1.1362 | 231800
2019-10-29 | 224490 | 0 | 0 | 224.49 | 529.07 | 629.62 | 1.1587 | 1.1587 | 224490
2019-10-30 | 225330 | 0 | 0 | 225.33 | 538.07 | 636.83 | 1.1749 | 1.1749 | 225330
2019-10-31 | 221630 | 0 | 0 | 221.63 | 636.33 | 727.42 | 1.3638 | 1.3638 | 221630
| 5698890 | 3502030 | 42940 | 9243.86 | 17417.87 | 20728.49 | 38.1464 | 38.1464 | 5698890
2019-11-01 | 212390 | 0 | 0 | 212.39 | 580.07 | 674.3 | 1.2544 | 1.2544 | 212390
2019-11-02 | 180320 | 0 | 0 | 180.32 | 464.84 | 539.82 | 1.0047 | 1.0047 | 180320
2019-11-03 | 224310 | 0 | 0 | 224.31 | 680.24 | 765.31 | 1.4455 | 1.4455 | 224310
2019-11-04 | 216900 | 0 | 0 | 216.9 | 746.03 | 828.51 | 1.5745 | 1.5745 | 216900
2019-11-05 | 207570 | 12500 | 0 | 220.07 | 631.77 | 717.1 | 1.3489 | 1.3489 | 207570
2019-11-06 | 170370 | 28890 | 0 | 199.26 | 552.99 | 645.19 | 1.1982 | 1.1982 | 170370
2019-11-07 | 97010 | 92040 | 0 | 189.05 | 568.04 | 666.18 | 1.2342 | 1.2342 | 97010
2019-11-08 | 98220 | 114790 | 0 | 213.01 | 555.99 | 648.47 | 1.2045 | 1.2045 | 98220
2019-11-09 | 220030 | 0 | 0 | 220.03 | 565.14 | 658.36 | 1.2235 | 1.2235 | 220030
2019-11-10 | 200370 | 0 | 0 | 200.37 | 537.31 | 634.21 | 1.1715 | 1.1715 | 200370
2019-11-11 | 192610 | 0 | 0 | 192.61 | 525.74 | 626.87 | 1.1526 | 1.1526 | 192610
2019-11-12 | 185110 | 0 | 0 | 185.11 | 539.63 | 641.68 | 1.1813 | 1.1813 | 185110
2019-11-13 | 175840 | 0 | 0 | 175.84 | 571.96 | 676.03 | 1.248 | 1.248 | 175840
2019-11-14 | 171340 | 0 | 0 | 171.34 | 570.02 | 673.33 | 1.2434 | 1.2434 | 171340
2019-11-15 | 168270 | 0 | 0 | 168.27 | 569.05 | 671.73 | 1.2408 | 1.2408 | 168270
2019-11-16 | 172670 | 0 | 0 | 172.67 | 555.65 | 657.62 | 1.2133 | 1.2133 | 172670
2019-11-17 | 176680 | 0 | 0 | 176.68 | 520.46 | 618.05 | 1.1385 | 1.1385 | 176680
2019-11-18 | 161040 | 0 | 0 | 161.04 | 510.84 | 596.67 | 1.1075 | 1.1075 | 161040
2019-11-19 | 159650 | 0 | 0 | 159.65 | 543.02 | 631.63 | 1.1746 | 1.1746 | 159650
2019-11-20 | 157940 | 0 | 0 | 157.94 | 458.63 | 538.24 | 0.99687 | 0.99687 | 157940
2019-11-21 | 156750 | 0 | 0 | 156.75 | 522.13 | 613.9 | 1.136 | 1.136 | 156750
2019-11-22 | 153960 | 0 | 0 | 153.96 | 670.22 | 752.43 | 1.4227 | 1.4227 | 153960
2019-11-23 | 180810 | 0 | 0 | 180.81 | 685.99 | 767.4 | 1.4534 | 1.4534 | 180810
2019-11-24 | 185710 | 0 | 0 | 185.71 | 616.91 | 703.57 | 1.3205 | 1.3205 | 185710
2019-11-25 | 154740 | 0 | 0 | 154.74 | 546.24 | 639.59 | 1.1858 | 1.1858 | 154740
2019-11-26 | 158300 | 0 | 0 | 158.3 | 551.69 | 645.15 | 1.1968 | 1.1968 | 158300
2019-11-27 | 146960 | 0 | 0 | 146.96 | 553.28 | 646.05 | 1.1993 | 1.1993 | 146960
2019-11-28 | 177950 | 0 | 0 | 177.95 | 647.96 | 748.52 | 1.3965 | 1.3965 | 177950
2019-11-29 | 155980 | 0 | 0 | 155.98 | 662.9 | 768.02 | 1.4309 | 1.4309 | 155980
2019-11-30 | 141180 | 0 | 0 | 141.18 | 631.03 | 725.55 | 1.3566 | 1.3566 | 141180
| 5160980 | 248220 | 0 | 5409.2 | 17335.77 | 20119.48 | 37.4553 | 37.4553 | 5160980
2019-12-01 | 144780 | 0 | 600 | 145.38 | 541.96 | 631.92 | 1.1739 | 1.1739 | 144780
2019-12-02 | 70910 | 0 | 73480 | 144.39 | 508.87 | 594.03 | 1.1029 | 1.1029 | 70910
2019-12-03 | 0 | 0 | 147620 | 147.62 | 552.25 | 648.66 | 1.2009 | 1.2009 | 0
2019-12-04 | 0 | 0 | 157840 | 157.84 | 634.68 | 729.53 | 1.3642 | 1.3642 | 0
2019-12-05 | 0 | 0 | 72750 | 72.75 | 557.22 | 643.12 | 1.2003 | 1.2003 | 0
2019-12-06 | 0 | 0 | 0 | 0 | 517.97 | 592.2 | 1.1102 | 1.1102 | 0
2019-12-07 | 0 | 0 | 0 | 0 | 471.18 | 550.87 | 1.022 | 1.022 | 0
2019-12-08 | 0 | 0 | 0 | 0 | 300 | 363.29 | 0.66329 | 0.66329 | 0
2019-12-09 | 0 | 0 | 0 | 0 | 448.61 | 525.05 | 0.97366 | 0.97366 | 0
2019-12-10 | 0 | 0 | 0 | 0 | 460.35 | 533.57 | 0.99392 | 0.99392 | 0
2019-12-11 | 0 | 0 | 0 | 0 | 517.27 | 599.11 | 1.1164 | 1.1164 | 0
2019-12-12 | 0 | 0 | 0 | 0 | 474.99 | 567.21 | 1.0422 | 1.0422 | 0
2019-12-13 | 0 | 0 | 0 | 0 | 456.54 | 545.82 | 1.0024 | 1.0024 | 0
2019-12-14 | 0 | 0 | 108610 | 108.61 | 660 | 772.08 | 1.4321 | 1.4321 | 0
2019-12-15 | 0 | 0 | 166720 | 166.72 | 651.74 | 765.12 | 1.4169 | 1.4169 | 0
2019-12-16 | 0 | 0 | 86880 | 86.88 | 355.91 | 417.18 | 0.77309 | 0.77309 | 0
2019-12-17 | 0 | 0 | 125360 | 125.36 | 460.36 | 537.13 | 0.99749 | 0.99749 | 0
2019-12-18 | 0 | 0 | 162190 | 162.19 | 662.28 | 770.56 | 1.4328 | 1.4328 | 0
2019-12-19 | 0 | 0 | 143180 | 143.18 | 661.7 | 769.05 | 1.4308 | 1.4308 | 0
2019-12-20 | 0 | 0 | 114370 | 114.37 | 681.55 | 789.22 | 1.4708 | 1.4708 | 0
2019-12-21 | 0 | 0 | 186780 | 186.78 | 723.11 | 822.14 | 1.5453 | 1.5453 | 0
2019-12-22 | 61250 | 0 | 72840 | 134.09 | 656.83 | 746.68 | 1.4035 | 1.4035 | 61250
2019-12-23 | 0 | 0 | 143510 | 143.51 | 679.24 | 766.39 | 1.4456 | 1.4456 | 0
2019-12-24 | 0 | 0 | 165620 | 165.62 | 690.37 | 775.89 | 1.4663 | 1.4663 | 0
2019-12-25 | 0 | 0 | 138750 | 138.75 | 683.3 | 767.44 | 1.4507 | 1.4507 | 0
2019-12-26 | 53970 | 0 | 82490 | 136.46 | 583.99 | 661.42 | 1.2454 | 1.2454 | 53970
2019-12-27 | 57880 | 0 | 80450 | 138.33 | 513.26 | 586.88 | 1.1001 | 1.1001 | 57880
2019-12-28 | 59640 | 0 | 83160 | 142.8 | 533.22 | 622.32 | 1.1555 | 1.1555 | 59640
2019-12-29 | 50380 | 0 | 87920 | 138.3 | 534.87 | 633.42 | 1.1683 | 1.1683 | 50380
2019-12-30 | 32480 | 48330 | 59000 | 139.81 | 488.4 | 577.53 | 1.0659 | 1.0659 | 32480
2019-12-31 | 0 | 24880 | 19790 | 44.67 | 536.01 | 620.28 | 1.1563 | 1.1563 | 0
| 531290 | 73210 | 2479910 | 3084.41 | 17198.03 | 19925.11 | 37.1231 | 37.1231 | 531290
2020-01-01 | 0 | 78060 | 30290 | 108.35 | 608.65 | 697.71 | 1.3064 | 1.3064 | 0
2020-01-02 | 0 | 67530 | 59540 | 127.07 | 604.81 | 705.49 | 1.3103 | 1.3103 | 0
2020-01-03 | 0 | 44110 | 79770 | 123.88 | 583.49 | 688.5 | 1.272 | 1.272 | 0
2020-01-04 | 0 | 61180 | 63270 | 124.45 | 625.31 | 728.43 | 1.3537 | 1.3537 | 0
2020-01-05 | 0 | 60790 | 70270 | 131.06 | 625.63 | 731.05 | 1.3567 | 1.3567 | 0
2020-01-06 | 0 | 22850 | 91290 | 114.14 | 642.26 | 750.34 | 1.3926 | 1.3926 | 0
2020-01-07 | 0 | 46300 | 86330 | 132.63 | 642.7 | 748 | 1.3907 | 1.3907 | 0
2020-01-08 | 0 | 47430 | 86780 | 134.21 | 642.56 | 738.8 | 1.3814 | 1.3814 | 0
2020-01-09 | 0 | 36700 | 100930 | 137.63 | 646.43 | 731.22 | 1.3776 | 1.3776 | 0
2020-01-10 | 0 | 35850 | 91660 | 127.51 | 643.39 | 726.04 | 1.3694 | 1.3694 | 0
2020-01-11 | 0 | 44320 | 80580 | 124.9 | 633.76 | 722.62 | 1.3564 | 1.3564 | 0
2020-01-12 | 0 | 65880 | 64650 | 130.53 | 588.72 | 675.95 | 1.2647 | 1.2647 | 0
2020-01-13 | 0 | 72610 | 56020 | 128.63 | 667.4 | 755.64 | 1.423 | 1.423 | 0
2020-01-14 | 0 | 133930 | 39430 | 173.36 | 674.6 | 763.36 | 1.438 | 1.438 | 0
2020-01-15 | 0 | 114660 | 39840 | 154.5 | 683.4 | 770.28 | 1.4537 | 1.4537 | 0
2020-01-16 | 0 | 71560 | 86560 | 158.12 | 672.03 | 757.68 | 1.4297 | 1.4297 | 0
2020-01-17 | 0 | 38560 | 121760 | 160.32 | 648.32 | 731.94 | 1.3803 | 1.3803 | 0
2020-01-18 | 0 | 36020 | 115980 | 152 | 642.72 | 726.01 | 1.3687 | 1.3687 | 0
2020-01-19 | 0 | 37680 | 112190 | 149.87 | 568.13 | 655.1 | 1.2232 | 1.2232 | 0
2020-01-20 | 0 | 38790 | 107940 | 146.73 | 631.41 | 718.55 | 1.35 | 1.35 | 0
2020-01-21 | 0 | 39510 | 104840 | 144.35 | 668.17 | 755.1 | 1.4233 | 1.4233 | 0
2020-01-22 | 0 | 67590 | 78940 | 146.53 | 694.58 | 782.35 | 1.4769 | 1.4769 | 0
2020-01-23 | 0 | 40140 | 107000 | 147.14 | 669.35 | 758.35 | 1.4277 | 1.4277 | 0
2020-01-24 | 0 | 39960 | 109450 | 149.41 | 572.15 | 650.6 | 1.2227 | 1.2227 | 0
2020-01-25 | 0 | 39630 | 109310 | 148.94 | 601.71 | 690.4 | 1.2921 | 1.2921 | 0
2020-01-26 | 0 | 40350 | 109480 | 149.83 | 600.87 | 693.5 | 1.2944 | 1.2944 | 0
2020-01-27 | 0 | 40460 | 108990 | 149.45 | 641 | 735.08 | 1.3761 | 1.3761 | 0
2020-01-28 | 0 | 40540 | 117290 | 157.83 | 693.61 | 786.44 | 1.48 | 1.48 | 0
2020-01-29 | 0 | 0 | 152350 | 152.35 | 716.72 | 804.06 | 1.5208 | 1.5208 | 0
2020-01-30 | 0 | 0 | 156650 | 156.65 | 678.94 | 767.4 | 1.4463 | 1.4463 | 0
2020-01-31 | 0 | 40850 | 118060 | 158.91 | 657.48 | 756.22 | 1.4137 | 1.4137 | 0
| 0 | 1543840 | 2857440 | 4401.28 | 19870.3 | 22702.21 | 42.5725 | 42.5725 | 0
2020-02-01 | 0 | 40350 | 120270 | 160.62 | 648.86 | 758.5 | 1.4074 | 1.4074 | 0
2020-02-02 | 0 | 37900 | 119620 | 157.52 | 592.9 | 702.32 | 1.2952 | 1.2952 | 0
2020-02-03 | 0 | 34810 | 120790 | 155.6 | 630.91 | 727.34 | 1.3582 | 1.3582 | 0
2020-02-04 | 0 | 37960 | 117690 | 155.65 | 591.39 | 707.8 | 1.2992 | 1.2992 | 0
2020-02-05 | 0 | 38120 | 114640 | 152.76 | 594.84 | 701.08 | 1.2959 | 1.2959 | 0
2020-02-06 | 0 | 39320 | 114600 | 153.92 | 624.45 | 729.88 | 1.3543 | 1.3543 | 0
2020-02-07 | 0 | 39300 | 111160 | 150.46 | 601.32 | 707.26 | 1.3086 | 1.3086 | 0
2020-02-08 | 0 | 36970 | 108480 | 145.45 | 640.02 | 748.5 | 1.3885 | 1.3885 | 0
2020-02-09 | 0 | 38550 | 106100 | 144.65 | 601.83 | 711.44 | 1.3133 | 1.3133 | 0
2020-02-10 | 0 | 39720 | 111110 | 150.83 | 622.18 | 728.04 | 1.3502 | 1.3502 | 0
2020-02-11 | 0 | 40340 | 111000 | 151.34 | 633.67 | 742.74 | 1.3764 | 1.3764 | 0
2020-02-12 | 0 | 40150 | 123440 | 163.59 | 619.33 | 724.9 | 1.3442 | 1.3442 | 0
2020-02-13 | 0 | 40730 | 130020 | 170.75 | 618.67 | 727.4 | 1.3461 | 1.3461 | 0
2020-02-14 | 0 | 37110 | 161330 | 198.44 | 632.33 | 740.58 | 1.3729 | 1.3729 | 0
2020-02-15 | 0 | 28370 | 209260 | 237.63 | 626.66 | 737.27 | 1.3639 | 1.3639 | 0
2020-02-16 | 0 | 30960 | 231090 | 262.05 | 666.34 | 773.81 | 1.4401 | 1.4401 | 0
2020-02-17 | 0 | 32240 | 206330 | 238.57 | 637.31 | 748.4 | 1.3857 | 1.3857 | 0
2020-02-18 | 0 | 35290 | 202060 | 237.35 | 635.99 | 733.5 | 1.3695 | 1.3695 | 0
2020-02-19 | 0 | 39270 | 187910 | 227.18 | 574.56 | 656.18 | 1.2307 | 1.2307 | 0
2020-02-20 | 0 | 51010 | 153880 | 204.89 | 528.25 | 615.68 | 1.1439 | 1.1439 | 0
2020-02-21 | 89030 | 19900 | 81140 | 190.07 | 528.04 | 618.44 | 1.1465 | 1.1465 | 89030
2020-02-22 | 144480 | 0 | 39540 | 184.02 | 513.13 | 592.18 | 1.1053 | 1.1053 | 144480
2020-02-23 | 140670 | 0 | 40400 | 181.07 | 508.68 | 590.64 | 1.0993 | 1.0993 | 140670
2020-02-24 | 149120 | 0 | 42390 | 191.51 | 533.66 | 612.92 | 1.1466 | 1.1466 | 149120
2020-02-25 | 63840 | 17710 | 104320 | 185.87 | 592.41 | 692.18 | 1.2846 | 1.2846 | 63840
2020-02-26 | 7480 | 36550 | 133570 | 177.6 | 605.92 | 688.3 | 1.2942 | 1.2942 | 7480
2020-02-27 | 58780 | 40400 | 84900 | 184.08 | 505.6 | 584.92 | 1.0905 | 1.0905 | 58780
2020-02-28 | 144920 | 0 | 40730 | 185.65 | 471.44 | 551.38 | 1.0228 | 1.0228 | 144920
2020-02-29 | 152460 | 0 | 40610 | 193.07 | 502.02 | 581.68 | 1.0837 | 1.0837 | 152460
| 950780 | 873030 | 3468380 | 5292.19 | 17082.71 | 19935.26 | 37.018 | 37.018 | 950780
2020-03-01 | 154260 | 0 | 40400 | 194.66 | 476.86 | 573.16 | 1.05 | 1.05 | 154260
2020-03-02 | 144180 | 0 | 37380 | 181.56 | 503.5 | 586.92 | 1.0904 | 1.0904 | 144180
2020-03-03 | 48720 | 32350 | 101880 | 182.95 | 547.39 | 632.56 | 1.18 | 1.18 | 48720
2020-03-04 | 35670 | 14600 | 130260 | 180.53 | 512.01 | 591.03 | 1.103 | 1.103 | 35670
2020-03-05 | 35530 | 14830 | 136970 | 187.33 | 513.1 | 595.07 | 1.1082 | 1.1082 | 35530
2020-03-06 | 87180 | 28630 | 65150 | 180.96 | 513.03 | 588.8 | 1.1018 | 1.1018 | 87180
2020-03-07 | 90960 | 26730 | 61190 | 178.88 | 517.32 | 591.5 | 1.1088 | 1.1088 | 90960
2020-03-08 | 29840 | 28370 | 107660 | 165.87 | 473.01 | 553 | 1.026 | 1.026 | 29840
2020-03-09 | 28720 | 27960 | 105180 | 161.86 | 483.52 | 566.46 | 1.05 | 1.05 | 28720
2020-03-10 | 28940 | 28950 | 105300 | 163.19 | 460.18 | 541.88 | 1.0021 | 1.0021 | 28940
2020-03-11 | 29490 | 28900 | 114030 | 172.42 | 478.04 | 560.28 | 1.0383 | 1.0383 | 29490
2020-03-12 | 85550 | 26350 | 54870 | 166.77 | 494.52 | 578.04 | 1.0726 | 1.0726 | 85550
2020-03-13 | 60860 | 30680 | 111000 | 202.54 | 517.76 | 594.46 | 1.1122 | 1.1122 | 60860
2020-03-14 | 31810 | 43300 | 139330 | 214.44 | 491.86 | 608.12 | 1.1 | 1.1 | 31810
2020-03-15 | 91100 | 34550 | 121500 | 247.15 | 487.86 | 583.88 | 1.0717 | 1.0717 | 91100
2020-03-16 | 88560 | 30620 | 123760 | 242.94 | 470.24 | 568.91 | 1.0392 | 1.0392 | 88560
2020-03-17 | 36330 | 35800 | 194880 | 267.01 | 487.1 | 586.63 | 1.0737 | 1.0737 | 36330
2020-03-18 | 36700 | 36850 | 208830 | 282.38 | 480.4 | 580.06 | 1.0605 | 1.0605 | 36700
2020-03-19 | 36740 | 35430 | 218900 | 291.07 | 476.96 | 573.48 | 1.0504 | 1.0504 | 36740
2020-03-20 | 36350 | 34790 | 235480 | 306.62 | 537.32 | 626.02 | 1.1633 | 1.1633 | 36350
2020-03-21 | 34300 | 36320 | 241770 | 312.39 | 594.64 | 677.88 | 1.2725 | 1.2725 | 34300
2020-03-22 | 35550 | 36520 | 237550 | 309.62 | 462.68 | 562.8 | 1.0255 | 1.0255 | 35550
2020-03-23 | 37030 | 34010 | 246640 | 317.68 | 457.65 | 557.6 | 1.0152 | 1.0152 | 37030
2020-03-24 | 36300 | 35960 | 251510 | 323.77 | 470.59 | 572.1 | 1.0427 | 1.0427 | 36300
2020-03-25 | 37020 | 36480 | 262460 | 335.96 | 459.25 | 559.5 | 1.0188 | 1.0188 | 37020
2020-03-26 | 36430 | 36140 | 274020 | 346.59 | 470.17 | 570.4 | 1.0406 | 1.0406 | 36430
2020-03-27 | 47680 | 36050 | 272220 | 355.95 | 514.71 | 617 | 1.1317 | 1.1317 | 47680
2020-03-28 | 149790 | 55730 | 202990 | 408.51 | 564.53 | 670.38 | 1.2349 | 1.2349 | 149790
2020-03-29 | 186260 | 40510 | 213050 | 439.82 | 554.26 | 659.7 | 1.214 | 1.214 | 186260
2020-03-30 | 234320 | 38590 | 193780 | 466.69 | 542.08 | 646.28 | 1.1884 | 1.1884 | 234320
2020-03-31 | 227200 | 28290 | 163430 | 418.92 | 546 | 650.56 | 1.1966 | 1.1966 | 227200
| 2279370 | 954290 | 4973370 | 8207.03 | 15558.54 | 18424.46 | 33.983 | 33.983 | 2279370
2020-04-01 | 233600 | 38880 | 144330 | 416.81 | 534.04 | 637.46 | 1.1715 | 1.1715 | 233600
2020-04-02 | 236080 | 38590 | 144060 | 418.73 | 548.38 | 652.32 | 1.2007 | 1.2007 | 236080
2020-04-03 | 235700 | 38250 | 149250 | 423.2 | 522.18 | 625.08 | 1.1473 | 1.1473 | 235700
2020-04-04 | 239280 | 38500 | 156260 | 434.04 | 525.9 | 627.98 | 1.1539 | 1.1539 | 239280
2020-04-05 | 216380 | 38020 | 165120 | 419.52 | 510.8 | 640.28 | 1.1511 | 1.1511 | 216380
2020-04-06 | 231790 | 39400 | 205300 | 476.49 | 270.04 | 913.38 | 1.1834 | 1.1834 | 231790
2020-04-07 | 155560 | 101340 | 105220 | 362.12 | 377.46 | 816.26 | 1.1937 | 1.1937 | 155560
2020-04-08 | 109770 | 161160 | 88500 | 359.43 | 516.82 | 618.34 | 1.1352 | 1.1352 | 109770
2020-04-09 | 237780 | 0 | 170080 | 407.86 | 555.02 | 663.8 | 1.2188 | 1.2188 | 237780
2020-04-10 | 207650 | 51170 | 169940 | 428.76 | 557.08 | 661.96 | 1.219 | 1.219 | 207650
2020-04-11 | 191870 | 231870 | 27870 | 451.61 | 569.48 | 674.46 | 1.2439 | 1.2439 | 191870
2020-04-12 | 213680 | 253660 | 57640 | 524.98 | 567.42 | 671.88 | 1.2393 | 1.2393 | 213680
2020-04-13 | 266900 | 282570 | 69160 | 618.63 | 581.86 | 685.12 | 1.267 | 1.267 | 266900
2020-04-14 | 197700 | 296780 | 181430 | 675.91 | 573.35 | 673.24 | 1.2466 | 1.2466 | 197700
2020-04-15 | 298300 | 102570 | 299060 | 699.93 | 596.48 | 715.16 | 1.3116 | 1.3116 | 298300
2020-04-16 | 303850 | 37260 | 313930 | 655.04 | 573.53 | 660.79 | 1.2343 | 1.2343 | 303850
2020-04-17 | 295480 | 43420 | 302530 | 641.43 | 602.97 | 706.11 | 1.3091 | 1.3091 | 295480
2020-04-18 | 306390 | 170780 | 283850 | 761.02 | 628.88 | 736.12 | 1.365 | 1.365 | 306390
2020-04-19 | 314190 | 39270 | 311810 | 665.27 | 584.42 | 688.04 | 1.2725 | 1.2725 | 314190
2020-04-20 | 281950 | 32340 | 279630 | 593.92 | 572.95 | 677.64 | 1.2506 | 1.2506 | 281950
2020-04-21 | 269790 | 28010 | 259130 | 556.93 | 565.04 | 669.2 | 1.2342 | 1.2342 | 269790
2020-04-22 | 274860 | 39310 | 218900 | 533.07 | 553.1 | 655.66 | 1.2088 | 1.2088 | 274860
2020-04-23 | 276060 | 45130 | 229680 | 550.87 | 556.12 | 659.06 | 1.2152 | 1.2152 | 276060
2020-04-24 | 259580 | 46600 | 279020 | 585.2 | 553.44 | 654.58 | 1.208 | 1.208 | 259580
2020-04-25 | 276800 | 45260 | 287380 | 609.44 | 542.84 | 644.98 | 1.1878 | 1.1878 | 276800
2020-04-26 | 276300 | 42930 | 286860 | 606.09 | 568.74 | 670.26 | 1.239 | 1.239 | 276300
2020-04-27 | 268330 | 45420 | 273950 | 587.7 | 549.68 | 651.24 | 1.2009 | 1.2009 | 268330
2020-04-28 | 46800 | 267820 | 283020 | 597.64 | 541.06 | 640.3 | 1.1814 | 1.1814 | 46800
2020-04-29 | 299590 | 45020 | 296980 | 641.59 | 564.98 | 667.16 | 1.2321 | 1.2321 | 299590
2020-04-30 | 315350 | 54720 | 316580 | 686.65 | 562.6 | 665.58 | 1.2282 | 1.2282 | 315350
| 7337360 | 2696050 | 6356470 | 16389.88 | 16326.66 | 20323.44 | 36.6501 | 36.6501 | 7337360
2020-05-01 | 186700 | 165030 | 299460 | 651.19 | 577.56 | 670.4 | 1.248 | 1.248 | 186700
2020-05-02 | 315230 | 236840 | 187220 | 739.29 | 608.8 | 690.28 | 1.2991 | 1.2991 | 315230
2020-05-03 | 270050 | 291600 | 286400 | 848.05 | 627.22 | 713.84 | 1.3411 | 1.3411 | 270050
2020-05-04 | 279490 | 276360 | 268640 | 824.49 | 619.97 | 709.98 | 1.3299 | 1.3299 | 279490
2020-05-05 | 254290 | 261060 | 263890 | 779.24 | 636.71 | 740.24 | 1.3769 | 1.3769 | 254290
2020-05-06 | 316060 | 76620 | 312710 | 705.39 | 604.7 | 705.74 | 1.3104 | 1.3104 | 316060
2020-05-07 | 314810 | 38260 | 310620 | 663.69 | 574.74 | 675.66 | 1.2504 | 1.2504 | 314810
2020-05-08 | 319100 | 31620 | 323680 | 674.4 | 570.51 | 668.65 | 1.2392 | 1.2392 | 319100
2020-05-09 | 310170 | 87270 | 311080 | 708.52 | 597.51 | 698.27 | 1.2958 | 1.2958 | 310170
2020-05-10 | 302030 | 64020 | 296890 | 662.94 | 586.28 | 687.12 | 1.2734 | 1.2734 | 302030
2020-05-11 | 328070 | 46900 | 325780 | 700.75 | 595.14 | 695.4 | 1.2905 | 1.2905 | 328070
2020-05-12 | 321470 | 48240 | 317900 | 687.61 | 590.92 | 690.74 | 1.2817 | 1.2817 | 321470
2020-05-13 | 321740 | 46440 | 320030 | 688.21 | 577.16 | 677.8 | 1.255 | 1.255 | 321740
2020-05-14 | 309300 | 74160 | 309750 | 693.21 | 610.72 | 685.64 | 1.2964 | 1.2964 | 309300
2020-05-15 | 193490 | 283070 | 284110 | 760.67 | 661.6 | 741.52 | 1.4031 | 1.4031 | 193490
2020-05-16 | 271980 | 223730 | 251910 | 747.62 | 625.66 | 726.42 | 1.3521 | 1.3521 | 271980
2020-05-17 | 315750 | 67860 | 315730 | 699.34 | 592.52 | 694.02 | 1.2865 | 1.2865 | 315750
2020-05-18 | 304180 | 47670 | 308040 | 659.89 | 585.32 | 674.36 | 1.2597 | 1.2597 | 304180
2020-05-19 | 280520 | 24810 | 266290 | 571.62 | 573.72 | 650.2 | 1.2239 | 1.2239 | 280520
2020-05-20 | 264300 | 39230 | 267730 | 571.26 | 577.54 | 667.18 | 1.2447 | 1.2447 | 264300
2020-05-21 | 291780 | 78080 | 284040 | 653.9 | 577.68 | 678.14 | 1.2558 | 1.2558 | 291780
2020-05-22 | 264790 | 233280 | 246110 | 744.18 | 609.26 | 709.79 | 1.3191 | 1.3191 | 264790
2020-05-23 | 245450 | 200830 | 236600 | 682.88 | 567.02 | 660.75 | 1.2278 | 1.2278 | 245450
2020-05-24 | 204180 | 147390 | 298560 | 650.13 | 574.02 | 670.98 | 1.245 | 1.245 | 204180
2020-05-25 | 205610 | 175370 | 281420 | 662.4 | 581.68 | 678.8 | 1.2605 | 1.2605 | 205610
2020-05-26 | 262210 | 155090 | 261080 | 678.38 | 587.48 | 683.62 | 1.2711 | 1.2711 | 262210
2020-05-27 | 230190 | 154320 | 278360 | 662.87 | 593.46 | 692.3 | 1.2858 | 1.2858 | 230190
2020-05-28 | 178360 | 188450 | 285480 | 652.29 | 589.26 | 689.54 | 1.2788 | 1.2788 | 178360
2020-05-29 | 71985 | 282850 | 286544 | 641.379 | 586.88 | 685.84 | 1.2727 | 1.2727 | 71985
2020-05-30 | 108890 | 243170 | 282450 | 634.51 | 623.44 | 657.43 | 1.2809 | 1.2809 | 108890
2020-05-31 | 145080 | 286650 | 294060 | 725.79 | 652.68 | 659.94 | 1.3126 | 1.3126 | 145080
| 7987255 | 4576270 | 8862564 | 21426.089 | 18537.16 | 21330.59 | 39.8678 | 39.8678 | 7987255
2020-06-01 | 245940 | 257530 | 251790 | 755.26 | 724.71 | 720.78 | 1.4455 | 1.4455 | 245940
2020-06-02 | 61880 | 305730 | 301080 | 668.69 | 705.14 | 703.93 | 1.4091 | 1.4091 | 61880
2020-06-03 | 46100 | 287450 | 287210 | 620.76 | 674.2 | 677.37 | 1.3516 | 1.3516 | 46100
2020-06-04 | 54280 | 296040 | 288700 | 639.02 | 682.18 | 683.53 | 1.3657 | 1.3657 | 54280
2020-06-05 | 106070 | 286940 | 285040 | 678.05 | 710.35 | 708.18 | 1.4185 | 1.4185 | 106070
2020-06-06 | 188350 | 289210 | 285110 | 762.67 | 750.92 | 742.13 | 1.493 | 1.493 | 188350
2020-06-07 | 112880 | 300770 | 291370 | 705.02 | 729.18 | 724.78 | 1.454 | 1.454 | 112880
2020-06-08 | 223290 | 277630 | 234720 | 735.64 | 757.93 | 729.14 | 1.4871 | 1.4871 | 223290
2020-06-09 | 296540 | 288720 | 279830 | 865.09 | 733.89 | 742.03 | 1.4759 | 1.4759 | 296540
2020-06-10 | 301400 | 303330 | 271490 | 876.22 | 704.63 | 696.7 | 1.4013 | 1.4013 | 301400
2020-06-11 | 245120 | 287230 | 249090 | 781.44 | 707.91 | 699.72 | 1.4076 | 1.4076 | 245120
2020-06-12 | 201840 | 293340 | 252640 | 747.82 | 694.39 | 685.64 | 1.38 | 1.38 | 201840
2020-06-13 | 266620 | 265000 | 234400 | 766.02 | 709.83 | 701.14 | 1.411 | 1.411 | 266620
2020-06-14 | 270930 | 262910 | 218090 | 751.93 | 724.48 | 714.22 | 1.4387 | 1.4387 | 270930
2020-06-15 | 250220 | 271380 | 264910 | 786.51 | 715.4 | 702.59 | 1.418 | 1.418 | 250220
2020-06-16 | 236980 | 268890 | 234870 | 740.74 | 697 | 678.93 | 1.3759 | 1.3759 | 236980
2020-06-17 | 256770 | 266830 | 236520 | 760.12 | 644.2 | 625.29 | 1.2695 | 1.2695 | 256770
2020-06-18 | 297740 | 291140 | 283240 | 872.12 | 653.93 | 635.07 | 1.289 | 1.289 | 297740
2020-06-19 | 227570 | 257400 | 252890 | 737.86 | 626.33 | 616.36 | 1.2427 | 1.2427 | 227570
2020-06-20 | 314680 | 267400 | 309410 | 891.49 | 644.2 | 636.5 | 1.2807 | 1.2807 | 314680
2020-06-21 | 302900 | 302290 | 279550 | 884.74 | 654.14 | 645.48 | 1.2996 | 1.2996 | 302900
2020-06-22 | 306900 | 308320 | 264380 | 879.6 | 662.77 | 648.85 | 1.3116 | 1.3116 | 306900
2020-06-23 | 316250 | 306420 | 216920 | 839.59 | 651.2 | 635.07 | 1.2863 | 1.2863 | 316250
2020-06-24 | 336120 | 335630 | 930 | 672.68 | 622.6 | 617.83 | 1.2404 | 1.2404 | 336120
2020-06-25 | 291410 | 291550 | 272230 | 855.19 | 627.89 | 624.87 | 1.2528 | 1.2528 | 291410
2020-06-26 | 313110 | 303770 | 307160 | 924.04 | 666.01 | 650.18 | 1.3162 | 1.3162 | 313110
2020-06-27 | 324000 | 318500 | 317250 | 959.75 | 701.18 | 674.74 | 1.3759 | 1.3759 | 324000
2020-06-28 | 316100 | 302260 | 309800 | 928.16 | 674.42 | 650.11 | 1.3245 | 1.3245 | 316100
2020-06-29 | 316280 | 323060 | 321520 | 960.86 | 715.73 | 702.04 | 1.4178 | 1.4178 | 316280
2020-06-30 | 300860 | 313380 | 322390 | 936.63 | 665.97 | 644.52 | 1.3105 | 1.3105 | 300860
| 7329130 | 8730050 | 7924530 | 23983.71 | 20632.71 | 20317.72 | 40.9504 | 40.9504 | 7329130
2020-07-01 | 328130 | 320170 | 325680 | 973.98 | 668.72 | 639.36 | 1.3081 | 1.3081 | 328130
2020-07-02 | 329080 | 327200 | 313460 | 969.74 | 658.31 | 633.56 | 1.2919 | 1.2919 | 329080
2020-07-03 | 316390 | 316590 | 306690 | 939.67 | 658.87 | 632.28 | 1.2911 | 1.2911 | 316390
2020-07-04 | 315040 | 311690 | 314220 | 940.95 | 701.17 | 678.25 | 1.3794 | 1.3794 | 315040
2020-07-05 | 323370 | 321730 | 323530 | 968.63 | 769.19 | 739.92 | 1.5091 | 1.5091 | 323370
2020-07-06 | 326820 | 326520 | 324250 | 977.59 | 807.63 | 769.85 | 1.5775 | 1.5775 | 326820
2020-07-07 | 297890 | 309540 | 309870 | 917.3 | 760.1 | 727.15 | 1.4872 | 1.4872 | 297890
2020-07-08 | 333930 | 332800 | 330530 | 997.26 | 776.42 | 748.86 | 1.5253 | 1.5253 | 333930
2020-07-09 | 317550 | 328310 | 326580 | 972.44 | 753.87 | 724.09 | 1.478 | 1.478 | 317550
2020-07-10 | 335270 | 335170 | 335120 | 1005.56 | 740.22 | 708.17 | 1.4484 | 1.4484 | 335270
2020-07-11 | 334450 | 333090 | 333130 | 1000.67 | 733.2 | 703.51 | 1.4367 | 1.4367 | 334450
2020-07-12 | 332780 | 332230 | 332380 | 997.39 | 744.01 | 717.14 | 1.4612 | 1.4612 | 332780
2020-07-13 | 329130 | 327060 | 307230 | 963.42 | 710.05 | 688.37 | 1.3984 | 1.3984 | 329130
2020-07-14 | 315780 | 289820 | 309740 | 915.34 | 691.99 | 678.22 | 1.3702 | 1.3702 | 315780
2020-07-15 | 293050 | 293920 | 285690 | 872.66 | 693.97 | 680.81 | 1.3748 | 1.3748 | 293050
2020-07-16 | 327760 | 327110 | 327570 | 982.44 | 726.2 | 704.53 | 1.4307 | 1.4307 | 327760
2020-07-17 | 303330 | 302760 | 307490 | 913.58 | 673.06 | 663.67 | 1.3367 | 1.3367 | 303330
2020-07-18 | 325350 | 320900 | 306860 | 953.11 | 689.85 | 674.9 | 1.3647 | 1.3647 | 325350
2020-07-19 | 330270 | 327690 | 323150 | 981.11 | 764.9 | 747.5 | 1.5124 | 1.5124 | 330270
2020-07-20 | 316990 | 315170 | 305350 | 937.51 | 751.9 | 732.03 | 1.4839 | 1.4839 | 316990
2020-07-21 | 328700 | 327710 | 327570 | 983.98 | 816.13 | 788.21 | 1.6043 | 1.6043 | 328700
2020-07-22 | 332830 | 332700 | 331840 | 997.37 | 916.65 | 876.9 | 1.7936 | 1.7936 | 332830
2020-07-23 | 302400 | 315380 | 308710 | 926.49 | 806.99 | 776.28 | 1.5833 | 1.5833 | 302400
2020-07-24 | 292900 | 283700 | 273060 | 849.66 | 685.54 | 665.55 | 1.3511 | 1.3511 | 292900
2020-07-25 | 293000 | 289280 | 298400 | 880.68 | 777.59 | 749.54 | 1.5271 | 1.5271 | 293000
2020-07-26 | 281740 | 286980 | 299500 | 868.22 | 679.22 | 659.11 | 1.3383 | 1.3383 | 281740
2020-07-27 | 320090 | 314230 | 249330 | 883.65 | 684.04 | 660.02 | 1.3441 | 1.3441 | 320090
2020-07-28 | 288770 | 300320 | 291060 | 880.15 | 723.3 | 697.86 | 1.4212 | 1.4212 | 288770
2020-07-29 | 304200 | 305630 | 286840 | 896.67 | 839.72 | 806.43 | 1.6462 | 1.6462 | 304200
2020-07-30 | 321640 | 319220 | 293930 | 934.79 | 1006.03 | 954.54 | 1.9606 | 1.9606 | 321640
2020-07-31 | 329060 | 329110 | 295400 | 953.57 | 922.65 | 879.44 | 1.8021 | 1.8021 | 329060
| 9827690 | 9803730 | 9604160 | 29235.58 | 23331.49 | 22506.05 | 45.8375 | 45.8375 | 9827690
2020-08-01 | 324100 | 321440 | 323350 | 968.89 | 838.36 | 806.89 | 1.6452 | 1.6452 | 324100
2020-08-02 | 280 | 160 | 200 | 0.64 | 347.15 | 363.08 | 0.71023 | 0.71023 | 280
2020-08-03 | 135620 | 140150 | 139400 | 415.17 | 602.86 | 587.25 | 1.1901 | 1.1901 | 135620
2020-08-04 | 322980 | 308590 | 298300 | 929.87 | 877.1 | 836.82 | 1.7139 | 1.7139 | 322980
2020-08-05 | 302620 | 295630 | 257440 | 855.69 | 908.58 | 857.75 | 1.7663 | 1.7663 | 302620
2020-08-06 | 316690 | 316350 | 285460 | 918.5 | 840.57 | 794.8 | 1.6354 | 1.6354 | 316690
2020-08-07 | 294750 | 284610 | 282140 | 861.5 | 833.95 | 784.67 | 1.6186 | 1.6186 | 294750
2020-08-08 | 300480 | 299730 | 275960 | 876.17 | 777 | 738.73 | 1.5157 | 1.5157 | 300480
2020-08-09 | 307740 | 276290 | 309750 | 893.78 | 810.51 | 778.48 | 1.589 | 1.589 | 307740
2020-08-10 | 320470 | 319150 | 311780 | 951.4 | 889.28 | 847.19 | 1.7365 | 1.7365 | 320470
2020-08-11 | 329960 | 329790 | 324420 | 984.17 | 826.87 | 785.73 | 1.6126 | 1.6126 | 329960
2020-08-12 | 315540 | 312770 | 302380 | 930.69 | 734.25 | 706.06 | 1.4403 | 1.4403 | 315540
2020-08-13 | 301710 | 298150 | 277500 | 877.36 | 752.09 | 730.32 | 1.4824 | 1.4824 | 301710
2020-08-14 | 321960 | 285780 | 323580 | 931.32 | 756.84 | 734.55 | 1.4914 | 1.4914 | 321960
2020-08-15 | 318620 | 313650 | 306180 | 938.45 | 679.53 | 665.73 | 1.3453 | 1.3453 | 318620
2020-08-16 | 303710 | 297430 | 285370 | 886.51 | 660.29 | 648.09 | 1.3084 | 1.3084 | 303710
2020-08-17 | 301120 | 297310 | 273780 | 872.21 | 660.25 | 646.66 | 1.3069 | 1.3069 | 301120
2020-08-18 | 277100 | 279620 | 270390 | 827.11 | 665.67 | 652.36 | 1.318 | 1.318 | 277100
2020-08-19 | 250500 | 242090 | 236160 | 728.75 | 662.23 | 652 | 1.3142 | 1.3142 | 250500
2020-08-20 | 318130 | 174470 | 315400 | 808 | 780.91 | 762.26 | 1.5432 | 1.5432 | 318130
2020-08-21 | 335760 | 333920 | 336020 | 1005.7 | 896.81 | 863.04 | 1.7599 | 1.7599 | 335760
2020-08-22 | 321130 | 326510 | 328310 | 975.95 | 919.13 | 884 | 1.8031 | 1.8031 | 321130
2020-08-23 | 325090 | 251750 | 323320 | 900.16 | 929.77 | 914.73 | 1.8445 | 1.8445 | 325090
2020-08-24 | 313410 | 320070 | 308250 | 941.73 | 833.24 | 772.71 | 1.6059 | 1.6059 | 313410
2020-08-25 | 329650 | 328410 | 292590 | 950.65 | 779.47 | 771.97 | 1.5514 | 1.5514 | 329650
2020-08-26 | 334820 | 334320 | 334120 | 1003.26 | 955.45 | 915.91 | 1.8714 | 1.8714 | 334820
2020-08-27 | 335320 | 334270 | 335350 | 1004.94 | 954.35 | 916.77 | 1.8711 | 1.8711 | 335320
2020-08-28 | 281270 | 290480 | 290780 | 862.53 | 907.39 | 874.79 | 1.7822 | 1.7822 | 281270
2020-08-29 | 335610 | 334780 | 335650 | 1006.04 | 1023.37 | 971.32 | 1.9947 | 1.9947 | 335610
2020-08-30 | 335010 | 334110 | 334980 | 1004.1 | 897.98 | 866.11 | 1.7641 | 1.7641 | 335010
2020-08-31 | 335400 | 336510 | 335270 | 1007.18 | 851.44 | 822.89 | 1.6743 | 1.6743 | 335400
| 9246550 | 8918290 | 8953580 | 27118.42 | 24852.69 | 23953.66 | 48.8064 | 48.8064 | 9246550
2020-09-01 | 334960 | 336030 | 335550 | 1006.54 | 713.72 | 701.77 | 1.4155 | 1.4155 | 334960
2020-09-02 | 331960 | 333400 | 332220 | 997.58 | 728.54 | 713.2 | 1.4417 | 1.4417 | 331960
2020-09-03 | 326820 | 322990 | 295980 | 945.79 | 743.14 | 729.56 | 1.4727 | 1.4727 | 326820
2020-09-04 | 316540 | 315950 | 261470 | 893.96 | 844.34 | 819.42 | 1.6638 | 1.6638 | 316540
2020-09-05 | 289830 | 279060 | 272940 | 841.83 | 901.45 | 867.46 | 1.7689 | 1.7689 | 289830
2020-09-06 | 294340 | 270710 | 247240 | 812.29 | 825.44 | 802.56 | 1.628 | 1.628 | 294340
2020-09-07 | 309050 | 272920 | 249200 | 831.17 | 844.83 | 815.76 | 1.6606 | 1.6606 | 309050
2020-09-08 | 248340 | 262100 | 241950 | 752.39 | 719.23 | 707.07 | 1.4263 | 1.4263 | 248340
2020-09-09 | 277310 | 147220 | 273610 | 698.14 | 681.28 | 672.91 | 1.3542 | 1.3542 | 277310
2020-09-10 | 335130 | 14620 | 331100 | 680.85 | 622.32 | 617.08 | 1.2394 | 1.2394 | 335130
2020-09-11 | 325130 | 0 | 328700 | 653.83 | 594.3 | 590.86 | 1.1852 | 1.1852 | 325130
2020-09-12 | 319500 | 0 | 319200 | 638.7 | 590.19 | 587.74 | 1.1779 | 1.1779 | 319500
2020-09-13 | 311620 | 0 | 305230 | 616.85 | 576.07 | 578.85 | 1.1549 | 1.1549 | 311620
2020-09-14 | 303730 | 0 | 291810 | 595.54 | 586.78 | 583.51 | 1.1703 | 1.1703 | 303730
2020-09-15 | 313670 | 0 | 252610 | 566.28 | 591.13 | 585.75 | 1.1769 | 1.1769 | 313670
2020-09-16 | 314720 | 0 | 231980 | 546.7 | 587.64 | 584.9 | 1.1725 | 1.1725 | 314720
2020-09-17 | 314130 | 0 | 216830 | 530.96 | 583.34 | 581.18 | 1.1645 | 1.1645 | 314130
2020-09-18 | 268320 | 0 | 241980 | 510.3 | 581.84 | 579.52 | 1.1614 | 1.1614 | 268320
2020-09-19 | 252240 | 0 | 238420 | 490.66 | 570.65 | 569.74 | 1.1404 | 1.1404 | 252240
2020-09-20 | 238030 | 0 | 217020 | 455.05 | 566.51 | 567.1 | 1.1336 | 1.1336 | 238030
2020-09-21 | 242660 | 0 | 194280 | 436.94 | 572.75 | 571.48 | 1.1442 | 1.1442 | 242660
2020-09-22 | 154380 | 41650 | 222500 | 418.53 | 597.15 | 598.32 | 1.1955 | 1.1955 | 154380
2020-09-23 | 191490 | 0 | 173900 | 365.39 | 554.51 | 547.82 | 1.1023 | 1.1023 | 191490
2020-09-24 | 203630 | 0 | 196670 | 400.3 | 568.09 | 575.78 | 1.1439 | 1.1439 | 203630
2020-09-25 | 140580 | 0 | 229450 | 370.03 | 545.24 | 570.15 | 1.1154 | 1.1154 | 140580
2020-09-26 | 115800 | 15070 | 238010 | 368.88 | 576.33 | 582.03 | 1.1584 | 1.1584 | 115800
2020-09-27 | 77580 | 0 | 271640 | 349.22 | 543.19 | 555.87 | 1.0991 | 1.0991 | 77580
2020-09-28 | 41750 | 0 | 311080 | 352.83 | 523.35 | 536.33 | 1.0597 | 1.0597 | 41750
2020-09-29 | 30980 | 0 | 323210 | 354.19 | 523.09 | 537.24 | 1.0603 | 1.0603 | 30980
2020-09-30 | 34270 | 0 | 318280 | 352.55 | 536.28 | 546.62 | 1.0829 | 1.0829 | 34270
| 7258490 | 2611720 | 7964060 | 17834.27 | 18992.72 | 18877.58 | 37.8703 | 37.8703 | 7258490
2020-10-01 | 34510 | 0 | 308670 | 343.18 | 582.22 | 589.43 | 1.1716 | 1.1716 | 34510
2020-10-02 | 31650 | 0 | 302230 | 333.88 | 569.2 | 580.42 | 1.1496 | 1.1496 | 31650
2020-10-03 | 32460 | 0 | 300040 | 332.5 | 550.21 | 561.46 | 1.1117 | 1.1117 | 32460
2020-10-04 | 32850 | 0 | 297080 | 329.93 | 567.83 | 579.59 | 1.1474 | 1.1474 | 32850
2020-10-05 | 29300 | 0 | 284240 | 313.54 | 571.03 | 581.05 | 1.1521 | 1.1521 | 29300
2020-10-06 | 59080 | 0 | 248280 | 307.36 | 581.34 | 590.17 | 1.1715 | 1.1715 | 59080
2020-10-07 | 106480 | 0 | 198410 | 304.89 | 552.92 | 564.85 | 1.1178 | 1.1178 | 106480
2020-10-08 | 265870 | 0 | 24590 | 290.46 | 583.65 | 595.86 | 1.1795 | 1.1795 | 265870
2020-10-09 | 134140 | 0 | 147360 | 281.5 | 582.74 | 592.02 | 1.1748 | 1.1748 | 134140
2020-10-10 | 0 | 0 | 290870 | 290.87 | 563.19 | 573.83 | 1.137 | 1.137 | 0
2020-10-11 | 33880 | 0 | 249650 | 283.53 | 558.73 | 568.87 | 1.1276 | 1.1276 | 33880
2020-10-12 | 29940 | 0 | 245440 | 275.38 | 576.05 | 584.3 | 1.1603 | 1.1603 | 29940
2020-10-13 | 29320 | 0 | 239020 | 268.34 | 601.99 | 604.53 | 1.2065 | 1.2065 | 29320
2020-10-14 | 34140 | 0 | 230900 | 265.04 | 608.88 | 610.48 | 1.2194 | 1.2194 | 34140
2020-10-15 | 32590 | 0 | 225890 | 258.48 | 602.76 | 601.41 | 1.2042 | 1.2042 | 32590
2020-10-16 | 34160 | 0 | 219090 | 253.25 | 597.56 | 596.74 | 1.1943 | 1.1943 | 34160
2020-10-17 | 36010 | 0 | 216080 | 252.09 | 609.58 | 608.46 | 1.218 | 1.218 | 36010
2020-10-18 | 33970 | 0 | 211270 | 245.24 | 578.55 | 588.87 | 1.1674 | 1.1674 | 33970
2020-10-19 | 32650 | 0 | 202440 | 235.09 | 584.21 | 591.87 | 1.1761 | 1.1761 | 32650
2020-10-20 | 11090 | 0 | 202830 | 213.92 | 565.13 | 564.96 | 1.1301 | 1.1301 | 11090
2020-10-21 | 29990 | 0 | 195250 | 225.24 | 627.16 | 623.09 | 1.2503 | 1.2503 | 29990
2020-10-22 | 0 | 0 | 217490 | 217.49 | 604.14 | 609.81 | 1.2139 | 1.2139 | 0
2020-10-23 | 34170 | 0 | 174280 | 208.45 | 559.92 | 573.17 | 1.1331 | 1.1331 | 34170
2020-10-24 | 33210 | 0 | 169390 | 202.6 | 962.08 | 260.12 | 1.2222 | 1.2222 | 33210
2020-10-25 | 33480 | 0 | 163460 | 196.94 | 1215.88 | 54.84 | 1.2707 | 1.2707 | 33480
2020-10-26 | 33210 | 0 | 156230 | 189.44 | 1249.99 | 50.63 | 1.3006 | 1.3006 | 33210
2020-10-27 | 36730 | 0 | 153910 | 190.64 | 1208.1 | 46.85 | 1.2549 | 1.2549 | 36730
2020-10-28 | 36110 | 0 | 150650 | 186.76 | 1220 | 48 | 1.268 | 1.268 | 36110
2020-10-29 | 36410 | 0 | 147930 | 184.34 | 1145.93 | 44.7 | 1.1906 | 1.1906 | 36410
2020-10-30 | 37440 | 0 | 140840 | 178.28 | 1172 | 46 | 1.218 | 1.218 | 37440
2020-10-31 | 36930 | 0 | 140090 | 177.02 | 1182 | 47 | 1.229 | 1.229 | 36930
| 1381770 | 0 | 6453900 | 7835.67 | 22734.97 | 14133.38 | 36.8684 | 36.8684 | 1381770
2020-11-01 | 31870 | 0 | 138710 | 170.58 | 1104.77 | 51.15 | 1.1559 | 1.1559 | 31870
2020-11-02 | 20710 | 0 | 141480 | 162.19 | 1166.42 | 49.24 | 1.2157 | 1.2157 | 20710
2020-11-03 | 0 | 0 | 182640 | 182.64 | 1243.56 | 49.41 | 1.293 | 1.293 | 0
2020-11-04 | 0 | 0 | 158070 | 158.07 | 1227.5 | 44.97 | 1.2725 | 1.2725 | 0
2020-11-05 | 0 | 0 | 152250 | 152.25 | 1224.16 | 43.25 | 1.2674 | 1.2674 | 0
2020-11-06 | 0 | 0 | 148790 | 148.79 | 1218.03 | 46.5 | 1.2645 | 1.2645 | 0
2020-11-07 | 0 | 0 | 145470 | 145.47 | 1229.88 | 46.33 | 1.2762 | 1.2762 | 0
2020-11-08 | 0 | 0 | 144120 | 144.12 | 1240.86 | 51.8 | 1.2927 | 1.2927 | 0
2020-11-09 | 0 | 0 | 142760 | 142.76 | 1243.77 | 45.16 | 1.2889 | 1.2889 | 0
2020-11-10 | 0 | 0 | 141270 | 141.27 | 1158.91 | 44.56 | 1.2035 | 1.2035 | 0
2020-11-11 | 0 | 0 | 140450 | 140.45 | 1181.43 | 42.1 | 1.2235 | 1.2235 | 0
2020-11-12 | 0 | 3710 | 128270 | 131.98 | 1156.36 | 40.9 | 1.1973 | 1.1973 | 0
2020-11-13 | 0 | 0 | 130150 | 130.15 | 1098.57 | 44.76 | 1.1433 | 1.1433 | 0
2020-11-14 | 0 | 0 | 130530 | 130.53 | 1117.3 | 54.5 | 1.1718 | 1.1718 | 0
2020-11-15 | 0 | 0 | 127840 | 127.84 | 1117.94 | 56.69 | 1.1746 | 1.1746 | 0
2020-11-16 | 0 | 9770 | 122720 | 132.49 | 1230.46 | 48.87 | 1.2793 | 1.2793 | 0
2020-11-17 | 0 | 0 | 128920 | 128.92 | 1114.36 | 40.96 | 1.1553 | 1.1553 | 0
2020-11-18 | 0 | 0 | 123040 | 123.04 | 1050.36 | 38.22 | 1.0886 | 1.0886 | 0
2020-11-19 | 0 | 0 | 121890 | 121.89 | 1204.16 | 39.82 | 1.244 | 1.244 | 0
2020-11-20 | 0 | 0 | 113820 | 113.82 | 1135.6 | 39.18 | 1.1748 | 1.1748 | 0
2020-11-21 | 0 | 0 | 110600 | 110.6 | 1168.08 | 39.97 | 1.208 | 1.208 | 0
2020-11-22 | 0 | 0 | 107880 | 107.88 | 1082.38 | 40.83 | 1.1232 | 1.1232 | 0
2020-11-23 | 0 | 5270 | 101460 | 106.73 | 1182.33 | 41.07 | 1.2234 | 1.2234 | 0
2020-11-24 | 0 | 36250 | 72490 | 108.74 | 1308.82 | 41.52 | 1.3503 | 1.3503 | 0
2020-11-25 | 0 | 35430 | 82960 | 118.39 | 1528.99 | 39.18 | 1.5682 | 1.5682 | 0
2020-11-26 | 0 | 13520 | 112410 | 125.93 | 734.21 | 625.19 | 1.3594 | 1.3594 | 0
2020-11-27 | 0 | 39660 | 86670 | 126.33 | 40.4 | 1094.4 | 1.1348 | 1.1348 | 0
2020-11-28 | 0 | 40670 | 93460 | 134.13 | 42.58 | 1120.03 | 1.1626 | 1.1626 | 0
2020-11-29 | 0 | 39590 | 100000 | 139.59 | 42.87 | 1126.43 | 1.1693 | 1.1693 | 0
2020-11-30 | 0 | 36540 | 93360 | 129.9 | 37.08 | 1028.72 | 1.0658 | 1.0658 | 0
| 52580 | 260410 | 3724480 | 4037.47 | 30632.14 | 6115.71 | 36.7478 | 36.7478 | 52580
2020-12-01 | 0 | 37750 | 91660 | 129.41 | 40.21 | 1084.05 | 1.1243 | 1.1243 | 0
2020-12-02 | 0 | 28200 | 91960 | 120.16 | 38.53 | 1131.94 | 1.1705 | 1.1705 | 0
2020-12-03 | 0 | 38850 | 89960 | 128.81 | 37.96 | 1120.68 | 1.1586 | 1.1586 | 0
2020-12-04 | 0 | 36070 | 85770 | 121.84 | 37.68 | 1190.65 | 1.2283 | 1.2283 | 0
2020-12-05 | 0 | 37630 | 81230 | 118.86 | 39.54 | 1052.24 | 1.0918 | 1.0918 | 0
2020-12-06 | 0 | 37800 | 80120 | 117.92 | 40.66 | 941.34 | 0.982 | 0.982 | 0
2020-12-07 | 0 | 37540 | 79060 | 116.6 | 39.85 | 988.27 | 1.0281 | 1.0281 | 0
2020-12-08 | 0 | 39720 | 77650 | 117.37 | 39.6 | 1040.53 | 1.0801 | 1.0801 | 0
2020-12-09 | 0 | 40700 | 91850 | 132.55 | 38.94 | 992.01 | 1.031 | 1.031 | 0
2020-12-10 | 0 | 40450 | 95480 | 135.93 | 41.92 | 1094.01 | 1.1359 | 1.1359 | 0
2020-12-11 | 0 | 35040 | 90500 | 125.54 | 997.63 | 373.31 | 1.3709 | 1.3709 | 0
2020-12-12 | 0 | 39020 | 99700 | 138.72 | 538.22 | 795.36 | 1.3336 | 1.3336 | 0
2020-12-13 | 0 | 34880 | 86170 | 121.05 | 40.46 | 1259.21 | 1.2997 | 1.2997 | 0
2020-12-14 | 0 | 38530 | 81080 | 119.61 | 38.78 | 1311.57 | 1.3503 | 1.3503 | 0
2020-12-15 | 0 | 39300 | 76530 | 115.83 | 37.26 | 1272.11 | 1.3094 | 1.3094 | 0
2020-12-16 | 0 | 20080 | 32740 | 52.82 | 27.52 | 802.14 | 0.82966 | 0.82966 | 0
2020-12-17 | 0 | 0 | 0 | 0 | 26.99 | 616.87 | 0.64386 | 0.64386 | 0
2020-12-18 | 0 | 0 | 0 | 0 | 33.24 | 876.98 | 0.91022 | 0.91022 | 0
2020-12-19 | 0 | 0 | 0 | 0 | 32.95 | 1162.27 | 1.1952 | 1.1952 | 0
2020-12-20 | 0 | 0 | 0 | 0 | 37.24 | 1152.91 | 1.1901 | 1.1901 | 0
2020-12-21 | 0 | 0 | 0 | 0 | 36.7 | 940.39 | 0.97709 | 0.97709 | 0
2020-12-22 | 0 | 0 | 0 | 0 | 37.95 | 1111.79 | 1.1497 | 1.1497 | 0
2020-12-23 | 0 | 0 | 0 | 0 | 35.48 | 1665.38 | 1.7009 | 1.7009 | 0
2020-12-24 | 0 | 0 | 0 | 0 | 36.75 | 1710 | 1.7468 | 1.7468 | 0
2020-12-25 | 0 | 0 | 0 | 0 | 36.53 | 1681.85 | 1.7184 | 1.7184 | 0
2020-12-26 | 0 | 19180 | 36530 | 55.71 | 37.92 | 1543.4 | 1.5813 | 1.5813 | 0
2020-12-27 | 0 | 34770 | 68510 | 103.28 | 40.03 | 1035.34 | 1.0754 | 1.0754 | 0
2020-12-28 | 0 | 40040 | 68670 | 108.71 | 36.09 | 1086.57 | 1.1227 | 1.1227 | 0
2020-12-29 | 0 | 39380 | 64620 | 104 | 32.84 | 1028.2 | 1.061 | 1.061 | 0
2020-12-30 | 0 | 44450 | 57140 | 101.59 | 40.31 | 1004.56 | 1.0449 | 1.0449 | 0
2020-12-31 | 0 | 40300 | 60120 | 100.42 | 40.49 | 963.84 | 1.0043 | 1.0043 | 0
| 0 | 799680 | 1687050 | 2486.73 | 2616.27 | 34029.77 | 36.646 | 36.646 | 0
2021-01-01 | 0 | 40440 | 59760 | 100.2 | 30.52 | 994.07 | 1.0246 | 1.0246 | 0
2021-01-02 | 0 | 40280 | 59410 | 99.69 | 34.94 | 1010.82 | 1.0458 | 1.0458 | 0
2021-01-03 | 0 | 38360 | 63030 | 101.39 | 43.08 | 940.74 | 0.98382 | 0.98382 | 0
2021-01-04 | 0 | 37730 | 62700 | 100.43 | 27.5 | 938.79 | 0.96629 | 0.96629 | 0
2021-01-05 | 0 | 38280 | 64370 | 102.65 | 33.98 | 942.14 | 0.97612 | 0.97612 | 0
2021-01-06 | 0 | 39350 | 67010 | 106.36 | 37.25 | 959.05 | 0.9963 | 0.9963 | 0
2021-01-07 | 0 | 38860 | 68580 | 107.44 | 35.86 | 996.66 | 1.0325 | 1.0325 | 0
2021-01-08 | 0 | 38090 | 64220 | 102.31 | 35.82 | 995.72 | 1.0315 | 1.0315 | 0
2021-01-09 | 0 | 37250 | 62450 | 99.7 | 35.42 | 955.37 | 0.99079 | 0.99079 | 0
2021-01-10 | 0 | 36710 | 62770 | 99.48 | 36.74 | 1007.91 | 1.0446 | 1.0446 | 0
2021-01-11 | 0 | 35300 | 56420 | 91.72 | 35.04 | 1038.29 | 1.0733 | 1.0733 | 0
2021-01-12 | 53110 | 17560 | 24890 | 95.56 | 35.96 | 926.45 | 0.96241 | 0.96241 | 53110
2021-01-13 | 59590 | 36850 | 0 | 96.44 | 35.62 | 942.58 | 0.9782 | 0.9782 | 59590
2021-01-14 | 60120 | 39240 | 0 | 99.36 | 37.58 | 935.01 | 0.97259 | 0.97259 | 60120
2021-01-15 | 61750 | 40360 | 0 | 102.11 | 36.57 | 944.68 | 0.98125 | 0.98125 | 61750
2021-01-16 | 66230 | 40130 | 0 | 106.36 | 35.36 | 941.26 | 0.97662 | 0.97662 | 66230
2021-01-17 | 60480 | 41040 | 0 | 101.52 | 37.87 | 935.23 | 0.9731 | 0.9731 | 60480
2021-01-18 | 63500 | 38090 | 0 | 101.59 | 36.37 | 1005.82 | 1.0422 | 1.0422 | 63500
2021-01-19 | 61340 | 40230 | 0 | 101.57 | 36.52 | 1007.98 | 1.0445 | 1.0445 | 61340
2021-01-20 | 60110 | 39280 | 0 | 99.39 | 34.54 | 958.09 | 0.99263 | 0.99263 | 60110
2021-01-21 | 59780 | 38050 | 0 | 97.83 | 33.93 | 974.65 | 1.0086 | 1.0086 | 59780
2021-01-22 | 59530 | 39370 | 0 | 98.9 | 32.24 | 1059.3 | 1.0915 | 1.0915 | 59530
2021-01-23 | 59690 | 39930 | 0 | 99.62 | 34.01 | 1059.55 | 1.0936 | 1.0936 | 59690
2021-01-24 | 59370 | 40220 | 0 | 99.59 | 35.96 | 1026.36 | 1.0623 | 1.0623 | 59370
2021-01-25 | 61440 | 39840 | 0 | 101.28 | 31.59 | 1054.18 | 1.0858 | 1.0858 | 61440
2021-01-26 | 61540 | 40280 | 0 | 101.82 | 36.7 | 997.18 | 1.0339 | 1.0339 | 61540
2021-01-27 | 60300 | 39090 | 0 | 99.39 | 33.82 | 955.77 | 0.98959 | 0.98959 | 60300
2021-01-28 | 58610 | 39400 | 0 | 98.01 | 34.02 | 942.83 | 0.97685 | 0.97685 | 58610
2021-01-29 | 57080 | 39540 | 0 | 96.62 | 29.76 | 926.12 | 0.95588 | 0.95588 | 57080
2021-01-30 | 56880 | 39680 | 0 | 96.56 | 30.68 | 909.14 | 0.93982 | 0.93982 | 56880
2021-01-31 | 55350 | 39610 | 0 | 94.96 | 31.08 | 917.42 | 0.9485 | 0.9485 | 55350
| 1195800 | 1188440 | 715610 | 3099.85 | 1076.33 | 30199.16 | 31.2755 | 31.2755 | 1195800
2021-02-01 | 53990 | 39750 | 0 | 93.74 | 31.27 | 894.45 | 0.92572 | 0.92572 | 53990
2021-02-02 | 54070 | 39780 | 0 | 93.85 | 31.96 | 858.08 | 0.89004 | 0.89004 | 54070
2021-02-03 | 55190 | 39800 | 0 | 94.99 | 30.61 | 794.24 | 0.82485 | 0.82485 | 55190
2021-02-04 | 56480 | 33820 | 0 | 90.3 | 35.86 | 925.48 | 0.96134 | 0.96134 | 56480
2021-02-05 | 59220 | 40390 | 0 | 99.61 | 33.01 | 944.7 | 0.97771 | 0.97771 | 59220
2021-02-06 | 56120 | 37190 | 0 | 93.31 | 48.28 | 875.3 | 0.92358 | 0.92358 | 56120
2021-02-07 | 38150 | 35540 | 0 | 73.69 | 478.36 | 508.05 | 0.98641 | 0.98641 | 38150
2021-02-08 | 51500 | 43770 | 0 | 95.27 | 507.44 | 519.26 | 1.0267 | 1.0267 | 51500
2021-02-09 | 55270 | 40360 | 0 | 95.63 | 502.56 | 513.28 | 1.0158 | 1.0158 | 55270
2021-02-10 | 55300 | 34100 | 0 | 89.4 | 401.84 | 427.51 | 0.82935 | 0.82935 | 55300
2021-02-11 | 60180 | 34700 | 0 | 94.88 | 637.57 | 223.78 | 0.86135 | 0.86135 | 60180
2021-02-12 | 63160 | 40460 | 0 | 103.62 | 28.64 | 956.96 | 0.9856 | 0.9856 | 63160
2021-02-13 | 62080 | 36720 | 0 | 98.8 | 36.75 | 1002.27 | 1.039 | 1.039 | 62080
2021-02-14 | 58260 | 38790 | 0 | 97.05 | 36.63 | 951.26 | 0.98789 | 0.98789 | 58260
2021-02-15 | 56480 | 40650 | 0 | 97.13 | 35.87 | 952.38 | 0.98825 | 0.98825 | 56480
2021-02-16 | 56120 | 39150 | 0 | 95.27 | 33.48 | 819.24 | 0.85272 | 0.85272 | 56120
2021-02-17 | 22470 | 51130 | 18950 | 92.55 | 32.05 | 856.28 | 0.88833 | 0.88833 | 22470
2021-02-18 | 53680 | 19780 | 19450 | 92.91 | 33.13 | 764.26 | 0.79739 | 0.79739 | 53680
2021-02-19 | 52900 | 39820 | 0 | 92.72 | 31.58 | 846.08 | 0.87766 | 0.87766 | 52900
2021-02-20 | 53500 | 39490 | 0 | 92.99 | 34.37 | 852.03 | 0.8864 | 0.8864 | 53500
2021-02-21 | 54030 | 40200 | 0 | 94.23 | 35.56 | 829.91 | 0.86547 | 0.86547 | 54030
2021-02-22 | 55800 | 40550 | 0 | 96.35 | 34.95 | 827.98 | 0.86293 | 0.86293 | 55800
2021-02-23 | 69830 | 80 | 11430 | 81.34 | 34.32 | 918.65 | 0.95297 | 0.95297 | 69830
2021-02-24 | 66030 | 17740 | 20470 | 104.24 | 33.35 | 828.68 | 0.86203 | 0.86203 | 66030
2021-02-25 | 60090 | 31830 | 0 | 91.92 | 32.61 | 841.22 | 0.87383 | 0.87383 | 60090
2021-02-26 | 59920 | 35650 | 0 | 95.57 | 32.76 | 820.14 | 0.8529 | 0.8529 | 59920
2021-02-27 | 66990 | 33400 | 0 | 100.39 | 34.61 | 771.76 | 0.80637 | 0.80637 | 66990
2021-02-28 | 64770 | 40400 | 0 | 105.17 | 38.38 | 753.62 | 0.792 | 0.792 | 64770
| 1571580 | 1005040 | 70300 | 2646.92 | 3317.8 | 22076.85 | 25.3946 | 25.3946 | 1571580
2021-03-01 | 59270 | 39430 | 0 | 98.7 | 34.01 | 786.33 | 0.82034 | 0.82034 | 59270
2021-03-02 | 56390 | 38250 | 0 | 94.64 | 34.45 | 817.07 | 0.85152 | 0.85152 | 56390
2021-03-03 | 57200 | 39480 | 0 | 96.68 | 33.45 | 774.24 | 0.80769 | 0.80769 | 57200
2021-03-04 | 57060 | 39340 | 0 | 96.4 | 35.54 | 761.44 | 0.79698 | 0.79698 | 57060
2021-03-05 | 55260 | 37830 | 0 | 93.09 | 30.47 | 671.73 | 0.7022 | 0.7022 | 55260
2021-03-06 | 53650 | 38680 | 0 | 92.33 | 36.32 | 781.54 | 0.81786 | 0.81786 | 53650
2021-03-07 | 36790 | 21840 | 21780 | 80.41 | 12.34 | 760.68 | 0.77302 | 0.77302 | 36790
2021-03-08 | 35780 | 22660 | 23790 | 82.23 | 169.1 | 670.21 | 0.83931 | 0.83931 | 35780
2021-03-09 | 38270 | 22020 | 22220 | 82.51 | 649.64 | 197.25 | 0.84689 | 0.84689 | 38270
2021-03-10 | 40530 | 24830 | 25000 | 90.36 | 569.27 | 199.9 | 0.76917 | 0.76917 | 40530
2021-03-11 | 40220 | 24650 | 25050 | 89.92 | 514.8 | 223.41 | 0.73821 | 0.73821 | 40220
2021-03-12 | 47380 | 23780 | 20580 | 91.74 | 542 | 177.28 | 0.71928 | 0.71928 | 47380
2021-03-13 | 44300 | 24610 | 24740 | 93.65 | 373.57 | 547.33 | 0.9209 | 0.9209 | 44300
2021-03-14 | 43990 | 24220 | 24230 | 92.44 | 475.7 | 485.54 | 0.96124 | 0.96124 | 43990
2021-03-15 | 42820 | 24420 | 24330 | 91.57 | 454.88 | 468.51 | 0.92339 | 0.92339 | 42820
2021-03-16 | 44170 | 24320 | 24410 | 92.9 | 370.94 | 392.03 | 0.76297 | 0.76297 | 44170
2021-03-17 | 42980 | 23950 | 23940 | 90.87 | 384.12 | 417.49 | 0.80161 | 0.80161 | 42980
2021-03-18 | 42070 | 23810 | 24530 | 90.41 | 505.45 | 511.28 | 1.0167 | 1.0167 | 42070
2021-03-19 | 41820 | 24490 | 24820 | 91.13 | 394.46 | 423.28 | 0.81774 | 0.81774 | 41820
2021-03-20 | 41700 | 24620 | 24600 | 90.92 | 317.17 | 421.2 | 0.73837 | 0.73837 | 41700
2021-03-21 | 28810 | 24420 | 39370 | 92.6 | 430.81 | 455.91 | 0.88672 | 0.88672 | 28810
2021-03-22 | 34380 | 25340 | 61090 | 120.81 | 484.55 | 511.38 | 0.99593 | 0.99593 | 34380
2021-03-23 | 24660 | 24420 | 76790 | 125.87 | 490.02 | 518.91 | 1.0089 | 1.0089 | 24660
2021-03-24 | 26040 | 25980 | 77300 | 129.32 | 499.05 | 519.44 | 1.0185 | 1.0185 | 26040
2021-03-25 | 24670 | 24920 | 65400 | 114.99 | 461.83 | 483.76 | 0.94559 | 0.94559 | 24670
2021-03-26 | 25270 | 24900 | 59480 | 109.65 | 451.65 | 472.41 | 0.92406 | 0.92406 | 25270
2021-03-27 | 25470 | 25280 | 69220 | 119.97 | 471.14 | 488.92 | 0.96006 | 0.96006 | 25470
2021-03-28 | 26500 | 26150 | 87860 | 140.51 | 541.81 | 546.49 | 1.0883 | 1.0883 | 26500
2021-03-29 | 26660 | 26420 | 98920 | 152 | 529.18 | 544.89 | 1.0741 | 1.0741 | 26660
2021-03-30 | 26630 | 29970 | 98850 | 155.45 | 582.41 | 586.64 | 1.169 | 1.169 | 26630
2021-03-31 | 25060 | 24510 | 114910 | 164.48 | 487.02 | 515.92 | 1.0029 | 1.0029 | 25060
| 1215800 | 849540 | 1183210 | 3248.55 | 11367.15 | 16132.41 | 27.4996 | 27.4996 | 1215800
2021-04-01 | 12570 | 32910 | 118470 | 163.95 | 562.27 | 568.86 | 1.1311 | 1.1311 | 12570
2021-04-02 | 32470 | 35250 | 96620 | 164.34 | 448.99 | 474.65 | 0.92364 | 0.92364 | 32470
2021-04-03 | 62850 | 10400 | 70520 | 143.77 | 467.68 | 490.51 | 0.95819 | 0.95819 | 62850
2021-04-04 | 96360 | 35900 | 18530 | 150.79 | 456.21 | 484.11 | 0.94032 | 0.94032 | 96360
2021-04-05 | 97300 | 36220 | 18540 | 152.06 | 454.03 | 481.2 | 0.93523 | 0.93523 | 97300
2021-04-06 | 104260 | 35740 | 13450 | 153.45 | 518.59 | 532.69 | 1.0513 | 1.0513 | 104260
2021-04-07 | 149280 | 41300 | 13940 | 204.52 | 447.06 | 474.26 | 0.92132 | 0.92132 | 149280
2021-04-08 | 135140 | 39420 | 13690 | 188.25 | 507.5 | 517.67 | 1.0252 | 1.0252 | 135140
2021-04-09 | 90210 | 10710 | 64930 | 165.85 | 465.6 | 481.47 | 0.94707 | 0.94707 | 90210
2021-04-10 | 31000 | 29430 | 95970 | 156.4 | 607.6 | 591.94 | 1.1995 | 1.1995 | 31000
2021-04-11 | 13530 | 37900 | 106350 | 157.78 | 462.07 | 477.51 | 0.93958 | 0.93958 | 13530
2021-04-12 | 13280 | 37220 | 106970 | 157.47 | 469.41 | 484.95 | 0.95436 | 0.95436 | 13280
2021-04-13 | 13220 | 37140 | 103980 | 154.34 | 502.03 | 504.45 | 1.0065 | 1.0065 | 13220
2021-04-14 | 13270 | 38340 | 106870 | 158.48 | 453.12 | 465.77 | 0.91889 | 0.91889 | 13270
2021-04-15 | 26710 | 26320 | 104810 | 157.84 | 454.01 | 468.56 | 0.92257 | 0.92257 | 26710
2021-04-16 | 25630 | 25780 | 110540 | 161.95 | 505.86 | 512.64 | 1.0185 | 1.0185 | 25630
2021-04-17 | 27030 | 26790 | 115680 | 169.5 | 482.51 | 496.44 | 0.97895 | 0.97895 | 27030
2021-04-18 | 29180 | 27240 | 156300 | 212.72 | 502.85 | 515.86 | 1.0187 | 1.0187 | 29180
2021-04-19 | 27070 | 26770 | 116390 | 170.23 | 466.24 | 477.77 | 0.94401 | 0.94401 | 27070
2021-04-20 | 28400 | 26280 | 151480 | 206.16 | 514.13 | 517.91 | 1.032 | 1.032 | 28400
2021-04-21 | 27850 | 26710 | 201730 | 256.29 | 533.31 | 538.05 | 1.0714 | 1.0714 | 27850
2021-04-22 | 26870 | 26590 | 222750 | 276.21 | 541.79 | 549.66 | 1.0915 | 1.0915 | 26870
2021-04-23 | 26870 | 26700 | 235180 | 288.75 | 526.33 | 539.92 | 1.0662 | 1.0662 | 26870
2021-04-24 | 39110 | 50110 | 283020 | 372.24 | 540.4 | 549.14 | 1.0895 | 1.0895 | 39110
2021-04-25 | 37130 | 49280 | 251940 | 338.35 | 542.04 | 551.55 | 1.0936 | 1.0936 | 37130
2021-04-26 | 36590 | 103000 | 259970 | 399.56 | 554.49 | 557.37 | 1.1119 | 1.1119 | 36590
2021-04-27 | 100240 | 179450 | 162730 | 442.42 | 588.82 | 596.69 | 1.1855 | 1.1855 | 100240
2021-04-28 | 35130 | 159400 | 226770 | 421.3 | 686.3 | 670.43 | 1.3567 | 1.3567 | 35130
2021-04-29 | 195750 | 71980 | 91180 | 358.91 | 533.73 | 546.01 | 1.0797 | 1.0797 | 195750
2021-04-30 | 230460 | 68420 | 46360 | 345.24 | 506.66 | 519.99 | 1.0266 | 1.0266 | 230460
| 1784760 | 1378700 | 3685660 | 6849.12 | 15301.63 | 15638.03 | 30.9397 | 30.9397 | 1784760
2021-05-01 | 189250 | 72980 | 60520 | 322.75 | 525.45 | 541.71 | 1.0672 | 1.0672 | 189250
2021-05-02 | 260140 | 37130 | 46410 | 343.68 | 520.88 | 540.32 | 1.0612 | 1.0612 | 260140
2021-05-03 | 237440 | 57650 | 51730 | 346.82 | 602.48 | 598.61 | 1.2011 | 1.2011 | 237440
2021-05-04 | 197370 | 94520 | 84050 | 375.94 | 589.6 | 595.15 | 1.1847 | 1.1847 | 197370
2021-05-05 | 213980 | 40660 | 134290 | 388.93 | 595.59 | 600.02 | 1.1956 | 1.1956 | 213980
2021-05-06 | 217350 | 38540 | 134310 | 390.2 | 696.39 | 692.69 | 1.3891 | 1.3891 | 217350
2021-05-07 | 202150 | 44120 | 152700 | 398.97 | 730.55 | 710.09 | 1.4406 | 1.4406 | 202150
2021-05-08 | 226490 | 41770 | 142250 | 410.51 | 625.24 | 624.41 | 1.2496 | 1.2496 | 226490
2021-05-09 | 252250 | 43170 | 102510 | 397.93 | 556.88 | 567.98 | 1.1249 | 1.1249 | 252250
2021-05-10 | 257220 | 40500 | 115840 | 413.56 | 575.07 | 578.08 | 1.1531 | 1.1531 | 257220
2021-05-11 | 191010 | 139440 | 107020 | 437.47 | 606.57 | 626.79 | 1.2334 | 1.2334 | 191010
2021-05-12 | 257250 | 39920 | 137910 | 435.08 | 585.84 | 682.22 | 1.2681 | 1.2681 | 257250
2021-05-13 | 186730 | 175110 | 81330 | 443.17 | 593.08 | 691.94 | 1.285 | 1.285 | 186730
2021-05-14 | 181820 | 19900 | 146770 | 348.49 | 548.47 | 642.45 | 1.1909 | 1.1909 | 181820
2021-05-15 | 146410 | 126570 | 28310 | 301.29 | 935.72 | 211.23 | 1.1469 | 1.1469 | 146410
2021-05-16 | 238280 | 29430 | 103720 | 371.43 | 1095.26 | 0 | 1.0953 | 1.0953 | 238280
2021-05-17 | 238450 | 79730 | 51580 | 369.76 | 1143.19 | 2.04 | 1.1452 | 1.1452 | 238450
2021-05-18 | 286820 | 40010 | 40220 | 367.05 | 1110.53 | 0.02 | 1.1105 | 1.1105 | 286820
2021-05-19 | 134170 | 56950 | 179360 | 370.48 | 1133.78 | 4.58 | 1.1384 | 1.1384 | 134170
2021-05-20 | 240450 | 47890 | 109970 | 398.31 | 1108.24 | 7.86 | 1.1161 | 1.1161 | 240450
2021-05-21 | 199370 | 45840 | 228520 | 473.73 | 1288.76 | 19.39 | 1.3082 | 1.3082 | 199370
2021-05-22 | 257920 | 42420 | 148950 | 449.29 | 809.97 | 363.32 | 1.1733 | 1.1733 | 257920
2021-05-23 | 292740 | 45210 | 121670 | 459.62 | 549.4 | 644.73 | 1.1941 | 1.1941 | 292740
2021-05-24 | 233730 | 19860 | 250330 | 503.92 | 583.15 | 681.72 | 1.2649 | 1.2649 | 233730
2021-05-25 | 280260 | 32680 | 141990 | 454.93 | 536.11 | 629.05 | 1.1652 | 1.1652 | 280260
2021-05-26 | 268160 | 39010 | 138430 | 445.6 | 548.99 | 641.46 | 1.1904 | 1.1904 | 268160
2021-05-27 | 286210 | 42530 | 138390 | 467.13 | 638.34 | 735.3 | 1.3736 | 1.3736 | 286210
2021-05-28 | 268280 | 60170 | 237510 | 565.96 | 686.51 | 784.58 | 1.4711 | 1.4711 | 268280
2021-05-29 | 285960 | 47010 | 266360 | 599.33 | 620.31 | 711.66 | 1.332 | 1.332 | 285960
2021-05-30 | 275050 | 45890 | 262750 | 583.69 | 582.72 | 676.85 | 1.2596 | 1.2596 | 275050
2021-05-31 | 265930 | 101620 | 198700 | 566.25 | 589.64 | 682.15 | 1.2718 | 1.2718 | 265930
| 7268640 | 1788230 | 4144400 | 13201.27 | 22312.71 | 15488.4 | 37.8011 | 37.8011 | 7268640
2021-06-01 | 246310 | 205160 | 58090 | 509.56 | 590.84 | 685.1 | 1.2759 | 1.2759 | 246310
2021-06-02 | 252620 | 229470 | 81890 | 563.98 | 598.14 | 693.48 | 1.2916 | 1.2916 | 252620
2021-06-03 | 257260 | 107790 | 199290 | 564.34 | 670.26 | 767.13 | 1.4374 | 1.4374 | 257260
2021-06-04 | 263900 | 97290 | 206370 | 567.56 | 622.05 | 711.28 | 1.3333 | 1.3333 | 263900
2021-06-05 | 246370 | 43200 | 270020 | 559.59 | 604.96 | 698.86 | 1.3038 | 1.3038 | 246370
2021-06-06 | 264150 | 46010 | 278080 | 588.24 | 602.61 | 694.77 | 1.2974 | 1.2974 | 264150
2021-06-07 | 166770 | 184360 | 280480 | 631.61 | 705.33 | 800.96 | 1.5063 | 1.5063 | 166770
2021-06-08 | 276880 | 217220 | 215460 | 709.56 | 769.23 | 867.04 | 1.6363 | 1.6363 | 276880
2021-06-09 | 274150 | 237520 | 280690 | 792.36 | 695.36 | 787.29 | 1.4827 | 1.4827 | 274150
2021-06-10 | 234650 | 252760 | 258880 | 746.29 | 644.97 | 946.15 | 1.5911 | 1.5911 | 234650
2021-06-11 | 292630 | 295690 | 291290 | 879.61 | 456.77 | 1860.55 | 2.3173 | 2.3173 | 292630
2021-06-12 | 308260 | 301870 | 309440 | 919.57 | 470.28 | 1981.13 | 2.4514 | 2.4514 | 308260
2021-06-13 | 299920 | 296970 | 299750 | 896.64 | 439.65 | 1455.66 | 1.8953 | 1.8953 | 299920
2021-06-14 | 239990 | 245750 | 262770 | 748.51 | 448.03 | 1017.12 | 1.4652 | 1.4652 | 239990
2021-06-15 | 289680 | 247030 | 194840 | 731.55 | 426.99 | 1011.17 | 1.4382 | 1.4382 | 289680
2021-06-16 | 303450 | 301120 | 223800 | 828.37 | 580.71 | 1043.11 | 1.6238 | 1.6238 | 303450
2021-06-17 | 311760 | 305040 | 276780 | 893.58 | 853.83 | 956.54 | 1.8104 | 1.8104 | 311760
2021-06-18 | 295920 | 231760 | 282060 | 809.74 | 647.54 | 741.45 | 1.389 | 1.389 | 295920
2021-06-19 | 299690 | 299640 | 189140 | 788.47 | 811.92 | 921.45 | 1.7334 | 1.7334 | 299690
2021-06-20 | 294960 | 236990 | 279910 | 811.86 | 851.97 | 962.85 | 1.8148 | 1.8148 | 294960
2021-06-21 | 254790 | 288580 | 267570 | 810.94 | 936.4 | 1021.08 | 1.9575 | 1.9575 | 254790
2021-06-22 | 250470 | 273610 | 272980 | 797.06 | 742.23 | 876.54 | 1.6188 | 1.6188 | 250470
2021-06-23 | 292570 | 206170 | 225760 | 724.5 | 660.42 | 758.44 | 1.4189 | 1.4189 | 292570
2021-06-24 | 267480 | 213710 | 238310 | 719.5 | 681.42 | 778.65 | 1.4601 | 1.4601 | 267480
2021-06-25 | 280300 | 135830 | 264540 | 680.67 | 640.87 | 744.116 | 1.385 | 1.385 | 280300
2021-06-26 | 322360 | 20770 | 321750 | 664.88 | 628 | 632 | 1.26 | 1.26 | 322360
2021-06-27 | 308420 | 153280 | 194290 | 655.99 | 624 | 612 | 1.236 | 1.236 | 308420
2021-06-28 | 318030 | 36320 | 317140 | 671.49 | 612 | 704 | 1.316 | 1.316 | 318030
2021-06-29 | 286810 | 286570 | 134420 | 707.8 | 672 | 780 | 1.452 | 1.452 | 286810
2021-06-30 | 245540 | 251860 | 209270 | 706.67 | 716 | 820 | 1.536 | 1.536 | 245540
| 8246090 | 6249340 | 7185060 | 21680.49 | 19404.78 | 27329.916 | 46.7347 | 46.7347 | 8246090
2021-07-01 | 284460 | 273130 | 249660 | 807.25 | 772 | 880 | 1.652 | 1.652 | 284460
2021-07-02 | 299570 | 301330 | 218430 | 819.33 | 720 | 820 | 1.54 | 1.54 | 299570
2021-07-03 | 275340 | 272460 | 198150 | 745.95 | 692 | 796 | 1.488 | 1.488 | 275340
2021-07-04 | 289560 | 195270 | 205710 | 690.54 | 692 | 792 | 1.484 | 1.484 | 289560
2021-07-05 | 311370 | 315280 | 319080 | 945.73 | 988 | 1116 | 2.104 | 2.104 | 311370
2021-07-06 | 306870 | 274090 | 300240 | 881.2 | 820 | 932 | 1.752 | 1.752 | 306870
2021-07-07 | 299350 | 300960 | 268970 | 869.28 | 928 | 1048 | 1.976 | 1.976 | 299350
2021-07-08 | 272880 | 284540 | 278100 | 835.52 | 808 | 920 | 1.728 | 1.728 | 272880
2021-07-09 | 269840 | 283640 | 248290 | 801.77 | 792 | 904 | 1.696 | 1.696 | 269840
2021-07-10 | 287220 | 274800 | 244630 | 806.65 | 836 | 948 | 1.784 | 1.784 | 287220
2021-07-11 | 208040 | 302110 | 293320 | 803.47 | 752 | 840 | 1.592 | 1.592 | 208040
2021-07-12 | 137550 | 144230 | 147180 | 428.96 | 784 | 908 | 1.692 | 1.692 | 137550
2021-07-13 | 325970 | 326670 | 324610 | 977.25 | 1116 | 1248 | 2.364 | 2.364 | 325970
2021-07-14 | 316330 | 320740 | 318470 | 955.54 | 1180 | 1316 | 2.496 | 2.496 | 316330
2021-07-15 | 334120 | 332750 | 334700 | 1001.57 | 1232 | 1368 | 2.6 | 2.6 | 334120
2021-07-16 | 327210 | 326440 | 327390 | 981.04 | 932 | 1056 | 1.988 | 1.988 | 327210
2021-07-17 | 329680 | 329090 | 329320 | 988.09 | 760 | 868 | 1.628 | 1.628 | 329680
2021-07-18 | 322910 | 322280 | 323250 | 968.44 | 768 | 872 | 1.64 | 1.64 | 322910
2021-07-19 | 333760 | 332540 | 332860 | 999.16 | 964 | 1092 | 2.056 | 2.056 | 333760
2021-07-20 | 281780 | 279310 | 281460 | 842.55 | 1024 | 1152 | 2.176 | 2.176 | 281780
2021-07-21 | 334110 | 333880 | 334330 | 1002.32 | 1208 | 1348 | 2.556 | 2.556 | 334110
2021-07-22 | 339080 | 338890 | 338910 | 1016.88 | 920 | 1044 | 1.964 | 1.964 | 339080
2021-07-23 | 338410 | 337680 | 338230 | 1014.32 | 832 | 956 | 1.788 | 1.788 | 338410
2021-07-24 | 335140 | 334600 | 335210 | 1004.95 | 732 | 840 | 1.572 | 1.572 | 335140
2021-07-25 | 336940 | 336700 | 337380 | 1011.02 | 728 | 836 | 1.564 | 1.564 | 336940
2021-07-26 | 338850 | 338380 | 338810 | 1016.04 | 744 | 856 | 1.6 | 1.6 | 338850
2021-07-27 | 339510 | 339380 | 339470 | 1018.36 | 908 | 1028 | 1.936 | 1.936 | 339510
2021-07-28 | 308980 | 316120 | 316180 | 941.28 | 1172 | 1280 | 2.452 | 2.452 | 308980
2021-07-29 | 340030 | 339950 | 340220 | 1020.2 | 920 | 1104 | 2.024 | 2.024 | 340030
2021-07-30 | 335200 | 335290 | 335180 | 1005.67 | 988 | 1092 | 2.08 | 2.08 | 335200
2021-07-31 | 216900 | 218550 | 225310 | 660.76 | 1000 | 1128 | 2.128 | 2.128 | 216900
| 9376960 | 9361080 | 9123050 | 27861.09 | 27712 | 31388 | 59.1 | 59.1 | 9376960
2021-08-01 | 177680 | 179860 | 178820 | 536.36 | 840 | 956 | 1.796 | 1.796 | 177680
2021-08-02 | 292580 | 289230 | 290650 | 872.46 | 1004 | 1132 | 2.136 | 2.136 | 292580
2021-08-03 | 260560 | 259470 | 258050 | 778.08 | 1140 | 1276 | 2.416 | 2.416 | 260560
2021-08-04 | 335140 | 334190 | 335730 | 1005.06 | 1244 | 1404 | 2.648 | 2.648 | 335140
2021-08-05 | 334450 | 334860 | 334810 | 1004.12 | 1300 | 1460 | 2.76 | 2.76 | 334450
2021-08-06 | 336840 | 336290 | 337340 | 1010.47 | 1232 | 1384 | 2.616 | 2.616 | 336840
2021-08-07 | 336460 | 335460 | 336730 | 1008.65 | 1064 | 1204 | 2.268 | 2.268 | 336460
2021-08-08 | 333500 | 333300 | 332100 | 998.9 | 996 | 1124 | 2.12 | 2.12 | 333500
2021-08-09 | 332840 | 334550 | 334450 | 1001.84 | 1276 | 1424 | 2.7 | 2.7 | 332840
2021-08-10 | 301480 | 330290 | 330150 | 961.92 | 1108 | 1244 | 2.352 | 2.352 | 301480
2021-08-11 | 322340 | 323160 | 325350 | 970.85 | 896 | 1016 | 1.912 | 1.912 | 322340
2021-08-12 | 295300 | 315850 | 308320 | 919.47 | 920 | 1036 | 1.956 | 1.956 | 295300
2021-08-13 | 284870 | 309630 | 303430 | 897.93 | 1004 | 1124 | 2.128 | 2.128 | 284870
2021-08-14 | 304060 | 319120 | 324200 | 947.38 | 1216 | 1356 | 2.572 | 2.572 | 304060
2021-08-15 | 280640 | 313870 | 317100 | 911.61 | 944 | 1064 | 2.008 | 2.008 | 280640
2021-08-16 | 245240 | 280050 | 267470 | 792.76 | 1040 | 1172 | 2.212 | 2.212 | 245240
2021-08-17 | 238340 | 265940 | 239730 | 744.01 | 876 | 1060 | 1.936 | 1.936 | 238340
2021-08-18 | 243080 | 242650 | 220210 | 705.94 | 988 | 1052 | 2.04 | 2.04 | 243080
2021-08-19 | 155970 | 259960 | 267530 | 683.46 | 952 | 1068 | 2.02 | 2.02 | 155970
2021-08-20 | 274750 | 285590 | 137860 | 698.2 | 856 | 976 | 1.832 | 1.832 | 274750
2021-08-21 | 255050 | 254950 | 213770 | 723.77 | 940 | 1064 | 2.004 | 2.004 | 255050
2021-08-22 | 286030 | 286230 | 203400 | 775.66 | 1100 | 1236 | 2.336 | 2.336 | 286030
2021-08-23 | 284410 | 219600 | 274930 | 778.94 | 1056 | 1200 | 2.256 | 2.256 | 284410
2021-08-24 | 267800 | 268810 | 158710 | 695.32 | 860 | 992 | 1.852 | 1.852 | 267800
2021-08-25 | 277500 | 288690 | 107140 | 673.33 | 900 | 1008 | 1.908 | 1.908 | 277500
2021-08-26 | 310900 | 312050 | 46350 | 669.3 | 896 | 1008 | 1.904 | 1.904 | 310900
2021-08-27 | 325150 | 324520 | 8140 | 657.81 | 900 | 1012 | 1.912 | 1.912 | 325150
2021-08-28 | 320190 | 229860 | 126770 | 676.82 | 1004 | 1132 | 2.136 | 2.136 | 320190
2021-08-29 | 277050 | 302530 | 75420 | 655 | 1028 | 1168 | 2.196 | 2.196 | 277050
2021-08-30 | 300380 | 307540 | 42460 | 650.38 | 988 | 1128 | 2.116 | 2.116 | 300380
2021-08-31 | 314170 | 158950 | 169460 | 642.58 | 888 | 1016 | 1.904 | 1.904 | 314170
| 8904750 | 8937050 | 7206580 | 25048.38 | 31456 | 35496 | 66.952 | 66.952 | 8904750
2021-09-01 | 286540 | 0 | 290080 | 576.62 | 752 | 860 | 1.612 | 1.612 | 286540
2021-09-02 | 263100 | 0 | 266050 | 529.15 | 764 | 872 | 1.636 | 1.636 | 263100
2021-09-03 | 283220 | 0 | 269150 | 552.37 | 724 | 832 | 1.556 | 1.556 | 283220
2021-09-04 | 276810 | 0 | 291130 | 567.94 | 708 | 832 | 1.54 | 1.54 | 276810
2021-09-05 | 232090 | 0 | 294530 | 526.62 | 696 | 820 | 1.516 | 1.516 | 232090
2021-09-06 | 210420 | 0 | 302910 | 513.33 | 712 | 920 | 1.632 | 1.632 | 210420
2021-09-07 | 235250 | 0 | 265620 | 500.87 | 844 | 796 | 1.64 | 1.64 | 235250
2021-09-08 | 276250 | 135930 | 287670 | 699.85 | 1036 | 1264 | 2.3 | 2.3 | 276250
2021-09-09 | 284400 | 63230 | 300440 | 648.07 | 976 | 1092 | 2.068 | 2.068 | 284400
2021-09-10 | 291700 | 152730 | 294780 | 739.21 | 1140 | 1268 | 2.408 | 2.408 | 291700
2021-09-11 | 250460 | 307070 | 297580 | 855.11 | 1316 | 1464 | 2.78 | 2.78 | 250460
2021-09-12 | 310500 | 324690 | 330650 | 965.84 | 1420 | 1460 | 2.88 | 2.88 | 310500
2021-09-13 | 288660 | 315500 | 298660 | 902.82 | 1036 | 1272 | 2.308 | 2.308 | 288660
2021-09-14 | 244140 | 271090 | 267830 | 783.06 | 968 | 1108 | 2.076 | 2.076 | 244140
2021-09-15 | 274900 | 198430 | 256360 | 729.69 | 964 | 1092 | 2.056 | 2.056 | 274900
2021-09-16 | 308020 | 47840 | 317510 | 673.37 | 808 | 928 | 1.736 | 1.736 | 308020
2021-09-17 | 282010 | 62070 | 291100 | 635.18 | 868 | 984 | 1.852 | 1.852 | 282010
2021-09-18 | 287970 | 34140 | 288850 | 610.96 | 960 | 1080 | 2.04 | 2.04 | 287970
2021-09-19 | 279570 | 35360 | 272820 | 587.75 | 856 | 972 | 1.828 | 1.828 | 279570
2021-09-20 | 258070 | 25360 | 271220 | 554.65 | 876 | 992 | 1.868 | 1.868 | 258070
2021-09-21 | 224330 | 74060 | 266100 | 564.49 | 1160 | 1304 | 2.464 | 2.464 | 224330
2021-09-22 | 262380 | 10220 | 265240 | 537.84 | 908 | 1032 | 1.94 | 1.94 | 262380
2021-09-23 | 112230 | 88410 | 192680 | 393.32 | 672 | 760 | 1.432 | 1.432 | 112230
2021-09-24 | 247890 | 73040 | 290130 | 611.06 | 864 | 988 | 1.852 | 1.852 | 247890
2021-09-25 | 283280 | 14080 | 279300 | 576.66 | 868 | 988 | 1.856 | 1.856 | 283280
2021-09-26 | 255130 | 2330 | 259820 | 517.28 | 832 | 940 | 1.772 | 1.772 | 255130
2021-09-27 | 237960 | 0 | 267190 | 505.15 | 836 | 944 | 1.78 | 1.78 | 237960
2021-09-28 | 245100 | 0 | 229030 | 474.13 | 788 | 896 | 1.684 | 1.684 | 245100
2021-09-29 | 213290 | 0 | 232010 | 445.3 | 752 | 864 | 1.616 | 1.616 | 213290
2021-09-30 | 153630 | 0 | 170390 | 324.02 | 512 | 584 | 1.096 | 1.096 | 153630
| 7659300 | 2235580 | 8206830 | 18101.71 | 26616 | 30208 | 56.824 | 56.824 | 7659300
2021-10-01 | 230950 | 0 | 201580 | 432.53 | 736 | 832 | 1.568 | 1.568 | 230950
2021-10-02 | 241940 | 0 | 184200 | 426.14 | 720 | 824 | 1.544 | 1.544 | 241940
2021-10-03 | 212810 | 0 | 215520 | 428.33 | 736 | 840 | 1.576 | 1.576 | 212810
2021-10-04 | 234320 | 0 | 175180 | 409.5 | 740 | 840 | 1.58 | 1.58 | 234320
2021-10-05 | 223940 | 0 | 184240 | 408.18 | 732 | 836 | 1.568 | 1.568 | 223940
2021-10-06 | 207800 | 0 | 164930 | 372.73 | 776 | 888 | 1.664 | 1.664 | 207800
2021-10-07 | 247900 | 0 | 115770 | 363.67 | 792 | 900 | 1.692 | 1.692 | 247900
2021-10-08 | 260150 | 0 | 99240 | 359.39 | 768 | 880 | 1.648 | 1.648 | 260150
2021-10-09 | 270300 | 0 | 86420 | 356.72 | 752 | 860 | 1.612 | 1.612 | 270300
2021-10-10 | 293500 | 0 | 54980 | 348.48 | 764 | 868 | 1.632 | 1.632 | 293500
2021-10-11 | 284910 | 0 | 56330 | 341.24 | 748 | 856 | 1.604 | 1.604 | 284910
2021-10-12 | 282960 | 0 | 48040 | 331 | 768 | 872 | 1.64 | 1.64 | 282960
2021-10-13 | 262920 | 0 | 56510 | 319.43 | 716 | 820 | 1.536 | 1.536 | 262920
2021-10-14 | 256080 | 0 | 56840 | 312.92 | 720 | 820 | 1.54 | 1.54 | 256080
2021-10-15 | 252130 | 0 | 56860 | 308.99 | 724 | 832 | 1.556 | 1.556 | 252130
2021-10-16 | 252830 | 0 | 54900 | 307.73 | 704 | 808 | 1.512 | 1.512 | 252830
2021-10-17 | 240300 | 0 | 55550 | 295.85 | 728 | 832 | 1.56 | 1.56 | 240300
2021-10-18 | 237370 | 0 | 50930 | 288.3 | 732 | 848 | 1.58 | 1.58 | 237370
2021-10-19 | 224690 | 0 | 51660 | 276.35 | 728 | 816 | 1.544 | 1.544 | 224690
2021-10-20 | 214570 | 0 | 53530 | 268.1 | 720 | 828 | 1.548 | 1.548 | 214570
2021-10-21 | 209230 | 0 | 55020 | 264.25 | 740 | 844 | 1.584 | 1.584 | 209230
2021-10-22 | 208750 | 0 | 50050 | 258.8 | 752 | 856 | 1.608 | 1.608 | 208750
2021-10-23 | 197340 | 0 | 46190 | 243.53 | 748 | 852 | 1.6 | 1.6 | 197340
2021-10-24 | 231240 | 0 | 54410 | 285.65 | 816 | 932 | 1.748 | 1.748 | 231240
2021-10-25 | 218730 | 0 | 43030 | 261.76 | 768 | 876 | 1.644 | 1.644 | 218730
2021-10-26 | 213110 | 0 | 45810 | 258.92 | 796 | 904 | 1.7 | 1.7 | 213110
2021-10-27 | 204210 | 0 | 40090 | 244.3 | 780 | 888 | 1.668 | 1.668 | 204210
2021-10-28 | 191080 | 0 | 41900 | 232.98 | 780 | 888 | 1.668 | 1.668 | 191080
2021-10-29 | 182320 | 0 | 45010 | 227.33 | 740 | 868 | 1.608 | 1.608 | 182320
2021-10-30 | 180600 | 0 | 44480 | 225.08 | 748 | 872 | 1.62 | 1.62 | 180600
2021-10-31 | 175310 | 0 | 40440 | 215.75 | 800 | 936 | 1.736 | 1.736 | 175310
| 7144290 | 0 | 2529640 | 9673.93 | 23272 | 26616 | 49.888 | 49.888 | 7144290
2021-11-01 | 146910 | 0 | 65050 | 211.96 | 840 | 964 | 1.804 | 1.804 | 146910
2021-11-02 | 169840 | 0 | 39530 | 209.37 | 836 | 956 | 1.792 | 1.792 | 169840
2021-11-03 | 168640 | 0 | 42780 | 211.42 | 848 | 960 | 1.808 | 1.808 | 168640
2021-11-04 | 163190 | 0 | 42540 | 205.73 | 840 | 956 | 1.796 | 1.796 | 163190
2021-11-05 | 150190 | 0 | 42310 | 192.5 | 832 | 964 | 1.796 | 1.796 | 150190
2021-11-06 | 148340 | 0 | 42890 | 191.23 | 784 | 912 | 1.696 | 1.696 | 148340
2021-11-07 | 151010 | 0 | 34470 | 185.48 | 752 | 860 | 1.612 | 1.612 | 151010
2021-11-08 | 147810 | 0 | 35970 | 183.78 | 1428 | 176 | 1.604 | 1.604 | 147810
2021-11-09 | 140260 | 0 | 40410 | 180.67 | 1552 | 56 | 1.608 | 1.608 | 140260
2021-11-10 | 132460 | 30410 | 14170 | 177.04 | 1356 | 52 | 1.408 | 1.408 | 132460
2021-11-11 | 90430 | 81580 | 0 | 172.01 | 1260 | 52 | 1.312 | 1.312 | 90430
2021-11-12 | 85110 | 87860 | 0 | 172.97 | 1280 | 52 | 1.332 | 1.332 | 85110
2021-11-13 | 86240 | 86760 | 0 | 173 | 1320 | 56 | 1.376 | 1.376 | 86240
2021-11-14 | 130320 | 44290 | 0 | 174.61 | 1324 | 52 | 1.376 | 1.376 | 130320
2021-11-15 | 79940 | 94750 | 0 | 174.69 | 1368 | 56 | 1.424 | 1.424 | 79940
2021-11-16 | 78910 | 92610 | 0 | 171.52 | 1364 | 52 | 1.416 | 1.416 | 78910
2021-11-17 | 77190 | 94550 | 0 | 171.74 | 1352 | 56 | 1.408 | 1.408 | 77190
2021-11-18 | 75480 | 93070 | 0 | 168.55 | 1384 | 48 | 1.432 | 1.432 | 75480
2021-11-19 | 72220 | 91980 | 0 | 164.2 | 1420 | 52 | 1.472 | 1.472 | 72220
2021-11-20 | 71120 | 91540 | 0 | 162.66 | 1380 | 52 | 1.432 | 1.432 | 71120
2021-11-21 | 130360 | 24110 | 0 | 154.47 | 1344 | 56 | 1.4 | 1.4 | 130360
2021-11-22 | 109810 | 43980 | 0 | 153.79 | 1280 | 48 | 1.328 | 1.328 | 109810
2021-11-23 | 106090 | 43400 | 0 | 149.49 | 960 | 440 | 1.4 | 1.4 | 106090
2021-11-24 | 103770 | 44050 | 0 | 147.82 | 640 | 740 | 1.38 | 1.38 | 103770
2021-11-25 | 99770 | 44170 | 0 | 143.94 | 672 | 776 | 1.448 | 1.448 | 99770
2021-11-26 | 93620 | 44050 | 0 | 137.67 | 676 | 788 | 1.464 | 1.464 | 93620
2021-11-27 | 94500 | 41730 | 0 | 136.23 | 628 | 732 | 1.36 | 1.36 | 94500
2021-11-28 | 92370 | 41720 | 0 | 134.09 | 624 | 728 | 1.352 | 1.352 | 92370
2021-11-29 | 97660 | 41620 | 0 | 139.28 | 592 | 696 | 1.288 | 1.288 | 97660
2021-11-30 | 86880 | 30620 | 0 | 117.5 | 612 | 724 | 1.336 | 1.336 | 86880
| 3380440 | 1288850 | 400120 | 5069.41 | 31548 | 13112 | 44.66 | 44.66 | 3380440
2021-12-01 | 94100 | 40000 | 0 | 134.1 | 624 | 740 | 1.364 | 1.364 | 94100
2021-12-02 | 91190 | 41480 | 0 | 132.67 | 640 | 756 | 1.396 | 1.396 | 91190
2021-12-03 | 89790 | 41700 | 0 | 131.49 | 624 | 744 | 1.368 | 1.368 | 89790
2021-12-04 | 88960 | 41850 | 0 | 130.81 | 636 | 748 | 1.384 | 1.384 | 88960
2021-12-05 | 91630 | 42010 | 0 | 133.64 | 600 | 772 | 1.372 | 1.372 | 91630
2021-12-06 | 31150 | 20990 | 0 | 52.14 | 260 | 256 | 0.516 | 0.516 | 31150
2021-12-07 | 0 | 0 | 0 | 0 | 0 | 444 | 0.444 | 0.444 | 0
2021-12-08 | 0 | 0 | 0 | 0 | 132 | 692 | 0.824 | 0.824 | 0
2021-12-09 | 0 | 0 | 0 | 0 | 576 | 692 | 1.268 | 1.268 | 0
2021-12-10 | 0 | 0 | 0 | 0 | 828 | 912 | 1.74 | 1.74 | 0
2021-12-11 | 0 | 0 | 0 | 0 | 848 | 920 | 1.768 | 1.768 | 0
2021-12-12 | 0 | 0 | 0 | 0 | 532 | 624 | 1.156 | 1.156 | 0
2021-12-13 | 0 | 0 | 0 | 0 | 592 | 680 | 1.272 | 1.272 | 0
2021-12-14 | 0 | 0 | 0 | 0 | 580 | 672 | 1.252 | 1.252 | 0
2021-12-15 | 0 | 0 | 0 | 0 | 524 | 608 | 1.132 | 1.132 | 0
2021-12-16 | 0 | 0 | 0 | 0 | 540 | 624 | 1.164 | 1.164 | 0
2021-12-17 | 93660 | 41860 | 0 | 135.52 | 688 | 780 | 1.468 | 1.468 | 93660
2021-12-18 | 70260 | 41700 | 0 | 111.96 | 628 | 724 | 1.352 | 1.352 | 70260
2021-12-19 | 69770 | 41630 | 0 | 111.4 | 616 | 708 | 1.324 | 1.324 | 69770
2021-12-20 | 69780 | 41430 | 0 | 111.21 | 620 | 716 | 1.336 | 1.336 | 69780
2021-12-21 | 71300 | 41670 | 0 | 112.97 | 588 | 692 | 1.28 | 1.28 | 71300
2021-12-22 | 21820 | 41800 | 50600 | 114.22 | 564 | 664 | 1.228 | 1.228 | 21820
2021-12-23 | 22910 | 42100 | 51000 | 116.01 | 604 | 704 | 1.308 | 1.308 | 22910
2021-12-24 | 41710 | 0 | 72060 | 113.77 | 628 | 724 | 1.352 | 1.352 | 41710
2021-12-25 | 39750 | 0 | 72940 | 112.69 | 632 | 732 | 1.364 | 1.364 | 39750
2021-12-26 | 20200 | 26670 | 64520 | 111.39 | 560 | 652 | 1.212 | 1.212 | 20200
2021-12-27 | 21420 | 21200 | 68790 | 111.41 | 596 | 692 | 1.288 | 1.288 | 21420
2021-12-28 | 0 | 42560 | 74320 | 116.88 | 580 | 636 | 1.216 | 1.216 | 0
2021-12-29 | 0 | 64800 | 44840 | 109.64 | 572 | 708 | 1.28 | 1.28 | 0
2021-12-30 | 0 | 67130 | 41570 | 108.7 | 572 | 672 | 1.244 | 1.244 | 0
2021-12-31 | 0 | 65630 | 41940 | 107.57 | 568 | 672 | 1.24 | 1.24 | 0
| 1029400 | 808210 | 582580 | 2420.19 | 17552 | 21360 | 38.912 | 38.912 | 1029400
2022-01-01 | 0 | 66000 | 42350 | 108.35 | 588 | 708 | 1.296 | 1.296 | 0
2022-01-02 | 0 | 77020 | 21230 | 98.25 | 624 | 740 | 1.364 | 1.364 | 0
2022-01-03 | 0 | 66130 | 41190 | 107.32 | 636 | 756 | 1.392 | 1.392 | 0
2022-01-04 | 0 | 104850 | 0 | 104.85 | 672 | 800 | 1.472 | 1.472 | 0
2022-01-05 | 0 | 150540 | 0 | 150.54 | 692 | 824 | 1.516 | 1.516 | 0
2022-01-06 | 0 | 136840 | 0 | 136.84 | 516 | 592 | 1.108 | 1.108 | 0
2022-01-07 | 0 | 133690 | 0 | 133.69 | 568 | 672 | 1.24 | 1.24 | 0
2022-01-08 | 0 | 124890 | 0 | 124.89 | 484 | 572 | 1.056 | 1.056 | 0
2022-01-09 | 0 | 123450 | 0 | 123.45 | 488 | 580 | 1.068 | 1.068 | 0
2022-01-10 | 0 | 58880 | 72710 | 131.59 | 512 | 604 | 1.116 | 1.116 | 0
2022-01-11 | 0 | 0 | 116020 | 116.02 | 500 | 592 | 1.092 | 1.092 | 0
2022-01-12 | 0 | 41920 | 80240 | 122.16 | 548 | 632 | 1.18 | 1.18 | 0
2022-01-13 | 0 | 36540 | 76000 | 112.54 | 632 | 748 | 1.38 | 1.38 | 0
2022-01-14 | 0 | 41360 | 73840 | 115.2 | 556 | 652 | 1.208 | 1.208 | 0
2022-01-15 | 0 | 39480 | 73470 | 112.95 | 572 | 676 | 1.248 | 1.248 | 0
2022-01-16 | 0 | 40110 | 74540 | 114.65 | 604 | 712 | 1.316 | 1.316 | 0
2022-01-17 | 0 | 40180 | 73320 | 113.5 | 540 | 636 | 1.176 | 1.176 | 0
2022-01-18 | 0 | 41870 | 75970 | 117.84 | 580 | 692 | 1.272 | 1.272 | 0
2022-01-19 | 0 | 42630 | 78820 | 121.45 | 560 | 660 | 1.22 | 1.22 | 0
2022-01-20 | 0 | 42260 | 81250 | 123.51 | 644 | 744 | 1.388 | 1.388 | 0
2022-01-21 | 0 | 42660 | 84040 | 126.7 | 664 | 764 | 1.428 | 1.428 | 0
2022-01-22 | 0 | 42510 | 83110 | 125.62 | 708 | 808 | 1.516 | 1.516 | 0
2022-01-23 | 0 | 42420 | 90330 | 132.75 | 652 | 752 | 1.404 | 1.404 | 0
2022-01-24 | 0 | 42670 | 89020 | 131.69 | 620 | 720 | 1.34 | 1.34 | 0
2022-01-25 | 0 | 41420 | 86640 | 128.06 | 616 | 712 | 1.328 | 1.328 | 0
2022-01-26 | 0 | 41640 | 79930 | 121.57 | 572 | 668 | 1.24 | 1.24 | 0
2022-01-27 | 0 | 39970 | 78700 | 118.67 | 572 | 668 | 1.24 | 1.24 | 0
2022-01-28 | 0 | 40800 | 74520 | 115.32 | 516 | 600 | 1.116 | 1.116 | 0
2022-01-29 | 0 | 20830 | 53700 | 74.53 | 360 | 424 | 0.784 | 0.784 | 0
2022-01-30 | 0 | 42010 | 109690 | 151.7 | 572 | 676 | 1.248 | 1.248 | 0
2022-01-31 | 0 | 41920 | 76570 | 118.49 | 452 | 528 | 0.98 | 0.98 | 0
| 0 | 1847490 | 1887200 | 3734.69 | 17820 | 20912 | 38.732 | 38.732 | 0
2022-02-01 | 0 | 42130 | 78370 | 120.5 | 552 | 644 | 1.196 | 1.196 | 0
2022-02-02 | 0 | 40290 | 78490 | 118.78 | 564 | 660 | 1.224 | 1.224 | 0
2022-02-03 | 56890 | 41980 | 23740 | 122.61 | 584 | 684 | 1.268 | 1.268 | 56890
2022-02-04 | 83590 | 42400 | 0 | 125.99 | 560 | 652 | 1.212 | 1.212 | 83590
2022-02-05 | 69250 | 20990 | 30610 | 120.85 | 568 | 660 | 1.228 | 1.228 | 69250
2022-02-06 | 83340 | 41550 | 0 | 124.89 | 540 | 640 | 1.18 | 1.18 | 83340
2022-02-07 | 84850 | 42490 | 0 | 127.34 | 540 | 632 | 1.172 | 1.172 | 84850
2022-02-08 | 29590 | 42640 | 51500 | 123.73 | 528 | 624 | 1.152 | 1.152 | 29590
2022-02-09 | 58070 | 42680 | 25590 | 126.34 | 568 | 664 | 1.232 | 1.232 | 58070
2022-02-10 | 83150 | 42430 | 0 | 125.58 | 560 | 656 | 1.216 | 1.216 | 83150
2022-02-11 | 81910 | 42510 | 0 | 124.42 | 544 | 640 | 1.184 | 1.184 | 81910
2022-02-12 | 83370 | 42430 | 0 | 125.8 | 548 | 644 | 1.192 | 1.192 | 83370
2022-02-13 | 84260 | 42700 | 0 | 126.96 | 532 | 632 | 1.164 | 1.164 | 84260
2022-02-14 | 99280 | 42650 | 0 | 141.93 | 536 | 632 | 1.168 | 1.168 | 99280
2022-02-15 | 100820 | 41610 | 0 | 142.43 | 536 | 632 | 1.168 | 1.168 | 100820
2022-02-16 | 99060 | 40670 | 0 | 139.73 | 564 | 668 | 1.232 | 1.232 | 99060
2022-02-17 | 95090 | 41480 | 0 | 136.57 | 524 | 628 | 1.152 | 1.152 | 95090
2022-02-18 | 89480 | 42580 | 0 | 132.06 | 544 | 648 | 1.192 | 1.192 | 89480
2022-02-19 | 90780 | 42430 | 0 | 133.21 | 528 | 632 | 1.16 | 1.16 | 90780
2022-02-20 | 90580 | 42690 | 0 | 133.27 | 528 | 628 | 1.156 | 1.156 | 90580
2022-02-21 | 89990 | 41680 | 0 | 131.67 | 512 | 612 | 1.124 | 1.124 | 89990
2022-02-22 | 91120 | 42550 | 0 | 133.67 | 548 | 652 | 1.2 | 1.2 | 91120
2022-02-23 | 101600 | 43400 | 0 | 145 | 564 | 672 | 1.236 | 1.236 | 101600
2022-02-24 | 97690 | 39090 | 0 | 136.78 | 420 | 504 | 0.924 | 0.924 | 97690
2022-02-25 | 113090 | 41890 | 0 | 154.98 | 532 | 640 | 1.172 | 1.172 | 113090
2022-02-26 | 110860 | 42010 | 0 | 152.87 | 528 | 636 | 1.164 | 1.164 | 110860
2022-02-27 | 106390 | 40330 | 0 | 146.72 | 512 | 616 | 1.128 | 1.128 | 106390
2022-02-28 | 105810 | 42520 | 0 | 148.33 | 504 | 612 | 1.116 | 1.116 | 105810
| 2279910 | 1154800 | 288300 | 3723.01 | 15068 | 17844 | 32.912 | 32.912 | 2279910
2022-03-01 | 106070 | 42530 | 0 | 148.6 | 544 | 644 | 1.188 | 1.188 | 106070
2022-03-02 | 106710 | 41990 | 0 | 148.7 | 528 | 636 | 1.164 | 1.164 | 106710
2022-03-03 | 105520 | 40530 | 0 | 146.05 | 596 | 704 | 1.3 | 1.3 | 105520
2022-03-04 | 102700 | 42650 | 0 | 145.35 | 600 | 704 | 1.304 | 1.304 | 102700
2022-03-05 | 104600 | 42510 | 0 | 147.11 | 572 | 676 | 1.248 | 1.248 | 104600
2022-03-06 | 108640 | 42640 | 0 | 151.28 | 560 | 668 | 1.228 | 1.228 | 108640
2022-03-07 | 81260 | 21210 | 50000 | 152.47 | 576 | 684 | 1.26 | 1.26 | 81260
2022-03-08 | 119670 | 42550 | 0 | 162.22 | 572 | 672 | 1.244 | 1.244 | 119670
2022-03-09 | 134220 | 21280 | 18120 | 173.62 | 580 | 692 | 1.272 | 1.272 | 134220
2022-03-10 | 157830 | 21180 | 21060 | 200.07 | 608 | 716 | 1.324 | 1.324 | 157830
2022-03-11 | 134460 | 45990 | 49040 | 229.49 | 616 | 724 | 1.34 | 1.34 | 134460
2022-03-12 | 201500 | 30460 | 30700 | 262.66 | 660 | 776 | 1.436 | 1.436 | 201500
2022-03-13 | 229360 | 80530 | 0 | 309.89 | 796 | 936 | 1.732 | 1.732 | 229360
2022-03-14 | 265300 | 28200 | 67600 | 361.1 | 1116 | 1304 | 2.42 | 2.42 | 265300
2022-03-15 | 272090 | 67230 | 66090 | 405.41 | 1136 | 1320 | 2.456 | 2.456 | 272090
2022-03-16 | 153890 | 278660 | 0 | 432.55 | 1012 | 1160 | 2.172 | 2.172 | 153890
2022-03-17 | 287820 | 150440 | 0 | 438.26 | 896 | 1032 | 1.928 | 1.928 | 287820
2022-03-18 | 250500 | 202740 | 0 | 453.24 | 728 | 832 | 1.56 | 1.56 | 250500
2022-03-19 | 218530 | 266280 | 0 | 484.81 | 712 | 812 | 1.524 | 1.524 | 218530
2022-03-20 | 189550 | 239700 | 0 | 429.25 | 708 | 812 | 1.52 | 1.52 | 189550
2022-03-21 | 183970 | 179050 | 0 | 363.02 | 652 | 748 | 1.4 | 1.4 | 183970
2022-03-22 | 84380 | 295480 | 0 | 379.86 | 432 | 876 | 1.308 | 1.308 | 84380
2022-03-23 | 235850 | 129590 | 0 | 365.44 | 52 | 1324 | 1.376 | 1.376 | 235850
2022-03-24 | 314400 | 63190 | 0 | 377.59 | 60 | 1348 | 1.408 | 1.408 | 314400
2022-03-25 | 267150 | 38850 | 0 | 306 | 52 | 1240 | 1.292 | 1.292 | 267150
2022-03-26 | 172290 | 107520 | 0 | 279.81 | 52 | 1200 | 1.252 | 1.252 | 172290
2022-03-27 | 238780 | 34730 | 0 | 273.51 | 56 | 1256 | 1.312 | 1.312 | 238780
2022-03-28 | 163080 | 191120 | 0 | 354.2 | 52 | 1480 | 1.532 | 1.532 | 163080
2022-03-29 | 285780 | 77190 | 0 | 362.97 | 56 | 1844 | 1.9 | 1.9 | 285780
2022-03-30 | 196230 | 175940 | 0 | 372.17 | 56 | 1832 | 1.888 | 1.888 | 196230
2022-03-31 | 276000 | 66340 | 0 | 342.34 | 56 | 1824 | 1.88 | 1.88 | 276000
| 5748130 | 3108300 | 302610 | 9159.04 | 15692 | 31476 | 47.168 | 47.168 | 5748130
2022-04-01 | 282510 | 69500 | 0 | 352.01 | 52 | 1812 | 1.864 | 1.864 | 282510
2022-04-02 | 261320 | 103110 | 0 | 364.43 | 56 | 1808 | 1.864 | 1.864 | 261320
2022-04-03 | 289210 | 89820 | 0 | 379.03 | 56 | 1732 | 1.788 | 1.788 | 289210
2022-04-04 | 259950 | 84980 | 0 | 344.93 | 52 | 1728 | 1.78 | 1.78 | 259950
2022-04-05 | 268380 | 88130 | 0 | 356.51 | 64 | 1736 | 1.8 | 1.8 | 268380
2022-04-06 | 270960 | 101500 | 0 | 372.46 | 48 | 1720 | 1.768 | 1.768 | 270960
2022-04-07 | 286560 | 45900 | 52370 | 384.83 | 52 | 1420 | 1.472 | 1.472 | 286560
2022-04-08 | 261440 | 0 | 102590 | 364.03 | 396 | 876 | 1.272 | 1.272 | 261440
2022-04-09 | 272420 | 0 | 98170 | 370.59 | 576 | 688 | 1.264 | 1.264 | 272420
2022-04-10 | 244300 | 56280 | 25280 | 325.86 | 572 | 684 | 1.256 | 1.256 | 244300
2022-04-11 | 274080 | 78870 | 0 | 352.95 | 624 | 736 | 1.36 | 1.36 | 274080
2022-04-12 | 265240 | 82750 | 35100 | 383.09 | 692 | 788 | 1.48 | 1.48 | 265240
2022-04-13 | 286680 | 97350 | 0 | 384.03 | 744 | 840 | 1.584 | 1.584 | 286680
2022-04-14 | 293000 | 81290 | 0 | 374.29 | 844 | 964 | 1.808 | 1.808 | 293000
2022-04-15 | 269050 | 40700 | 0 | 309.75 | 740 | 856 | 1.596 | 1.596 | 269050
2022-04-16 | 254910 | 35050 | 0 | 289.96 | 668 | 780 | 1.448 | 1.448 | 254910
2022-04-17 | 241920 | 30590 | 0 | 272.51 | 656 | 772 | 1.428 | 1.428 | 241920
2022-04-18 | 245970 | 35080 | 0 | 281.05 | 596 | 708 | 1.304 | 1.304 | 245970
2022-04-19 | 259970 | 35050 | 0 | 295.02 | 836 | 984 | 1.82 | 1.82 | 259970
2022-04-20 | 266980 | 57550 | 0 | 324.53 | 816 | 956 | 1.772 | 1.772 | 266980
2022-04-21 | 250520 | 50080 | 0 | 300.6 | 904 | 1076 | 1.98 | 1.98 | 250520
2022-04-22 | 257970 | 35030 | 0 | 293 | 912 | 1088 | 2 | 2 | 257970
2022-04-23 | 255990 | 34940 | 0 | 290.93 | 884 | 1056 | 1.94 | 1.94 | 255990
2022-04-24 | 237510 | 31550 | 0 | 269.06 | 740 | 876 | 1.616 | 1.616 | 237510
2022-04-25 | 237620 | 35060 | 0 | 272.68 | 676 | 792 | 1.468 | 1.468 | 237620
2022-04-26 | 245560 | 28160 | 0 | 273.72 | 768 | 908 | 1.676 | 1.676 | 245560
2022-04-27 | 205550 | 78560 | 0 | 284.11 | 596 | 708 | 1.304 | 1.304 | 205550
2022-04-28 | 63040 | 109260 | 152620 | 324.92 | 648 | 756 | 1.404 | 1.404 | 63040
2022-04-29 | 182550 | 16920 | 93270 | 292.74 | 660 | 760 | 1.42 | 1.42 | 182550
2022-04-30 | 156010 | 0 | 128730 | 284.74 | 572 | 680 | 1.252 | 1.252 | 156010
| 7447170 | 1633060 | 688130 | 9768.36 | 16500 | 31288 | 47.788 | 47.788 | 7447170
2022-05-01 | 154950 | 0 | 128400 | 283.35 | 676 | 780 | 1.456 | 1.456 | 154950
2022-05-02 | 186910 | 0 | 107950 | 294.86 | 836 | 984 | 1.82 | 1.82 | 186910
2022-05-03 | 224670 | 0 | 94710 | 319.38 | 820 | 960 | 1.78 | 1.78 | 224670
2022-05-04 | 283950 | 0 | 39620 | 323.57 | 604 | 724 | 1.328 | 1.328 | 283950
2022-05-05 | 263160 | 0 | 32590 | 295.75 | 600 | 720 | 1.32 | 1.32 | 263160
2022-05-06 | 131260 | 0 | 142970 | 274.23 | 268 | 1068 | 1.336 | 1.336 | 131260
2022-05-07 | 171020 | 0 | 103760 | 274.78 | 0 | 1188 | 1.188 | 1.188 | 171020
2022-05-08 | 203300 | 0 | 79240 | 282.54 | 0 | 1288 | 1.288 | 1.288 | 203300
2022-05-09 | 203200 | 0 | 109550 | 312.75 | 0 | 1220 | 1.22 | 1.22 | 203200
2022-05-10 | 56000 | 0 | 274420 | 330.42 | 0 | 1148 | 1.148 | 1.148 | 56000
2022-05-11 | 29260 | 29160 | 280830 | 339.25 | 0 | 1128 | 1.128 | 1.128 | 29260
2022-05-12 | 46000 | 34510 | 271550 | 352.06 | 0 | 1188 | 1.188 | 1.188 | 46000
2022-05-13 | 101290 | 34690 | 252580 | 388.56 | 0 | 1384 | 1.384 | 1.384 | 101290
2022-05-14 | 192910 | 37420 | 166920 | 397.25 | 0 | 1392 | 1.392 | 1.392 | 192910
2022-05-15 | 103050 | 37750 | 258870 | 399.67 | 0 | 1488 | 1.488 | 1.488 | 103050
2022-05-16 | 30050 | 28630 | 302780 | 361.46 | 0 | 1272 | 1.272 | 1.272 | 30050
2022-05-17 | 26250 | 22960 | 274120 | 323.33 | 0 | 1208 | 1.208 | 1.208 | 26250
2022-05-18 | 37000 | 34510 | 250560 | 322.07 | 0 | 1272 | 1.272 | 1.272 | 37000
2022-05-19 | 35820 | 35030 | 268080 | 338.93 | 0 | 1260 | 1.26 | 1.26 | 35820
2022-05-20 | 123490 | 35380 | 201980 | 360.85 | 0 | 1304 | 1.304 | 1.304 | 123490
2022-05-21 | 34970 | 34260 | 272050 | 341.28 | 0 | 1224 | 1.224 | 1.224 | 34970
2022-05-22 | 25130 | 24820 | 247950 | 297.9 | 0 | 1168 | 1.168 | 1.168 | 25130
2022-05-23 | 29940 | 30870 | 216340 | 277.15 | 0 | 1208 | 1.208 | 1.208 | 29940
2022-05-24 | 32240 | 32030 | 244470 | 308.74 | 0 | 1220 | 1.22 | 1.22 | 32240
2022-05-25 | 34650 | 33860 | 207460 | 275.97 | 0 | 1156 | 1.156 | 1.156 | 34650
2022-05-26 | 34090 | 33510 | 201860 | 269.46 | 0 | 1180 | 1.18 | 1.18 | 34090
2022-05-27 | 29480 | 29020 | 233750 | 292.25 | 0 | 1160 | 1.16 | 1.16 | 29480
2022-05-28 | 35160 | 34970 | 268160 | 338.29 | 0 | 1208 | 1.208 | 1.208 | 35160
2022-05-29 | 35440 | 35120 | 280090 | 350.65 | 0 | 1176 | 1.176 | 1.176 | 35440
2022-05-30 | 34140 | 34380 | 268610 | 337.13 | 0 | 1152 | 1.152 | 1.152 | 34140
2022-05-31 | 34000 | 33520 | 261370 | 328.89 | 0 | 1172 | 1.172 | 1.172 | 34000
| 2962780 | 686400 | 6343590 | 9992.77 | 3804 | 36000 | 39.804 | 39.804 | 2962780
2022-06-01 | 77390 | 30220 | 194850 | 302.46 | 0 | 1140 | 1.14 | 1.14 | 77390
2022-06-02 | 192250 | 28580 | 70390 | 291.22 | 0 | 1256 | 1.256 | 1.256 | 192250
2022-06-03 | 27781.28 | 27480 | 228360 | 283.6213 | 0 | 1148 | 1.148 | 1.148 | 27781.28
2022-06-04 | 28088.72 | 27820 | 214710 | 270.6187 | 0 | 1160 | 1.16 | 1.16 | 28088.72
2022-06-05 | 30237.68 | 31106.53 | 208429.73 | 269.7739 | 0 | 1156 | 1.156 | 1.156 | 30237.68
2022-06-06 | 66234.64 | 31321.84 | 170088.23 | 267.6447 | 0 | 1184 | 1.184 | 1.184 | 66234.64
2022-06-07 | 34967.68 | 34661.63 | 239922.04 | 309.5514 | 0 | 1164 | 1.164 | 1.164 | 34967.68
2022-06-08 | 34980 | 34330 | 259930 | 329.24 | 0 | 1144 | 1.144 | 1.144 | 34980
2022-06-09 | 35000 | 34330 | 274660 | 343.99 | 0 | 1184 | 1.184 | 1.184 | 35000
2022-06-10 | 31380 | 31070 | 270320 | 332.77 | 0 | 1100 | 1.1 | 1.1 | 31380
2022-06-11 | 35150 | 34740 | 267700 | 337.59 | 0 | 1200 | 1.2 | 1.2 | 35150
2022-06-12 | 35000 | 34740 | 267240 | 336.98 | 0 | 1188 | 1.188 | 1.188 | 35000
2022-06-13 | 34760 | 34740 | 268800 | 338.3 | 0 | 1236 | 1.236 | 1.236 | 34760
2022-06-14 | 47060 | 35120 | 253870 | 336.05 | 0 | 1196 | 1.196 | 1.196 | 47060
2022-06-15 | 109390 | 34900 | 207160 | 351.45 | 0 | 1272 | 1.272 | 1.272 | 109390
2022-06-16 | 151070 | 34990 | 181710 | 367.77 | 0 | 1560 | 1.56 | 1.56 | 151070
2022-06-17 | 167500 | 35070 | 186290 | 388.86 | 0 | 1884 | 1.884 | 1.884 | 167500
2022-06-18 | 133980 | 38410 | 254620 | 427.01 | 0 | 1832 | 1.832 | 1.832 | 133980
2022-06-19 | 284830 | 34400 | 287040 | 606.27 | 0 | 1964 | 1.964 | 1.964 | 284830
2022-06-20 | 240250 | 34070 | 265800 | 540.12 | 0 | 1420 | 1.42 | 1.42 | 240250
2022-06-21 | 200860 | 32870 | 254660 | 488.39 | 0 | 1476 | 1.476 | 1.476 | 200860
2022-06-22 | 154420 | 21880 | 262580 | 438.88 | 0 | 1448 | 1.448 | 1.448 | 154420
2022-06-23 | 249930 | 34810 | 144310 | 429.05 | 0 | 1392 | 1.392 | 1.392 | 249930
2022-06-24 | 113040 | 34850 | 285960 | 433.85 | 0 | 1396 | 1.396 | 1.396 | 113040
2022-06-25 | 158520 | 35070 | 265750 | 459.34 | 0 | 1428 | 1.428 | 1.428 | 158520
2022-06-26 | 167820 | 35000 | 261700 | 464.52 | 0 | 1396 | 1.396 | 1.396 | 167820
2022-06-27 | 183730 | 34300 | 269090 | 487.12 | 0 | 1416 | 1.416 | 1.416 | 183730
2022-06-28 | 161770 | 99680 | 237880 | 499.33 | 0 | 1460 | 1.46 | 1.46 | 161770
2022-06-29 | 218970 | 34570 | 265530 | 519.07 | 0 | 1628 | 1.628 | 1.628 | 218970
2022-06-30 | 256800 | 34800 | 282270 | 573.87 | 0 | 1864 | 1.864 | 1.864 | 256800
| 3663160 | 1059930 | 7101620 | 11824.71 | 0 | 41292 | 41.292 | 41.3333 | 3663160
2022-07-01 | 277720 | 163730 | 293560 | 735.01 | 0 | 1920 | 1.92 | 1.92 | 277720
2022-07-02 | 240560 | 242940 | 265700 | 749.2 | 0 | 2540 | 2.54 | 2.54 | 240560
2022-07-03 | 222030 | 206260 | 256880 | 685.17 | 0 | 2560 | 2.56 | 2.56 | 222030
2022-07-04 | 271820 | 270430 | 307840 | 850.09 | 0 | 2324 | 2.324 | 2.324 | 271820
2022-07-05 | 270870 | 269430 | 315500 | 855.8 | 0 | 2556 | 2.556 | 2.556 | 270870
2022-07-06 | 277460 | 276180 | 334100 | 887.74 | 0 | 2240 | 2.24 | 2.24 | 277460
2022-07-07 | 253540 | 274100 | 310100 | 837.74 | 0 | 1728 | 1.728 | 1.728 | 253540
2022-07-08 | 270550 | 269360 | 297520 | 837.43 | 0 | 2104 | 2.104 | 2.104 | 270550
2022-07-09 | 87860 | 90880 | 102400 | 281.14 | 0 | 1464 | 1.464 | 1.464 | 87860
2022-07-10 | 69260 | 68520 | 83130 | 220.91 | 108 | 524 | 0.632 | 0.632 | 69260
2022-07-11 | 261340 | 260120 | 310900 | 832.36 | 512 | 1340 | 1.852 | 1.852 | 261340
2022-07-12 | 276750 | 276370 | 326050 | 879.17 | 512 | 1336 | 1.848 | 1.848 | 276750
2022-07-13 | 276820 | 276500 | 330800 | 884.12 | 468 | 1296 | 1.764 | 1.764 | 276820
2022-07-14 | 234850 | 233970 | 280300 | 749.12 | 332 | 1172 | 1.504 | 1.504 | 234850
2022-07-15 | 276700 | 275980 | 334900 | 887.58 | 288 | 1296 | 1.584 | 1.584 | 276700
2022-07-16 | 271870 | 270190 | 327050 | 869.11 | 384 | 1340 | 1.724 | 1.724 | 271870
2022-07-17 | 277320 | 276480 | 334620 | 888.42 | 244 | 1104 | 1.348 | 1.348 | 277320
2022-07-18 | 277350 | 277030 | 334230 | 888.61 | 280 | 932 | 1.212 | 1.212 | 277350
2022-07-19 | 277370 | 276910 | 334680 | 888.96 | 280 | 900 | 1.18 | 1.18 | 277370
2022-07-20 | 271610 | 275190 | 326760 | 873.56 | 200 | 1020 | 1.22 | 1.22 | 271610
2022-07-21 | 259650 | 275790 | 333950 | 869.39 | 164 | 1052 | 1.216 | 1.216 | 259650
2022-07-22 | 277110 | 276750 | 335200 | 889.06 | 280 | 1020 | 1.3 | 1.3 | 277110
2022-07-23 | 277750 | 277340 | 333470 | 888.56 | 576 | 1356 | 1.932 | 1.932 | 277750
2022-07-24 | 270790 | 270160 | 324210 | 865.16 | 736 | 1660 | 2.396 | 2.396 | 270790
2022-07-25 | 258230 | 218500 | 189660 | 666.39 | 532 | 1284 | 1.816 | 1.816 | 258230
| 6287180 | 6149110 | 7323510 | 19759.8 | 5896 | 38068 | 43.964 | 43.964 | 276260
297130
8099580
331130
331040
331150
331360
331600
332380
332610
218560
277300
332580
121060
336810
290440
255470
247440
306490
334480
334080
334050
333840
333410
333150
321650
320310
328130
315270
285030
221400
306120
266570
225190
9300100
193440
231570
278110
254740
200700
236730
324570
268210
296460
284210
304530
312960
285400
247550
109610
213740
219950
170200
174750
249630
281650
299320
233890
250760
229720
280360
254870
234910
296310
288220
7507070
262100
252880
240480
238800
214200
193150
169510
214030
226920
250190
193370
214570
256350
324700
317300
311890
296870
282370
271880
284260
311220
286100
274870
259900
262910
253790
233000
228400
220800
212950
203790
7763550
190940
191320
186420
176490
166820
163260
178500
170770
152700
193240
178940
159760
157420
214690
301000
202920
214840
215880
208720
202080
162520
146370
185850
160460
154710
151430
151710
155800
150800
143270
5389630
139300
136350
130790
126250
92750
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
625440
0
0
0
0
0
0
0
0
0
0
0
56860
86390
88700
54460
41690
41160
41010
42450
43680
43600
41620
42230
42050
43630
43440
43550
43680
43590
43790
43210
970790
43230
43070
43070
43120
43230
43360
43210
43090
43240
43110
43280
43350
43050
43220
21530
0
0
0
0
0
21410
0
0
0
0
0
0
101400
748970
136000
130500
121270
121190
127490
127410
127290
130670
133840
136370
111200
0
0
137750
159290
144490
172320
172090
172360
172330
174770
176030
165460
159260
159790
169520
169490
174550
183950
181480
168760
4416920
169830
207040
198970
244100
201800
161220
180590
180890
167390
83380
239730
209500
243870
271150
293420
280210
284300
87980
190420
226200
287480
217930
169660
217140
123720
98030
149910
240700
248860
282620
6158040
278670
250530

## Meter Calibrations
METER CHANGE HISTORY RECORD
|  | OLD METER DETAILS | [6 empty] | NEW METER DETAILS
| METER (TRANSMITTER/ GAUGE) | [6 empty] | Meter Replaced on
S. NO. | [6 empty] | Closing Meter Reading |  |  |  | ACCURAC Y |  |  | Initial Meter Reading
|  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS | CALIBRATION VALIDITY (FROM/TO) |  |  |  | NEW ENERGY METER NO. | MAKE OF METER | CLASS | CALIBRATION VALIDITY (FROM/TO)
[5 empty] | FROM | TO | [5 empty] | FROM | TO
1 | TG-1 | 34140731734 | SCHNEIDER | 1 | 2019-05-17 | 2020-05-16 | 65576.88 | 2020-05-29 | 540180078685 | SCHNEIDER | 1 | 2020-05-14 | 2021-05-13 | 0.055
2 | TG-2 | 34140731733 | SCHNEIDER | 1 | 2019-05-17 | 2020-05-16 | 48659.04 | 2020-05-29 | 540180079101 | SCHNEIDER | 1 | 2020-05-14 | 2021-05-13 | 0.05
3 | TG-3 | 34140731738 | SCHNEIDER | 1 | 2019-05-17 | 2020-05-16 | 50337.98 | 2020-05-29 | 540180078676 | SCHNEIDER | 1 | 2020-05-13 | 2021-05-12 | 0
4 | AUX. T/F 1 | 34153341596 | SCHNEIDER | 0.5 | 2019-05-17 | 2020-05-16 | 219.6074 | 2020-05-30 | 540180087883 | SCHNEIDER | 0.5 | 2020-05-13 | 2021-05-12 | 54.32
5 | AUX. T/F 2 | 34153341597 | SCHNEIDER | 0.5 | 2019-05-17 | 2020-05-16 | 258.427 | 2020-05-30 | 540180087890 | SCHNEIDER | 0.5 | 2020-05-14 | 2021-05-13 | 54.68
|  | OLD METER DETAILS | [6 empty] | NEW METER DETAILS
| METER (TRANSMITTER/ GAUGE) | [6 empty] | Meter Replaced on
S. NO. | [6 empty] | Closing Meter Reading |  |  |  | ACCURAC Y |  |  | Initial Meter Reading
|  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS | CALIBRATION VALIDITY (FROM/TO) |  |  |  | NEW ENERGY METER NO. | MAKE OF METER | CLASS | CALIBRATION VALIDITY (FROM/TO)
[5 empty] | FROM | TO | [5 empty] | FROM | TO
1 | TG-1 | 540180000000 | SCHNEIDER | 1 | 2020-05-14 | 2021-05-13 | 43545.15 | 2021-05-11 | 34140731734 | SCHNEIDER | 1 | 2021-04-15 | 2022-04-14 | 0
2 | TG-2 | 540180000000 | SCHNEIDER | 1 | 2020-05-14 | 2021-05-13 | 36707.34 | 2021-05-11 | 34140731733 | SCHNEIDER | 1 | 2021-04-15 | 2022-04-14 | 0
3 | TG-3 | 540180000000 | SCHNEIDER | 1 | 2020-05-13 | 2021-05-12 | 53733.95 | 2021-05-11 | 34140731738 | SCHNEIDER | 1 | 2021-04-16 | 2022-04-15 | 0
4 | AUX. T/F 1 | 540180087883 | SCHNEIDER | 0.5 | 2020-05-13 | 2021-05-12 | 182300.31 | 2021-05-11 | 34153341596 | SCHNEIDER | 0.5 | 2021-04-16 | 2022-04-15 | 0
5 | AUX. T/F 2 | 540180087890 | SCHNEIDER | 0.5 | 2020-05-14 | 2021-05-13 | 231444.11 | 2021-05-11 | 34153341597 | SCHNEIDER | 0.5 | 2021-04-15 | 2022-04-14 | 0
|  | OLD METER DETAILS | [6 empty] | NEW METER DETAILS
| METER (TRANSMITTER/ GAUGE) | [6 empty] | Meter Replaced on
S. NO. | [6 empty] | Closing Meter Reading |  |  |  | ACCURAC Y |  |  | Initial Meter Reading
|  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS | CALIBRATION VALIDITY (FROM/TO) |  |  |  | NEW ENERGY METER NO. | MAKE OF METER | CLASS | CALIBRATION VALIDITY (FROM/TO)
[5 empty] | FROM | TO | [5 empty] | FROM | TO
4 | AUX. T/F 1 | 34153341596 | SCHNEIDER | 0.5 | 2021-04-16 | 2022-04-15 | 31763.36 | 2021-06-25 | Q0333445 | SECURE | 0.2s | Installed and Sealed by HPSLDC
5 | AUX. T/F 2 | 34153341597 | SCHNEIDER | 0.5 | 2021-04-15 | 2022-04-14 | 32516.96 | 2021-06-25 | Q0333450 | SECURE | 0.2s | Installed and Sealed by HPSLDC
| METER (TRANSMITTER/ GAUGE) | OLD METER DETAILS | [6 empty] | NEW METER DETAILS
S. NO. |  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS | CALIBRATION VALIDITY (FROM/TO) |  | Closing Meter Reading | Meter Replaced on | NEW ENERGY METER NO. | MAKE OF METER | ACCURAC Y | CALIBRATION VALIDITY (FROM/TO) |  | Initial
[11 empty] | CLASS |  |  | Meter Reading
[5 empty] | FROM | TO | [5 empty] | FROM | TO
1 | TG-1 | 34140731734 | SCHNEIDER | 1 | 2021-04-15 | 2022-04-15 | 69337.13 | 2022-06-02 | 540180078685 | SCHNEIDER | 1 | 2022-04-04 | 2023-04-04 | 0
2 | TG-2 | 34140731733 | SCHNEIDER | 1 | 2021-04-15 | 2022-04-15 | 38597.76 | 2022-06-02 | 540180079101 | SCHNEIDER | 1 | 2022-04-04 | 2023-04-04 | 0
3 | TG-3 | 34140731738 | SCHNEIDER | 1 | 2021-04-16 | 2022-04-15 | 47984.7 | 2022-06-02 | 540180078676 | SCHNEIDER | 1 | 2022-04-04 | 2023-04-04 | 0
| METER (TRANSMITTER/ GAUGE) | OLD METER DETAILS | [6 empty] | NEW METER DETAILS
S. NO. |  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS | CALIBRATION VALIDITY (FROM/TO) |  | Closing Meter Reading | Meter Replaced on | NEW ENERGY METER NO. | MAKE OF METER | ACCURAC Y | CALIBRATION VALIDITY (FROM/TO) |  | Initial Meter
[11 empty] | CLASS |  |  | Reading
[5 empty] | FROM | TO | [5 empty] | FROM | TO | KWh
1 | TG-1 | 540180078685 | SCHNEIDER | 1 | 2022-04-04 | 2023-04-04 | 54778.33 | 2023-05-02 | 34140731734 | SCHNEIDER | 1 | 2023-03-28 | 2024-03-28 | 0
2 | TG-2 | 540180079101 | SCHNEIDER | 1 | 2022-04-04 | 2023-04-04 | 35782.63 | 2023-05-02 | 34140731733 | SCHNEIDER | 1 | 2023-03-28 | 2024-03-28 | 0
3 | TG-3 | 540180078676 | SCHNEIDER | 1 | 2022-04-04 | 2023-04-04 | 41456.74 | 2023-05-02 | 34140731738 | SCHNEIDER | 1 | 2023-03-28 | 2024-03-28 | 0
| METER (TRANSMITTER/ GAUGE) | OLD METER DETAILS | [6 empty] | NEW METER DETAILS
S. NO. |  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS | CALIBRATION VALIDITY (FROM/TO) |  | Closing Meter Reading | Meter Replaced on | NEW ENERGY METER NO. | MAKE OF METER | ACCURAC Y | CALIBRATION VALIDITY (FROM/TO) |  | Initial Meter
[11 empty] | CLASS |  |  | Reading
[5 empty] | FROM | TO | [5 empty] | FROM | TO
1 | TG-1 | 34140731734 | SCHNEIDER | 1 | 2023-03-28 | 2024-03-28 | 47258.61 | 2024-04-03 | 540180078685 | SCHNEIDER | 1 | 2024-03-15 | 2025-03-15 | 0
2 | TG-2 | 34140731733 | SCHNEIDER | 1 | 2023-03-28 | 2024-03-28 | 48569.7 | 2024-04-03 | 540180079101 | SCHNEIDER | 1 | 2024-03-15 | 2025-03-15 | 0
3 | TG-3 | 34140731738 | SCHNEIDER | 1 | 2023-03-28 | 2024-03-28 | 48236.86 | 2024-04-03 | 540180078676 | SCHNEIDER | 1 | 2024-03-15 | 2025-03-15 | 0
|  | OLD METER DETAILS | [6 empty] | NEW METER DETAILS
| METER (TRANSMITTER/ GAUGE) | [6 empty] | Meter Replaced on
S. NO. |  |  |  |  | CALIBRATION VALIDITY (FROM/TO) |  | Closing Meter Reading |  |  |  | ACCURAC Y | CALIBRATION VALIDITY (FROM/TO) |  | Initial Meter Reading
|  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS |  |  |  |  | NEW ENERGY METER NO. | MAKE OF METER | CLASS
[5 empty] | FROM | TO | [5 empty] | FROM | TO
1 | TG-1 | 540180078685 | SCHNEIDER | 1 | 2024-03-15 | 2025-03-15 | 53125.55 | 2025-04-03 | 34140731734 | SCHNEIDER | 1 | 2025-02-25 | 2026-02-25 | 0
2 | TG-1 | 540180079101 | SCHNEIDER | 1 | 2024-03-15 | 2025-03-15 | 53140.91 | 2025-04-03 | 34140731733 | SCHNEIDER | 1 | 2025-02-25 | 2026-02-25 | 0
3 | TG-1 | 540180078676 | SCHNEIDER | 1 | 2024-03-15 | 2025-03-15 | 52055.23 | 2025-04-03 | 34140731738 | SCHNEIDER | 1 | 2025-02-25 | 2026-02-25 | 0
| Auxiliary ENERGY METER NO. | OLD METER DETAILS | [5 empty] | Meter Replaced on | NEW METER DETAILS
S. NO. |  |  |  |  | CALIBRATION VALIDITY (FROM/TO) |  | Closing Meter Reading |  |  |  | ACCURAC Y | CALIBRATION VALIDITY (FROM/TO) |  | Initial Meter Reading
|  | OLD ENERGY METER NO. | MAKE OF METER | ACCURACY CLASS |  |  |  |  | NEW ENERGY METER NO. | MAKE OF METER | CLASS
1 | AUX. T/F 1 | 34153341596 | SCHNEIDER | 0.5 | 2019-05-17 | 2020-05-16 | 219.6074 | 2020-05-30 | 540180087883 | SCHNEIDER | 0.5 | 2020-05-13 | 2021-05-12 | 54.32
2 | AUX. T/F 2 | 34153341597 | SCHNEIDER | 0.5 | 2019-05-17 | 2020-05-16 | 258.427 | 2020-05-30 | 540180087890 | SCHNEIDER | 0.5 | 2020-05-14 | 2021-05-13 | 54.68
3 | AUX. T/F 1 | 540180087883 | SCHNEIDER | 0.5 | 2020-05-13 | 2021-05-12 | 182300.31 | 2021-05-11 | 34153341596 | SCHNEIDER | 0.5 | 2021-04-16 | 2022-04-15 | 0
3 | AUX. T/F 2 | 540180087890 | SCHNEIDER | 0.5 | 2020-05-14 | 2021-05-13 | 231444.11 | 2021-05-11 | 34153341597 | SCHNEIDER | 0.5 | 2021-04-15 | 2022-04-14 | 0
3 | AUX. T/F 1 | 34153341596 | SCHNEIDER | 0.5 | 2021-04-16 | 2022-04-15 | 31763.36 | 2021-06-25 | Q0333445 | SECURE | 0.2s | Installed and Sealed by HPSLDC
3 | AUX. T/F 2 | 34153341597 | SCHNEIDER | 0.5 | 2021-04-15 | 2022-04-14 | 32516.96 | 2021-06-25 | Q0333450 | SECURE | 0.2s | Installed and Sealed by HPSLDC
Loop meters details and calibration
Auxiliary ENERGY METER NO. | MAKE OF METER | ACCURAC Y | CALIBRATION VALIDITY (FROM/TO)
|  | CLASS |  |  |  |  | Meter serial no
|  |  | FROM | TO
Q033445 | Secure | 0.2s | 2020-11-24 | 2021-11-23
Q033450 | Secure | 0.2s | 2020-11-24 | 2021-11-23
Q033445 | Secure | 0.2s | 2021-11-20 | 2022-11-19
Q033450 | Secure | 0.2s | 2021-11-20 | 2022-11-19
Q033445 | Secure | 0.2s | 2023-11-18 | 2024-11-17
Q033450 | Secure | 0.2s | 2023-11-18 | 2024-11-17
Q033445 | Secure | 0.2s | 2024-11-17 | 2025-11-16
Q033450 | Secure | 0.2s | 2024-11-17 | 2025-11-16

## loop meters
Sr.No. | old meter Serial no. | make and class | date of testing | validity | date of change | replaced meter Serial no. | validity
main1 | HPU06240 | Secure, 0.2s | 2018-10-03 | 2019-10-02 | 2019-06-19 | HPU06250 | 2020-06-18
check1 | HPU06109 | Secure, 0.2s | 2018-10-03 | 2019-10-02 | 2019-06-19 | HPU06251 | 2020-06-18
main2 | HPU06107 | Secure, 0.2s | 2018-10-03 | 2019-10-02 | meters not changed, only calibrated in this duration
check2 | HPU06108 | Secure, 0.2s | 2018-10-03 | 2019-10-02
Sr.No. | old meter Serial no. | make and class | date of testing | validity | date of change | replaced meter Serial no. | validity
main1 | HPU06250 | Secure, 0.2s | 2019-05-15 | 2020-05-14 | 2020-01-30 | HPU06240 | 2021-01-29
check1 | HPU06251 | Secure, 0.2s | 2019-05-15 | 2020-05-14 | 2020-01-30 | HPU06109 | 2021-01-29
main2 | HPU06107 | Secure, 0.2s | 2019-05-15 | 2020-05-14 | 2020-01-30 | HPU06239 | 2021-01-29
check2 | HPU06108 | Secure, 0.2s | 2019-05-15 | 2020-05-14 | 2020-01-30 | HPU06110 | 2021-01-29
Sr.No. | old meter Serial no. | make and class | date of testing | validity | date of change | replaced meter Serial no. | validity
main1 | HPU06240 | Secure, 0.2s | meters are changed only in this duration |  | 2021-03-03 | HPU06107 | 2022-03-02
check1 | HPU06109 | Secure, 0.2s |  |  | 2021-03-03 | HPU06108 | 2022-03-02
main2 | HPU06239 | Secure, 0.2s |  |  | 2021-03-03 | HPU06250 | 2022-03-02
check2 | HPU06110 | Secure, 0.2s |  |  | 2021-03-03 | HPU06251 | 2022-03-02
Sr.No. | old meter Serial no. | make and class | date of testing | validity | date of change | replaced meter Serial no. | validity
main1 | HPU06107 | Secure, 0.2s | meters are changed only in this duration |  | 2021-06-25 | Q0333420 | 2022-06-24
check1 | HPU06108 | Secure, 0.2s |  |  | 2021-06-25 | Q0333442 | 2022-06-24
main2 | HPU06250 | Secure, 0.2s |  |  | 2021-06-25 | Q0333350 | 2022-06-24
check2 | HPU06251 | Secure, 0.2s |  |  | 2021-06-25 | Q0333438 | 2022-06-24
Sr.No. | old meter Serial no. | make and class | date of testing | validity | date of change | replaced meter Serial no. | validity
main1 | Q0333420 | Secure, 0.2s | 2023-06-20 | 2024-06-19 | meters not changed, only calibrated in this duration
check1 | Q0333442 | Secure, 0.2s | 2023-06-20 | 2024-06-19
main2 | Q0333350 | Secure, 0.2s | 2023-06-20 | 2024-06-19
check2 | Q0333438 | Secure, 0.2s | 2023-06-20 | 2024-06-19
Sr.No. | old meter Serial no. | make and class | date of testing | validity | date of change | replaced meter Serial no. | validity
main1 | Q0333420 | Secure, 0.2s | 2024-06-15 | 2025-06-14 | meters not changed, only calibrated in this duration
check1 | Q0333442 | Secure, 0.2s | 2024-06-15 | 2025-06-14
main2 | Q0333350 | Secure, 0.2s | 2024-06-15 | 2025-06-14
check2 | Q0333438 | Secure, 0.2s | 2024-06-15 | 2025-06-14
Sr.No. | old meter Serial no. | make and class | date of testing | validity | date of change | replaced meter Serial no. | validity
main1 | Q0333420 | Secure, 0.2s | 2025-04-04 | 2026-04-03 | meters not changed, only calibrated in this duration
check1 | Q0333442 | Secure, 0.2s | 2025-04-04 | 2026-04-03
main2 | Q0333350 | Secure, 0.2s | 2025-04-04 | 2026-04-03
check2 | Q0333438 | Secure, 0.2s | 2025-04-04 | 2026-04-03