Monitoring Report

###### PUBLICATION DATE  14.10.2020
VERSION  v. 1.1 
RELATED SUPPORT - TEMPLATE GUIDE Monitoring Report v. 1.1

This document contains the following Sections

Key Project Information

SECTION A - Description of project

SECTION B - Implementation of project

SECTION C - Description of monitoring system applied by the project

SECTION D - Data and parameters

SECTION E - Calculation of SDG Impacts

SECTION F - Safeguards Reporting

SECTION G - Stakeholder inputs and legal disputes

### KEY PROJECT INFORMATION

##### Key Project Information

| GS ID (s) of Project (s) | GS745 |
| --- | --- |
| Title of the project (s) covered by monitoring report | Gaziantep Landfill Gas to Energy Project, Turkey |
| Version number of the PDD/VPA-DD (s) applicable to this monitoring report | 11 |
| Version number of the monitoring report | 04 |
| Completion date of the monitoring report | 14/08/2022 |
| Date of project design certification | 21/06/2011 |
| Date of Last Annual Report | N.A. |
| Monitoring period number | 02 |
| Duration of this monitoring period | 01/11/2018 to 31/10/2021 (inclusive of both dates) |
| Project Representative | EKI Energy Services Limited |
| Host Country | Turkey |
| Activity Requirements applied | Community Services Activities Renewable Energy Activities Land Use and Forestry Activities/Risks & Capacities N/A |
| Methodology (ies) applied and version number | ACM0001 “Flaring or use of landfill gas” Version 18.0 |
| Product Requirements applied | GHG Emissions Reduction & Sequestration Renewable Energy Label N/A |

##### Table 1 - Sustainable Development Contributions Achieved

| Sustainable Development Goals Targeted | SDG Impact | Amount Achieved | Units/ Products |
| --- | --- | --- | --- |
| SDG 13- Take urgent action to combat climate change and its impacts | Emission reductions | 246,347 | GS-VER |
| SDG 7– Ensure access to affordable, reliable, sustainable and modern energy for all | ## MWh of renewable energy generated | 117,063.41 | MWh |
| SDG 8 – Promote sustained, inclusive and sustainable economic growth, full and productive employment and descent work for all | Number employment through project | 17 people employed and 9 trainings conducted | Number |

##### Table 2 – Product Vintages

|  |  | Amount Achieved |  |  |
| --- | --- | --- | --- | --- |
| Start Dates | End Dates | SDG 7 | SDG 8 | SDG 13 |
| 01/11/2018 | 31/12/2018 | 6,937.50 MWh | 16 workers employed | 13,723 tCO2e |
| 01/01/2019 | 31/12/2019 | 39,928.20 MWh | 15 workers employed and 6 training conducted | 82,116 tCO2e |
| 01/01/2020 | 31/12/2020 | 37,716.83 MWh | 20 workers employed and 2 trainings conducted | 82,116 tCO2e |
| 01/01/2021 | 31/10/2021 | 32,480.88 MWh | 20 workers employed and 1 training conducted | 68,392 tCO2e |

#### SECTION A. DESCRIPTION OF PROJECT

##### A.1. General description of project

CEV Enerji Üretim San. ve Tic. Ltd. Şti. Has developed and operating the Gaziantep Landfill Gas to Energy Project. The project utilizes the landfill gas originating from the Gaziantep landfill of the Gaziantep city and generates electricity from it through gas engines. The project activity is operational with a total of 5 gas engines, JGC 416 GS-L.L make with a rated power of 1.131 MWe each and total installed capacity of 5.655 MW. The activity generates approximately 21 GWh per year of electricity and delivers it to the Turkish national grid. This has been checked during the on-site visit during the validation stage and also from the generation license of the project activity.

The first crediting period start date of the project was 01/02/2010 with choice of renewable crediting period. The PDD submitted for renewal indicates the second renewable crediting period start date as 24/01/2018. The gap between the two crediting periods is due to delay in submitting the request for renewal by the PP to GS before the end of first crediting period. As the request has been submitted after the end of first crediting period date, the subsequent crediting period shall begin by the end of 4 weeks GS review.

Purpose of the Project activity

The main purpose of the project activity is to generate electrical energy through sustainable means using landfill gas, to delivers the generated output to the Turkish national grid to contribute to climate change mitigation efforts.

The details of the project and the state of installation are mentioned in the Table 3:

Table 2 – Project Details

| Name of the SPVs | Capacity in MW | Connection with Grid | State | Usage of Electricity |
| --- | --- | --- | --- | --- |
| CEV Enerji Üretim San. ve Tic. Ltd. Şti. | 5.655 Mwe | Turkish national grid | Gaziantep | Sale to grid |

The project activity is promoted by CEV Enerji Üretim San. Ve Tic. Ltd. Şti. Thus, CEV Enerji Üretim San. Ve Tic. Ltd. Şti. Is acting as PP for the project activity.

Sectoral Scope 01: 	Grid-connected electricity generation from renewable sources

Sectoral Scope 13: 	Waste Handling and Disposal

Methodology: 	ACM0001 “Consolidated Baseline and Monitoring Methodology for Landfill Gas Project Activities” Version 18.0

Project Type: 		I. Renewable energy projects

Tools referred with above methodology are:

- “Gold Standard Procedures for the renewal of a crediting Period”;

- “Emissions from solid waste disposal sites” version 08;

- “Baseline, project and/or leakage emissions from electricity consumption and monitoring of electricity generation” version 02.0

- “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” version 03.0;

- “Assessment of the validity of the original / current baseline and update of the baseline at the renewal of the crediting period” version 03.0.1;

- “Tool to calculate the emission factor for an electricity system” version 05.0

Scenario existing prior to the implementation of project activity:

The scenario existing prior to the implementation of the project activity, is electricity delivered to the grid by the project activity that would have otherwise been generated by the operation of grid-connected power plants and by the addition of new generation sources, as reflected in the combined margin (CM) calculations described in the “Tool to calculate the emission factor for an electricity system”.

Baseline Scenario:

The establishment and description of the baseline scenario is discussed the guidance of the document “Gold Standard Procedures for the renewal of a crediting Period”. According to the referred document the Project participants shall provide an assessment on the validity of the original baseline or update through, and assessment carried out as per the “Tool to assess the validity of the original / current baseline and to update the baseline at the renewal of a crediting period”.

The “Tool to assess the validity of the original / current baseline and to update the baseline at the renewal of a crediting period” version 03.0.1 provides a stepwise procedure to assess the continued validity of the baseline and to update the baseline at the renewal of a crediting period, as required by paragraph 49 (a) of the modalities and procedures of the clean development mechanism.

The tool consists of two steps. The first step provides an approach to evaluate whether the current baseline is still valid for the next crediting period. The second step provides an approach to update the baseline in case that the current baseline is not valid anymore for the next crediting period.

Contribution to sustainable development

As the project developer, CEV Enerji Üretim San. ve Tic. Ltd. Şti. Believes that efficient utilization of all kinds of natural resources with a harmony coupled with responsible environmental considerations is vital for sustainable development of Turkey and the World. This has been a guiding factor for the shareholders towards the concept of designation and installation of an LFG project. Other than the objective of climate change mitigation through significant reduction in greenhouse gas (GHG) emissions, the project has been carried out to provide social and economic contribution to the region in a sustainable way. The benefits that will be gained by the realization of the project compared to the business-as-usual scenario can be summarized under four main indicators:

- Environmental: The project activity replaces the grid electricity, which is constituted of different fuel sources causing greenhouse gas emissions. By replacing in the consumption of these fuels, it contributes to conservation of water, soil, flora and faunas and transfers these natural resources and additional supply of these primary energy sources to the future generations. In the absence of the project activity, an equivalent amount of electricity would have been generated from the power plants connected to the grid, majority of which are based on fossil fuels. Thus, the project is replacing the greenhouse gas emissions (CO2, CH4) and other pollutants (CO, NMVOC, particulate matters) occurring from extraction, processing, transportation and burning of fossil-fuels for power generation connected to the national grid.

- Social: Local employment is enhanced by all project activities during construction and operation the project. As a result, local poverty and unemployment is partially eliminated by increased job opportunities and project business activities. Construction materials for the foundations, cables and other auxiliary equipment are preferentially sourced locally. Moreover, as contribution of the project to welfare of the region, the quality of the electricity consumed in the region is increased by local electricity production, which also contributes decreasing of distribution losses.

- Technological: Implementation of the project will contribute to wider deployment of LFG technology in local and national level. It will support improved energy security, alternative sustainable energy, and renewable energy industry development. This also strengthen pillars of Turkish electricity supply based on ecologically sound technology.

- Economical: Firstly, the project helps to accelerate the growth of the LFG industry and stimulate the designation and production of renewable energy technologies in Turkey. Then, other entrepreneurs irrespective of sector be encouraged to invest in LFG power generations. It also assist to reduce Turkey’s increasing energy deficit and diversify the electricity generation mix while reducing import dependency, especially natural gas. Importantly, rural development is maintained in the areas around the project site by providing infrastructural investments to these remote villages.

##### A.2. Location of project

The Project is located at the Gaziantep landfill site, in Gaziantep province, Turkey. It is approximately 9 km south of the Gaziantep city center, close to Akbulut town, Bağlarbaşı district.

The project is located in Akbulut Village, Şahinbey District, Gaziantep Province, Turkey.

| Name of the PP | Province | Latitude | Longitude |
| --- | --- | --- | --- |
| CEV Enerji Üretim San. ve Tic. Ltd. Şti. | Gaziantep | 36° 59' 12" N | 37° 24' 11" E |

Figure 1: The Location of Project Activity

##### A.3. Reference of applied methodology

Title		: Grid-connected electricity generation from renewable sources

Reference	: The project activity meets the eligibility criteria of large-scale project as the methane destruction component exceeds the 60,000 tCO2 limit

Methodology	: ACM 0001 “Consolidated Baseline and Monitoring Methodology for Landfill Gas Project Activities” Version 18.0

Type I		: Energy industries (renewable / non-renewable sources)

Tools referred with above methodology and applicable for project activity are:

- “Gold Standard Procedures for the renewal of a crediting Period”;

- “Emissions from solid waste disposal sites” version 08;

- “Baseline, project and/or leakage emissions from electricity consumption and monitoring of electricity generation” version 02.0

- “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” version 03.0;

- “Assessment of the validity of the original / current baseline and update of the baseline at the renewal of the crediting period” version 03.0.1;

- “Tool to calculate the emission factor for an electricity system” version 05.0

##### A.4. Crediting period of project

The project activity is a GS Registered project with the ID of GS 745. The first crediting period start date of the project was 01/02/2010 with choice of renewable crediting period. The PDD submitted for renewal indicates the second renewable crediting period start date as 24/01/2018. The gap between the two crediting periods is due to delay in submitting the request for renewal by the PP to GS before the end of first crediting period. As the request has been submitted after the end of first crediting period date, the subsequent crediting period shall begin by the end of 4 weeks GS review. The Crediting Period under GS4GG is as follows:

1st crediting period: 20/01/2010 to 19/01/2017

2nd crediting period: 24/01/2018 to 23/01/2025

#### SECTION B. IMPLEMENTATION OF PROJECT

##### B.1. Description of implemented project

The project activity involves the collection and utilization of the LFG with an electricity component with total installed capacity of 5.655 MWe. The project activity involves the collection and utilization of the LFG with an electricity component. The whole installation has 15 years design life.

The details of equipment installed at CEV Enerji Üretim San. ve Tic. Ltd. Şti. are as follows:

| Equipment | Specification |
| --- | --- |
| Gas Engine | Manufacturer: GE Jenbacher A-6200 Type: JGS416GS-L.L Rated Power: 1131 kW GM1 Serial No: 6262071 GM2 Serial No: 1021385 GM3 Serial No: 1021394 GM4 Serial No: 1021397 GM5 Serial No: 1021400 |
| Gas Analyzer | Manufacturer: EMERSON / X-Stream Type: PDS 103-912GC.A01 Serial Number: XMC09902465136 |
| Flowmeter | Manufacturer: SIERRA Instruments Model: 640S-NAA-L13-M0-E2-P2-V4-DD-5 Serial Number: 127736 |

B.1.1 Forward Action Requests

Not Applicable

##### B.2. Post-Design Certification changes

B.2.1. Temporary deviations from the approved Monitoring & Reporting Plan, methodology or standardized baseline

As per clause no 5.1.50 of GS4GG principles and requirement, 1.2 which states that " Transitioning projects, maintaining their existing crediting cycle shall undergo Performance Certification no later than the f-irst two years after project implementation or design certification, whichever is later, and once every three years after that, unless the Verifier provides a convincing case for less frequent visits as part of the Verification Report". However the performance certification gap compared to previous and ongoing verification is more than 3 years (from 24/01/2018 the project verification should had happened), and thus GS has allowed to claim maximum 3 years prior to the date of VVB site visit (actual on site visit for the project happened on 01/11/2021) and thus PP has planned to claim verification of 3 years prior to the date of site visit.

Further the PP ensured that there were no gaps in reporting of SDG contributions during the aforementioned period where gap in consecutive verification had been identified and the project continued to record the contributions towards SDG 7, SDG 8 and SDG 13 however no claims are being made for the period where gap had been identified and on a conservative note the SDG benefits for the aforementioned period has been considered to be zero.

B.2.2. Corrections

Not Applicable

B.2.3. Changes to start date of crediting period

Not Applicable

B.2.4. Permanent changes from the Design Certified monitoring plan, applied methodology or applied standardized baseline

Not Applicable

B.2.5. Changes to project design of approved project

Not Applicable

#### SECTION C. DESCRIPTION OF MONITORING SYSTEM APPLIED BY THE PROJECT

Monitoring is being carried out following the procedures set by the consolidated baseline methodology ACM0001 and all applicable tools of the above explained parameters. The monitoring consists of:

- Amount of landfill gas combusted in power generation units

- Temperature of the landfill gas sent to power generation to ensure compliance regarding dry basis for measurement

- Amount of landfill gas flared

- Concentration of methane of the landfill gas

- Total amount of electricity exported to the grid

- Operating hours of power generation units

- Total amount of the electricity imported from the grid

Responsibilities for monitoring

The project owner is responsible for the operation and maintenance of the landfill and the installed equipment. The project owner is also responsible for the administration of the data, setting up a GSVER team who will be responsible for monitoring all data required to estimate emission reductions.

In the diagram below the organization of monitoring management and data application is presented.

Monitoring equipment onsite

Aggregation of the monitoring data

Project owner w/support of VER consultant

- Development of monitoring report

DOE

Gaziantep VER team

- Quality assurance & control of the monitoring equipment.

- Supported by the VER consultant

Municipal Waste

Waste Collection and Transportation

LFG

Landfill Area

Gas Engines

MSW

Landfill Gas Extraction System

Electricity

Grid Connection

Figure 2- Project boundary

Registration of the monitored data

The Gaziantep GSVER-Team is responsible for quality assurance and quality control of the monitoring equipment. The data measured by the monitoring equipment is being stored and processed into a monitoring report, which is submitted by the project owner. All the monitored data will be stored during the crediting period and for at least two years after the end of the crediting period, whichever occurs later.

Corrective actions and emergency preparedness

The VER-Team regularly checks the monitoring system on errors. In the case of errors, corrective actions will be undertaken by the VER-Team, or if required, by the supplier of the monitoring equipment.

QA/QC procedure

Strong quality assurance and quality control procedure are being taken to monitor the equipment and data collection. Equipment and facilities are subject to a regular maintenance and testing regime to ensure accuracy following supplier’s manual. In case of data deficiency or in correct data reading, the data will be crosschecked with other parameters and data leading to the most conservative emission reductions will be considered for the calculation of the emission reductions.

Measuring of exported and imported electricity

The main meter for the monitoring of the electricity imports and export is at grid connection. Monthly protocols based on the readings, that are confirmed by both TEIAŞ, and the project developer are prepared by the end of each month and stored. These protocols are also the basis of invoicing for the electricity sales from the project activity. The electricity meters are bidirectional and measures both the imported and exported electricity from and to the grid.

Loss of Data

If there is any loss of data, the lost data will be counted as “0” unless methodology or tools or validation verification manuals of UNFCCC request otherwise.

Trainings

Health and safety Trainings: Trainings on occupational safety, which is provided by Health and Safety Officer. This training complies with national health and safety regulations 20/06/2012 Dated 6331 Numbered Law according to 30/06/2012-28339 Official Paper.

#### SECTION D. DATA AND PARAMETERS

##### D.1. Data and parameters fixed ex ante or at renewal of crediting period

- SDG13 (Indicators 13.3.2)

| Data/parameter | OXtop-layer |
| --- | --- |
| Unit | Dimensionless |
| Description | Fraction of methane that would be oxidized in the top layer of the SWDS in the baseline |
| Source of data | Consistent with how oxidation is accounted for in the methodological tool “Emissions from solid waste disposal sites” |
| Value(s) applied | 0.1 |
| Choice of data or Measurement methods and procedures | Applicable under ACM0001 |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data/parameter | OX |
| --- | --- |
| Unit | Dimensionless |
| Description | Oxidation factor (reflecting the amount of methane from SWDS that is oxidized in the soil or other material covering the waste) |
| Source of data | Based on extensive review of published literature on this subject, including the IPCC 2006 Guidelines for National Greenhouse Gas Inventories |
| Value(s) applied | 0.1 |
| Choice of data or Measurement methods and procedures | Applicable under “Emissions from solid disposal sites” |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data/parameter | GWPCH4 |
| --- | --- |
| Unit | tCO2e/tCH4 |
| Description | Global Warming Potential of CH4 |
| Source of data | IPCC |
| Value(s) applied | 28 according to the IPCC Fifth Assessment Report, 2014 (AR5) |
| Choice of data or Measurement methods and procedures | As per ACM0001 |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data/parameter | nPJ |
| --- | --- |
| Unit | Dimensionless |
| Description | Efficiency of the LFG capture system that is installed in the project activity |
| Source of data | - |
| Value(s) applied | 40% |
| Choice of data or Measurement methods and procedures | Applicable under ACM0001 |
| Purpose of data | Baseline emissions |
| Additional comment | The efficiency factor is based on the observations on actual performance of the power plant. |

| Data/parameter | Ru |
| --- | --- |
| Unit | Pa.m3/kmol.K |
| Description | Universal ideal gases constant |
| Source of data | “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” |
| Value(s) applied | 8,314 |
| Choice of data or Measurement methods and procedures | Applicable under “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data/parameter | MMCH4 |
| --- | --- |
| Unit | kg/kmol |
| Description | Molecular mass of CH4 |
| Source of data | “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” |
| Value(s) applied | Compound; Structure; Molecular mass (kg/kmol). Methane; CH4; 16.04. |
| Choice of data or Measurement methods and procedures | Applicable under “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data/parameter | default |
| --- | --- |
| Unit | - |
| Description | Default value for the model correction factor to account for model uncertainties |
| Source of data | - |
| Value(s) applied | 0.75 |
| Choice of data or Measurement methods and procedures | The project activity falls under option A |
| Purpose of data | Baseline emissions |
| Additional comment |  |

| Data/parameter | F |
| --- | --- |
| Unit | - |
| Description | Fraction of methane in the SWDS gas (volume fraction) |
| Source of data | IPCC 2006 Guidelines for National Greenhouse Gas Inventories |
| Value(s) applied | 0.5 |
| Choice of data or Measurement methods and procedures | Applicable under “Emissions from solid disposal sites” |
| Purpose of data | Baseline emissions |
| Additional comment |  |

| Data/parameter | DOCf,default |
| --- | --- |
| Unit | Weight fraction |
| Description | Default value for the fraction of degradable organic carbon (DOC) in MSW that can decompose in the SWDS |
| Source of data | IPCC 2006 Guidelines for National Greenhouse Gas Inventories |
| Value(s) applied | 0.5 |
| Choice of data or Measurement methods and procedures | Applicable under “Emissions from solid disposal sites” |
| Purpose of data | Baseline emissions |
| Additional comment | The project activity falls under option A |

| Data/parameter | MCFdefault |
| --- | --- |
| Unit | - |
| Description | Methane correction factor |
| Source of data | IPCC 2006 Guidelines for National Greenhouse Gas Inventories |
| Value(s) applied | 1 |
| Choice of data or Measurement methods and procedures | Applicable under “Emissions from solid disposal sites” |
| Purpose of data | Baseline emissions |
| Additional comment | The baseline falls under the definition “anaerobic managed solid waste disposal site |

| Data/parameter | DOCj |
| --- | --- |
| Unit | - |
| Description | Fraction of degradable organic carbon in waste type j (weight fraction) |
| Source of data | IPCC 2006 Guidelines for National Greenhouse Gas Inventories (adapted from Volume 5, Table 2.4, and Table 2.5) |
| Value(s) applied | The following values for the different waste types have been applied: Waste type j; DOCj (% wet waste). Wood and wood products; 43. Pulp, paper and cardboard; 40. Food, food waste, beverages and tobacco; 15. Textiles; 24. Garden, yard and park waste; 20. Glass, plastic, metal, other inert; 0. |
| Choice of data or Measurement methods and procedures | Applicable under “Emissions from solid disposal sites” |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data/parameter | kj |
| --- | --- |
| Unit | 1/yr. |
| Description | Decay rate for the waste type j |
| Source of data | IPCC 2006 Guidelines for National Greenhouse Gas Inventories (Volume 5, Table 3.3) |
| Value(s) applied | The following values for the different waste types have been applied: Waste type j. Slowly degrading; Pulp, paper, cardboard; 0.04. Wood, wood products and straw; 0.02. Moderately degrading; Other (non-food) organic putrescible garden and park waste; 0.05. Rapidly degrading; Food, food waste, sewage sludge, beverages and tobacco; 0.06. |
| Choice of data or Measurement methods and procedures | The “Tool to determine methane emissions avoided from disposal of waste at a solid waste disposal site” lists decay rates for different waste types. Average temperate in Gaziantep over the year is 15.0 °C and annual precipitation is 553.3 mm. Based on these data, the selection of appropriate kj values are made according to a “boreal and temperate” and “dry” climate. Unclassified SW types of nappies, rubber and leather are covered in the “Pulp, paper and cardboard” classification. Ceramics, soil and sand are covered in the “Glass, plastic, metal, other inert waste” classification. |
| Purpose of data | Baseline emission |
| Additional comment | - |

| Data/parameter | EFgrid,CM |
| --- | --- |
| Unit | tCO2/MWh |
| Description | Combined Margin emission factor |
| Source of data | Calculated as per “Tool to calculate the emission factor for an electricity system” |
| Value(s) applied | 0.5325 |
| Choice of data or Measurement methods and procedures | Applicable under “Tool to calculate the emission factor for an electricity system” |
| Purpose of data | Baseline and project emissions |
| Additional comment | - |

| Data/parameter | FCH4,BL,y |
| --- | --- |
| Unit | tCH4 |
| Description | Methane emissions that would be captured and destroyed to comply with national or local safety requirements or legal regulations in the year y |
| Source of data | National laws and regulations http://mevzuat.basbakanlik.gov.tr |
| Value(s) applied | 0 |
| Choice of data or Measurement methods and procedures | Fixed value has been applied |
| Purpose of data | Calculation of baseline emissions |
| Additional comment | - |

##### D.2 Data and parameters monitored

SDG 7 (Indicators 7.2.1)

| Data / Parameter | EGBL,k,y |
| --- | --- |
| Unit | MWh |
| Description | Net amount of electricity generated using LFG |
| Source of data | Electricity meters |
| Value(s) applied | Year; Value. 01/11/2018 – 31/12/2018; 6,937.50. 01/01/2019 – 31/12/2019; 39,928.20. 01/01/2020 – 31/12/2020; 37,716.83. 01/01/2021 – 31/10/2021; 32,480.88. Total; 117,063.41. |
| Measurement methods and procedures | The electricity generated using LFG is measured continuously with an electricity meter |
| Monitoring frequency | Continuous |
| QA/QC procedures | In accordance with the “Regulation on “Measurement and Measuring Tools”, the meters have to be calibrated within a frequency of once per 10 years. |
| Purpose of data | The electricity meters are used to measure the net electricity exported to the grid and used for billing purposes. Therefore, the meters are sealed by TEİAŞ (Turkish Electricity Transmission CO). |
| Additional comment | - |

| Data / Parameter | ECPJ,y |
| --- | --- |
| Unit | MWh |
| Description | Quantity of electricity consumed by the project activity |
| Source of data | Electricity meter |
| Value(s) applied | Year; Value. 01/11/2018 – 31/12/2018; 0.038. 01/01/2019 – 31/12/2019; 0.514. 01/01/2020 – 31/12/2020; 0.642. 01/01/2021 – 31/10/2021; 1.211. Total; 2.405. |
| Measurement methods and procedures | The electricity consumption is measured from electricity meters and aggregated annually. |
| Monitoring frequency | Continuous |
| QA/QC procedures | In accordance with the “Regulation on “Measurement and Measuring Tools”, the meters have to be calibrated within a frequency of once per 10 years. |
| Purpose of data | The electricity consumption is monitored using the same bi-directional electricity meter, which is used to measure the electricity exported to the grid. The electricity meters are used to measure the electricity consumption are used for billing purposes. Therefore, the meters are sealed by TEİAŞ (Turkish Electricity Transmission CO). |
| Additional comment | - |

| Data / Parameter | TDLy |
| --- | --- |
| Unit | % |
| Description | Average technical transmission and distribution losses |
| Source of data | Default value |
| Value(s) applied | TDLj,y: 20% (used to calculate PEEC) TDLk,y: 3% (used to calculate BEEC) |
| Measurement methods and procedures | “Tool to calculate baseline, project and/or leakage emissions from electricity consumption” version 01. |
| Monitoring frequency | - |
| QA/QC procedures | - |
| Purpose of data | Baseline and Project emissions |
| Additional comment | - |

| Data / Parameter | Avoided fossil fuel consumption |
| --- | --- |
| Unit | t/GWh, m3/GWh |
| Description | Access to affordable and clean energy services |
| Source of data | It is assumed that the net electricity generation during the monitoring period is distributed among fossil fuels with the same weight as the fossil fuels. These values are multiplied with the fuel consumption intensities given below to find the respective reduction of fossil fuel consumption. |
| Value(s) applied | The baseline consists of consumption of different fossil fuels. The fuel consumption and electricity generation figures are compared with the project generation to show how much baseline fuel consumption is avoided on a fuel type basis. The fossil fuel consumption intensity (t/GWh, m3/GWh) are ex-ante and are as following: Fuel Type; Fuel Consumption Intensity [t/GWh, m3/GWh]. Coal; 395. Lignite; 1,585. Fuel Oil; 301. Diesel Oil; 492. LPG; 0. Naphtha; 243. Natural Gas; 218. The project has generated 117,063.41 MWh in the monitoring period. This corresponds to the following expected fuel avoidance: Fuel Type; Avoided Fuel Consumption [t, m3]. Coal; 45,193. Lignite; 181,346. Fuel Oil; 34,438. Diesel Oil; 56,291. LPG; -. Naphtha; 27,802. Natural Gas; 24,942. |
| Measurement methods and procedures | - |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | To ensure that the project generates and supplies clean energy to the national grid, improving the carbon intensity of the power mix. |
| Additional comment | - |

SDG 13 (Indicators 13.2.1)

| Data / Parameter | BEy |
| --- | --- |
| Unit | tCO2e |
| Description | Emission reductions achieved per year |
| Source of data | Calculated from the power generated per year |
| Value(s) applied | Period; BEy (tCO2e). 01/11/2018 - 31/12/2018; 13,723.5. 01/01/2019 - 31/12/2019; 82,116. 01/01/2020 - 31/12/2020; 82,116. 01/01/2021 - 31/10/2021; 68,392.5. Total; 246,348. |
| Measurement methods and procedures | Calculated |
| Monitoring frequency | Continuous monitoring and monthly recording. |
| QA/QC procedures | N.A. |
| Purpose of data | To Monitor SDG 13 Indicator |
| Additional comment | - |

| Data / Parameter | LFGelec |
| --- | --- |
| Unit | m3 |
| Description | Quantity of methane destroyed by generation of electricity |
| Source of data | Measured continuously through a mass flow meter |
| Value(s) applied | Period; LFGelec (m3). 01/11/2018 - 31/12/2018; 11,91,310.54. 01/01/2019 - 31/12/2019; 63,01,864.52. 01/01/2020 - 31/12/2020; 57,42,518.25. 01/01/2021 - 31/10/2021; 56,90,908.51. Total; 1,89,26,601.82. |
| Measurement methods and procedures | The monitoring system works with continuous measurement devices. It is programmed to automatically save every 10 min. values. The data are stored automatically at the server for 2 years. |
| Monitoring frequency | Continuous monitoring and monthly recording. |
| QA/QC procedures | - |
| Purpose of data | Calculation of baseline emissions |
| Additional comment | - |

| Data / Parameter | Operation of the energy plant |
| --- | --- |
| Unit | Hours |
| Description | Operation of the energy plant |
| Source of data | Project developer |
| Value(s) applied | Gas Engine; Operation Hours (h) within the monitoring period. GM1; 58062. GM2; 62779. GM3; 60887. GM4; 56917. GM5; 59074. |
| Measurement methods and procedures | The counting devices of the engines are counting the operational hours continuously as the operational hours are also used for maintenance reasons. |
| Monitoring frequency | Continuous monitoring and monthly recording. |
| QA/QC procedures | N.A. |
| Purpose of data | Calculation of baseline emissions |
| Additional comment | - |

| Data / Parameter | AF |
| --- | --- |
| Unit | % |
| Description | Regulatory requirements relating landfill gas projects |
| Source of data | National laws and regulations. |
| Value(s) applied | 0 |
| Measurement methods and procedures | The counting devices of the engines are counting the operational hours continuously as the operational hours are also used for maintenance reasons. |
| Monitoring frequency | Continuous monitoring and monthly recording. |
| QA/QC procedures | In case of a change of Article 27 of the relevant regulation “Control of Solid Waste Regulation”, this change will be included to the monitoring plan. |
| Purpose of data | Calculation of baseline emissions |
| Additional comment | Since there is no change in the legislative structure that forces old landfill sites to utilize landfill gas and no change to article 27 of the relevant regulation “Control of Solid Waste Regulation”, AF and hence MDBL has been considered 0. |

| Data / Parameter | Opj,h |
| --- | --- |
| Unit | - |
| Description | Operation of the equipment that consumes the LFG |
| Source of data | - |
| Value(s) applied | The operation of the plant h is monitored by: - Products generated (such as electricity generation) Opj,h=0 when: - No products are generated in hour h Otherwise Opj,h=1 |
| Measurement methods and procedures | - |
| Monitoring frequency | Hourly |
| QA/QC procedures | - |
| Purpose of data | Baseline calculations |
| Additional comment | - |

| Data / Parameter | Management of SWDS |
| --- | --- |
| Unit | - |
| Description | Management of SWDS |
| Source of data | One of the following sources are used: - Original design of the landfill - Technical specifications for the management of the SWDS - Local or national regulations |
| Value(s) applied | - |
| Measurement methods and procedures | Project developer refers to the original design of the landfill to ensure that any practice to increase methane generation have been occurring prior to the implementation of the project activity. Any change in the management of the SWDS after the implementation of the project activity is justified by referring to technical or regulatory specifications. |
| Monitoring frequency | Annually |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | - |

| Data / Parameter | vCH4,t,db,engine |
| --- | --- |
| Unit | m3 gas CH4/ m3 dry gas |
| Description | Volumetric fraction of CH4 in a time interval t on a dry basis |
| Source of data | - |
| Value(s) applied | 0.49 |
| Measurement methods and procedures | Continuous gas analyzer operating in dry basis |
| Monitoring frequency | Continuous |
| QA/QC procedures | Calibration includes reading verification with a standard gas (single calibration gas or mixture calibration gas). Calibration and frequency of calibration is according to manufacturer’s specifications. |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data / Parameter | Vt,db,engine |
| --- | --- |
| Unit | Nm3/year |
| Description | Volumetric flow of the gaseous stream in time interval t on a dry basis |
| Source of data | - |
| Value(s) applied | Year; Value. 01/11/2018 – 31/12/2018; 2,431,246. 01/01/2019 – 31/12/2019; 12,860,948. 01/01/2020 – 31/12/2020; 11,719,425. 01/01/2021 – 31/10/2021; 11,614,099. Total; 38,625,718. |
| Measurement methods and procedures | Directly, using Thermal mass flow measuring system by Sierra Steelmass 640s with the serial number 127736. The accuracy of the measurement is 1.0% F/S. |
| Monitoring frequency | Continuous |
| QA/QC procedures | - |
| Purpose of data | Baseline emissions |
| Additional comment | - |

| Data / Parameter | Tt |
| --- | --- |
| Unit | K |
| Description | Temperature of the gaseous stream in time interval t |
| Source of data | - |
| Value(s) applied | 60°C |
| Measurement methods and procedures | Direct measurement |
| Monitoring frequency | Continuous |
| QA/QC procedures | Periodic calibration against a primary device provided by an independent accredited laboratory. In accordance with the “Regulation on Measurement and Measuring Tools”, the meters are calibrated within a frequency of once per 10 years. |
| Purpose of data | Since all parameters are converted to normal conditions during the monitoring process, this parameter is only monitored to verify the applicability condition is met related gaseous stream flow temperature being 60°C. |
| Additional comment | - |

| Data / Parameter | SO2 emission |
| --- | --- |
| Unit | kg/MWh |
| Description | The air quality is related to pollutants such as SOx which are being emitted in the baseline scenario. As a representative indicator of air pollution, SO2 is selected as further oxidation of sulfur dioxide may lead to acid rains and as it is a precursor to particulates in the atmosphere, both of which are environmental concerns. |
| Source of data | Turkish Greenhouse Gas Inventory and electricity generation values of project |
| Value(s) applied | Total SO2 emission related to electricity generation is about 2.5 Mt in 2019 according to National Inventory of Turkey. Considering that electricity generation in 2019 is 245,300 GWh, SO2 emission per MWh is calculated as 10.19 kg/MWh. Within the monitoring period a total of 117,063.41 MWh electricity has been generated and delivered to the national grid system utilizing the LFG. This corresponds to 1228.6 tons of SO2 reductions. |
| Measurement methods and procedures | Indirectly, by measuring net electricity generation and multiplication with the baseline SO2 intensity of the Turkish grid. |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | - |

| Data / Parameter | NOx emission |
| --- | --- |
| Unit | kg/MWh |
| Description | The air quality is related to pollutants such as NOx which are being emitted in the baseline scenario. As a representative indicator of air pollution, nitrogen oxide is selected because mono-nitrogen oxides eventually form nitric acid when dissolved in atmospheric moisture, forming a component of acid rain. |
| Source of data | Turkish Greenhouse Gas Inventory and electricity generation values of project |
| Value(s) applied | Total NOx emission related to electricity generation is about 0.77 Mt in 2019 according to National Inventory of Turkey6. NOx emission per MWh is calculated as 3.139 kg. Within the monitoring period a total of 117,063.81 MWh electricity has been generated and delivered to the national grid system utilizing the LFG. This corresponds to 378.47 tons of NOx reductions. |
| Measurement methods and procedures | Indirectly, by measuring net electricity generation and multiplication with the baseline NOx intensity of the Turkish grid. |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | - |

| Data / Parameter | Reduction of odor |
| --- | --- |
| Unit | - |
| Description | - |
| Source of data | Interview with local community |
| Value(s) applied | By effectively collecting LFG that would otherwise be emitted freely, the project reduces H2S (a foul-smelling gas) and VOC emissions. |
| Measurement methods and procedures | - |
| Monitoring frequency | Periodically |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | In the baseline situation, the gases were being emitted freely from the landfill site and blown away in the wind direction, frequently towards nearby neighborhoods. |
| Data / Parameter | Reduction of Volatile Organic Compounds |
| Unit | m3 |
| Description | - |
| Source of data | By measuring the amount of methane destroyed through combustion or flaring. |
| Value(s) applied | The non-methane VOCs are typically roughly 2% of methane emissions. The methane destroyed by the Project annually is 12,621 tons = 17,606,042.56 m3 Baseline VOCs emissions: 17,606,042.56 m3*2% = 352,120.8 m3 The VOC destruction by combustion or flaring can be expected to be greater than 98%. This leads to the following baseline emissions of VOCs: VOCs Reduced = 352,120.8 m3*98% = 345,078.4 m3 For the current monitoring period: 345,078.4 m3*3 years = 1,035,253 m3 VOCs reduced |
| Measurement methods and procedures | Indirectly, by monitoring amount of methane destroyed |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | - |

| Data / Parameter | Reduction of discharged cooling water in the baseline |
| --- | --- |
| Unit | m3/MWh |
| Description | Water quality and quantity |
| Source of data | The net electricity generation of the project is being recorded and multiplied with the ex-ante cooling water discharge intensity. |
| Value(s) applied | In 2018, 7.5 billion m3 cooling water was discharged by thermal power plants in Turkey. Net electricity generation in thermal power plants in 2018 was 205,231,208 MWh, corresponding to 36.5 m3/MWh discharged cooling water intensity. Estimated discharged cooling water reduction in monitoring period is: 36.5 m3/MWh * 117,063.41 MWh = 4,272,814.465 m3 |
| Measurement methods and procedures | The net electricity generation of the project was recorded and multiplied with the ex-ante cooling water discharge intensity. |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | This is a conservative approach because most of the cooling water discharge stems from thermal and nuclear (not existing) power plants. |

| Data / Parameter | H2S emission |
| --- | --- |
| Unit | kg |
| Description | H2S is emitted from the landfill site freely to the atmosphere, creating bad odor and worsens the living conditions of the nearby communities. Although there are several odorous gases in LFG, as a representative indicator of air pollution, hydrogen sulfide is selected because it is a very poisonous, flammable gas with the characteristic foul odor of rotten eggs. |
| Source of data | By measuring LFG destruction and multiplying with the ex-ante baseline H2S intensity of the LFG. |
| Value(s) applied | The gas measurements on the project site show that the H2S concentration in the LFG is 52.8 ppm on average. The project is expected to destroy 12,621 tons of methane annually. This corresponds to 1,359.9 kg of avoided H2S. |
| Measurement methods and procedures | By measuring LFG destruction and multiplying with the ex- ante baseline H2S intensity of the LFG. |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | - |

| Data / Parameter | Leachate management |
| --- | --- |
| Unit | - |
| Description | - |
| Source of data | Project developer |
| Value(s) applied | The leachate is properly collected, stored and transported safely to the municipal treatment facility. |
| Measurement methods and procedures | The leakage is sent to sewage treatment facility of Gaziantep Metropolitan Municipality where the leachate water is disposed. There is declaration of Gaziantep Metropolitan Municipality indicates that they are responsible of collecting the leachate from the project site. |
| Monitoring frequency | Annually |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | - |

| Data / Parameter | Hazardous waste processing |
| --- | --- |
| Unit | - |
| Description | - |
| Source of data | Assessment of waste management practice |
| Value(s) applied | The landfill is only accepting municipal waste and not accepting hazardous waste. In accordance with the currently law and regulations, hazardous waste is only managed at special purpose facilities. |
| Measurement methods and procedures | - |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | To ensure that the project is not function as a hazardous waste disposal or processing facility (i.e., as a hazardous waste gasification – or incineration facility). |
| Additional comment |  |

SDG 8 (Indicators 8.6.1)

| Data / Parameter | Quality of employment |
| --- | --- |
| Unit | Number |
| Description | Number of trainings |
| Source of data | Number of Trainings sessions held |
| Value(s) applied | 9 trainings conducted. Sr No.; Training Date. 1; 08-09/05/2019. 2; 03-04/04/2019. 3; 24-25/12/2019. 4; 16-17/07/2019. 5; 18-19/06/2019. 6; 21-22/02/2019. 7; 02-03/03/2020. 8; 27-28/07/2020. 9; 05-06/01/2021. |
| Measurement methods and procedures | Training certificates |
| Monitoring frequency | Once for each monitoring period |
| QA/QC procedures | Training certificates or training attendance records are provided during each monitoring period. |
| Purpose of data | Monitoring the trainings to justify contribution to SDG 8.6.1. Protect labour rights and promote safe and secure working environments for all workers, including migrant workers, in particular women migrants, and those in precarious employment. |
| Additional comment | - |

SDG 8 (Indicators 8.5.2)

| Data / Parameter | Quality of employment |
| --- | --- |
| Unit | - |
| Description | Safe and healthy working conditions |
| Source of data | Attendance at trainings, assessment of working conditions by checking safety material, tasks of the personnel etc. |
| Value(s) applied | The project activity provides a safe working environment to its employees. The employees are also given training and education on occupational health and safety issues. |
| Measurement methods and procedures | Training certificates and safety materials built in the project site which ensures safe and healthy working conditions are checked. Safety materials built in the project site are; - Electricity shock warnings - Fire extinguishers - First aid station - Precautions against coronavirus - Prohibited actions and warnings for transformer - Protective equipment and warning signs The evidence (photographs) on safety materials built in the project site are shared with DOE for consideration. |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | To ensure that necessary safety equipment is available and properly used and the working environment does not present health risks or hazardous tasks. |
| Additional comment | - |

| Data / Parameter | Quantitative employment and income generation |
| --- | --- |
| Unit | - |
| Description | Number of employments |
| Source of data | Social security records of the employees |
| Value(s) applied | 16 employments generated during 2018 15 employments generated during 2019 20 employments generated during 2020 20 employments generated during 2021 Thus, the average number of employments generated during the current monitoring period is considered to be 17. List of employees: Name; Profession. Süleyman Konuş; Technician. Yusuf Acar; Technician. Doğan Irmak; Technician. Hamza Şeker; Worker. Burak Akay; Accountant. Ismail Cengiz; Office Worker. Mahmut Öztürk; Gardener. Arif Kahraman; Electrician. Faruk Naim; Technician. Mustafa Bozkurt; Security. Ahmet Şeker; Technician. Cüneyt Öner; Operator. Do Min Ko; Manager. Hüseyin Kahraman; Electrician. Mehmet Şeker; Worker. Ertuğrul Şeker; Worker. Adem Bilgili; Plumber. Mustafa Yilmaz; Construction Equipment Technician. Mehmet Ersin Ari; Electrician. Ömer Faruk Anik; Electrical and Electronics Engineer. Ibrahim Halil Kalkan; Electrician. Erdal Yalçin; Worker. Yusuf Yilmaz; Machine Technician. Suat Ramazan Özbolat; Machine Technician. Mustafa Kalkan; Electrician. Serhat Kiliç; Electrician. Ibrahim Altunbaş; Electrician. Ökkeş Pekmezci; Machine Oils Technician. Aydin Altunova; General Area Curator. Muhammet Hakan Incirli; Machine Maintainer. Cuma Saridağ; Machine Maintainer. Ahmet Tosun; Security. Mehmet Uruç; General Area Curator. Erkan Ercan; Electrician. Average number of employment generated during current monitoring period is considered to be 17. |
| Measurement methods and procedures | The number of working people is measured based on social insurance registries and receipts of employees. |
| Monitoring frequency | Annually |
| QA/QC procedures | - |
| Purpose of data | To exhibit employment performance of the plant |
| Additional comment | - |

| Data / Parameter | Value of the imported natural gas avoided (conservative) |
| --- | --- |
| Unit | - |
| Description | Balance of payments and investment |
| Source of data | The avoided natural gas amount is taken from the indicator “Access to affordable and clean energy services”. The energy content of this amount is multiplied by the ex-ante natural gas price. |
| Value(s) applied | Within the monitoring period a total of 117,063.41 MWh has been generated through utilization of LFG. This corresponds to a natural gas price estimated to be 1,893,336 USD. |
| Measurement methods and procedures | - |
| Monitoring frequency | Continuously |
| QA/QC procedures | - |
| Purpose of data | - |
| Additional comment | In baseline situation, some portions of liquid and solid fossil fuels are extracted in the host country. However, most of the natural gas consumed in the host country is imported. Average natural gas price at the current situation is 4.74 USD/MMBtu. 1 MMBTU = 0.293071 MWh, therefore 4.74 USD/MMBtu = 16.1736 USD/MWh |

##### D.3. Comparison of monitored parameters with last monitoring period,

Not applicable for non-Community Service Activities.

##### D.4. Implementation of sampling plan

No sampling is required.

#### SECTION E. CALCULATION OF SDG IMPACTS

##### E.1. Calculation of baseline value or estimation of baseline situation of each SDG Impact

246,347 tCO2e (for SDG 13)

0 MWh (for SDG 7)

0 employment generated and 0 trainings conducted (for SDG 8)

According to the referred methodology the emission reductions are calculated with the following equation:

Where:

| ERy | Emission reductions in year y (tCO2e/year) |
| --- | --- |
| BEy | Baseline emissions in year y (tCO2e/year) |
| PEy | Project emissions in year y (tCO2e/year) |

Baseline emissions

In accordance with the applicable methodologies the baseline is estimated as follows:

BEY=1-OXtop-layer*FCH4,PJ,y-FCH,BL,y*GWPCH4+BEEC,y

Where:

| BE,y | Baseline emissions in year y (tCO2e/yr) |
| --- | --- |
| OX | Fraction of methane in the LFG that would be oxidized in the top layer of the SWDS in the baseline |
| FCH4,PJ,y | Amount of methane in the LFG which is flared and/or used in the project activity in year y (tCH4/yr). |
| FCH4,BL,y | Amount of methane in the LFG which is flared in the baseline in year y (tCH4/yr). |
| GWPCH4 | Global Warming Potential for methane |
| BEEC,y | Baseline emissions associated with the electricity generation in year y (tCO2e/yr). |

Ex post determination of FCH4,PJ,y

Since the project activity only covers utilization of LFG in power plant the FCH4,PJ,y is equal to FCH4,EL,y where FCH4,EL,y is amount of methane in the LFG which is used for electricity generation in year y (tCO2e/yr) and is determined using the “Tool to determine the mass flow of a greenhouse gas in a gaseous stream”.

FCH4,EL,y is determined using the “Tool to determine the mass flow of a greenhouse gas in a gaseous stream”.

The tool provides procedures to determine the following parameter:

| Parameter | SI Unit | Description |
| --- | --- | --- |
| Fi,t | kg/h | Mass flow of greenhouse gas i (CO2, CH4, N2O, SF6 or a PFC) in the gaseous stream in time interval t. |

The mass flow of CH4 in LFG is determined through measurement of the flow and volumetric fraction of the gaseous stream (LFG). The “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” provides 6 different ways to make these measurements and the corresponding calculation option for Fi,t.

| Option | Flow of Gaseous Stream | Volumetric Fraction |
| --- | --- | --- |
| A | Volume flow-dry basis | Dry or wet basis |
| B | Volume flow-wet basis | Dry basis |
| C | Volume flow-wet basis | Wet basis |
| D | Mass flow-dry basis | Dry or wet basis |
| E | Mass flow-wet basis | Dry basis |
| F | Mass flow-wet basis | Wet basis |

Option A is applied in the project activity. Since option B and E have not been selected as an option, the absolute humidity of the gaseous stream will not be determined.

Option A:

According to the “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” version 02.0.0, flow measurement on a dry measurement is not doable for a wet gaseous stream. Therefore, it will be demonstrated that the temperature of the gaseous stream (Tt) is less than 600C (333.15 K) at the flow measurement point.

The mass flow of CH4 (FCH4,t) is determined as follows:

With

Where:

| FCH4,t | Mass flow of CH4 in the gaseous stream in time interval t (kg gas/h) |
| --- | --- |
| Vt,db | Volumetric flow of the gaseous stream in time interval t on a dry basis (m3 dry gas/h) |
| vCH4,t,db | Volumetric fraction of CH4 in the gaseous stream in a time interval t on a dry basis (m3 gas CH4/m3 dry gas) |
| pCH4,t | Density of CH4 in the gaseous stream in time interval t (kg gas CH4/ m3 gas CH4) |
| Pt | Absolute pressure of the gaseous stream in time interval t (Pa) |
| MMCH4 | Molecular Mass of CH4 (kg/kmol) |
| Ru | Universal ideal gases content (Pa.m3/kmol.K) |
| Tt | Temperature of gaseous stream in time interval t (K) |

Baseline emissions associated with electricity generation (BEEC,y)

The baseline emissions associated with electricity generation in year y (BEEC,y) is calculated in accordance with the “Tool to calculate baseline, project and leakage emissions from electricity consumption” version 1. The electricity source k in the tool corresponds to the sources of electricity generated by the grid, which is identified as the most plausible baseline scenario. ECBL,k,y in the tool is equivalent to the net amount of electricity generated using LFG in year y.

Generic approach

In the generic approach, baseline emissions from consumption of electricity are calculated based on the quantity of electricity consumed, an emission factor for electricity generation and a factor to account for transmission losses, as follows:

Where:

| BEEC,y | Baseline emissions from electricity consumption in year y (tCO2e/yr) |
| --- | --- |
| ECBL,k,y | Net amount of electricity generated using LFG in year y (MWh/yr) |
| EFEL,k,y | Emission factor for electricity generation source k in year y (tCO2e/MWh) |
| TDLk,y | Average technical and transmission and distribution losses for providing electricity to source k in year y |
| k | the sources of electricity generated by the grid |

Determination of FCH4,BL,y

This step provides a procedure to determine the amount of methane that would have been captured and destroyed (by flaring) in the baseline due to regulatory requirements, or to address safety and odour concerns. ACM0001 “Flaring or Use of Landfill Gas” provides 4 cases and corresponding instructions.

| Situation at the start of the project activity: | Requirement to destroy methane | Existing LFG capture system |
| --- | --- | --- |
| Case 1: No requirement to destroy methane exists and no existing LFG capture system | No | No |
| Case 2: Requirement to destroy methane exists and no existing LFG capture system | Yes | No |
| Case 3: No requirement to destroy methane exists and an LFG capture system exists | No | Yes |
| Case4: Requirement to destroy methane exists and LFG capture system exists | Yes | Yes |

The situation at the start of the project activity falls under case 1 since there are no legal requirements in Turkey to destroy methane and the LFG was not captured prior to the project activity.

Therefore:

FCH4,BL,y=0

Project Emissions

In accordance with ACM0001 “Flaring or Use of Landfill Gas”, the project emissions are calculated as follows:

Where:

| PEEC,y | Emission from consumption of electricity due to the project activity in year y (tCO2e/yr). |
| --- | --- |

Since there is no consumption of fossil fuels due to the project activity, for the purpose other than electricity generation, there are no emissions from fossil fuel consumption and therefore PEFC,y is equal to “0” and has not been included in equation.

The project emissions from consumption of electricity by the project activity PEEC,y shall be calculated using the “Tool to calculate baseline, project and/or leakage emissions from electricity consumption”. When applying the tool, electricity sources j in the tool corresponds to the sources of electricity consumed due to the project activity.

PEEC,y is calculated as follows:

Where:

| PEEC,y | Project emissions from electricity consumption in year y (tCO2e/year) |
| --- | --- |
| ECPJ,y | Quantity of electricity consumed by the project electricity consumption source j in year y (MWh/year) |
| EFEL,j,y | Emission factor for electricity generation for source j in year y (tCO2e/MWh) |
| TDLj,y | Average technical transmission and distribution losses for providing electricity to source j in year y |

The combined margin emission factor of the applicable electricity system has been determined as emission factor for the electricity system (EFEL,j,y), in line with Option A1 of scenario A (Electricity consumption from grid) under the “Tool to calculate baseline, project and/or leakage emissions from electricity consumption”.

##### E.2. Calculation of project value or estimation of project situation of each SDG Impact

SDG 7: Affordable and Clean Energy

- For the current monitoring period, the clean energy generation contributed by the project activity is 117,063.41 MWh.

SDG 13 Climate Action:

- For the current monitoring period, the emission reductions contributed by the project activity (ER) is calculated as follows:

ERy = BEy - PEy - LEy

- Where:

ERy	=	Emission reductions (tCO2e)

- BEy	=	Baseline emissions (tCO2e)

- PEy	=	Project emissions due to electricity consumption from the grid (tCO2e)

- LEy      	=	Leakage emissions (tCO2e)

| - Period | BEy (tCO2e/year) | PEy (tCO2e/year) | LEy (tCO2e/year) | ERy (tCO2e/year) |
| --- | --- | --- | --- | --- |
| - 01/11/2018-31/12/2018 | 13,723.5 | 0.02 | 0 | 13,723 |
| - 2019 | 82,116.0 | 0.30 | 0 | 82,116 |
| - 2020 | 82,116.0 | 0.37 | 0 | 82,116 |
| - 01/01/2021-31/10/2021 | 68,393.5 | 0.70 | 0 | 68,392 |
| - Total | 246,348.0 | 1.40 | 0 | 246,347 |

SDG 8: Decent Work and Economic Growth

The project leads to employment opportunities which would not have been possible in the baseline scenario. The project generated 17 employment opportunities and also 9 trainings conducted for the current monitoring period.

##### E.3. Calculation of leakage

In accordance with ACM0001 “Flaring or Use of Landfill Gas”, no leakage effects are accounted.

##### E.4. Calculation of net benefits or direct calculation for each SDG Impact

| SDG | SDG Impact | Baseline estimate | Project estimate | Net benefit |
| --- | --- | --- | --- | --- |
| 13 | Take urgent action to combat Climate Change and its impacts | 246,348 tCO2e | 1.40 tCO2e | 246,347 tCO2e |
| 7 | Ensure access to affordable, reliable, sustainable and modern energy for all | 0 MWh | 117,063.41 MWh | 117,063.41 MWh |
| 8 | Promote sustained, inclusive and sustainable economic growth, full and productive employment and decent work for all | - | 17 employment generated and 9 trainings conducted | 17 employment generated and 9 trainings conducted |

##### E.5. Comparison of actual SDG Impacts with estimates in approved PDD

| SDG |  | Values estimated in ex ante calculation of approved PDD for this monitoring period | Actual values achieved during this monitoring period |
| --- | --- | --- | --- |
| 13 |  | 246,348 tCO2e | 246,347 tCO2e |
| 7 |  | 63,513 MWh | 117,063.41 MWh |
| 8 |  | Employment to at least 10 people and minimum 1 training per year | 17 employment generated and 9 trainings conducted |

E.5.1. Explanation of calculation of value estimated ex ante calculation of approved PDD for this monitoring period

SDG7: Affordable and Clean Energy

The annual estimated power generation for the project activity is 21,171 MWh, thus considering number of days covered during present monitoring period to be 1096, the estimated power generation will be 63,513 MWh.

SDG 13: Climate Action

The annual estimated emission reduction for the project activity is 82,116 tCO2e, thus considering number of days covered during present monitoring period to be 1096, the estimated emission reduction contributing towards SDG 13 will be 246,348 tCO2e.

SDG 8: Decent Work and Economic Growth

The project is estimated to provide employment to at least 10 people and minimum 1 training per year.

##### E.6. Remarks on increase in achieved SDG Impacts from estimated value in approved PDD

Actual electricity generation is on higher side however this is attributed towards increased LFG flow and not in control of project owner. Also, as a conservative approach considering the increased power generation, the project owner has decided to cap the emission reductions to the extent of annual estimated emission reductions as per the registered PDD and thus accordingly the MR has been revised following the rule prescribed in para 2.1.4 of Rule Clarification “Assessment Approach for Reporting Higher Ex-post Emission Reductions” .

Thus with the application of this rule, the SDG contributions are not over estimated and conservative approach is being followed to report the project level indicators.

#### SECTION F. SAFEGUARDS REPORTING

As per the Safeguarding Principle Assessment presented in the Transition Annex of the project, there are no safeguarding principles which are to be included in the monitoring plan or hold any relevance to the project activity. Also, there are not any impact (positive/negative/slightly) for any mitigation measures, being applicable to any of the safeguarding principles. Hence, this section is not relevant.

#### SECTION G. STAKEHOLDER INPUTS AND LEGAL DISPUTES

##### G.1. List all Inputs and Grievances which have been received via the Continuous Input and Grievance Mechanism together with their respective responses/mitigations.

- Stakeholder consultation for the project has been carried out at validation stage. Since the project was registered under previous version of GS, hence, no specific mechanism defined for on-going stakeholder consultations post implementation. Prior to validation, various unofficial meetings have been carried out between the project owner and local communities. Since an EIA report was not required by the Ministry of Environment and Forest, no official EIA meeting was organized.

- Moreover, stakeholder engagement procedure was being conducted at the Gaziantep LFG control room with the local stakeholders and heads of the Akbulut Village on within verification process. The contact information of Company Executive of the company was given to Mukhtars (heads of the village) of Akbulut Villages so that the local stakeholders will be able to reach company executive whenever they have any complaints, suggestions, or ideas about the project. Since mukhtar is the head of the village, he is the main contact person between the project owner and the local stakeholders. Muhtar made sure that there is continuous communication between the two parties. Moreover, logbook was delivered to the head of Akbulut Village. The logbook is present at project site in order to account continuous ongoing grievance mechanism.

##### G.2. Report on any stakeholder mitigations that were agreed to be monitored.

Not Applicable since there were no stakeholder mitigations were agreed to be monitored for the current monitoring period.

##### G.3. Provide details of any legal contest that has arisen with the project during the monitoring period

Not Applicable since the project did not receive any legal disputes during the current monitoring period.

Appendix 1- Monitoring Equipment Calibration Schedule

Table 3: Electricity Meters Calibration Schedule

| Specification | Main Meter | Validity | Spare Meter | Validity |
| --- | --- | --- | --- | --- |
| Type | LSM50 |  | C510.AMT.5851.RS485 |  |
| Year of Manufacture | 2019 |  | 2015 |  |
| Serial Number | 50002081 |  | 65000306 |  |
| Date of Calibration | 02/10/2019 | 01/10/2029 | 15/04/2015 | 14/04/2025 |
| Manufacturing standard / Class | 0.5S |  | 0.5S |  |

Table 4: Gas Analyzer Calibration Schedule

| Specification |  | Validity |
| --- | --- | --- |
| Type | X-STREAM-2M 1.10 23.06.09 |  |
| Year of Manufacture | 2009 |  |
| Serial Number | XMC09902465136 |  |
| Date of Calibration | 22/09/2009 | Valid all the time |

Table 5: Flowmeter Calibration Schedule

| Specification |  | Validity |
| --- | --- | --- |
| Model | 640S-NAA-L13-M0-E2-P2-V4-DD-5 |  |
| Year of Manufacture | 2009 |  |
| Serial Number | 127736 |  |
| Date of Calibration | 28/09/2009 | Valid all the time |

Revision History

| Version | Date | Remarks |
| --- | --- | --- |
| 1.1 | 14 October 2020 | Hyperlinked section summary to enable quick access to key sections Improved clarity on Key Project Information Section for POA monitoring Forward action request section Improved Clarity on SDG contribution/SDG Impact term used throughout Clarity on safeguard reporting Clarity on design changes Leakage section added for VER/CER projects Addition of Comparison of monitored parameters with last monitoring period Provision of an accompanying Guide to help the user understand detailed rules and requirements |
| 1.0 | 10 July 2017 | Initial adoption |

https://registry.goldstandard.org/projects/details/1171

https://cdm.unfccc.int/methodologies/DB/JPYB4DYQUXQPZLBDVPHA87479EMY9M

Round down value

This value is the average of employment generation in 2018, 2019, 2020 and 2021.

- https://cdm.unfccc.int/methodologies/DB/203B03KT6N8QCC0R1C56DFOF9OYO2T/view.html

https://www.ghgprotocol.org/sites/default/files/ghgp/Global-Warming-Potential-Values%20%28Feb%2016%202016%29_1.pdf

https://www.teias.gov.tr/tr-TR/turkiye-elektrik-uretim-iletim-istatistikleri

https://webdosya.csb.gov.tr/db/iklim/icerikler/sera_gazi_em-syon-raporu-20200506141834.pdf

https://www.statista.com/statistics/892878/electricity-generation-by-fuel-turkey/

“Estimating Landfill Greenhouse Gas Emissions from Measured Ambient Methane Concentrations and Dispersion Modeling”, Figueroa, Cooper, and Mackie, Link:

http://cee.ucf.edu/odormodeling/publications/Final_Paper_-_Figueroa_et_al_-_AWMA_2008.pdf

27 “Gas Recovery and Utilization From Municipal Solid Waste Landfills”, Todd Potas. Link:

http://www.anl.gov/PCS/acsfuel/preprint%20archive/Files/38_3_CHICAGO_08-93_0895.pdf

https://www.enerjiportali.com/tuik-2018-termik-santral-su-atiksu-ve-atik-istatistiklerini-yayimladi/

https://www.epias.com.tr/wp-content/uploads/2019/06/EPIAS_Annual_Electricity_Marker_Report_2018.pdf

Source: Feasibility study of the Project

https://www.botas.gov.tr/uploads/dosyaYoneticisi/500881-temmuz_2021_tarifesi_30062021.pdf

The parameter (Fi,t) under the “Tool to determine the mass flow of a greenhouse gas in gaseous stream” corresponds to the parameter (FCH4,EL,y) under ACM0001.

FCH4,t described under the “Tool to determine the mass flow of a greenhouse gas in a gaseous stream” corresponds to FCH4,EL,y described under ACM0001 “Flaring or use of a landfill gas”.

Round down value

- Whenever emission reductions are capped, both the original and capped values used for calculations must be transparently reported.  Use brackets to denote original values.