## CER-Spreadsheet
Project: La La Hydropower Project, Vietnam
| Number of Monitoring Period | 1
| Monitoring Period | 01/10/2017 - 29/04/2019
| Version of the Spreadsheet | 2
| Date | 2022-07-06
| Author | Daniel Wunderlin ecotawa AG
Emission Reduction Estimated for the Validation (according to PDD)
| Annual Electricity Production Estimated according to PDD |  | 11980 | MWh | 2017-10-01
| Combined Margin |  | 0.5764 | tCO2/MWh | 2019-04-29
| Annual Emission Reduction |  | 6905 | tCO2/y | 576
| Emission Reduction during monitoring Period |  | 10896.6575 | tCO2/7 y
| Actual Emission reductions achieved during this MP |  | 7884 | tCO2
| Emission Reduction Estimated Ex-ante vs actual emission reduction |  | -27.65%

## Output & CERs
LALA CDM Monitoring Output and CERs
| Month-year | Electricity supplied to the grid (ACCORDING TO MAIN METER M11) | Electricity consumption from the grid | Net Electricity as per EVN records | Net Electricity (Sales Invoices) | Baseline emissions | Project emissions | Leakage emissions | Emission Reductions
|  | PEG | EC |  |  | BE | PE | LE | ER
|  | MWh | MWh | MWh | MWh | tCO2 | tCO2 | tCO2 | tCO2
| 2017-10-31 | 876.417 | 0.181 | 876.236 | 876.236 | 505 | 0 | 0 | 505
| 2017-11-30 | 1020.1048 | 0.12663 | 1019.9782 | 1025.105 | 587 | 0 | 0 | 587
| 2017-12-31 | 857.482 | 0.188 | 857.294 | 857.294 | 494 | 0 | 0 | 494
1586
| 2018-01-31 | 703.514 | 0.16 | 703.354 | 703.354 | 405 | 0 | 0 | 405
| 2018-02-28 | 417.166 | 0.219 | 416.947 | 416.947 | 240 | 0 | 0 | 240
| 2018-03-31 | 354.454 | 1.033 | 353.421 | 353.421 | 203 | 0 | 0 | 203 | Emission Reduction
| 2018-04-30 | 275.392 | 0.086 | 275.306 | 275.306 | 158 | 0 | 0 | 158
| 2018-05-31 | 281.997 | 0.321 | 281.676 | 281.676 | 162 | 0 | 0 | 162 | BE = (PEG - EC) x EF grid,CM
| 2018-06-30 | 458.013 | 0.109 | 457.904 | 457.904 | 263 | 0 | 0 | 263 | ER = BE - PE - LE
| 2018-07-31 | 1339.911 | 0.074 | 1339.837 | 1339.837 | 772 | 0 | 0 | 772
| 2018-08-31 | 2163.556 | 0.006 | 2163.55 | 2163.55 | 1247 | 0 | 0 | 1247
| 2018-09-30 | 1744.6391 | 0.007 | 1744.6321 | 1744.6321 | 1005 | 0 | 0 | 1005 | (1) Project Emission = 0 because power density > 10 W/m2
| 2018-10-31 | 1047.5675 | 0.025 | 1047.5425 | 1047.5425 | 603 | 0 | 0 | 603 | (2) No Leakage emissions are integrated according to Methodology ACM0002
| 2018-11-30 | 642.3762 | 0.38994 | 641.9863 | 645.2162 | 370 | 0 | 0 | 370
| 2018-12-31 | 524.0332 | 0.153 | 523.8802 | 523.8802 | 301 | 0 | 0 | 301
5729
| 2019-01-31 | 399.1727 | 0.103 | 399.0697 | 399.0697 | 230 | 0 | 0 | 230
| 2019-02-28 | 233.5958 | 0.193 | 233.4028 | 233.4028 | 134 | 0 | 0 | 134
| 2019-03-31 | 183.4785 | 0.243 | 183.2355 | 183.2355 | 105 | 0 | 0 | 105
| 2019-04-30 | 174.4452 | 0.465 | 173.9802 | 173.9802 | 100 | 0 | 0 | 100
569
| Total: | 13697.3151 | 4.0826 | 13693.2326 | 13701.5893 | 7884 | 0 | 0 | 7884
13693.2326
Error factor applied for delayed calibrations

## InputData Supply PEG
LALA HPP CDM Monitoring Input Sheet
Unit | MWh |  | STARTING FIGURES OF THE MAIN METER | [10 empty] | STARTING FIGURES OF THE BACK-UP METER
|  |  | tarrif 1 | tarrif 2 | tarrif 3 | [8 empty] | tarrif 1 | tarrif 2 | tarrif 3
Year | 2012-2019 | Reading in Oct -2012 | 35.23 | 9.37 | 15.73 | [5 empty] | YEAR |  | Reading in Oct -2012 | 35.356 | 9.406 | 15.786 |  |  |  | SUPPLY
Main Meter | [10 empty] | Backup Meter
M11 |  | Seri Nr: 11060674 | [8 empty] | M12 |  |  | Serial Nr: 11060670
Month | Date | Time | Meter Reading |  |  | Power generation without measurement | Respons. Person | Ref. Document | Note | Tổng lượng điện bán cho EVN | Month | Date | Time | Meter Reading |  |  | Power generation without measurement | Respons. Person | Ref. Document | Note | Tổng lượng điện bán cho EVN
|  |  | tarrif 1 | tarrif 2 | tarrif 3 | [8 empty] | tarrif 1 | tarrif 2 | tarrif 3
2012-04-30 | 31/05/2016 | 24:00 | - | - | - | [5 empty] | 2012-04-30 | 31/05/2016 | 24:00 |  |  |  |  | Ngũ Văn Tài
2012-10-01 | 31.10.2012 | 24:00 | 562.55 | 170.59 | 248.35 | 11.054 | Nguyễn Hoàng Thắng | File1.1 |  | 910.106 | 2012-10-01 | 2012-10-31 | 24:00 | 563.64 | 171.09 | 249.1 | 11.08 | Nguyễn Hoàng Thắng | File1.1 |  | 912.202
2012-11-01 | 30.11.2012 | 24:00 | 770.75 | 438.02 | 424.07 | 7.816 | Nguyễn Hoàng Thắng | File1.2 |  | 643.534 | 2012-11-01 | 2012-11-30 | 24:00 | 772.23 | 438.93 | 425.19 | 7.83 | Nguyễn Hoàng Thắng | File1.2 |  | 644.69
2012-12-01 | 31.12.2012 | 24:00 | 906.39 | 673.54 | 502.14 | 5.391 | Nguyễn Hoàng Thắng | File1.3 |  | 443.839 | 2012-12-01 | 2012-12-31 | 24:00 | 908 | 674.75 | 503.43 | 5.398 | Nguyễn Hoàng Thắng | File1.3 |  | 444.432
2013-01-01 | 31.01.2013 | 24:00 | 1001.76 | 886.92 | 528.09 | 4.016 | Lã Quý Quyền | File1.4 |  | 330.684 | 2013-01-01 | 2013-01-31 | 24:00 | 1003.44 | 888.45 | 529.47 | 4.022 | Lã Quý Quyền | File1.4 |  | 331.158
2013-02-01 | 28.02.2013 | 24:00 | 1049.95 | 1067.75 | 529.61 | 2.767 | Lã Quý Quyền | File1.5 |  | 227.773 | 2013-02-01 | 2013-02-28 | 24:00 | 1051.68 | 1069.55 | 531 | 2.77 | Lã Quý Quyền | File1.5 |  | 228.1
2013-03-01 | 2013-03-31 | 24:00 | 1074.26 | 1229.23 | 529.61 | 2.229 | Lã Quý Quyền | File1.6 |  | 183.561 | 2013-03-01 | 2013-03-31 | 24:00 | 1075.99 | 1231.29 | 531 | 2.232 | Lã Quý Quyền | File1.6 |  | 183.818
2013-04-01 | 2013-04-30 | 24:00 | 1099.5 | 1397.61 | 529.76 | 2.325 | Lã Quý Quyền | File1.7 |  | 191.445 | 2013-04-01 | 2013-04-30 | 24:00 | 1101.21 | 1399.98 | 531.16 | 2.329 | Lã Quý Quyền | File1.7 |  | 191.741
2013-05-01 | 2013-05-31 | 24:00 | 1162.42 | 1557.83 | 563.02 | 3.077 | Lã Quý Quyền | File1.8 |  | 253.323 | 2013-05-01 | 2013-05-31 | 24:00 | 1164.25 | 1560.45 | 564.5 | 3.082 | Lã Quý Quyền | File1.8 |  | 253.768
2013-06-01 | 2013-06-30 | 24:00 | 1250.72 | 1646.64 | 585.63 | 2.397 | Lã Quý Quyền | File1.9 |  | 197.323 | 2013-06-01 | 2013-06-30 | 24:00 | 1252.72 | 1649.43 | 587.17 | 2.401 | Lã Quý Quyền | File1.9 |  | 197.719
2013-07-01 | 2013-07-31 | 24:00 | 1559.55 | 1743.21 | 659.23 | 5.748 | Lã Quý Quyền | File1.10 |  | 473.252 | 2013-07-01 | 2013-07-31 | 24:00 | 1562.19 | 1746.23 | 660.93 | 5.76 | Lã Quý Quyền | File1.10 |  | 474.27
2013-08-01 | 2013-08-31 | 24:00 | 1887.75 | 1857.44 | 766.06 | 6.591 | Lã Quý Quyền | File1.11 |  | 542.669 | 2013-08-01 | 2013-08-31 | 24:00 | 1891.05 | 1860.76 | 768.05 | 6.606 | Lã Quý Quyền | File1.11 |  | 543.904
2013-09-01 | 2013-09-30 | 24:00 | 2404.2 | 2012.09 | 998.98 | 10.848 | Lã Quý Quyền | File1.12 |  | 893.172 | 2013-09-01 | 2013-09-30 | 24:00 | 2408.65 | 2015.74 | 1001.46 | 10.872 | Lã Quý Quyền | File1.12 |  | 895.118
2013-10-01 | 2013-10-31 | 24:00 | 3315.84 | 2300.41 | 1408.06 | 19.308 | Lã Quý Quyền | File1.13 |  | 1589.732 | 2013-10-01 | 2013-10-31 | 24:00 | 3322.35 | 2304.65 | 1411.46 | 19.351 | Lã Quý Quyền | File1.13 |  | 1593.259
2013-11-01 | 2013-11-30 | 24:00 | 4278.16 | 2616.07 | 1840.43 | 20.57 | Lã Quý Quyền | File1.14 | plus 3.795 MWh after calibration | 1693.575 | 2013-11-01 | 2013-11-30 | 24:00 | 4286.86 | 2620.96 | 1844.78 | 20.615 | Lã Quý Quyền | File1.14 | plus 3.795 after calibration | 1697.32
2013-12-01 | 2013-12-31 | 24:00 | 4957.33 | 2874.55 | 2153.52 | 15.009 | Lã Quý Quyền | File1.15 |  | 1239.526 | 2013-12-01 | 2013-12-31 | 24:00 | 4967.13 | 2879.85 | 2158.38 | 15.033 | Lã Quý Quyền | File1.15 |  | 1237.727
2014-01-01 | 2014-01-31 | 24:00 | 5227.75 | 3131.93 | 2297.17 | 8.058 | Hồ Tiến Sỹ | File1.16 |  | 663.392 | 2014-01-01 | 2014-01-31 | 24:00 | 5237.92 | 3137.57 | 2302.29 | 8.069 | Hồ Tiến Sỹ | File1.16 |  | 664.351
2014-02-01 | 2014-02-28 | 24:00 | 5335.89 | 3352.88 | 2323.35 | 4.263 | Hồ Tiến Sỹ | File1.17 |  | 351.007 | 2014-02-01 | 2014-02-28 | 24:00 | 5346.17 | 3358.86 | 2328.58 | 4.27 | Hồ Tiến Sỹ | File1.17 |  | 351.56
2014-03-01 | 2014-03-31 | 24:00 | 5392.72 | 3557.75 | 2325.05 | 3.161 | Hồ Tiến Sỹ | File1.18 |  | 260.239 | 2014-03-01 | 2014-03-31 | 24:00 | 5403.12 | 3564.1 | 2330.28 | 3.167 | Hồ Tiến Sỹ | File1.18 |  | 260.723
2014-04-01 | 2014-04-30 | 24:00 | 5439.1 | 3713.08 | 2338.15 | 2.578 | Hồ Tiến Sỹ | File1.19 |  | 212.232 | 2014-04-01 | 2014-04-30 | 24:00 | 5449.58 | 3719.82 | 2343.42 | 2.584 | Hồ Tiến Sỹ | File1.19 |  | 212.736
2014-05-01 | 2014-05-31 | 24:00 | 5467.12 | 3845.05 | 2340.24 | 1.945 | Hồ Tiến Sỹ | File1.20 |  | 160.135 | 2014-05-01 | 2014-05-31 | 24:00 | 5477.66 | 3852.08 | 2345.53 | 1.949 | Hồ Tiến Sỹ | File1.20 |  | 160.501
2014-06-01 | 2014-06-30 | 24:00 | 5591.41 | 3961.98 | 2380.34 | 3.376 | Hồ Tiến Sỹ | File1.21 |  | 277.944 | 2014-06-01 | 2014-06-30 | 24:00 | 5602.23 | 3969.28 | 2385.75 | 3.384 | Hồ Tiến Sỹ | File1.21 |  | 278.606
2014-07-01 | 2014-07-31 | 24:00 | 5847.18 | 4050.55 | 2441.16 | 4.862 | Hồ Tiến Sỹ | File1.22 |  | 400.298 | 2014-07-01 | 2014-07-31 | 24:00 | 5858.65 | 4058.11 | 2446.74 | 4.875 | Hồ Tiến Sỹ | File1.22 |  | 401.365
2014-08-01 | 2014-08-31 | 24:00 | 6187.65 | 4169.74 | 2517.81 | 6.436 | Hồ Tiến Sỹ | File1.23 |  | 529.874 | 2014-08-01 | 2014-08-31 | 24:00 | 6199.95 | 4177.67 | 2523.66 | 6.453 | Hồ Tiến Sỹ | File1.23 |  | 531.327
2014-09-01 | 2014-09-30 | 24:00 | 6454.96 | 4273.14 | 2567.11 | 5.04 | Hồ Tiến Sỹ | File1.24 |  | 414.97 | 2014-09-01 | 2014-09-30 | 24:00 | 6467.85 | 4281.36 | 2573.12 | 5.052 | Hồ Tiến Sỹ | File1.24 |  | 415.998
2014-10-01 | 2014-10-31 | 24:00 | 6693.87 | 4384.12 | 2584.68 | 4.409 | Hồ Tiến Sỹ | File1.25 |  | 363.051 | 2014-10-01 | 2014-10-31 | 24:00 | 6707.22 | 4392.66 | 2590.76 | 4.42 | Hồ Tiến Sỹ | File1.25 |  | 363.89
2014-11-01 | 2014-11-30 | 24:00 | 6795.54 | 4598.52 | 2603.76 | 4.016 | Hồ Tiến Sỹ | File1.26 | minus 0.49 after calibration | 330.644 | 2014-11-01 | 2014-11-30 | 24:00 | 6808.9 | 4607.66 | 2609.91 | 4.024 | Hồ Tiến Sỹ | File1.26 | minus 0.49 after calibration | 331.316
2014-12-01 | 2014-12-31 | 24:00 | 6976.78 | 4864.58 | 2664.61 | 6.098 | Hồ Tiến Sỹ | File1.27 |  | 502.052 | 2014-12-01 | 2014-12-31 | 24:00 | 6990.29 | 4874.21 | 2671.01 | 6.108 | Hồ Tiến Sỹ | File1.27 |  | 502.932
2015-01-01 | 2015-01-31 | 24:00 | 7026.98 | 5115.19 | 2667.62 | 3.646 | Hồ Tiến Sỹ | File1.28 |  | 300.174 | 2015-01-01 | 2015-01-31 | 24:00 | 7040.4 | 5125.3 | 2674.04 | 3.651 | Hồ Tiến Sỹ | File1.28 |  | 300.579
2015-02-01 | 2015-02-28 | 24:00 | 7072.98 | 5314.02 | 2667.62 | 2.938 | Hồ Tiến Sỹ | File1.29 |  | 241.892 | 2015-02-01 | 2015-02-28 | 24:00 | 7086.37 | 5324.55 | 2674.04 | 2.943 | Hồ Tiến Sỹ | File1.29 |  | 242.277
2015-03-01 | 2015-03-31 | 24:00 | 7085.92 | 5480.89 | 2667.62 | 1.165 | Hồ Tiến Sỹ | File1.30 |  | 178.645 | 2015-03-01 | 2015-03-31 | 24:00 | 7099.22 | 5491.84 | 2674.04 | 1.167 | Hồ Tiến Sỹ | File1.30 |  | 178.973
2015-04-01 | 2015-04-30 | 24:00 | 7094.14 | 5603.11 | 2667.62 | 1.565 | Hồ Tiến Sỹ | File1.31 |  | 128.875 | 2015-04-01 | 2015-04-30 | 24:00 | 7107.32 | 5614.41 | 2674.04 | 1.568 | Hồ Tiến Sỹ | File1.31 |  | 129.102
2015-05-01 | 2015-05-31 | 24:00 | 7100.18 | 5698.67 | 2667.62 | 1.219 | Hồ Tiến Sỹ | File1.32 |  | 100.381 | 2015-05-01 | 2015-05-31 | 24:00 | 7113.24 | 5710.27 | 2674.04 | 1.221 | Hồ Tiến Sỹ | File1.32 |  | 100.559
2015-06-01 | 2015-06-30 | 24:00 | 7115.49 | 5805.53 | 2673.24 | 1.533 | Hồ Tiến Sỹ | File1.33 |  | 126.257 | 2015-06-01 | 2015-06-30 | 24:00 | 7128.46 | 5817.36 | 2679.71 | 1.536 | Hồ Tiến Sỹ | File1.33 |  | 126.444
2015-07-01 | 2015-07-31 | 24:00 | 7362.04 | 5893.74 | 2726.39 | 4.655 | Hồ Tiến Sỹ | File1.34 |  | 383.255 | 2015-07-01 | 2015-07-31 | 24:00 | 7375.36 | 5905.77 | 2733.09 | 4.664 | Hồ Tiến Sỹ | File1.34 |  | 384.026
2015-08-01 | 2015-08-31 | 24:00 | 7606.23 | 5971.73 | 2737.19 | 3.996 | Hồ Tiến Sỹ | File1.35 |  | 328.984 | 2015-08-01 | 2015-08-31 | 24:00 | 7619.99 | 5984.08 | 2743.96 | 4.006 | Hồ Tiến Sỹ | File1.35 |  | 329.804
2015-09-01 | 2015-09-30 | 24:00 | 8105.78 | 6147.38 | 2921.03 | 10.308 | Lê Cao anh | File1.36 |  | 848.732 | 2015-09-01 | 2015-09-30 | 24:00 | 8120.61 | 6160.15 | 2928.24 | 10.332 | Lê Cao anh | File1.36 |  | 850.638
2015-10-01 | 2015-10-31 | 24:00 | 8580.37 | 6320.63 | 3067.23 | 9.528 | Lê Cao anh | File1.37 |  | 784.512 | 2015-10-01 | 2015-10-31 | 24:00 | 8596.02 | 6333.91 | 3074.9 | 9.55 | Lê Cao anh | File1.37 |  | 786.28
2015-11-01 | 2015-11-30 | 24:00 | 9107.07 | 6622.36 | 3341.37 | 13.257 | Lê Cao anh | File1.38 | Plus 2.198 after calibration | 1091.511 | 2015-11-01 | 2015-11-30 | 24:00 | 9123.74 | 6636.34 | 3349.84 | 13.288 | Lê Cao anh | File1.38 | plus 2.208 after calibration | 1094.01
2015-12-01 | 2015-12-31 | 24:00 | 9302.35 | 6949.64 | 3383.85 | 6.781 | Lê Cao anh | File1.39 |  | 558.259 | 2015-12-01 | 2015-12-31 | 24:00 | 9318.79 | 6964.45 | 3392.93 | 6.795 | Lê Cao anh | File1.39 |  | 559.455
2016-01-01 | 2016-01-31 | 24:00 | 9424.64 | 7257.84 | 3395.69 | 5.308 | Lê Cao anh | File1.40 |  | 437.022 | 2016-01-01 | 2016-01-31 | 24:00 | 9441.13 | 7273.31 | 3404.91 | 5.318 | Lê Cao anh | File1.40 |  | 437.862
2016-02-01 | 2016-02-29 | 24:00 | 9458.42 | 7493.51 | 3395.69 | 3.233 | Lê Cao anh | File1.41 |  | 266.217 | 2016-02-01 | 2016-02-29 | 24:00 | 9474.98 | 7509.26 | 3404.91 | 3.238 | Lê Cao anh | File1.41 |  | 266.562
2016-03-01 | 2016-03-31 | 24:00 | 9470.52 | 7685.55 | 3395.69 | 2.45 | Lê Cao anh | File1.42 |  | 201.69 | 2016-03-01 | 2016-03-31 | 24:00 | 9487.41 | 7701.32 | 3404.91 | 2.454 | Lê Cao anh | File1.42 |  | 202.036
2016-04-01 | 2016-04-30 | 24:00 | 9490.28 | 7829.06 | 3395.69 | 1.959 | Lê Minh Tiến | File1.43 |  | 161.311 | 2016-04-01 | 2016-04-30 | 24:00 | 9507.5 | 7844.87 | 3404.91 | 1.964 | Lê Minh Tiến | File1.43 |  | 161.676
2016-05-01 | 2016-05-31 | 24:00 | 9503.83 | 7985.51 | 3396.18 | 2.046 | Lê Minh Tiến | File1.44 |  | 168.444 | 2016-05-01 | 2016-05-31 | 24:00 | 9521.31 | 8001.34 | 3405.42 | 2.049 | Lê Minh Tiến | File1.44 |  | 168.741
2016-06-01 | 2016-06-30 | 24:00 | 9518.99 | 8136.54 | 3397.44 | 2.009 | Lê Minh Tiến | File1.45 |  | 165.441 | 2016-06-01 | 2016-06-30 | 24:00 | 9536.66 | 8152.48 | 3406.71 | 2.013 | Lê Minh Tiến | File1.45 |  | 165.767
2016-07-01 | 2016-07-31 | 24:00 | 9723.9 | 8197.1 | 3426.25 | 3.531 | Lê Minh Tiến | File1.46 |  | 290.749 | 2016-07-01 | 2016-07-31 | 24:00 | 9742.01 | 8213.21 | 3435.61 | 3.54 | Lê Minh Tiến | File1.46 |  | 291.44
2016-08-01 | 2016-08-31 | 24:00 | 10093.5 | 8333.26 | 3529.28 | 7.305 | Lê Minh Tiến | File1.47 |  | 601.485 | 2016-08-01 | 2016-08-31 | 24:00 | 10112.43 | 8349.66 | 3539.01 | 7.323 | Lê Minh Tiến | File1.47 |  | 602.947
2016-09-01 | 2016-09-30 | 24:00 | 10563.383 | 8508.924 | 3672.936 | 9.47 | Lê Minh Tiến | File1.48 |  | 779.733 | 2016-09-01 | 2016-09-30 | 24:00 | 10583.125 | 8525.79 | 3683.198 | 9.492 | Lê Minh Tiến | File1.48 |  | 781.521
2016-10-01 | 2016-10-31 | 24:00 | 11193.077 | 8711.572 | 3921.912 | 12.976 | Lê Minh Tiến | File1.49 |  | 1068.342 | 2016-10-01 | 2016-10-31 | 24:00 | 11214.262 | 8728.76 | 3932.945 | 13.006 | Lê Minh Tiến | File1.49 |  | 1070.848
2016-11-01 | 2016-11-30 | 24:00 | 12042.916 | 9010.134 | 4309.505 | 18.432 | Lê Minh Tiến | File1.50 | Minus 0.470 after calibration | 1517.092 | 2016-11-01 | 2016-11-30 | 24:00 | 12066.064 | 9027.976 | 4321.402 | 18.474 | Lê Minh Tiến | File1.50 | minus 0.470 after calibration | 1520.531
2016-12-01 | 2016-12-31 | 24:00 | 12634.293 | 9318.699 | 4582.374 | 14.074 | Lê Minh Tiến | File1.51 |  | 1158.737 | 2016-12-01 | 2016-12-31 | 24:00 | 12658.578 | 9337.099 | 4594.792 | 14.1 | Lê Minh Tiến | File1.51 |  | 1160.927
2017-01-01 | 2017-01-31 | 24:00 | 13002.887 | 9638.951 | 4714.832 | 9.856 | Lê Minh Tiến | File1.52 |  | 811.448 | 2017-01-01 | 2017-01-31 | 24:00 | 13027.834 | 9657.944 | 4727.605 | 9.875 | Lê Minh Tiến | File1.52 |  | 813.039
2017-02-01 | 2017-02-28 | 24:00 | 13181.471 | 9950.725 | 4738.591 | 6.169 | Lê Minh Tiến | File1.53 |  | 507.948 | 2017-02-01 | 2017-02-28 | 24:00 | 13206.688 | 9970.187 | 4751.455 | 6.179 | Lê Minh Tiến | File1.53 |  | 508.768
2017-03-01 | 2017-03-31 | 24:00 | 13261.988 | 10276.89 | 4738.591 | 4.88 | Lê Minh Tiến | File1.54 |  | 401.802 | 2017-03-01 | 2017-03-31 | 24:00 | 13287.294 | 10297.084 | 4751.455 | 4.89 | Lê Minh Tiến | File1.54 |  | 402.613
2017-04-01 | 2017-04-30 | 24:00 | 13305.127 | 10516.64 | 4738.591 | 3.395 | Lê Minh Tiến | File1.55 |  | 279.494 | 2017-04-01 | 2017-04-30 | 24:00 | 13330.431 | 10537.473 | 4751.455 | 3.402 | Lê Minh Tiến | File1.55 |  | 280.124
2017-05-01 | 2017-05-31 | 24:00 | 13394.355 | 10783.614 | 4750.105 | 4.413 | Lê Minh Tiến | File1.56 |  | 363.303 | 2017-05-01 | 2017-05-31 | 24:00 | 13419.714 | 10804.962 | 4763.036 | 4.42 | Lê Minh Tiến | File1.56 |  | 363.933
2017-06-01 | 2017-06-30 | 24:00 | 13594.426 | 11101.782 | 4806.697 | 6.898 | Lê Minh Tiến | File1.57 |  | 567.933 | 2017-06-01 | 2017-06-30 | 24:00 | 13620.206 | 11123.824 | 4819.796 | 6.913 | Lê Minh Tiến | File1.57 |  | 569.201
2017-07-01 | 2017-07-31 | 24:00 | 14247.219 | 11296.271 | 4974.402 | 12.18 | Lê Minh Tiến | File1.58 |  | 1002.807 | 2017-07-01 | 2017-07-31 | 24:00 | 14274.112 | 11318.77 | 4987.767 | 12.202 | Lê Minh Tiến | File1.58 |  | 1004.621
2017-08-01 | 2017-08-31 | 24:00 | 14885.953 | 11484.828 | 5277.924 | 13.57 | Lê Minh Tiến | File1.59 |  | 1117.243 | 2017-08-01 | 2017-08-31 | 24:00 | 14914.332 | 11507.74 | 5291.936 | 13.6 | Lê Minh Tiến | File1.59 |  | 1119.759
2017-09-01 | 2017-09-30 | 24:00 | 15503.539 | 11677.395 | 5554.844 | 13.045 | Lê Minh Tiến | File1.60 |  | 1074.028 | 2017-09-01 | 2017-09-30 | 24:00 | 15533.252 | 11700.691 | 5569.431 | 13.072 | Lê Minh Tiến | File1.60 |  | 1076.294
2017-10-01 | 2017-10-31 | 24:00 | 16019.735 | 11822.419 | 5780.686 | 10.645 | Lê Minh Tiến | File1.61 |  | 876.417 | 2017-10-01 | 2017-10-31 | 24:00 | 16050.559 | 11845.939 | 5795.719 | 10.666 | Lê Minh Tiến | File1.61 |  | 878.177
2017-11-01 | 2017-11-30 | 24:00 | 16491.865 | 12129.403 | 6038.519 | 12.435 | Lê Minh Tiến | File1.62 | Plus 0.719 after calibration | 1025.231 | 2017-11-01 | 2017-11-30 | 24:00 | 16523.607 | 12153.483 | 6054.17 | 12.46 | Lê Minh Tiến | File1.62 | Plus 0.721 after calibration | 1027.304
2017-12-01 | 2017-12-31 | 24:00 | 16815.491 | 12455.442 | 6256.751 | 10.415 | Lê Minh Tiến | File1.63 |  | 857.482 | 2017-12-01 | 2017-12-31 | 24:00 | 16847.657 | 12480.198 | 6272.829 | 10.433 | Lê Minh Tiến | File1.63 |  | 858.991
2018-01-01 | 2018-01-31 | 24:00 | 17060.191 | 12833.164 | 6346.388 | 8.545 | Lê Minh Tiến | File1.64 |  | 703.514 | 2018-01-01 | 2018-01-31 | 24:00 | 17092.502 | 12858.696 | 6362.938 | 8.561 | Lê Minh Tiến | File1.64 |  | 704.891
2018-02-01 | 2018-02-28 | 24:00 | 17183.381 | 13125.047 | 6353.548 | 5.067 | Lê Minh Tiến | File1.65 |  | 417.166 | 2018-02-01 | 2018-02-28 | 24:00 | 17215.989 | 13150.931 | 6370.119 | 5.075 | Lê Minh Tiến | File1.65 |  | 417.828
2018-03-01 | 2018-03-31 | 24:00 | 17224.812 | 13442.375 | 6353.548 | 4.305 | Lê Minh Tiến | File1.66 |  | 354.454 | 2018-03-01 | 2018-03-31 | 24:00 | 17257.613 | 13468.779 | 6370.119 | 4.314 | Lê Minh Tiến | File1.66 |  | 355.158
2018-04-01 | 2018-04-30 | 24:00 | 17261.727 | 13667.243 | 6370.502 | 3.345 | Lê Minh Tiến | File1.67 |  | 275.392 | 2018-04-01 | 2018-04-30 | 24:00 | 17294.998 | 13693.691 | 6387.104 | 3.351 | Lê Minh Tiến | File1.67 |  | 275.931
2018-05-01 | 2018-05-31 | 24:00 | 17297.583 | 13916.771 | 6370.54 | 3.425 | Lê Minh Tiến | File1.68 |  | 281.997 | 2018-05-01 | 2018-05-31 | 24:00 | 17331.372 | 13943.342 | 6387.123 | 3.433 | Lê Minh Tiến | File1.68 |  | 282.611
2018-06-01 | 2018-06-30 | 24:00 | 17437.164 | 14219.047 | 6392.259 | 5.563 | Lê Minh Tiến | File1.69 |  | 458.013 | 2018-06-01 | 2018-06-30 | 24:00 | 17471.172 | 14246.235 | 6409.019 | 5.575 | Lê Minh Tiến | File1.69 |  | 459.014
2018-07-01 | 2018-07-31 | 24:00 | 18247.503 | 14464.01 | 6693.142 | 16.274 | Lê Cao Anh | File1.70 |  | 1339.911 | 2018-07-01 | 2018-07-31 | 24:00 | 18283.389 | 14491.818 | 6710.686 | 16.314 | Lê Cao Anh | File1.70 |  | 1343.153
2018-08-01 | 2018-08-31 | 24:00 | 19490.585 | 14859.361 | 7244.543 | 26.278 | Lê Cao Anh | File1.71 |  | 2163.556 | 2018-08-01 | 2018-08-31 | 24:00 | 19530.002 | 14888.233 | 7263.507 | 26.3502 | Lê Cao Anh | File1.71 |  | 2169.4988
2018-09-01 | 2018-09-30 | 24:00 | 20505.311 | 15166.353 | 7688.654 | 21.1899 | Lê Cao Anh | File1.72 |  | 1744.6391 | 2018-09-01 | 2018-09-30 | 24:00 | 20547.353 | 15195.938 | 7708.562 | 21.2413 | Lê Cao Anh | File1.72 |  | 1748.8697
2018-10-01 | 2018-10-31 | 24:00 | 21102.702 | 15355.636 | 7962.271 | 12.7235 | Lê Cao Anh | File1.73 |  | 1047.5675 | 2018-10-01 | 2018-10-31 | 24:00 | 21146.096 | 15385.602 | 7982.9 | 12.7529 | Lê Cao Anh | File1.73 |  | 1049.9921
2018-11-01 | 2018-11-30 | 24:00 | 21320.141 | 15751.838 | 7998.444 | 7.7978 | Lê Cao Anh | File1.74 | Plus 3.588 after calibration | 645.6042 | 2018-11-01 | 2018-11-30 | 24:00 | 21363.937 | 15782.55 | 8019.266 | 7.8139 | Lê Cao Anh | File1.74 | plus 3.588 after calibration | 646.9291
2018-12-01 | 2018-12-31 | 24:00 | 21470.784 | 16128.141 | 8001.896 | 6.3648 | Lê Cao Anh | File1.75 |  | 524.0332 | 2018-12-01 | 2018-12-31 | 24:00 | 21514.846 | 16159.512 | 8022.729 | 6.376 | Lê Cao Anh | File1.75 |  | 524.958
2019-01-01 | 2019-01-31 | 24:00 | 21517.712 | 16485.234 | 8001.896 | 4.8483 | Lê Cao Anh | File1.76 |  | 399.1727 | 2019-01-01 | 2019-01-31 | 24:00 | 21561.877 | 16517.187 | 8022.729 | 4.8565 | Lê Cao Anh | File1.76 |  | 399.8495
2019-02-01 | 2019-02-28 | 24:00 | 21529.547 | 16709.832 | 8001.896 | 2.8372 | Lê Cao Anh | File1.77 |  | 233.5958 | 2019-02-01 | 2019-02-28 | 24:00 | 21573.801 | 16742.217 | 8022.729 | 2.8434 | Lê Cao Anh | File1.77 |  | 234.1106
2019-03-01 | 2019-03-31 | 24:00 | 21538.807 | 16886.279 | 8001.896 | 2.2285 | Lê Cao Anh | File1.78 |  | 183.4785 | 2019-03-01 | 2019-03-31 | 24:00 | 21583.133 | 16919.025 | 8022.729 | 2.2337 | Lê Cao Anh | File1.78 |  | 183.9063
2019-04-01 | 2019-04-30 | 24:00 | 21547.782 | 17053.868 | 8001.896 | 2.1188 | Lê Cao Anh | File1.79 |  | 174.4452 | 2019-04-01 | 2019-04-30 | 24:00 | 21592.239 | 17086.917 | 8022.729 | 2.124 | Lê Cao Anh | File1.79 |  | 174.874
Formulas:
Date = +EOMONTH([M12],0)
MWh = +EOMONTH([Unit],0)

## inputdata consumption EC (hidden)
Unit | MWh
|  |  | Biểu 1 | Biểu 2 | Biểu 3 | [7 empty] | Biểu 1 | Biểu 2 | Biểu 3
Năm | 2012-2019 | Chỉ số đọc lúc bắt đầu đc tính tiền từ nhà máy | 0.46 | 0.01 | 0 |  |  |  |  | YEAR |  | Chỉ số đọc lúc bắt đầu đc tính tiền từ nhà máy | 0.46 | 0.01 | 0 | 0.47 | SUPPLY
Đồng hồ chính (đồng hồ được tính tiền với EVN) | [9 empty] | Đồng hồ dự phòng
M11 |  | seri đồng hồ: 11060674 | [7 empty] | M12 |  |  | Serial Nr: 11060670
Tháng | Ngày | Giờ | chỉ số đọc đồng hồ |  |  | Người chốt chỉ số công tơ | Ref. Document (ly làm) | Ghi chú (nêu rõ tháng nào có thời gian kiểm định đồng hồ và số lượng điện ko được thanh toán trong quá trình kiểm định) | Tổng lượng điện mua | Tháng | Ngày | Năm | chỉ số đọc đồng hồ |  |  | Người chốt chỉ số công tơ | Ref. Document | Ghi chú (nêu rõ tháng nào có thời gian kiểm định đồng hồ và số lượng điện ko được thanh toán trong quá trình kiểm định) | Tổng lượng điện mua
|  |  | Biểu 1 | Biểu 2 | Biểu 3 | [7 empty] | Biểu 1 | Biểu 2 | Biểu 3
2012-10-01 |  | 24:00 | 0.5 | 0.02 | 0 | Nguyễn Hoàng Thắng |  |  |  | 2012-10-01 |  | 24:00 | 0.5 | 0.02 | 0 | Nguyễn Hoàng Thắng
2012-11-01 |  | 24:00 | 0.97 | 0.03 | 0.01 | Nguyễn Hoàng Thắng |  |  |  | 2012-11-01 |  | 24:00 | 0.99 | 0.03 | 0.01 | Nguyễn Hoàng Thắng
2012-12-01 |  | 24:00 | 1.2 | 0.03 | 0.07 | Nguyễn Hoàng Thắng |  |  |  | 2012-12-01 |  | 24:00 | 1.23 | 0.03 | 0.07 | Nguyễn Hoàng Thắng |  | đồng hồ dự phòng hỏng từ 1/12 đến 22/12
2013-01-01 |  | 24:00 | 1.29 | 0.03 | 0.14 | Lã Quý Quyền |  |  |  | 2013-01-01 |  | 24:00 | 1.33 | 0.03 | 0.16 | Lã Quý Quyền
2013-02-01 |  | 24:00 | 1.53 | 0.03 | 0.17 | Lã Quý Quyền |  |  | 0.27 | 2013-02-01 |  | 24:00 | 1.58 | 0.03 | 0.19 | Lã Quý Quyền |  |  | 0.28
2013-03-01 |  | 24:00 | 1.9 | 0.04 | 0.26 | Lã Quý Quyền |  |  | 0.47 | 2013-03-01 |  | 24:00 | 1.96 | 0.04 | 0.29 | Lã Quý Quyền |  |  | 0.49
2013-04-01 |  | 24:00 | 2.3 | 0.05 | 0.35 | Lã Quý Quyền |  |  | 0.5 | 2013-04-01 |  | 24:00 | 2.38 | 0.05 | 0.38 | Lã Quý Quyền |  |  | 0.52
2013-05-01 |  | 24:00 | 2.82 | 0.07 | 0.61 | Lã Quý Quyền |  |  | 0.8 | 2013-05-01 |  | 24:00 | 2.93 | 0.08 | 0.66 | Lã Quý Quyền |  |  | 0.86
2013-06-01 |  | 24:00 | 3.32 | 0.18 | 0.85 | Lã Quý Quyền |  |  | 0.85 | 2013-06-01 |  | 24:00 | 3.46 | 0.18 | 0.92 | Lã Quý Quyền |  |  | 0.89
2013-07-01 |  | 24:00 | 3.61 | 0.33 | 1.13 | Lã Quý Quyền |  |  | 0.72 | 2013-07-01 |  | 24:00 | 3.75 | 0.34 | 1.21 | Lã Quý Quyền |  |  | 0.74
2013-08-01 |  | 24:00 | 3.76 | 0.39 | 1.31 | Lã Quý Quyền |  |  | 0.39 | 2013-08-01 |  | 24:00 | 3.8 | 0.4 | 1.39 | Lã Quý Quyền |  |  | 0.29
2013-09-01 |  | 24:00 | 3.85 | 0.46 | 1.38 | Lã Quý Quyền |  |  | 0.08 | 2013-09-01 |  | 24:00 | 4 | 0.47 | 1.46 | Lã Quý Quyền |  |  | 0.34
2013-10-01 |  | 24:00 | 3.87 | 0.46 | 1.38 | Lã Quý Quyền |  |  | 0.02 | 2013-10-01 |  | 24:00 | 4.02 | 0.48 | 1.46 | Lã Quý Quyền |  |  | 0.03
2013-11-01 |  | 24:00 | 4.86 | 0.49 | 1.38 | Lã Quý Quyền |  | trừ 1.000 chênh lệch sau kiểm định | 0.02 | 2013-11-01 |  | 24:00 | 5.01 | 0.51 | 1.46 | Lã Quý Quyền |  | trừ 1.000 chênh lệch sau kiểm định | 0.02
2013-12-01 |  | 24:00 | 4.88 | 0.49 | 1.38 | Lã Quý Quyền |  |  | 0.02 | 2013-12-01 |  | 24:00 | 5.03 | 0.51 | 1.46 | Lã Quý Quyền |  |  | 0.02
2014-01-01 |  | 24:00 | 4.94 | 0.5 | 1.39 | Hồ Tiến Sỹ |  |  | 0.08 | 2014-01-01 |  | 24:00 | 5.09 | 0.51 | 1.47 | Hồ Tiến Sỹ |  |  | 0.07
2014-02-01 |  | 24:00 | 5.04 | 0.5 | 1.42 | Hồ Tiến Sỹ |  |  | 0.13 | 2014-02-01 |  | 24:00 | 5.2 | 0.51 | 1.51 | Hồ Tiến Sỹ |  |  | 0.15
2014-03-01 |  | 24:00 | 5.35 | 0.5 | 1.54 | Hồ Tiến Sỹ |  |  | 0.43 | 2014-03-01 |  | 24:00 | 5.52 | 0.51 | 1.63 | Hồ Tiến Sỹ |  |  | 0.44
2014-04-01 |  | 24:00 | 5.92 | 0.5 | 1.84 | Hồ Tiến Sỹ |  |  | 0.87 | 2014-04-01 |  | 24:00 | 6.12 | 0.51 | 1.95 | Hồ Tiến Sỹ |  |  | 0.92
2014-05-01 |  | 24:00 | 6.56 | 0.53 | 2.1 | Hồ Tiến Sỹ |  |  | 0.93 | 2014-05-01 |  | 24:00 | 6.78 | 0.55 | 2.23 | Hồ Tiến Sỹ |  |  | 0.98
2014-06-01 |  | 24:00 | 6.88 | 0.54 | 2.27 | Hồ Tiến Sỹ |  |  | 0.5 | 2014-06-01 |  | 24:00 | 7.12 | 0.56 | 2.41 | Hồ Tiến Sỹ |  |  | 0.53
2014-07-01 |  | 24:00 | 6.97 | 0.6 | 2.35 | Hồ Tiến Sỹ |  |  | 0.23 | 2014-07-01 |  | 24:00 | 7.22 | 0.62 | 2.49 | Hồ Tiến Sỹ |  |  | 0.24
2014-08-01 |  | 24:00 | 7.02 | 0.61 | 2.44 | Hồ Tiến Sỹ |  |  | 0.15 | 2014-08-01 |  | 24:00 | 7.27 | 0.63 | 2.58 | Hồ Tiến Sỹ |  |  | 0.15
2014-09-01 |  | 24:00 | 7.19 | 0.67 | 2.64 | Hồ Tiến Sỹ |  |  | 0.43 | 2014-09-01 |  | 24:00 | 7.45 | 0.7 | 2.79 | Hồ Tiến Sỹ |  |  | 0.46
2014-10-01 |  | 24:00 | 7.29 | 0.73 | 2.71 | Hồ Tiến Sỹ |  |  | 0.23 | 2014-10-01 |  | 24:00 | 7.55 | 0.75 | 2.86 | Hồ Tiến Sỹ |  |  | 0.22
2014-11-01 |  | 24:00 | 7.92 | 0.8 | 2.74 | Hồ Tiến Sỹ |  | trừ 0.410 chênh lệch sau kiểm định | 0.32 | 2014-11-01 |  | 24:00 | 8.19 | 0.83 | 2.9 | Hồ Tiến Sỹ |  | trừ 0.410 chênh lệch sau kiểm định | 0.35
2014-12-01 |  | 24:00 | 7.96 | 0.8 | 2.76 | Hồ Tiến Sỹ |  |  | 0.06 | 2014-12-01 |  | 24:00 | 8.24 | 0.83 | 2.92 | Hồ Tiến Sỹ |  |  | 0.07
2015-01-01 |  | 24:00 | 8.34 | 0.8 | 2.8 | Hồ Tiến Sỹ |  |  | 0.42 | 2015-01-01 |  | 24:00 | 8.63 | 0.83 | 2.96 | Hồ Tiến Sỹ |  |  | 0.43
2015-02-01 |  | 24:00 | 8.6 | 0.8 | 2.89 | Hồ Tiến Sỹ |  |  | 0.35 | 2015-02-01 |  | 24:00 | 8.91 | 0.83 | 3.07 | Hồ Tiến Sỹ |  |  | 0.39
2015-03-01 |  | 24:00 |  |  |  | Hồ Tiến Sỹ |  |  | -12.29 | 2015-03-01 |  | 24:00 |  |  |  | Hồ Tiến Sỹ |  |  | -12.81
2015-04-01 |  | 24:00 | 10.2 | 0.91 | 3.41 | Hồ Tiến Sỹ |  |  | 14.52 | 2015-04-01 |  | 24:00 | 10.56 | 0.93 | 3.62 | Hồ Tiến Sỹ |  |  | 15.11
2015-05-01 |  | 24:00 | 11.32 | 1.11 | 4.01 | Hồ Tiến Sỹ |  |  | 1.92 | 2015-05-01 |  | 24:00 | 11.7 | 1.14 | 4.23 | Hồ Tiến Sỹ |  |  | 1.96
2015-06-01 |  | 24:00 |  |  |  | Hồ Tiến Sỹ |  |  | -16.44 | 2015-06-01 |  | 24:00 |  |  |  | Hồ Tiến Sỹ |  |  | -17.07
2015-07-01 |  | 24:00 |  |  |  | Hồ Tiến Sỹ |  |  | 0 | 2015-07-01 |  | 24:00 |  |  |  | Hồ Tiến Sỹ |  |  | 0
2015-08-01 |  | 24:00 | 12.91 | 1.5 | 5.23 | Hồ Tiến Sỹ |  |  | 19.64 | 2015-08-01 |  | 24:00 | 13.35 | 1.54 | 5.5 | Hồ Tiến Sỹ |  |  | 20.39
2015-09-01 |  | 24:00 | 13.11 | 1.57 | 5.41 | Lê Cao anh |  |  | 0.45 | 2015-09-01 |  | 24:00 | 13.55 | 1.61 | 5.69 | Lê Cao anh |  |  | 0.46
2015-10-01 |  | 24:00 | 13.19 | 1.6 | 5.56 | Lê Cao anh |  |  | 0.26 | 2015-10-01 |  | 24:00 | 13.63 | 1.64 | 5.85 | Lê Cao anh |  |  | 0.27
2015-11-01 |  | 24:00 | 13.59 | 1.6 | 5.6 | Lê Cao anh |  | Trừ 0.250 chênh lệch sau kiểm định | 0.19 | 2015-11-01 |  | 24:00 | 14.04 | 1.64 | 5.88 | Lê Cao anh |  | Trừ 0.250 chênh lệch sau kiểm định | 0.19
2015-12-01 |  | 24:00 | 13.84 | 1.6 | 5.64 | Lê Cao anh |  |  | 0.29 | 2015-12-01 |  | 24:00 | 14.3 | 1.64 | 5.93 | Lê Cao anh |  |  | 0.31
2016-01-01 |  | 24:00 | 13.97 | 1.6 | 5.67 | Lê Cao anh |  |  | 0.16 | 2016-01-01 |  | 24:00 | 14.43 | 1.64 | 5.96 | Lê Cao anh |  |  | 0.16
2016-02-01 |  | 24:00 | 14.1 | 1.6 | 5.69 | Lê Cao anh |  |  | 0.15 | 2016-02-01 |  | 24:00 | 14.57 | 1.64 | 5.99 | Lê Cao anh |  |  | 0.17
2016-03-01 |  | 24:00 | 14.19 | 1.62 | 5.9 | Lê Cao anh |  |  | 0.32 | 2016-03-01 |  | 24:00 | 14.98 | 1.66 | 6.2 | Lê Cao anh |  |  | 0.64
2016-04-01 |  | 24:00 | 15.3 | 1.66 | 6.52 | Lê Minh Tiến |  |  | 1.77 | 2016-04-01 |  | 24:00 | 15.81 | 1.7 | 6.84 | Lê Minh Tiến |  |  | 1.51
2016-05-01 |  | 24:00 | 16.11 | 1.73 | 7.02 | Lê Minh Tiến |  |  | 1.38 | 2016-05-01 |  | 24:00 | 16.65 | 1.77 | 7.35 | Lê Minh Tiến |  |  | 1.42
2016-06-01 |  | 24:00 | 16.87 | 1.81 | 7.47 | Lê Minh Tiến |  |  | 1.29 | 2016-06-01 |  | 24:00 | 17.43 | 1.86 | 7.82 | Lê Minh Tiến |  |  | 1.34
2016-07-01 |  | 24:00 | 17.22 | 1.95 | 7.83 | Lê Minh Tiến |  |  | 0.85 | 2016-07-01 |  | 24:00 | 17.8 | 2 | 8.2 | Lê Minh Tiến |  |  | 0.89
2016-08-01 |  | 24:00 | 17.44 | 2.02 | 8.1 | Lê Minh Tiến |  |  | 0.56 | 2016-08-01 |  | 24:00 | 18.02 | 2.08 | 8.48 | Lê Minh Tiến |  |  | 0.58
2016-09-01 |  | 24:00 | 17.565 | 2.062 | 8.231 | Lê Minh Tiến |  |  | 0.298 | 2016-09-01 |  | 24:00 | 18.161 | 2.123 | 8.62 | Lê Minh Tiến |  |  | 0.324
2016-10-01 |  | 24:00 | 17.623 | 2.064 | 8.329 | Lê Minh Tiến |  |  | 0.158 | 2016-10-01 |  | 24:00 | 18.222 | 2.126 | 8.721 | Lê Minh Tiến |  |  | 0.165
2016-11-01 |  | 24:00 | 18.593 | 2.174 | 8.35 | Lê Minh Tiến |  | Trừ 1.020 chênh lệch sau kiểm định | 0.081 | 2016-11-01 |  | 24:00 | 19.187 | 2.242 | 8.742 | Lê Minh Tiến |  | Trừ 1.013 chênh lệch sau kiểm định | 0.089
2016-12-01 |  | 24:00 | 18.633 | 2.175 | 8.361 | Lê Minh Tiến |  |  | 0.052 | 2016-12-01 |  | 24:00 | 19.228 | 2.244 | 8.753 | Lê Minh Tiến |  |  | 0.054
2017-01-01 |  | 24:00 | 18.698 | 2.176 | 8.385 | Lê Minh Tiến |  |  | 0.09 | 2017-01-01 |  | 24:00 | 19.294 | 2.244 | 8.777 | Lê Minh Tiến |  |  | 0.09
2017-02-01 |  | 24:00 | 18.836 | 2.176 | 8.451 | Lê Minh Tiến |  |  | 0.204 | 2017-02-01 |  | 24:00 | 19.437 | 2.245 | 8.847 | Lê Minh Tiến |  |  | 0.214
2017-03-01 |  | 24:00 | 19.087 | 2.177 | 8.583 | Lê Minh Tiến |  |  | 0.384 | 2017-03-01 |  | 24:00 | 19.703 | 2.246 | 8.984 | Lê Minh Tiến |  |  | 0.404
2017-04-01 |  | 24:00 | 19.429 | 2.197 | 8.71 | Lê Minh Tiến |  |  | 0.489 | 2017-04-01 |  | 24:00 | 20.059 | 2.266 | 9.122 | Lê Minh Tiến |  |  | 0.514
2017-05-01 |  | 24:00 | 20.19 | 2.207 | 9.159 | Lê Minh Tiến |  |  | 1.22 | 2017-05-01 |  | 24:00 | 20.846 | 2.276 | 9.585 | Lê Minh Tiến |  |  | 1.26
2017-06-01 |  | 24:00 | 20.788 | 2.209 | 9.495 | Lê Minh Tiến |  |  | 0.936 | 2017-06-01 |  | 24:00 | 21.467 | 2.278 | 9.936 | Lê Minh Tiến |  |  | 0.974
2017-07-01 |  | 24:00 | 20.958 | 2.291 | 9.737 | Lê Minh Tiến |  |  | 0.494 | 2017-07-01 |  | 24:00 | 21.642 | 2.361 | 10.193 | Lê Minh Tiến |  |  | 0.515
2017-08-01 |  | 24:00 | 21.124 | 2.379 | 9.755 | Lê Minh Tiến |  |  | 0.272 | 2017-08-01 |  | 24:00 | 21.813 | 2.451 | 10.212 | Lê Minh Tiến |  |  | 0.28
2017-09-01 |  | 24:00 | 21.147 | 2.409 | 9.764 | Lê Minh Tiến |  |  | 0.062 | 2017-09-01 |  | 24:00 | 21.837 | 2.481 | 10.223 | Lê Minh Tiến |  |  | 0.065
2017-10-01 |  | 24:00 | 21.236 | 2.473 | 9.792 | Lê Minh Tiến |  |  | 0.181 | 2017-10-01 |  | 24:00 | 21.928 | 2.547 | 10.253 | Lê Minh Tiến |  |  | 0.187
2017-11-01 |  | 24:00 | 21.454 | 2.722 | 9.812 | Lê Minh Tiến |  | Trừ 0.361 chênh lệch sau kiểm định | 0.126 | 2017-11-01 |  | 24:00 | 22.162 | 2.786 | 10.273 | Lê Minh Tiến |  | Trừ 0.362 chênh lệch sau kiểm định | 0.131
2017-12-01 |  | 24:00 | 21.608 | 2.74 | 9.828 | Lê Minh Tiến |  |  | 0.188 | 2017-12-01 |  | 24:00 | 22.318 | 2.805 | 10.289 | Lê Minh Tiến |  |  | 0.191
2018-01-01 |  | 24:00 | 21.724 | 2.74 | 9.872 | Lê Minh Tiến |  |  | 0.16 | 2018-01-01 |  | 24:00 | 22.441 | 2.805 | 10.342 | Lê Minh Tiến |  |  | 0.176
2018-02-01 |  | 24:00 | 21.87 | 2.74 | 9.945 | Lê Minh Tiến |  |  | 0.219 | 2018-02-01 |  | 24:00 | 22.598 | 2.805 | 10.421 | Lê Minh Tiến |  |  | 0.236
2018-03-01 |  | 24:00 | 22.214 | 2.744 | 10.63 | Lê Minh Tiến |  |  | 1.033 | 2018-03-01 |  | 24:00 | 22.966 | 2.812 | 10.555 | Lê Minh Tiến |  |  | 0.509
2018-04-01 |  | 24:00 | 22.662 | 2.754 | 10.258 | Lê Minh Tiến |  |  | 0.086 | 2018-04-01 |  | 24:00 | 23.435 | 2.824 | 10.764 | Lê Minh Tiến |  |  | 0.69
2018-05-01 |  | 24:00 | 22.876 | 2.767 | 10.352 | Lê Minh Tiến |  |  | 0.321 | 2018-05-01 |  | 24:00 | 23.662 | 2.838 | 10.863 | Lê Minh Tiến |  |  | 0.34
2018-06-01 |  | 24:00 | 22.959 | 2.767 | 10.378 | Lê Minh Tiến |  |  | 0.109 | 2018-06-01 |  | 24:00 | 23.749 | 2.839 | 10.893 | Lê Minh Tiến |  |  | 0.118
2018-07-01 |  | 24:00 | 22.986 | 2.78 | 10.412 | Lê Cao Anh |  |  | 0.074 | 2018-07-01 |  | 24:00 | 23.779 | 2.853 | 10.928 | Lê Cao Anh |  |  | 0.079
2018-08-01 |  | 24:00 | 22.99 | 2.782 | 10.412 | Lê Cao Anh |  |  | 0.006 | 2018-08-01 |  | 24:00 | 23.782 | 2.855 | 10.928 | Lê Cao Anh |  |  | 0.005
2018-09-01 |  | 24:00 | 22.996 | 2.783 | 10.412 | Lê Cao Anh |  |  | 0.007 | 2018-09-01 |  | 24:00 | 23.788 | 2.856 | 10.928 | Lê Cao Anh |  |  | 0.007
2018-10-01 |  | 24:00 | 23.011 | 2.791 | 10.414 | Lê Cao Anh |  |  | 0.025 | 2018-10-01 |  | 24:00 | 23.803 | 2.864 | 10.931 | Lê Cao Anh |  |  | 0.026
2018-11-01 |  | 24:00 | 23.289 | 3.181 | 10.524 | Lê Cao Anh |  | Trừ 0.390 chênh lệch sau kiểm định | 0.388 | 2018-11-01 |  | 24:00 | 24.092 | 3.254 | 11.044 | Lê Cao Anh |  | Trừ 0.390 chênh lệch sau kiểm định | 0.402
2018-12-01 |  | 24:00 | 23.41 | 3.182 | 10.555 | Lê Cao Anh |  |  | 0.153 | 2018-12-01 |  | 24:00 | 24.217 | 3.256 | 11.079 | Lê Cao Anh |  |  | 0.162
2019-01-01 |  | 24:00 | 23.484 | 3.183 | 10.583 | Lê Cao Anh |  |  | 0.103 | 2019-01-01 |  | 24:00 | 24.292 | 3.256 | 11.107 | Lê Cao Anh |  |  | 0.103
2019-02-01 |  | 24:00 | 23.624 | 3.183 | 10.636 | Lê Cao Anh |  |  | 0.193 | 2019-02-01 |  | 24:00 | 24.441 | 3.256 | 11.16 | Lê Cao Anh |  |  | 0.202
2019-03-01 |  | 24:00 | 23.755 | 3.184 | 10.747 | Lê Cao Anh |  |  | 0.243 | 2019-03-01 |  | 24:00 | 24.578 | 3.257 | 11.275 | Lê Cao Anh |  |  | 0.253
2019-04-01 |  | 24:00 | 24.031 | 3.196 | 10.924 | Lê Cao Anh |  |  | 0.465 | 2019-04-01 |  | 24:00 | 24.872 | 3.271 | 11.463 | Lê Cao Anh |  |  | 0.496

## InputData Reservoir Level
Lala CDM Monitoring Input Sheet Reservoir level / area
[6 empty] | Z | W | F | ∆W | ∆F
[6 empty] | m | m3 | m2
[6 empty] | 299 | 192.21 | 384.41 | 1004.67 | 1413.79
[6 empty] | 300 | 1196.88 | 1798.2 | 2157.37 | 739.52
[6 empty] | 301 | 3354.25 | 2537.72 | 2810.11 | 1062.28
[6 empty] | 302 | 6164.36 | 3600 | 3363.73 | 1400
[6 empty] | 303 | 9528.09 | 5000 | 5640.09 | 74908.91
[6 empty] | 304 | 15168.18 | 79908.91 | 10955.16 | -65592.99
[6 empty] | 305 | 26123.34 | 14315.92 | 16780.48 | 4584.08
[6 empty] | 306 | 42903.82 | 18900 | 22365.49 | 6598.82
[6 empty] | 307 | 65269.31 | 25498.82 | 27654.06 | 6301.18
[6 empty] | 308 | 92923.37 | 31800 | 36676.34 | 12137.07
[6 empty] | 309 | 129599.71 | 43937.07 | 48103.66 | 8457.17
[6 empty] | 310 | 177703.37 | 52394.24 | 57465.8 | 10296.96
[6 empty] | 311 | 235169.17 | 62691.2 | 756.171 | 201.5794
Graph: Relation between Volume, Surface area and water level at dam site of upper cascade
YEAR | 2012 - 2019 |  |  |  | WATEL LEVEL
Ruler at main dam site inlet gate
Month | Date | Time | Highest Water Level [m a.s.l.] | Ref. Document | Comments
2012-10-31
2012-11-30 | 2012-11-20 | 16:30 | 308 | File 21.1
2012-12-31 | 2012-12-13 | 9:00 | 308 | File 21.2
2013-01-31 | 2013-01-04 | 16:45 | 307.9 | File 21.3
2013-02-28 | 2013-02-11 | 9:00 | 308 | File 21.4
2013-03-31 | 2013-03-25 | 9:00 | 308.1 | File 21.5 |  | 12 bis 13 |  | 1848.1 | 308.0167
2013-04-30 | 2013-04-22 | 9:00 | 308.1 | File 21.6
2013-05-31 | 2013-05-02 | 9:15 | 308.1 | File 21.7
2013-06-30 | 2016-06-05 | 16:00 | 308.1 | File 21.8 |  | 13 bis 14 |  | 3697 | 308.0833
2013-07-31 | 2013-06-07 | 7:45 | 308 | File 21.9
2013-08-31 | 2013-08-27 | 7:15 | 307.9 | File 21.10
2013-09-30 | 2013-09-22 | 7:45 | 308.1 | File 21.11
2013-10-31 | 2013-10-07 | 17:00 | 308.2 | File 21.12 |  | 14 bis 15 |  | 3695.4 | 307.95
2013-11-30 | 2013-11-06 | 7:30 | 308.2 | File 21.12
2013-12-31 | 2013-12-15 | 19:45 | 308.2 | File 21.13
2014-01-31 | 2014-01-06 | 7:00 | 308 | File 21.14 |  | 15 bsi 16 |  | 3699.6 | 308.3
2014-02-28 | 2014-02-17 | 9:00 | 308.1 | File 21.15
2014-03-31 | 2014-03-01 | 9:00 | 308 | File 21.16
2014-04-30 | 2014-04-10 | 6:45 | 308.1 | File 21.17
2014-05-31 | 2014-05-29 | 16:30 | 307.3 | File 21.17 |  | 16 bis 17 |  | 3702 | 308.5
2014-06-30 | 2014-06-10 | 16:20 | 308 | File 21.18
2014-07-31 | 2014-07-14 | 9:45 | 308 | File 21.19
2014-08-31 | 2014-08-26 | 5:40 | 308 | File 21.20 |  | 17 bis 18 |  | 3706 | 308.8333
2014-09-30 | 2014-09-23 | 16:50 | 308 | File 21.21
2014-10-31 | 2014-10-26 | 9:30 | 308 | File 21.22
2014-11-30 | 2014-11-03 | 9:00 | 308 | File 21.23 |  | 18 bs 19 |  | 3708.8 | 309.0667
2014-12-31 | 2014-12-02 | 9:30 | 308 | File 21.24
2015-01-31 | 2015-01-26 | 16:35 | 308 | File 21.25
2015-02-28 | 2015-02-04 | 9:00 | 308.1 | File 21.26
2015-03-31 | 2015-03-16 | 9:00 | 308.2 | File 21.27
2015-04-30 | 2015-04-20 | 9:00 | 307.8 | File 21.28
2015-05-31 | 2015-05-03 | 9:00 | 308.1 | File 21.29
2015-06-30 | 2015-06-23 | 9:00 | 308.6 | File 21.30
2015-07-31 | 2015-07-05 | 14:15 | 307.9 | File 21.31
2015-08-31 | 2015-08-05 | 6:10 | 308.1 | File 21.32
2015-09-30 | 2015-09-01 | 6:15 | 308.2 | File 21.33
2015-10-31 | 2015-10-01 | 21:10 | 308.4 | File 21.34
2015-11-30 | 2015-11-14 | 6:10 | 308.6 | File 21.35
2015-12-31 | 2015-12-20 | 6:00 | 308.6 | File 21.36
2016-01-31 | 2016-01-05 | 9:10 | 308.6 | File 21.37
2016-02-29 | 2016-02-05 | 9:00 | 308.3 | File 21.38
2016-03-31 | 2016-03-13 | 16:35 | 308 | File 21.39
2016-04-30 | 2016-04-15 | 9:00 | 308.2 | File 21.40
2016-05-31 | 2016-05-14 | 9:00 | 308.5 | File 21.41
2016-06-30 | 2016-06-08 | 9:10 | 308.6 | File 21.42
2016-07-31 | 2016-07-10 | 7:50 | 308.2 | File 21.43
2016-08-31 | 2016-08-15 | 7:00 | 308.6 | File 21.44
2016-09-30 | 2016-09-21 | 7:55 | 308.6 | File 21.45
2016-10-31 | 2016-10-31 | 6:40 | 308.3 | File 21.46
2016-11-30 | 2016-11-28 | 9:15 | 308.6 | File 21.47
2016-12-31 | 2016-12-08 | 16:40 | 308.6 | File 21.48
2017-01-31 | 2017-01-11 | 8:20 | 308.6 | File 21.49
2017-02-28 | 2017-02-20 | 9:00 | 308.8 | File 21.50
2017-03-31 | 2017-03-13 | 9:10 | 308.8 | File 21.51
2017-04-30 | 2017-04-07 | 9:00 | 308.5 | File 21.52
2017-05-31 | 2017-05-01 | 9:00 | 308.8 | File 21.53
2017-06-30 | 2017-06-07 | 1:05 | 308.8 | File 21.54
2017-07-31 | 2017-07-16 | 9:00 | 308.8 | File 21.55
2017-08-31 | 2017-08-26 | 19:30 | 308.8 | File 21.56
2017-09-30 | 2017-09-26 | 7:50 | 308.8 | File 21.57
2017-10-31 | 2017-10-28 | 11:05 | 308.8 | File 21.58
2017-11-30 | 2017-11-23 | 16:30 | 308.8 | File 21.59
2017-12-31 | 2017-12-09 | 9:00 | 308.8 | File 21.60
2018-01-31 | 2018-01-01 | 6:30 | 308.8 | File 21.61
2018-02-28 | 2018-02-01 | 16:40 | 308.8 | File 21.62
2018-03-31 | 2018-03-05 | 8:00 | 309 | File 21.63
2018-04-30 | 2019-04-02 | 9:15 | 309 | File 21.64
2018-05-31 | 2018-05-06 | 3:30 | 309 | File 21.65
2018-06-30 | 2018-06-07 | 8:50 | 309 | File 21.66
2018-07-31 | 2018-07-12 | 6:30 | 309 | File 21.67
2018-08-31 | 2018-08-04 | 8:45 | 308.6 | File 21.68
2018-09-30 | 2018-09-16 | 19:25 | 308.6 | File 21.69
2018-10-31 | 2018-10-25 | 20:30:00 | 309 | File 21.70
2018-11-30 | 2018-11-03 | 8:15 | 309.2 | File 21.71
2018-12-31 | 2018-12-01 | 9:20 | 309.2 | File 21.72
2019-01-31 | 2019-01-01 | 9:10 | 309.2 | File 21.73
2019-02-28 | 2019-02-04 | 9:05 | 309.1 | File 21.74
2019-03-31 | 2019-03-31 | 13:35 | 308.7 | File 21.75
2019-04-30 | 2019-04-15 | 9:05 | 309.2 | File 21.76
Upper Reservoir |  |  | m a.s.l. | Area of Reservoir according to graph 1 (m2)
Highest Water level in 2012: |  |  | 308 | 31800
Highest Water level in 2013: |  |  | 308.2 | 34227.414
Highest Water level in 2014: |  |  | 308.1 | 33013.707
Highest Water level in 2015: |  |  | 308.6 | 39082.242
Highest Water level in 2016: |  |  | 308.6 | 39082.242
Highest Water level in 2017: |  |  | 308.8 | 41509.656
Highest Water level in 2018: |  |  | 309.2 | 45628.504
Highest Water level in 2019: |  |  | 309.2 | 45628.504

## Input data monthly1
Input data monthly
MONTH-YEAR | SUPPLY Measured by the main meter M11 | SUPPLY measured by the backup meter M12 | TOTAL ELECTRICITY GENERATION | Consumption main meter M11 | Consumption backup meter M12 | TOTAL ELECTRICITY CONSUMPTION
2012-10-31 | 910.106 | 912.202 | 910.106 | 0.52 | 0.52 | 0.52
2012-11-30 | 643.534 | 644.69 | 643.534 | 0.49 | 0.51 | 0.49
2012-12-31 | 443.839 | 444.432 | 443.839 | 0.29 | 0.3 | 0.29
2013-01-31 | 330.684 | 331.158 | 330.684 | 0.16 | 0.19 | 0.16
2013-02-28 | 227.773 | 228.1 | 227.773 | 0.27 | 0.28 | 0.27
2013-03-31 | 183.561 | 183.818 | 183.561 | 0.47 | 0.49 | 0.47
2013-04-30 | 191.445 | 191.741 | 191.445 | 0.5 | 0.52 | 0.5
2013-05-31 | 253.323 | 253.768 | 253.323 | 0.8 | 0.86 | 0.8
2013-06-30 | 197.323 | 197.719 | 197.323 | 0.85 | 0.89 | 0.85
2013-07-31 | 473.252 | 474.27 | 473.252 | 0.72 | 0.74 | 0.72
2013-08-31 | 542.669 | 543.904 | 542.669 | 0.39 | 0.29 | 0.39
2013-09-30 | 893.172 | 895.118 | 893.172 | 0.23 | 0.34 | 0.23
2013-10-31 | 1589.732 | 1593.259 | 1589.732 | 0.02 | 0.03 | 0.02
2013-11-30 | 1693.575 | 1697.32 | 1693.575 | 0.02 | 0.01 | 0.02
2013-12-31 | 1235.731 | 1237.727 | 1235.731 | 0.02 | 0.02 | 0.02
2014-01-31 | 663.392 | 664.351 | 663.392 | 0.08 | 0.07 | 0.08
2014-02-28 | 351.007 | 351.56 | 351.007 | 0.13 | 0.15 | 0.13
2014-03-31 | 260.239 | 260.723 | 260.239 | 0.43 | 0.44 | 0.43
2014-04-30 | 212.232 | 212.736 | 212.232 | 0.87 | 0.92 | 0.87
2014-05-31 | 160.135 | 160.501 | 160.135 | 0.93 | 0.98 | 0.93
2014-06-30 | 277.944 | 278.606 | 277.944 | 0.5 | 0.53 | 0.5
2014-07-31 | 400.298 | 401.365 | 400.298 | 0.23 | 0.24 | 0.23
2014-08-31 | 529.874 | 531.327 | 529.874 | 0.15 | 0.15 | 0.15
2014-09-30 | 414.97 | 415.998 | 414.97 | 0.43 | 0.46 | 0.43
2014-10-31 | 363.051 | 363.89 | 363.051 | 0.23 | 0.22 | 0.23
2014-11-30 | 330.644 | 331.316 | 330.644 | 0.32 | 0.35 | 0.32
2014-12-31 | 502.052 | 502.932 | 502.052 | 0.06 | 0.07 | 0.06
2015-01-31 | 300.174 | 300.579 | 300.174 | 0.42 | 0.43 | 0.42
2015-02-28 | 241.892 | 242.277 | 241.892 | 0.35 | 0.39 | 0.35
2015-03-31 | 178.645 | 178.973 | 178.645 | -12.29 | -12.81 | -12.29
2015-04-30 | 128.875 | 129.102 | 128.875 | 14.52 | 15.11 | 14.52
2015-05-31 | 100.381 | 100.559 | 100.381 | 1.92 | 1.96 | 1.92
2015-06-30 | 126.257 | 126.444 | 126.257 | -16.44 | -17.07 | -16.44
2015-07-31 | 383.255 | 384.026 | 383.255 | 0 | 0 | 0
2015-08-31 | 328.984 | 329.804 | 328.984 | 19.64 | 20.39 | 19.64
2015-09-30 | 848.732 | 850.638 | 848.732 | 0.45 | 0.46 | 0.45
2015-10-31 | 784.512 | 786.28 | 784.512 | 0.26 | 0.27 | 0.26
2015-11-30 | 1091.511 | 1094.01 | 1091.511 | 0.19 | 0.19 | 0.19
2015-12-31 | 558.259 | 559.455 | 558.259 | 0.29 | 0.31 | 0.29
2016-01-31 | 437.022 | 437.862 | 437.022 | 0.16 | 0.16 | 0.16
2016-02-29 | 266.217 | 266.562 | 266.217 | 0.15 | 0.17 | 0.15
2016-03-31 | 201.69 | 202.036 | 201.69 | 0.32 | 0.64 | 0.32
2016-04-30 | 161.311 | 161.676 | 161.311 | 1.77 | 1.51 | 1.77
2016-05-31 | 168.444 | 168.741 | 168.444 | 1.38 | 1.42 | 1.38
2016-06-30 | 165.441 | 165.767 | 165.441 | 1.29 | 1.34 | 1.29
2016-07-31 | 290.749 | 291.44 | 290.749 | 0.85 | 0.89 | 0.85
2016-08-31 | 601.485 | 602.947 | 601.485 | 0.56 | 0.58 | 0.56
2016-09-30 | 779.733 | 781.521 | 779.733 | 0.298 | 0.324 | 0.298
2016-10-31 | 1068.342 | 1070.848 | 1068.342 | 0.158 | 0.165 | 0.158
2016-11-30 | 1517.092 | 1520.531 | 1517.092 | 0.081 | 0.089 | 0.081
2016-12-31 | 1158.737 | 1160.927 | 1158.737 | 0.052 | 0.054 | 0.052
2017-01-31 | 811.448 | 813.039 | 811.448 | 0.09 | 0.09 | 0.09
2017-02-28 | 507.948 | 508.768 | 507.948 | 0.204 | 0.214 | 0.204
2017-03-31 | 401.802 | 402.613 | 401.802 | 0.384 | 0.404 | 0.384
2017-04-30 | 279.494 | 280.124 | 279.494 | 0.489 | 0.514 | 0.489
2017-05-31 | 363.303 | 363.933 | 363.303 | 1.22 | 1.26 | 1.22
2017-06-30 | 567.933 | 569.201 | 567.933 | 0.936 | 0.974 | 0.936
2017-07-31 | 1002.807 | 1004.621 | 1002.807 | 0.494 | 0.515 | 0.494
2017-08-31 | 1117.243 | 1119.759 | 1117.243 | 0.272 | 0.28 | 0.272
2017-09-30 | 1074.028 | 1076.294 | 1074.028 | 0.062 | 0.065 | 0.062
2017-10-31 | 876.417 | 878.177 | 876.417 | 0.181 | 0.187 | 0.181
2017-11-30 | 1025.231 | 1027.304 | 1025.231 | 0.126 | 0.131 | 0.126
2017-12-31 | 857.482 | 858.991 | 857.482 | 0.188 | 0.191 | 0.188
2018-01-31 | 703.514 | 704.891 | 703.514 | 0.16 | 0.176 | 0.16
2018-02-28 | 417.166 | 417.828 | 417.166 | 0.219 | 0.236 | 0.219
2018-03-31 | 354.454 | 355.158 | 354.454 | 1.033 | 0.509 | 1.033
2018-04-30 | 275.392 | 275.931 | 275.392 | 0.086 | 0.69 | 0.086
2018-05-31 | 281.997 | 282.611 | 281.997 | 0.321 | 0.34 | 0.321
2018-06-30 | 458.013 | 459.014 | 458.013 | 0.109 | 0.118 | 0.109
2018-07-31 | 1339.911 | 1343.153 | 1339.911 | 0.074 | 0.079 | 0.074
2018-08-31 | 2163.556 | 2169.4988 | 2163.556 | 0.006 | 0.005 | 0.006
2018-09-30 | 1744.6391 | 1748.8697 | 1744.6391 | 0.007 | 0.007 | 0.007
2018-10-31 | 1047.5675 | 1049.9921 | 1047.5675 | 0.025 | 0.026 | 0.025
2018-11-30 | 645.6042 | 646.9291 | 645.6042 | 0.388 | 0.402 | 0.388
2018-12-31 | 524.0332 | 524.958 | 524.0332 | 0.153 | 0.162 | 0.153
2019-01-31 | 399.1727 | 399.8495 | 399.1727 | 0.103 | 0.103 | 0.103
2019-02-28 | 233.5958 | 234.1106 | 233.5958 | 0.193 | 0.202 | 0.193
2019-03-31 | 183.4785 | 183.9063 | 183.4785 | 0.243 | 0.253 | 0.243
2019-04-30 | 174.4452 | 174.874 | 174.4452 | 0.465 | 0.496 | 0.465
Note on C17: +3.795, chênh lệch sau kiểm định
Note on D17: +3.795 chênh lệch sau kiểm định
Note on F17: trừ 1.000 sl sau kiểm định
Note on G17: trừ 1.010 cl sau kiểm định
Note on C29: trừ 0.49 chênh lệch sau kiểm định
Note on D29: trừ 0.49 chênh lệch sau kiểm định
Note on F29: trừ 0.410 chênh lệch sau kiểm định
Note on G29: trừ 0.410 chênh lệch sau kiểm định
Note on C41: cộng 2.198 cL sau kiểm định
Note on D41: cộng 2.208 cl sau kiểm định
Note on F41: Trừ 0.250 chênh lệch sau kiểm định
Note on G41: Trừ 0.250 chênh lệch sau kiểm định
Note on C53: trừ 0.470 cl sau kiểm định
Note on D53: trừ 0.470 cl sau kiểm định
Note on F53: Trừ 1.020 chênh lệch sau kiểm định
Note on G53: Trừ 1.013 chênh lệch sau kiểm định
Note on C65: cộng 0.719 cl sau kiểm định
Note on D65: cộng 0.721 cl sau kiểm định
Note on F65: Trừ 0.361 chênh lệch sau kiểm định
Note on G65: Trừ 0.362 chênh lệch sau kiểm định
Note on C77: cộng 3.588 cl sau kiểm định
Note on D77: cộng 3.588 cl sau kiểm định
Note on F77: Trừ 0.390 chênh lệch sau kiểm định
Note on G77: Trừ 0.390 chênh lệch sau kiểm định

## Fixed para
LALA HPP CDM Monitoring Fixed Parameters
ID | Parameter | Description | Unit | Meter conversion Factor agreed by EVN and CC1 | Factor for CER-Calculation | Reference
1 | EFgrid,CM | Combined margin in the year | tCO2/MWh | 0.5764 | 0.5764
2 | M11 | Coefficient for electric meter |  | 1000 | 1
3 | M12 | Coefficient for electric meter |  | 1000 | 1
Fixed Parameter
| ID | Parameter | Description |  | Unit | Value | Source (Reference)
| 1 | EFgrid,CM | Combined margin |  | tCO2/MWh | 0.5764 | PDD, MONRE, Vietnam, File 82

## QC-QA
Lala CDM Monitoring Quality Assurance and Control
Control of equipment maintenance
| Meter place | Type | Serial No | Meter accuracy class | Calibr. Frequency/yr
| M11 | Elster A 1700 |  | 0.5S | 2
| M12 | Elster A 1700 |  | 0.5S | 2
| Quality Assurance/Control | max 2.5% difference according to accuracy norms in Vietnam (main 0.5% / backup 1%)
| Parameter | Value (%) | Reference value (%) | Status | Comments/Expla-nations
Month | Difference of electricity between the main meter and the sub-meter
2012-10-01 | -2.096 | 99.77% | 97.5% | TRUE
2012-11-01 | -1.156 | 99.82% | 97.5% | TRUE
2012-12-01 | -0.593 | 99.87% | 97.5% | TRUE
2013-01-01 | -0.474 | 99.86% | 97.5% | TRUE
2013-02-01 | -0.327 | 99.86% | 97.5% | TRUE
2013-03-01 | -0.257 | 99.86% | 97.5% | TRUE
2013-04-01 | -0.296 | 99.85% | 97.5% | TRUE
2013-05-01 | -0.445 | 99.82% | 97.5% | TRUE
2013-06-01 | -0.396 | 99.8% | 97.5% | TRUE
2013-07-01 | -1.018 | 99.78% | 97.5% | TRUE
2013-08-01 | -1.235 | 99.77% | 97.5% | TRUE
2013-09-01 | -1.946 | 99.78% | 97.5% | TRUE
2013-10-01 | -3.527 | 99.78% | 97.5% | TRUE
2013-11-01 | -3.745 | 99.78% | 97.5% | TRUE
2013-12-01 | -1.996 | 99.84% | 97.5% | TRUE
2014-01-01 | -0.959 | 99.86% | 97.5% | TRUE
2014-02-01 | -0.553 | 99.84% | 97.5% | TRUE
2014-03-01 | -0.484 | 99.81% | 97.5% | TRUE
2014-04-01 | -0.504 | 99.76% | 97.5% | TRUE
2014-05-01 | -0.366 | 99.77% | 97.5% | TRUE
2014-06-01 | -0.662 | 99.76% | 97.5% | TRUE
2014-07-01 | -1.067 | 99.73% | 97.5% | TRUE
2014-08-01 | -1.453 | 99.73% | 97.5% | TRUE
2014-09-01 | -1.028 | 99.75% | 97.5% | TRUE
2014-10-01 | -0.839 | 99.77% | 97.5% | TRUE
2014-11-01 | -0.672 | 99.8% | 97.5% | TRUE
2014-12-01 | -0.88 | 99.82% | 97.5% | TRUE
2015-01-01 | -0.405 | 99.87% | 97.5% | TRUE
2015-02-01 | -0.385 | 99.84% | 97.5% | TRUE
2015-03-01 | -0.328 | 99.82% | 97.5% | TRUE
2015-04-01 | -0.227 | 99.82% | 97.5% | TRUE
2015-05-01 | -0.178 | 99.82% | 97.5% | TRUE
2015-06-01 | -0.187 | 99.85% | 97.5% | TRUE
2015-07-01 | -0.771 | 99.8% | 97.5% | TRUE
2015-08-01 | -0.82 | 99.75% | 97.5% | TRUE
2015-09-01 | -1.906 | 99.78% | 97.5% | TRUE
2015-10-01 | -1.768 | 99.77% | 97.5% | TRUE
2015-11-01 | -2.499 | 99.77% | 97.5% | TRUE
2015-12-01 | -1.196 | 99.79% | 97.5% | TRUE
2016-01-01 | -0.84 | 99.81% | 97.5% | TRUE
2016-02-01 | -0.345 | 99.87% | 97.5% | TRUE
2016-03-01 | -0.346 | 99.83% | 97.5% | TRUE
2016-04-01 | -0.365 | 99.77% | 97.5% | TRUE
2016-05-01 | -0.297 | 99.82% | 97.5% | TRUE
2016-06-01 | -0.326 | 99.8% | 97.5% | TRUE
2016-07-01 | -0.691 | 99.76% | 97.5% | TRUE
2016-08-01 | -1.462 | 99.76% | 97.5% | TRUE
2016-09-01 | -1.788 | 99.77% | 97.5% | TRUE
2016-10-01 | -2.506 | 99.77% | 97.5% | TRUE
2016-11-01 | -3.439 | 99.77% | 97.5% | TRUE
2016-12-01 | -2.19 | 99.81% | 97.5% | TRUE
2017-01-01 | -1.591 | 99.8% | 97.5% | TRUE
2017-02-01 | -0.82 | 99.84% | 97.5% | TRUE
2017-03-01 | -0.811 | 99.8% | 97.5% | TRUE
2017-04-01 | -0.63 | 99.77% | 97.5% | TRUE
2017-05-01 | -0.63 | 99.83% | 97.5% | TRUE
2017-06-01 | -1.268 | 99.78% | 97.5% | TRUE
2017-07-01 | -1.814 | 99.82% | 97.5% | TRUE
2017-08-01 | -2.516 | 99.77% | 97.5% | TRUE
2017-09-01 | -2.266 | 99.79% | 97.5% | TRUE
2017-10-01 | -1.76 | 99.8% | 97.5% | TRUE
2017-11-01 | -2.073 | 99.8% | 97.5% | TRUE
2017-12-01 | -1.509 | 99.82% | 97.5% | TRUE
2018-01-01 | -1.377 | 99.8% | 97.5% | TRUE
2018-02-01 | -0.662 | 99.84% | 97.5% | TRUE
2018-03-01 | -0.704 | 99.8% | 97.5% | TRUE
2018-04-01 | -0.539 | 99.8% | 97.5% | TRUE
2018-05-01 | -0.614 | 99.78% | 97.5% | TRUE
2018-06-01 | -1.001 | 99.78% | 97.5% | TRUE
2018-07-01 | -3.242 | 99.76% | 97.5% | TRUE
2018-08-01 | -5.9428 | 99.73% | 97.5% | TRUE
2018-09-01 | -4.2306 | 99.76% | 97.5% | TRUE
2018-10-01 | -2.4246 | 99.77% | 97.5% | TRUE
2018-11-01 | -1.3249 | 99.79% | 97.5% | TRUE
2018-12-01 | -0.92477 | 99.82% | 97.5% | TRUE
2019-01-01 | -0.67678 | 99.83% | 97.5% | TRUE
2019-02-01 | -0.51475 | 99.78% | 97.5% | TRUE
2019-03-01 | -0.4278 | 99.77% | 97.5% | TRUE
2019-04-01 | -0.42879 | 99.75% | 97.5% | TRUE

## Power Density
Power Density
PD = Cap,PJ / A,PJ
| Where | Cap,PJ = inbuilt capactity of hydropower plant (project activity)
A,PJ = Maximum Area of Reservoir during Monitoring
| Parameter | Description | Unit | Value-2012 | Value-2013 | Value-2014 | Value-2015 | Value-2016 | Value-2017 | Value-2018 | Value-2019
| Cap; PJ | Inbuilt capacity of the new hydropower plant | W | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000 | 3000000
| A,PJ | Maximum area of reservoir during monitoring period | m2 | 31800 | 34227.414 | 33013.707 | 39082.242 | 39082.242 | 41509.656 | 45628.504 | 45628.504
| PD | Power Density of the Monitoring Period | W/m2 | 94.3396 | 87.649 | 90.8713 | 76.7612 | 76.7612 | 72.2723 | 65.7484 | 65.7484 | Based on the highest water level during the monitoring period (water level: 309.20 m a.s.l.