## Title Page
Reducing Gas Leakages within the Jalalabad Gas Distribution Network in Bangladesh
VCS 2737 – VCS- Verification Period 3
CDM Methodology AM0023 V4 (Version 04.0.0)
Version # of Submission | 3

## ER Total
VCS 2737 – VCS Verification Period 3
Reducing Gas Leakages within the Jalalabad Gas Distribution Network in Bangladesh
Total VERs for Monitoring Period |  |  |  |  | 2022-01-01
| TCO2e |  | 365 | days in monitoring period after December 31, 2021 | 2022-12-31
monitoring measuring | 1150336
Total | 1150336
|  |  | Start of monitoring period | End of Monitoring Period
|  |  | 2022-01-01 | 2022-12-31
Actual BECAP | 1124521
Comparison BECAP | 1124520.9643 | 365 | days | (The comparison BECAP adjusted for the actual number of days in the monitoring period is less than the ERs calculated during the Monitoring period. Therefore, the BECAP is the number of ERs claimed)
VERs Allowed under BE Cap
Total | 1124520.9643

## Total
Leak Codes | GPS coordinate | Jalalabad Gas Transmission and Distribution System Limited | Before repair | [5 empty] | Repair | monitoring period is 2022 year
|  | Address | Date of measuring | # of HFS | M-1 |  | M-2 |  | Later of Date of repair and start date of Monitoring Period | Date of monitoring | Checked zero by GS / HFS # | M-1 |  | M-2 |  | Date of repair | Checked Zero by GS after repair | Leak rate, lpm | Difference between Baseline leak and Monitoring Measurement for period before monitoring date, (l/m) | Difference between Baseline Leak and Monitoring Measurement for period after monitoring date or after Re-Repair for reemerged leaks or after repair new leaks till the end of the second VCS monitoring period, (l/m) | Convert from l/m to m3/hr ((60)/1000), m3/hr methane (fsample). From the start of the 2nd VCS monitoring period until the Monitoring Measurement | Convert from l/m to m3/hr ((60)/1000), m3/hr methane (fsample) for period after monitoring date or after Re-Repair for reemerged leaks or after repair new leaks till the end of the 2nd VCS monitoring period | Conversion Factor T(CH4)/ m3(CH4) (ConvFactor) | The concentration of methane in the HFS sample flow from leak, Percentage of methane (C Sample) of HFS reading | Concentration of Methane in the background in the component (not automatically adjusted by HFS), Percentage of methane (Cback) not already incorporated in HFS reading | Flow of Methane m3/h, (FCH4)= (Fsample)* (Csample - Cback). for period from start VCS monitoring period to Monitoring Measurement | Flow of Methane m3/h, (FCH4)= (Fsample)* (Csample - Cback) for period after monitoring date or after Re-Repair for reemerged leaks or after repair new leaks till the end of the 2nd VCS monitoring period | Uncertainty factor, Utotal (UR,j) | Methane conversion factor (GWP) | Total Tonnes of CO2 per hour for period from start of the 2nd VCS monitoring period to Monitoring Measurement (TCO2e) | Total Tonnes of CO2 per hour for period after monitoring date or after Re-Repair for reemerged leaks or after repair new leaks till the end of of the 2nd VCS monitoring period (TCO2e) | Cut off date during the 2nd VCS monitoring period (date) | Hours of commercial shutoff for period before monitoring date during the 2nd VCS monitoring period (hours) | Hours of commercial shutoff for period after monitoring date or after Re-Repair for reemerged leaks or after repair new leaks till the end of the 2nd VCS monitoring period (hours) | Number of Operational Hours (Ti, j) for period before monitoring date during the 2nd VCS monitoring period (hours) | Number of Operational Hours (Ti, j) for period after monitoring date or after Re-Repair for reemerged leaks or after repair new leaks till the end of the 2nd VCS monitoring period (hours) | Total VERs Claimed for the 2nd VCS monitoring period (TCO2e) | Start of monitoring period | End of Monitoring Period
[5 empty] | Leak rate, lpm | # in HFS memory | Leak rate, lpm | # in HFS memory |  |  |  | Leak rate, lpm | # in HFS memory | Leak rate, lpm | # in HFS memory
[38 empty] | 2022-01-01 | 2023-01-01
HBG-1.CR.1.1 | 24163079128006 | Shaistagong, Johur Chan Bibi Woman Collage | 2019-09-05 | NQ1003 | 5.8 | 98 | 5.8 | 99 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6816 | 1943.9997 | 61.1116
HBG-1.RR.1.1 | 24230579124215 | Hobiganj, Zasher Abda, Zasher Abda Road, Wakhil Pal | 2019-01-20 | NQ1002 | 2.8 | 5 | 2.8 | 6 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6288 | 2471.9997 | 29.5021
HBG-1.RR.2.1 | 24230759124207 | Hobiganj, Zasher Abda, Zasher Abda Road, Brisha Pal | 2019-01-20 | NQ1002 | 1.1 | 9 | 1.1 | 10 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6288 | 2471.9997 | 11.5901
HBG-1.RR.3.1 | 24230839124206 | Hobiganj, Zasher Abda, Zasher Abda Road, Diju Bonik | 2019-01-20 | NQ1002 | 11.1 | 13 | 11.1 | 14 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6288 | 2471.9997 | 116.9549
HBG-1.RR.4.1 | 24230839124206 | Hobiganj, Zasher Abda, Zasher Abda Road, Sumon Votta Chargo | 2019-01-20 | NQ1002 | 1.9 | 15 | 1.9 | 16 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6288 | 2471.9997 | 20.0193
HBG-1.RR.5.1 | 24230839124206 | Hobiganj, Zasher Abda, Zasher Abda Road, Pran Gopal Bonik | 2019-01-20 | NQ1002 | 5.7 | 20 | 5.7 | 21 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6288 | 2471.9997 | 60.0579
HBG-1.RR.6.1 | 24230969124201 | Hobiganj, Zasher Abda, Zasher Abda Road, Pronob Chondro Shill | 2019-01-20 | NQ1002 | 6.3 | 24 | 6.3 | 25 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6288 | 2471.9997 | 66.3798
HBG-1.RR.7.1 | 24230979124204 | Hobiganj, Zasher Abda, Zasher Abda Road, Reba Rani Sarkar | 2019-01-20 | NQ1002 | 9.3 | 28 | 9.2 | 29 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6288 | 2471.9997 | 96.9356
HBG-1.RR.8.1 | 24231099124205 | Hobiganj, Zasher Abda, Zasher Abda Road, Sujit Chandra | 2019-01-20 | NQ1002 | 1.8 | 34 | 1.7 | 35 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6288 | 2471.9997 | 17.912
HBG-1.RR.9.1 | 24230999124224 | Hobiganj, Noahati,Word - 3, kulendro Das | 2019-01-20 | NQ1002 | 10.5 | 40 | 10.5 | 41 | 2022-01-01 | [9 empty] | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0
HBG-1.RR.10.1 | 24230949124223 | Hobiganj, Noahati,Word - 3,Priyotosh Sorkar | 2019-01-20 | NQ1002 | 3.8 | 45 | 3.8 | 46 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6384 | 2375.9997 | 40.0386
HBG-1.RR.11.1 | 24164529126279 | Syaistagonj, Thana Road, Nurul Islam | 2019-08-31 | NQ1002 | 6.6 | 169 | 6.6 | 170 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6624 | 2135.9997 | 69.5408
HBG-1.RR.12.1 | 24163789127073 | Syaistagonj, Daud Nagar Bazar, Ranju | 2019-08-31 | NQ1002 | 16.8 | 171 | 16.9 | 172 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 6624 | 2135.9997 | 178.0665
HBG-1.RR.13.1 | 24163789127073 | Syaistagonj, Daud Nagar Bazar, Ranju | 2019-08-31 | NQ1002 | 11.4 | 173 | 11.4 | 174 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6624 | 2135.9997 | 120.1159
HBG-1.RR.14.1 | 24163479127086 | Syaistagonj, Mahalul Sunm, Girls School Road, Begum Anowara Jakariya | 2019-08-31 | NQ1002 | 12.3 | 175 | 12.3 | 176 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6624 | 2135.9997 | 129.5987
HBG-1.RR.15.1 | 24163459127085 | Syaistagonj, Mahalul Sunm, Girls School Road, Md. Abdul Hamid | 2019-08-31 | NQ1002 | 12.3 | 177 | 12 | 178 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6624 | 2135.9997 | 126.4378
HBG-1.RR.17.1 | 24163459127085 | Syaistagonj, Mahalul Sunm, Girls School Road, Harun Munshi | 2019-08-31 | NQ1002 | 63.4 | 181 | 63.4 | 182 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 63.4 | 63.4 | 3.804 | 3.804 | 0.0007168 | 100% | 0% | 3.804 | 3.804 | 0.0011869 | 28 | 0.076257 | 0.076257 |  | 0 | 0 | 6624 | 2135.9997 | 668.0129
HBG-1.RR.17.2 | 24163459127085 | Syaistagonj, Mahalul Sunm, Girls School Road, Harun Munshi | 2019-08-31 | NQ1002 | 33.5 | 183 | 33.5 | 184 | 2022-01-01 | [9 empty] | 33.5 | 33.5 | 2.01 | 2.01 | 0.0007168 | 100% | 0% | 2.01 | 2.01 | 0.0011869 | 28 | 0.040294 | 0.040294 | 2022-03-06 12:00 | 0 | 0
HBG-1.RR.18.1 | 24163189127145 | Syaistagonj, Mahalul Sunm, Girls School Road, Afser Mia | 2019-09-01 | NQ1002 | 11.8 | 205 | 11.5 | 206 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6624 | 2135.9997 | 121.1695
HBG-1.RR.19.1 | 24163189127145 | Syaistagonj, Mahalul Sunm, Girls School Road, Abdul Hai | 2019-09-01 | NQ1002 | 9.3 | 207 | 9.3 | 208 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6624 | 2135.9997 | 97.9893
HBG-1.RR.20.1 | 24163219127159 | Syaistagonj, Mahalul Sunm, Girls School Road, Mamun Mia | 2019-09-01 | NQ1002 | 13.3 | 209 | 13.3 | 210 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6624 | 2135.9997 | 140.1352
HBG-1.RR.21.1 | 24230579124215 | Habiganj, Jassarabda, Nopur Das | 2019-01-20 | NQ1002 | 13.7 | 3 | 13.7 | 4 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6288 | 2471.9997 | 144.3498
HBG-1.RR.22.1 | 24230669124212 | Habiganj, Jassarabda, Gosai Chandro | 2019-01-20 | NQ1002 | 9.9 | 7 | 9.9 | 8 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6288 | 2471.9997 | 104.3112
HBG-1.RR.23.1 | 24230799124201 | Habiganj, Jassarabda, Netendro Sarker | 2019-01-20 | NQ1002 | 7.2 | 11 | 7.2 | 12 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6288 | 2471.9997 | 75.8627
HBG-1.RR.24.1 | 24230839124206 | Habiganj, Jassarabda, Motilal Chandro | 2019-01-20 | NQ1002 | 1.2 | 18 | 1.2 | 19 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6288 | 2471.9997 | 12.6438
HBG-1.RR.25.1 | 24230839124206 | Habiganj, Jassarabda, Asotos Deb | 2019-01-20 | NQ1002 | 5.1 | 22 | 5.1 | 23 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6288 | 2471.9997 | 53.7361
HBG-1.RR.26.1 | 24230989124205 | Habiganj, Jassarabda, Makhon Pal | 2019-01-20 | NQ1002 | 10.9 | 26 | 10.9 | 27 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6288 | 2471.9997 | 114.8476
HBG-1.RR.27.1 | 24231019124205 | Habiganj, Jassarabda, Neshet Sarker | 2019-01-20 | NQ1002 | 7.8 | 30 | 7.8 | 31 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6288 | 2471.9997 | 82.1846
HBG-1.RR.28.1 | 24231109124205 | Habiganj, Jassarabda, Robi Pal | 2019-01-20 | NQ1002 | 3.1 | 32 | 3.1 | 33 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6288 | 2471.9997 | 32.6631
HBG-1.RR.29.1 | 24231109124205 | Habiganj, Jassarabda, Prodip Sarker, Besaide Shat Songo Mondir | 2019-01-20 | NQ1002 | 2.8 | 36 | 2.8 | 37 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6288 | 2471.9997 | 29.5021
HBG-1.RR.30.1 | 24231109124205 | Habiganj, Jassarabda, Gourango Deb, Besaide Shat Songo Mondir | 2019-01-20 | NQ1002 | 1.2 | 38 | 1.2 | 39 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6288 | 2471.9997 | 12.6438
HBG-1.RR.31.1 | 24163799127104 | Shaistaganj, Daudnagor Bazar, Trafic Point, Samiron Datta | 2019-08-31 | NQ1002 | 11.1 | 185 | 11.1 | 186 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6624 | 2135.9997 | 116.9549
HBG-1.RR.32.1 | 24163769127124 | Shaistaganj, Daudnagor Bazar, Azgor Hosen | 2019-08-31 | NQ1002 | 22.5 | 187 | 22.5 | 188 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 22.5 | 22.5 | 1.35 | 1.35 | 0.0007168 | 100% | 0% | 1.35 | 1.35 | 0.0011869 | 28 | 0.027063 | 0.027063 |  | 0 | 0 | 6624 | 2135.9997 | 237.0708
HBG-1.RR.33.1 | 24163369127235 | Shaistaganj, Biramchar Road, Balla Rail Gate, Amdadul Haque | 2019-08-31 | NQ1002 | 25.4 | 189 | 25.1 | 190 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 25.1 | 25.1 | 1.506 | 1.506 | 0.0007168 | 100% | 0% | 1.506 | 1.506 | 0.0011869 | 28 | 0.03019 | 0.03019 |  | 0 | 0 | 6624 | 2135.9997 | 264.4657
HBG-1.RR.34.1 | 24163589127238 | Shaistaganj, Shaistaganj Station Road, Balla Rail gate, Abdur Rohim | 2019-08-31 | NQ1002 | 13.8 | 191 | 13.8 | 192 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6624 | 2135.9997 | 145.4034
HBG-1.RR.35.1 | 24163339127307 | Shaistaganj, South Lengapara, Opposite Of BADC, Aksir Mia | 2019-08-31 | NQ1002 | 38 | 193 | 38.1 | 194 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 38.1 | 38.1 | 2.286 | 2.286 | 0.0007168 | 100% | 0% | 2.286 | 2.286 | 0.0011869 | 28 | 0.045826 | 0.045826 |  | 0 | 0 | 6624 | 2135.9997 | 401.4399
HBG-1.RR.36.1 | 24163599127245 | Shaistaganj, Shaistaganj Station Road, Balla Rail Gate, Shamima | 2019-08-31 | NQ1002 | 20.5 | 195 | 20.5 | 196 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 20.5 | 20.5 | 1.23 | 1.23 | 0.0007168 | 100% | 0% | 1.23 | 1.23 | 0.0011869 | 28 | 0.024657 | 0.024657 |  | 0 | 0 | 6624 | 2135.9997 | 215.9979
HBG-1.RR.36.2 | 24163599127245 | Shaistaganj, Shaistaganj Station Road, Balla Rail Gate, Shamima | 2022-04-03 | LU1001 | 11.3 | 118 | 11.3 | 119 | 2022-04-03 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 4416 | 2135.9997 | 89.052
HBG-1.RR.37.1 | 24163599127245 | Shaistaganj, Shaistaganj Station Road, Balla Rail Gate, Shamima | 2019-08-31 | NQ1002 | 4.8 | 197 | 4.9 | 198 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6624 | 2135.9997 | 51.6288
HBG-1.RR.38.1 | 24163579127234 | Shaistaganj, Shaistaganj Station Road, Balla Rail Gate, Babul | 2019-08-31 | NQ1002 | 5.7 | 199 | 5.7 | 200 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6624 | 2135.9997 | 60.0579
HBG-1.RR.39.1 | 24163789127213 | Shaistaganj, Shaistaganj Station Road, Balla Rail Gate, Shah Jahan | 2019-08-31 | NQ1002 | 12.7 | 201 | 12.7 | 202 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6624 | 2135.9997 | 133.8133
HBG-1.RR.39.2 | 24163789127213 | Shaistaganj, Shaistaganj Station Road, Balla Rail Gate, Shah Jahan | 2021-01-11 | MN1032 | 2.5 | 5 | 2.5 | 6 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6624 | 2135.9997 | 26.3412
HBG-1.RR.40.1 | 24163789127213 | Shaistaganj, Shaistaganj Station Road, Balla Rail Gate, Abdul Monnaf | 2019-08-31 | NQ1002 | 8.1 | 203 | 8.1 | 204 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6624 | 2135.9997 | 85.3455
HBG-1.RR.41.1 | 24231649124331 | Hobiganj, Baterpur, Kalegastola, Word # 3, H # 2137, Nantu Ray | 2019-01-20 | NQ1000 | 4 | 105 | 4 | 106 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6384 | 2375.9997 | 42.1459
HBG-1.RR.42.1 | 24231759124345 | Hobiganj, Baterpur, Kalegastola, Word # 3, Omor Chandra Das | 2019-01-20 | NQ1000 | 19.1 | 107 | 19.2 | 108 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 19.2 | 19.2 | 1.152 | 1.152 | 0.0007168 | 100% | 0% | 1.152 | 1.152 | 0.0011869 | 28 | 0.023094 | 0.023094 |  | 0 | 0 | 6384 | 2375.9997 | 202.3004
HBG-1.RR.43.1 | 24231169124322 | Hobiganj, Baterpur, Kalegastola, Garne park, H # 1955, Ponkoz Sutrodhar | 2019-01-20 | NQ1000 | 11.2 | 109 | 10.9 | 110 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6336 | 2423.9997 | 114.8476
HBG-1.RR.44.1 | 24231039124329 | Hobiganj, Baterpur, Kalegastola, Garne park, H # 1950, Tahamina Begum | 2019-01-20 | NQ1000 | 2.4 | 111 | 2.4 | 112 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6336 | 2423.9997 | 25.2876
HBG-1.RR.45.1 | 24230969124337 | Hobiganj, Baterpur, Kalegastola, Garne park, Word # 3, H # 1945, Abul Hossain | 2019-01-20 | NQ1000 | 1.5 | 113 | 1.5 | 114 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6336 | 2423.9997 | 15.8047
HBG-1.RR.46.1 | 24230929124324 | Hobiganj, Baterpur, Kalegastola, Garne park, Word # 3, H # 1946/3, Narawon das | 2019-01-20 | NQ1000 | 7.8 | 117 | 7.8 | 118 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6336 | 2423.9997 | 82.1846
HBG-1.RR.47.1 | 24231289124342 | Hobiganj, Baterpur, Kalegastola, Garne park, Word # 3, H # 1940, Md. Abdur Rahman | 2019-01-20 | NQ1000 | 22.4 | 119 | 22.4 | 120 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 22.4 | 22.4 | 1.344 | 1.344 | 0.0007168 | 100% | 0% | 1.344 | 1.344 | 0.0011869 | 28 | 0.026943 | 0.026943 |  | 0 | 0 | 6336 | 2423.9997 | 236.0172
HBG-1.RR.48.1 | 24231239124344 | Hobiganj, Baterpur, Kalegastola, Garne park, Word # 3, H # 1938, Abdul Haque | 2019-01-20 | NQ1000 | 18.3 | 121 | 18.2 | 122 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 6336 | 2423.9997 | 191.764
HBG-1.RR.49.1 | 24163779126552 | Shaistaganj, South Borchor, Amir Hosen | 2019-08-31 | NQ1003 | 13.3 | 540 | 13.3 | 541 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6624 | 2135.9997 | 140.1352
HBG-1.RR.50.1 | 24163749126554 | Shaistaganj, South Borchor, Nur Hosen | 2019-08-31 | NQ1003 | 5 | 542 | 5 | 543 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6624 | 2135.9997 | 52.6824
HBG-1.RR.51.1 | 24163969126589 | Shaistaganj, South Borchor, Station Road, Abdul Kasem | 2019-08-31 | NQ1003 | 11.6 | 544 | 10.9 | 545 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6624 | 2135.9997 | 114.8476
HBG-1.RR.52.1 | 24163709127001 | Shaistaganj, Talugary, Station Road, Nazma Begum | 2019-08-31 | NQ1003 | 10.7 | 546 | 10.2 | 547 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6624 | 2135.9997 | 107.4721
HBG-1.RR.53.1 | 24163729126598 | Shaistaganj, Talugary, Station Road, Sanjob Ali | 2019-08-31 | NQ1003 | 12.3 | 548 | 12.3 | 549 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6624 | 2135.9997 | 129.5987
HBG-1.RR.54.1 | 24163739126590 | Shaistaganj, South Borchor, Talugary, Station Road, Mostafijur Rahman Ripon | 2019-08-31 | NQ1003 | 11.3 | 550 | 11.3 | 551 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6624 | 2135.9997 | 119.0622
HBG-1.RR.55.1 | 24163489127000 | Shaistaganj, Talugary, Station Road, Rafiqullah | 2019-08-31 | NQ1003 | 11.8 | 552 | 11.8 | 553 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6624 | 2135.9997 | 124.3305
HBG-1.RR.56.1 | 24163469127000 | Shaistaganj, Talugary, Station Road, Abdul Jalil | 2019-08-31 | NQ1003 | 12.9 | 554 | 12.9 | 555 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6624 | 2135.9997 | 135.9206
HBG-1.RR.57.1 | 24163469126595 | Shaistaganj, Talugary, Station Road, Abdul Kayum | 2019-08-31 | NQ1003 | 10.5 | 556 | 10.3 | 557 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6624 | 2135.9997 | 108.5258
HBG-1.RR.58.1 | 24114499131042 | Chunarughat, Chondona, Ward # 6, H # 287, Lila Bhaban | 2019-09-01 | NQ1003 | 10.6 | 590 | 10.6 | 591 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6456 | 2303.9997 | 111.6867
HBG-1.RR.59.1 | 24114499131039 | Chunarughat, Chondona, Ward # 6, Uttam Kumar | 2019-09-01 | NQ1003 | 8.7 | 592 | 8.7 | 593 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6456 | 2303.9997 | 91.6674
HBG-1.RR.60.1 | 24114159131013 | Chunarughat, Chondona, Ward # 04, H # 49, Kripesh Dev | 2019-09-01 | NQ1003 | 4.2 | 594 | 4.2 | 595 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6456 | 2303.9997 | 44.2532
HBG-1.RR.61.1 | 24231609124320 | Habiganj,Batirpur Residential Area,Ward# 3, Sudeb Sarkar, H# 2134 | 2019-01-20 | NQ1005 | 1.3 | 1 | 1.2 | 2 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6384 | 2375.9997 | 12.6438
HBG-1.RR.62.1 | 24231619124323 | Habiganj,Batirpur Residential Area,Ward# 3, Joydeb Sarkar, H# 2133 | 2019-01-20 | NQ1005 | 2.3 | 3 | 2.3 | 4 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6384 | 2375.9997 | 24.2339
HBG-1.RR.63.1 | 24231649124329 | Habiganj,Batirpur Residential Area,Ward# 3, Mohaprovu Banik, H# 2164 | 2019-01-20 | NQ1005 | 2.7 | 5 | 2.7 | 6 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6384 | 2375.9997 | 28.4485
HBG-1.RR.64.1 | 24231749124345 | Habiganj,Batirpur Residential Area,Ward# 3, Lokkhi Sarkar, H# 2156/1 | 2019-01-20 | NQ1005 | 1 | 7 | 1 | 8 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 6384 | 2375.9997 | 10.5365
HBG-1.RR.65.1 | 24231449124271 | Habiganj,Baipass, Noyahati Road, Hazi Imtiaz Monjil, Ataur Rahman Selim | 2019-01-20 | NQ1005 | 3.2 | 9 | 3.2 | 10 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6384 | 2375.9997 | 33.7167
HBG-1.RR.66.1 | 24231099124255 | Habiganj,Baipass, Noyahati Road, Motilal Suttradhor, H# 2353 | 2019-01-20 | NQ1005 | 10.8 | 11 | 11.3 | 12 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6384 | 2375.9997 | 119.0622
HBG-1.RR.67.1 | 24230899124253 | Habiganj,Baipass, Noyahati , Ward# 3, Somvu Manik | 2019-01-20 | NQ1005 | 1.4 | 13 | 1.4 | 14 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6288 | 2471.9997 | 14.7511
HBG-1.RR.68.1 | 24164269126417 | Shaistaganj, Udain R/A, Dhunu Mia | 2019-08-31 | NQ1003 | 12 | 520 | 12.1 | 521 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6624 | 2135.9997 | 127.4914
HBG-1.RR.69.1 | 24164269126417 | Shaistaganj, Udain R/A, Sofiqul Islam | 2019-08-31 | NQ1003 | 13.1 | 522 | 13.1 | 523 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6624 | 2135.9997 | 138.0279
HBG-1.RR.70.1 | 24164269126417 | Shaistaganj, Udain R/A, Anis Mia | 2019-08-31 | NQ1003 | 14.3 | 524 | 14.3 | 525 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6624 | 2135.9997 | 150.6717
HBG-1.RR.71.1 | 24164229126446 | Shaistaganj, Udain R/A, Shain Mia | 2019-08-31 | NQ1003 | 13.9 | 526 | 13.9 | 527 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6624 | 2135.9997 | 146.4571
HBG-1.RR.71.2 | 24164229126446 | Shaistaganj, Udain R/A, Shain Mia | 2022-04-03 | LU1001 | 2.6 | 116 | 2.5 | 117 | 2022-04-03 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 4416 | 2135.9997 | 19.7018
HBG-1.RR.72.1 | 24163969126526 | Shaistaganj, Udain R/A, Taijul Islam | 2019-08-31 | NQ1003 | 8.9 | 528 | 8.9 | 529 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6624 | 2135.9997 | 93.7747
HBG-1.RR.73.1 | 24163839126520 | Shaistaganj, Udain R/A, Boshir Voban | 2019-08-31 | NQ1003 | 5.9 | 530 | 5.9 | 531 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6624 | 2135.9997 | 62.1652
HBG-1.RR.74.1 | 24163769126513 | Shaistaganj, Udain R/A, Minara | 2019-08-31 | NQ1003 | 10.9 | 532 | 10.9 | 533 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6624 | 2135.9997 | 114.8476
HBG-1.RR.75.1 | 24163539126543 | Shaistaganj, South Borcor, Talukgorai, Baccu Mia | 2019-08-31 | NQ1003 | 12.6 | 534 | 12.6 | 535 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6624 | 2135.9997 | 132.7597
HBG-1.RR.76.1 | 24163329126532 | Shaistaganj, South Borcor, Talukgorai, Abdul Rob | 2019-08-31 | NQ1003 | 26.2 | 536 | 26.2 | 537 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 26.2 | 26.2 | 1.572 | 1.572 | 0.0007168 | 100% | 0% | 1.572 | 1.572 | 0.0011869 | 28 | 0.031513 | 0.031513 |  | 0 | 0 | 6624 | 2135.9997 | 276.0558
HBG-1.RR.77.1 | 24163329126532 | Shaistaganj, South Borcor, Talukgorai, Lal Mia | 2019-08-31 | NQ1003 | 9.2 | 538 | 9.2 | 539 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6624 | 2135.9997 | 96.9356
HBG-1.RR.78.1 | 24162689128088 | Shaistaganj, Sabaspur, Aklas | 2019-09-01 | NQ1003 | 23.2 | 558 | 23.2 | 559 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 23.2 | 23.2 | 1.392 | 1.392 | 0.0007168 | 100% | 0% | 1.392 | 1.392 | 0.0011869 | 28 | 0.027905 | 0.027905 |  | 0 | 0 | 6816 | 1943.9997 | 244.4464
HBG-1.RR.79.1 | 24162689128088 | Shaistaganj, Sabaspur, Dainer Security Survice | 2019-09-01 | NQ1003 | 17.5 | 562 | 17.5 | 563 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6816 | 1943.9997 | 184.3884
HBG-1.RR.79.2 | 24162689128088 | Shaistaganj, Sabaspur, Dainer Security Survice | 2020-10-12 | NQ1003 | 6.3 | 28 | 6.3 | 29 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6816 | 1943.9997 | 66.3798
HBG-1.RR.80.1 | 24162669128101 | Shaistaganj, Sabaspur, Station Road, Mahi Cottage | 2019-09-01 | NQ1003 | 13.1 | 564 | 13.1 | 565 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6816 | 1943.9997 | 138.0279
HBG-1.RR.81.1 | 24164499126297 | Shayestaganj, Thana Road, Police Station | 2019-08-31 | NQ1011 | 14.3 | 379 | 14.4 | 380 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6624 | 2135.9997 | 151.7253
HBG-1.RR.81.2 | 24164499126297 | Shayestaganj, Thana Road, Police Station | 2022-04-03 | LU1001 | 11.6 | 114 | 11.6 | 115 | 2022-04-03 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 4416 | 2135.9997 | 91.4162
HBG-1.RR.82.1 | 24164329126385 | Shayestaganj, Thana Road, Sufia Cottage, H # 5 | 2019-08-31 | NQ1011 | 20.6 | 381 | 20.6 | 382 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 20.6 | 20.6 | 1.236 | 1.236 | 0.0007168 | 100% | 0% | 1.236 | 1.236 | 0.0011869 | 28 | 0.024778 | 0.024778 |  | 0 | 0 | 6624 | 2135.9997 | 217.0515
HBG-1.RR.83.1 | 24164289126392 | Shayestaganj, Thana Road, Aliganj Bazar, Mojammel Haq | 2019-08-31 | NQ1011 | 12.1 | 383 | 11.7 | 384 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6624 | 2135.9997 | 123.2768
HBG-1.RR.84.1 | 24164289126392 | Shayestaganj, Thana Road, Aliganj Bazar, Shafiq Mia | 2019-08-31 | NQ1011 | 12.8 | 385 | 12.8 | 386 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6624 | 2135.9997 | 134.867
HBG-1.RR.85.1 | 24163779127164 | Shayestaganj, Station Road, Doudnagar Bazar, Himmot Ali | 2019-08-31 | NQ1011 | 11.3 | 387 | 11.3 | 388 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6624 | 2135.9997 | 119.0622
HBG-1.RR.86.1 | 24163779127164 | Shayestaganj, Station Road, Doudnagar Bazar, Himmot Ali | 2019-08-31 | NQ1011 | 13 | 389 | 13 | 390 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6624 | 2135.9997 | 136.9743
HBG-1.RR.86.2 | 24163779127164 | Shayestaganj, Station Road, Doudnagar Bazar, Himmot Ali | 2020-10-17 | NQ1003 | 2.1 | 40 | 2.1 | 41 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6624 | 2135.9997 | 22.1266
HBG-1.RR.87.1 | 24163589127181 | Shayestaganj, Station Road, Mohlul Sunam R/A, Selim | 2019-08-31 | NQ1011 | 11 | 395 | 11 | 396 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6624 | 2135.9997 | 115.9013
HBG-1.RR.88.1 | 24163589127181 | Shayestaganj, Station Road, Mohlul Sunam R/A, Sadek Mohol | 2019-08-31 | NQ1011 | 7.9 | 399 | 8 | 400 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6624 | 2135.9997 | 84.2919
HBG-1.RR.89.1 | 24163409127194 | Shayestaganj, Station Road, Mohlul Sunam R/A, Zafor Sadek | 2019-08-31 | NQ1011 | 10.9 | 401 | 10.9 | 402 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6624 | 2135.9997 | 114.8476
HBG-1.RR.90.1 | 24163409127176 | Shayestaganj, Station Road, Mohlul Sunam R/A, Azgor Ali | 2019-08-31 | NQ1011 | 21.3 | 403 | 21.3 | 404 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 6624 | 2135.9997 | 224.4271
HBG-1.RR.91.1 | 24163189127203 | Saistaganj, Mohlul Sunam R/A, Md. Rafiqul Islam | 2019-08-31 | NQ1011 | 22 | 411 | 21.3 | 412 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 6624 | 2135.9997 | 224.4271
HBG-1.RR.92.1 | 24163189127203 | Saistaganj, Mohlul Sunam R/A, Limon | 2019-08-31 | NQ1011 | 6.1 | 413 | 6.1 | 414 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6624 | 2135.9997 | 64.2725
HBG-1.RR.93.1 | 24163189127177 | Saistaganj, Mohlul Sunam R/A, Kodom Ali | 2019-08-31 | NQ1011 | 9.9 | 415 | 9.9 | 416 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6624 | 2135.9997 | 104.3112
HBG-1.RR.94.1 | 24163209127389 | Saistaganj, Station Road, Workshop Area, A. Harun Villa | 2019-08-31 | NQ1011 | 14.3 | 417 | 14.3 | 418 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6816 | 1943.9997 | 150.6717
HBG-1.RR.95.1 | 24163259127374 | Saistaganj, Station Road, Workshop Area, Safwan School & College | 2019-08-31 | NQ1011 | 10.9 | 421 | 10.9 | 422 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6816 | 1943.9997 | 114.8476
HBG-1.RR.96.1 | 24163259127359 | Saistaganj, Station Road, Workshop Area, Faruk torofdar | 2019-08-31 | NQ1011 | 4.8 | 423 | 4.7 | 424 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6816 | 1943.9997 | 49.5215
HBG-1.RR.97.1 | 24163339127372 | Saistaganj, Station Road, Workshop Area, Md. Kawas mia | 2019-08-31 | NQ1011 | 24 | 425 | 24 | 426 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 24 | 24 | 1.44 | 1.44 | 0.0007168 | 100% | 0% | 1.44 | 1.44 | 0.0011869 | 28 | 0.028867 | 0.028867 |  | 0 | 0 | 6816 | 1943.9997 | 252.8756
HBG-1.RR.98.1 | 24163309127457 | Saistaganj, Station Road, Workshop Area, Sita Rani | 2019-08-31 | NQ1011 | 17.9 | 427 | 18.1 | 428 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6816 | 1943.9997 | 190.7103
HBG-1.RR.99.1 | 24163309127457 | Saistaganj, Station Road, Workshop Area, Silpi Pal | 2019-08-31 | NQ1011 | 4.1 | 429 | 4.1 | 430 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6816 | 1943.9997 | 43.1996
HBG-1.RR.100.1 | 24163099127542 | Saistaganj, Station Road, Workshop Area, Abdus Sohid | 2019-08-31 | NQ1011 | 94.9 | 431 | 94.9 | 432 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 94.9 | 94.9 | 5.694 | 5.694 | 0.0007168 | 100% | 0% | 5.694 | 5.694 | 0.0011869 | 28 | 0.11415 | 0.11415 |  | 0 | 0 | 6816 | 1943.9997 | 999.9121
HBG-1.RR.101.1 | 24162809128102 | Syaistagonj, Lenja Para, Abdul Wahid | 2019-09-01 | NQ1002 | 3.8 | 211 | 3.8 | 212 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6816 | 1943.9997 | 40.0386
HBG-1.RR.102.1 | 24161349128333 | Syaistagonj, Kutirgaw, Lutfur Rahman | 2019-09-01 | NQ1002 | 11.5 | 213 | 11.5 | 214 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6816 | 1943.9997 | 121.1695
HBG-1.RR.103.1 | 24161449128335 | Syaistagonj, Kutirgaw, Abdur Shahid | 2019-09-01 | NQ1002 | 15.3 | 215 | 15.3 | 216 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6816 | 1943.9997 | 161.2082
HBG-1.RR.104.1 | 24160919128378 | Syaistagonj, Kutirgaw, Saimimur Rahman | 2019-09-01 | NQ1002 | 9.4 | 217 | 9.4 | 218 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6816 | 1943.9997 | 99.0429
HBG-1.RR.105.1 | 24160589128352 | Syaistagonj, Notunbridge, S.R Hotel (Abashik) | 2019-09-01 | NQ1002 | 2.1 | 219 | 2.1 | 220 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6816 | 1943.9997 | 22.1266
HBG-1.RR.106.1 | 24160969128328 | Syaistagonj, Notunbridge, Hazi Rohamotulla | 2019-09-01 | NQ1002 | 6.6 | 221 | 6.6 | 222 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6816 | 1943.9997 | 69.5408
HBG-1.RR.107.1 | 24111879131263 | Hobigonj, Chunarughat, Balla Road, Chondina, Abdul Awol | 2019-09-02 | NQ1002 | 8.4 | 260 | 8.4 | 261 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6456 | 2303.9997 | 88.5064
HBG-1.RR.108.1 | 24104949130464 | Chunarughat, Dewargash, Mostofa Ahmed | 2019-09-02 | NQ1002 | 5 | 262 | 5 | 263 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6456 | 2303.9997 | 52.6824
HBG-1.RR.109.1 | 24201729132224 | Bahubal, South Bahubal, Kali Kumar | 2019-09-03 | NQ1002 | 11.5 | 276 | 11.5 | 277 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6312 | 2447.9997 | 121.1695
HBG-1.RR.110.1 | 24201609132241 | Bahubal, South Bahubal, Jhantu Dhor | 2019-09-03 | NQ1002 | 15.8 | 278 | 15.8 | 279 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6312 | 2447.9997 | 166.4764
HBG-1.RR.111.1 | 24201439132265 | Bahubal, South Bahubal, Nithun Das | 2019-09-03 | NQ1002 | 13.3 | 280 | 13.5 | 281 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6312 | 2447.9997 | 142.2425
HBG-1.RR.112.1 | 24201919132197 | Bahubal, Hospital Alaka, Lal Mia | 2019-09-04 | MP1006 | 12.3 | 21 | 12.3 | 22 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6312 | 2447.9997 | 129.5987
HBG-1.RR.113.1 | 24202699132202 | Bahubal, Hospital Alaka, Lizon Super Market | 2019-09-04 | MP1006 | 9.7 | 23 | 9.7 | 24 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6312 | 2447.9997 | 102.2039
HBG-1.RR.114.1 | 24241339133497 | Bahubal, Putizury, Nowapara, Md. Fayek | 2019-09-04 | MP1006 | 10.8 | 25 | 10.8 | 26 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6312 | 2447.9997 | 113.794
HBG-1.RR.115.1 | 24241339133497 | Bahubal, Putizury, Nowapara, Sofiqur Rohman | 2019-09-04 | MP1006 | 11.9 | 27 | 11.9 | 28 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6312 | 2447.9997 | 125.3841
HBG-1.RR.116.1 | 24241149133503 | Bahubal, Putizury, Nowapara, Khurseda Begum | 2019-09-04 | MP1006 | 8.8 | 29 | 8.8 | 30 | 2022-01-01 | [9 empty] | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0
HBG-1.RR.117.1 | 24240929133504 | Bahubal, Putizury, Nowapara, Nizamuddin | 2019-09-04 | MP1006 | 11.6 | 31 | 11.6 | 32 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6312 | 2447.9997 | 122.2232
HBG-1.RR.118.1 | 24241259133596 | Bahubal, Putizury, Jadobpur, Ali Babu | 2019-09-04 | MP1006 | 16.1 | 33 | 16.1 | 34 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6312 | 2447.9997 | 169.6373
HBG-1.RR.119.1 | 24244499133521 | Bahubal, Putizury, Palbary, Nisy Kanto Pal | 2019-09-04 | MP1006 | 10.1 | 35 | 10.1 | 36 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6312 | 2447.9997 | 106.4185
HBG-1.RR.120.1 | 24244499133521 | Bahubal, Putizury, Palbary, Koruna Pal | 2019-09-04 | MP1006 | 12.8 | 37 | 12.8 | 38 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6312 | 2447.9997 | 134.867
HBG-1.RR.121.1 | 24244499133521 | Bahubal, Putizury, Palbary, Somor Pal | 2019-09-04 | MP1006 | 9.3 | 39 | 9.3 | 40 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6312 | 2447.9997 | 97.9893
HBG-1.RR.122.1 | 24115129131079 | Hobigonj, Chunarughat, Model Thana | 2019-09-05 | MP1006 | 15.8 | 41 | 15.8 | 42 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6456 | 2303.9997 | 166.4764
HBG-1.RR.123.1 | 24141039130083 | Hobigonj, Chunarughat, Sreekuta, Jeaiul Bari | 2019-09-05 | MP1006 | 8.6 | 43 | 8.2 | 44 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6456 | 2303.9997 | 86.3991
HBG-1.RR.124.1 | 24140869130089 | Hobigonj, Chunarughat, Sreekuta, Abdul Ahad | 2019-09-05 | MP1006 | 9.1 | 45 | 9.1 | 46 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6456 | 2303.9997 | 95.882
HBG-1.RR.125.1 | 24175829130527 | Bahubal, Mirpur Bazar, Collage Road, Nurul Amin | 2019-09-07 | MP1006 | 10 | 83 | 10 | 84 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6792 | 1967.9997 | 105.3648
HBG-1.RR.126.1 | 24175799130526 | Bahubal, Mirpur Bazar, Collage Road, Abinas Master | 2019-09-07 | MP1006 | 8.6 | 85 | 7.9 | 86 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6792 | 1967.9997 | 83.2382
HBG-1.RR.127.1 | 24182799131102 | Bahubal, Kamargaw, Abru Mia | 2019-09-07 | MP1006 | 12.5 | 87 | 12.5 | 88 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6792 | 1967.9997 | 131.706
HBG-1.RR.128.1 | 24231099124411 | Habiganj, Ramkrisna Mission Road, H # 1883 | 2019-09-08 | MP1006 | 10.1 | 109 | 10.1 | 110 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6408 | 2351.9997 | 106.4185
HBG-1.RR.129.1 | 24231099124411 | Habiganj, Ramkrisna Mission Road, H # 1884 | 2019-09-08 | MP1006 | 8.5 | 111 | 7.9 | 112 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6408 | 2351.9997 | 83.2382
HBG-1.RR.130.1 | 24231949124389 | Habiganj, Ghatia Para, Subol Das | 2019-09-08 | MP1006 | 12.1 | 113 | 11.6 | 114 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6336 | 2423.9997 | 122.2232
HBG-1.RR.130.2 | 24231949124389 | Habiganj, Ghatia Para, Subol Das | 2019-09-08 | MP1006 | 6.4 | 115 | 6.4 | 116 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6336 | 2423.9997 | 67.4335
HBG-1.RR.131.1 | 24231949124389 | Habiganj, Ghatia Para, Subol Das | 2019-09-08 | MP1006 | 11.8 | 117 | 11.8 | 118 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6336 | 2423.9997 | 124.3305
HBG-1.RR.132.1 | 24231949124389 | Habiganj, Ghatia Para, Sama Kanto Sarker | 2019-09-08 | MP1006 | 4.2 | 119 | 4.2 | 120 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6336 | 2423.9997 | 44.2532
HBG-1.RR.133.1 | 24231859124392 | Habiganj, Ghatia Para, Payeri Mohon | 2019-09-08 | MP1006 | 20.5 | 121 | 19.8 | 122 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 19.8 | 19.8 | 1.188 | 1.188 | 0.0007168 | 100% | 0% | 1.188 | 1.188 | 0.0011869 | 28 | 0.023815 | 0.023815 |  | 0 | 0 | 6336 | 2423.9997 | 208.6223
HBG-1.RR.134.1 | 24231789124384 | Habiganj, Ghatia Para, Zitandro Lal Das | 2019-09-08 | MP1006 | 12.5 | 123 | 12.5 | 124 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6336 | 2423.9997 | 131.706
HBG-1.RR.135.1 | 24231789124384 | Habiganj, Ghatia Para, Anil Das | 2019-09-08 | MP1006 | 13.4 | 125 | 13.4 | 126 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6336 | 2423.9997 | 141.1888
HBG-1.RR.135.2 | 24231789124384 | Habiganj, Ghatia Para, Anil Das | 2022-09-22 | NQ1007 | 5.2 | 14 | 5.2 | 15 | 2022-09-22 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 0 | 2423.9997 | 15.161
HBG-1.RR.136.1 | 24231789124384 | Habiganj, Ghatia Para, Monoranjon Das | 2019-09-08 | MP1006 | 6.7 | 127 | 6.7 | 128 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6336 | 2423.9997 | 70.5944
HBG-1.RR.137.1 | 24231789124384 | Habiganj, Ghatia Para, Dilip Das | 2019-09-08 | MP1006 | 12.4 | 129 | 12.4 | 130 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6336 | 2423.9997 | 130.6524
HBG-1.RR.138.1 | 24231719124404 | Habiganj, Ghatia Para, Bikas Chowdhury | 2019-09-08 | MP1006 | 12 | 131 | 12 | 132 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6336 | 2423.9997 | 126.4378
HBG-1.RR.139.1 | 24231749124381 | Habiganj, Ghatia Para, Lal Mohon Das | 2019-09-08 | MP1006 | 5 | 133 | 5 | 134 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6336 | 2423.9997 | 52.6824
HBG-1.RR.140.1 | 24231749124381 | Habiganj, Ghatia Para, Mollal Roy | 2019-09-08 | MP1006 | 18.4 | 135 | 17.5 | 136 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6336 | 2423.9997 | 184.3884
HBG-1.RR.141.1 | 24231749124381 | Habiganj, Ghatia Para, Luxmi Mollik | 2019-09-08 | MP1006 | 3.2 | 137 | 3.2 | 138 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6336 | 2423.9997 | 33.7167
HBG-1.RR.142.1 | 24231819124374 | Habiganj, Ghatia Para, Bissonath Sarker | 2019-09-08 | MP1006 | 4.3 | 139 | 4.3 | 140 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6336 | 2423.9997 | 45.3069
HBG-1.RR.143.1 | 24231819124374 | Habiganj, Ghatia Para, Roghunath Sarker | 2019-09-08 | MP1006 | 13.2 | 141 | 13.2 | 142 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6336 | 2423.9997 | 139.0816
HBG-1.RR.143.2 | 24231819124374 | Habiganj, Ghatia Para, Roghunath Sarker | 2022-09-22 | NQ1007 | 3.1 | 16 | 3.1 | 17 | 2022-09-22 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 0 | 2423.9997 | 9.0383
HBG-1.RR.144.1 | 24231819124374 | Habiganj, Ghatia Para, Naraion Sarker | 2019-09-08 | MP1006 | 2.2 | 145 | 2.2 | 146 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6336 | 2423.9997 | 23.1803
HBG-1.RR.145.1 | 24231719124376 | Habiganj, Ghatia Para, Susen Talukder | 2019-09-08 | MP1006 | 6.7 | 147 | 6.7 | 148 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6336 | 2423.9997 | 70.5944
HBG-1.RR.146.1 | 24231719124376 | Habiganj, Ghatia Para, Nikhel Das | 2019-09-08 | MP1006 | 34.8 | 149 | 34.8 | 150 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 34.8 | 34.8 | 2.088 | 2.088 | 0.0007168 | 100% | 0% | 2.088 | 2.088 | 0.0011869 | 28 | 0.041857 | 0.041857 |  | 0 | 0 | 6336 | 2423.9997 | 366.6695
HBG-1.RR.147.1 | 24231629124366 | Habiganj, Ghatia Para, Nantu Roy | 2019-09-08 | MP1006 | 1.5 | 151 | 1.5 | 152 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6336 | 2423.9997 | 15.8047
HBG-1.RR.148.1 | 24231629124366 | Habiganj, Ghatia Para, Chitto Ranjon | 2019-09-08 | MP1006 | 8.5 | 153 | 8.5 | 154 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6336 | 2423.9997 | 89.5601
HBG-1.RR.149.1 | 24231559124359 | Habiganj, Ghatia Para, Herandro | 2019-09-08 | MP1006 | 12.9 | 155 | 12.9 | 156 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6336 | 2423.9997 | 135.9206
HBG-1.RR.150.1 | 24231559124359 | Habiganj, Ghatia Para, Hory Pado Pal | 2019-09-08 | MP1006 | 10.9 | 157 | 10.9 | 158 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6336 | 2423.9997 | 114.8476
HBG-1.RR.150.2 | 24231559124359 | Habiganj, Ghatia Para, Hory Pado Pal | 2021-01-18 | LU1001 | 7.9 | 35 | 7.9 | 36 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6336 | 2423.9997 | 83.2382
HBG-1.RR.151.1 | 24113769131138 | Chunarughat, Balla Cross Road, Napnur Chowdhury Ahmed | 2019-09-01 | NQ1002 | 11.6 | 223 | 11.6 | 224 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6456 | 2303.9997 | 122.2232
HBG-1.RR.152.1 | 24113669131135 | Chunarughat, Balla Cross Road, Arju Mia | 2019-09-01 | NQ1002 | 3.4 | 225 | 3.6 | 226 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6456 | 2303.9997 | 37.9313
HBG-1.RR.153.1 | 24113939131154 | Chunarughat, Balla Cross Road, Romjan Ali | 2019-09-01 | NQ1002 | 8.4 | 227 | 8.4 | 228 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6456 | 2303.9997 | 88.5064
HBG-1.RR.154.1 | 24113699131158 | Chunarughat, Balla Cross Road, Arju Mia | 2019-09-01 | NQ1002 | 10.6 | 229 | 10.6 | 230 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6456 | 2303.9997 | 111.6867
HBG-1.RR.155.1 | 24113459131167 | Chunarughat, Balla Cross Road, Faruk | 2019-09-01 | NQ1002 | 10.7 | 231 | 10.7 | 232 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6456 | 2303.9997 | 112.7403
HBG-1.RR.156.1 | 24113539131181 | Chunarughat, Balla Cross Road, Rojob Ali Member Bari, Ameer Ali | 2019-09-01 | NQ1002 | 6 | 233 | 6 | 234 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6456 | 2303.9997 | 63.2189
HBG-1.RR.157.1 | 24113729131179 | Chunarughat, Balla Cross Road, Haque Vila | 2019-09-01 | NQ1002 | 3.5 | 238 | 3.5 | 239 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6456 | 2303.9997 | 36.8777
HBG-1.RR.158.1 | 24114549131119 | Chunarughat, College Road, Opposite of Upazila Parisod, Dipasis Kumar | 2019-09-02 | NQ1002 | 16.4 | 240 | 16.8 | 241 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6456 | 2303.9997 | 177.0129
HBG-1.RR.159.1 | 24114529131144 | Chunarughat, Balla Road, H # 70, Toyeba | 2019-09-02 | NQ1002 | 8 | 242 | 8 | 243 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6456 | 2303.9997 | 84.2919
HBG-1.RR.160.1 | 24113969131184 | Chunarughat, Balla Road, Nurul Amin | 2019-09-02 | NQ1002 | 7.5 | 244 | 7.5 | 245 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6456 | 2303.9997 | 79.0236
HBG-1.RR.161.1 | 24115119131148 | Chunarughat, Chunarughat Bazar, Upazila Post Office Road, H # 76 | 2019-09-02 | NQ1002 | 10.4 | 246 | 10.5 | 247 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 1416 | 0 | 5040 | 2303.9997 | 92.7499
HBG-1.RR.162.1 | 24114819131192 | Chunarughat, Balla Road, Front of Rose Valley Kindergarten, Hazi Mannan | 2019-09-02 | NQ1002 | 10.4 | 248 | 10 | 249 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6456 | 2303.9997 | 105.3648
HBG-1.RR.163.1 | 24114899131180 | Chunarughat, Balla Road, Muksud Ali | 2019-09-02 | NQ1002 | 6 | 250 | 6 | 251 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6456 | 2303.9997 | 63.2189
HBG-1.RR.164.1 | 24114899131180 | Chunarughat, Balla Road, Anwar Ali | 2019-09-02 | NQ1002 | 4.5 | 252 | 4.5 | 253 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6456 | 2303.9997 | 47.4142
HBG-1.RR.165.1 | 24113739131240 | Chunarughat, Balla Road, Nazim | 2019-09-02 | NQ1002 | 3 | 254 | 3.1 | 255 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6456 | 2303.9997 | 32.6631
HBG-1.RR.166.1 | 24113719131193 | Chunarughat, Balla Road, Sahab Vila | 2019-09-02 | NQ1002 | 5.5 | 256 | 5.5 | 257 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6456 | 2303.9997 | 57.9506
HBG-1.RR.167.1 | 24114289131180 | Chunarughat, Balla Road, Mamun | 2019-09-02 | NQ1002 | 8.5 | 258 | 8.4 | 259 | 2022-01-01 | [9 empty] | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0
HBG-1.RR.168.1 | 24124479130224 | Chunarughat, Gogaura, Serajul Islam | 2019-09-03 | NQ1002 | 54.7 | 264 | 54.7 | 265 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 54.7 | 54.7 | 3.282 | 3.282 | 0.0007168 | 100% | 0% | 3.282 | 3.282 | 0.0011869 | 28 | 0.065793 | 0.065793 |  | 0 | 0 | 6456 | 2303.9997 | 576.3455
HBG-1.RR.169.1 | 24124479130224 | Chunarughat, Gogaura, Mohibul Chowdhury | 2019-09-03 | NQ1002 | 5.1 | 266 | 5.2 | 267 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6456 | 2303.9997 | 54.7897
HBG-1.RR.170.1 | 24124649130222 | Chunarughat, Gogaura, Abdul Momim | 2019-09-03 | NQ1002 | 8.3 | 268 | 8.3 | 269 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6456 | 2303.9997 | 87.4528
HBG-1.RR.171.1 | 24124649130222 | Chunarughat, Gogaura, Abdul Momim | 2019-09-03 | NQ1002 | 10.8 | 270 | 10.8 | 271 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6456 | 2303.9997 | 113.794
HBG-1.RR.172.1 | 24124649130222 | Chunarughat, Gogaura, Sadekul | 2019-09-03 | NQ1002 | 6.8 | 272 | 6.8 | 273 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6456 | 2303.9997 | 71.6481
HBG-1.RR.173.1 | 24124649130222 | Chunarughat, Gogaura, Sadekul | 2019-09-03 | NQ1002 | 4.7 | 274 | 4.7 | 275 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6456 | 2303.9997 | 49.5215
HBG-1.RR.174.1 | 24205519132195 | Bahubal, Hamidnagor, Ishak | 2019-09-04 | MP1006 | 4.3 | 1 | 4.3 | 2 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6312 | 2447.9997 | 45.3069
HBG-1.RR.175.1 | 24205539132212 | Bahubal, Hamidnagor, Gonesh | 2019-09-04 | MP1006 | 11.5 | 3 | 11.5 | 4 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6312 | 2447.9997 | 121.1695
HBG-1.RR.176.1 | 24205779132274 | Bahubal, Hamidnagor, Madhupur Road, Chobor Monjil | 2019-09-04 | MP1006 | 11.1 | 5 | 11 | 6 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6312 | 2447.9997 | 115.9013
HBG-1.RR.177.1 | 24205949132269 | Bahubal, Hamidnagor, Madhupur Road, Jolekha Begom | 2019-09-04 | MP1006 | 12.4 | 7 | 12.4 | 8 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6312 | 2447.9997 | 130.6524
HBG-1.RR.178.1 | 24205999132284 | Bahubal, Hamidnagor, Madhupur Road, Mala Khatun | 2019-09-04 | MP1006 | 6.5 | 9 | 6.5 | 10 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6312 | 2447.9997 | 68.4871
HBG-1.RR.179.1 | 24210149132275 | Bahubal, Hamidnagor, Madhupur Road, Abul Kashem | 2019-09-04 | MP1006 | 4.1 | 11 | 4.1 | 12 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6312 | 2447.9997 | 43.1996
HBG-1.RR.180.1 | 24205559132282 | Bahubal, Hamidnagor, Madhupur Road, Ajijunnesa Monjil | 2019-09-04 | MP1006 | 5 | 13 | 5 | 14 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6312 | 2447.9997 | 52.6824
HBG-1.RR.180.2 | 24205559132282 | Bahubal, Hamidnagor, Madhupur Road, Ajijunnesa Monjil | 2022-03-13 | LU1001 | 13.1 | 50 | 13.1 | 51 | 2022-03-13 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 4608 | 2447.9997 | 111.1786
HBG-1.RR.181.1 | 24205439132316 | Bahubal, Hamidnagor, Madhupur Road, Hafiz Villa | 2019-09-04 | MP1006 | 15.2 | 15 | 15.2 | 16 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6312 | 2447.9997 | 160.1545
HBG-1.RR.181.2 | 24205439132316 | Bahubal, Hamidnagor, Madhupur Road, Hafiz Villa | 2022-03-13 | LU1001 | 7.3 | 54 | 7.3 | 55 | 2022-03-13 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 4608 | 2447.9997 | 61.9545
HBG-1.RR.182.1 | 24205389132334 | Bahubal, Hamidnagor, Madhupur Road, Afjal Mia | 2019-09-04 | MP1006 | 10.7 | 17 | 10.7 | 18 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6312 | 2447.9997 | 112.7403
HBG-1.RR.182.2 | 24205389132334 | Bahubal, Hamidnagor, Madhupur Road, Afjal Mia | 2021-08-24 | LX1011 | 11.7 | 37 | 11.5 | 38 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6312 | 2447.9997 | 121.1695
HBG-1.RR.183.1 | 24205409132325 | Bahubal, Hamidnagor, Madhupur Road, Parvin | 2019-09-04 | MP1006 | 8.4 | 19 | 8.4 | 20 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6312 | 2447.9997 | 88.5064
HBG-1.RR.184.1 | 24162829127577 | Shaistaganj, Sabashpur, Joynal | 2019-09-05 | MP1006 | 8.6 | 49 | 8.6 | 50 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6816 | 1943.9997 | 90.6137
HBG-1.RR.185.1 | 24162829127577 | Shaistaganj, Sabashpur, Kuddus Mia | 2019-09-05 | MP1006 | 15.4 | 51 | 15.4 | 52 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6816 | 1943.9997 | 162.2618
HBG-1.RR.186.1 | 24162539128000 | Shaistaganj, Sabashpur, South Side Of Sabashpur Primary School, DPEO Vila | 2019-09-05 | MP1006 | 5.4 | 53 | 5.4 | 54 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6816 | 1943.9997 | 56.897
HBG-1.RR.187.1 | 24175479131002 | Bahubal, Mirpur, U.P Road, Talukder Vila | 2019-09-05 | MP1006 | 15.6 | 55 | 15.6 | 56 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6792 | 1967.9997 | 164.3691
HBG-1.RR.188.1 | 24175369131022 | Bahubal, Mirpur, U.P Road, Liakot Ali | 2019-09-05 | MP1006 | 11.4 | 57 | 11.4 | 58 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6792 | 1967.9997 | 120.1159
HBG-1.RR.189.1 | 24175369131022 | Bahubal, Mirpur, U.P Road, Surot Ali | 2019-09-05 | MP1006 | 11.4 | 59 | 10.9 | 60 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6792 | 1967.9997 | 114.8476
HBG-1.RR.190.1 | 24175369131022 | Bahubal, Mirpur, U.P Road, Sundor Ali | 2019-09-05 | MP1006 | 12.8 | 61 | 12.8 | 62 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6792 | 1967.9997 | 134.867
HBG-1.RR.191.1 | 24180439130574 | Bahubal, Mirpur, Baniyagao Road, M. Samsuddin | 2019-09-07 | MP1006 | 13.1 | 63 | 13.1 | 64 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6792 | 1967.9997 | 138.0279
HBG-1.RR.192.1 | 24180319130580 | Bahubal, Mirpur, Baniyagao Road, Doroz Mia | 2019-09-07 | MP1006 | 12.4 | 65 | 12.2 | 66 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6792 | 1967.9997 | 128.5451
HBG-1.RR.193.1 | 24180279130585 | Bahubal, Mirpur, Baniyagao Road, Sahed Monjil | 2019-09-07 | MP1006 | 10.2 | 67 | 10.2 | 68 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6792 | 1967.9997 | 107.4721
HBG-1.RR.193.2 | 24180279130585 | Bahubal, Mirpur, Baniyagao Road, Sahed Monjil | 2022-10-11 | NQ1007 | 4.7 | 61 | 4.7 | 62 | 2022-10-11 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 0 | 1967.9997 | 11.1254
HBG-1.RR.194.1 | 24180299131029 | Bahubal, Mirpur, Baniyagao Road, Abdul Ali | 2019-09-07 | MP1006 | 2.6 | 69 | 2.6 | 70 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6792 | 1967.9997 | 27.3949
HBG-1.RR.195.1 | 24180419131039 | Bahubal, Mirpur, Baniyagao Road, Younus Ali | 2019-09-07 | MP1006 | 3.7 | 71 | 3.7 | 72 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6792 | 1967.9997 | 38.985
HBG-1.RR.196.1 | 24180899131023 | Bahubal, Mirpur, East Rupsongkor, Joshim | 2019-09-07 | MP1006 | 6 | 73 | 6.1 | 74 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6792 | 1967.9997 | 64.2725
HBG-1.RR.197.1 | 24180899131023 | Bahubal, Mirpur, East Rupsongkor, Faruque | 2019-09-07 | MP1006 | 9.6 | 75 | 9.6 | 76 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6792 | 1967.9997 | 101.1502
HBG-1.RR.198.1 | 24180499131048 | Bahubal, Mirpur, East Rupsongkor, Didar Ali | 2019-09-07 | MP1006 | 6.3 | 77 | 6.3 | 78 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6792 | 1967.9997 | 66.3798
HBG-1.RR.199.1 | 24180499131048 | Bahubal, Mirpur, East Rupsongkor, Abdal Ali | 2019-09-07 | MP1006 | 12.2 | 79 | 12.2 | 80 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6792 | 1967.9997 | 128.5451
HBG-1.RR.200.1 | 24180329131034 | Bahubal, Mirpur, East Rupsongkor, Nirod Chandra Das | 2019-09-07 | MP1006 | 11.8 | 81 | 11.7 | 82 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6792 | 1967.9997 | 123.2768
HBG-1.RR.201.1 | 24113859131012 | Chunarughat, Chondona, Ward # 04, H # 44, Jishu Dev | 2019-09-01 | NQ1003 | 12.7 | 598 | 12.7 | 599 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6456 | 2303.9997 | 133.8133
HBG-1.RR.202.1 | 24113699131024 | Chunarughat, Chondona, Ward # 04, H # 42, Benu Mali Pal | 2019-09-01 | NQ1003 | 7.3 | 600 | 7.3 | 601 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6456 | 2303.9997 | 76.9163
HBG-1.RR.203.1 | 24113699131033 | Chunarughat, Chondona, Ward # 04, Susandro Dev | 2019-09-01 | NQ1003 | 5.5 | 602 | 5.5 | 603 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6456 | 2303.9997 | 57.9506
HBG-1.RR.204.1 | 24113609131035 | Chunarughat, Chondona, Ward # 04, H # 34, Siddharto Sonkar | 2019-09-01 | NQ1003 | 11 | 604 | 11 | 605 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6456 | 2303.9997 | 115.9013
HBG-1.RR.205.1 | 24113449131038 | Chunarughat, Chondona, Ward # 04, Kritish Chondra | 2019-09-01 | NQ1003 | 10 | 606 | 10 | 607 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6456 | 2303.9997 | 105.3648
HBG-1.RR.206.1 | 24113239131035 | Chunarughat, Chondona, Ward # 04, H # 27, Hirendra Dev | 2019-09-01 | NQ1003 | 9.7 | 608 | 9.7 | 609 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6456 | 2303.9997 | 102.2039
HBG-1.RR.207.1 | 24122089130538 | Chunarughat, North Bazar, M.C. Bhabon | 2019-09-02 | NQ1003 | 13 | 610 | 13 | 611 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6456 | 2303.9997 | 136.9743
HBG-1.RR.207.2 | 24122089130538 | Chunarughat, North Bazar, M.C. Bhabon | 2022-03-12 | LU1001 | 6.2 | 44 | 6.2 | 45 | 2022-03-12 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 4776 | 2303.9997 | 52.7979
HBG-1.RR.208.1 | 24121479130590 | Chunarughat, North Bazar, Abdur Rahman | 2019-09-02 | NQ1003 | 6.8 | 612 | 6.3 | 613 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6456 | 2303.9997 | 66.3798
HBG-1.RR.209.1 | 24121389131001 | Chunarughat, North Bazar, Abhijit Bhabon | 2019-09-02 | NQ1003 | 5.6 | 614 | 5.6 | 615 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6456 | 2303.9997 | 59.0043
HBG-1.RR.210.1 | 24121259131009 | Chunarughat, North Bazar, Abdur Rashid | 2019-09-02 | NQ1003 | 3.7 | 616 | 3.7 | 617 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6456 | 2303.9997 | 38.985
HBG-1.RR.210.2 | 24121259131009 | Chunarughat, North Bazar, Abdur Rashid | 2021-08-24 | LU1001 | 5.8 | 1 | 5.8 | 2 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6456 | 2303.9997 | 61.1116
HBG-1.RR.211.1 | 24121089131029 | Chunarughat, North Bazar, Sumovi Niketon | 2019-09-02 | NQ1003 | 12.9 | 618 | 12.9 | 619 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6456 | 2303.9997 | 135.9206
HBG-1.RR.212.1 | 24121009131032 | Chunarughat, North Bazar, Ward # 02, Nurul Islam | 2019-09-02 | NQ1003 | 13.1 | 620 | 12.8 | 621 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6456 | 2303.9997 | 134.867
HBG-1.RR.213.1 | 24120989131065 | Chunarughat, North Bazar, East Borail Road, Safat Ali | 2019-09-02 | NQ1003 | 11.6 | 622 | 11.6 | 623 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6456 | 2303.9997 | 122.2232
HBG-1.RR.214.1 | 24120689131049 | Chunarughat, North Bazar, Mowla Mia | 2019-09-02 | NQ1003 | 22 | 624 | 22 | 625 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 22 | 22 | 1.32 | 1.32 | 0.0007168 | 100% | 0% | 1.32 | 1.32 | 0.0011869 | 28 | 0.026461 | 0.026461 |  | 0 | 0 | 6456 | 2303.9997 | 231.8026
HBG-1.RR.215.1 | 24124899130255 | Chunarughat, Gugaura, Haji Loskor Chairman Bari Road, Abdul Kaiyum | 2019-09-03 | NQ1003 | 14.9 | 1 | 14.7 | 2 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6456 | 2303.9997 | 154.8863
HBG-1.RR.215.2 | 24124899130255 | Chunarughat, Gugaura, Haji Loskor Chairman Bari Road, Abdul Kaiyum | 2022-03-12 | LU1001 | 10.3 | 42 | 10.3 | 43 | 2022-03-12 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 4776 | 2303.9997 | 87.7126
HBG-1.RR.216.1 | 24125989130175 | Chunarughat, Gugaura, Kazi Khondokar Road, Talukdar Bari, Awaj Uddin | 2019-09-03 | NQ1003 | 8.1 | 3 | 8.1 | 4 | 2022-01-01 | [9 empty] | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0
HBG-1.RR.217.1 | 24130049130166 | Chunarughat, Gugaura, Kazi Khondokar Road, Talukdar Bari, Molida Begum | 2019-09-03 | NQ1003 | 12 | 5 | 11.6 | 6 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6456 | 2303.9997 | 122.2232
HBG-1.RR.218.1 | 24130059130159 | Chunarughat, Gugaura, Kazi Khondokar Road, Talukdar Bari,Abdul Kuddus | 2019-09-03 | NQ1003 | 12.3 | 7 | 12.3 | 8 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6456 | 2303.9997 | 129.5987
HBG-1.RR.219.1 | 24130059130159 | Chunarughat, Gugaura, Kazi Khondokar Road, Talukdar Bari, Mostafizur Rahman | 2019-09-03 | NQ1003 | 7.3 | 9 | 7.3 | 10 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6456 | 2303.9997 | 76.9163
HBG-1.RR.220.1 | 24125879130141 | Chunarughat, Gugaura, Kazi Khondokar Road, Talukdar Bari, Shaira Khatun | 2019-09-03 | NQ1003 | 5.7 | 11 | 5.7 | 12 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6456 | 2303.9997 | 60.0579
HBG-1.RR.221.1 | 24125819130140 | Chunarughat, Gugaura, Kazi Khondokar Road, Talukdar Bari, Abdul Basit | 2019-09-03 | NQ1003 | 7.2 | 13 | 7.2 | 14 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6456 | 2303.9997 | 75.8627
HBG-1.RR.222.1 | 24125729130141 | Chunarughat, Gugaura, Kazi Khondokar Road, Talukdar Bari, Md. Akkas Talukdar | 2019-09-03 | NQ1003 | 4.3 | 15 | 4.3 | 16 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6456 | 2303.9997 | 45.3069
HBG-1.RR.223.1 | 24205799132218 | Bahubal, Hamidnagar, Abdul Motin | 2019-09-04 | NQ1003 | 11.4 | 38 | 11.4 | 39 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6312 | 2447.9997 | 120.1159
HBG-1.RR.224.1 | 24210079132224 | Bahubal, Hamidnagar, Mohammad Ayat Ali | 2019-09-04 | NQ1003 | 9.7 | 40 | 9.7 | 41 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6312 | 2447.9997 | 102.2039
HBG-1.RR.225.1 | 24210049132210 | Bahubal, Hamidnagar, Abdul Ohid | 2019-09-04 | NQ1003 | 14.9 | 42 | 14.8 | 43 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6312 | 2447.9997 | 155.9399
HBG-1.RR.226.1 | 24210049132176 | Bahubal, Hamidnagar, Sobullah | 2019-09-04 | NQ1003 | 7.6 | 44 | 7 | 45 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6312 | 2447.9997 | 73.7554
HBG-1.RR.227.1 | 24210179132241 | Bahubal, Hamidnagar, Abdul Motin | 2019-09-04 | NQ1003 | 5 | 46 | 5 | 47 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6312 | 2447.9997 | 52.6824
HBG-1.RR.228.1 | 24210969132255 | Bahubal, Hamidnagar, Nahar Aktar | 2019-09-04 | NQ1003 | 6.8 | 48 | 6.8 | 49 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6312 | 2447.9997 | 71.6481
HBG-1.RR.229.1 | 24205349132358 | Bahubal, Hamidnagar, Modupur Tea Garden Road, Dudu Mia | 2019-09-04 | NQ1003 | 11.2 | 50 | 10.7 | 51 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6312 | 2447.9997 | 112.7403
HBG-1.RR.230.1 | 24205429132357 | Bahubal, Hamidnagar, Modupur Tea Garden Road, Golam Rabbany | 2019-09-04 | NQ1003 | 9.5 | 52 | 9.1 | 53 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6312 | 2447.9997 | 95.882
HBG-1.RR.230.2 | 24205429132357 | Bahubal, Hamidnagar, Modupur Tea Garden Road, Golam Rabbany | 2022-09-21 | NQ1007 | 8.9 | 12 | 8.9 | 13 | 2022-09-21 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 0 | 2447.9997 | 26.2055
HBG-1.RR.231.1 | 24083709129138 | Chunarughat, National Tea Estate Company, Asst. Manager Bunglow | 2019-09-05 | NQ1003 | 58.1 | 83 | 58.1 | 84 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 58.1 | 58.1 | 3.486 | 3.486 | 0.0007168 | 100% | 0% | 3.486 | 3.486 | 0.0011869 | 28 | 0.069882 | 0.069882 |  | 0 | 0 | 6456 | 2303.9997 | 612.1696
HBG-1.RR.232.1 | 24140709130099 | Chunarughat, Naropati, Hosen Ali | 2019-09-05 | NQ1003 | 12.3 | 85 | 12.6 | 86 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6456 | 2303.9997 | 132.7597
HBG-1.RR.233.1 | 24140709130099 | Chunarughat, Naropati, Afroj Master | 2019-09-05 | NQ1003 | 8.9 | 87 | 8.9 | 88 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6456 | 2303.9997 | 93.7747
HBG-1.RR.234.1 | 24140709130099 | Chunarughat, Naropati, Rafik | 2019-09-05 | NQ1003 | 5.7 | 89 | 5.7 | 90 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6456 | 2303.9997 | 60.0579
HBG-1.RR.235.1 | 24180169131161 | Bahubal, Mirpur,Kachuyadi, Badrul Alam | 2019-09-07 | NQ1003 | 13.8 | 108 | 13.8 | 109 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6792 | 1967.9997 | 145.4034
HBG-1.RR.236.1 | 24180169131161 | Bahubal, Mirpur,Kachuyadi, Siddike Ali | 2019-09-07 | NQ1003 | 8.3 | 110 | 8.3 | 111 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6792 | 1967.9997 | 87.4528
HBG-1.RR.237.1 | 24180299131166 | Bahubal, Mirpur,Kachuyadi, Abdul Ali Mia | 2019-09-07 | NQ1003 | 9.5 | 112 | 8.8 | 113 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6792 | 1967.9997 | 92.721
HBG-1.RR.238.1 | 24180299131166 | Bahubal, Mirpur, Kachuyadi, Akbor Hosen | 2019-09-07 | NQ1003 | 5.4 | 114 | 5.4 | 115 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6792 | 1967.9997 | 56.897
HBG-1.RR.239.1 | 24180489131168 | Bahubal, Mirpur, Kachuyadi, Aminul Islam | 2019-09-07 | NQ1003 | 8.3 | 116 | 8.3 | 117 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6792 | 1967.9997 | 87.4528
HBG-1.RR.240.1 | 24175609131149 | Bahubal, Mirpur, Kachuyadi, Samsu Mia | 2019-09-07 | NQ1003 | 5.2 | 118 | 5.2 | 119 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6792 | 1967.9997 | 54.7897
HBG-1.RR.241.1 | 24175409131144 | Bahubal, Mirpur, Kachuyadi, Saidul Islam | 2019-09-07 | NQ1003 | 8.8 | 120 | 9.3 | 121 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6792 | 1967.9997 | 97.9893
HBG-1.RR.242.1 | 24175409131144 | Bahubal, Mirpur, Kachuyadi, Tajul Islam | 2019-09-07 | NQ1003 | 12.7 | 122 | 12.7 | 123 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6792 | 1967.9997 | 133.8133
HBG-1.RR.243.1 | 24175409131144 | Bahubal, Mirpur, Kachuyadi, Jaynullah | 2019-09-07 | NQ1003 | 27.5 | 124 | 27.5 | 125 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 27.5 | 27.5 | 1.65 | 1.65 | 0.0007168 | 100% | 0% | 1.65 | 1.65 | 0.0011869 | 28 | 0.033077 | 0.033077 |  | 0 | 0 | 6792 | 1967.9997 | 289.7532
HBG-1.RR.244.1 | 24180159131127 | Bahubal, Mirpur, Kachuyadi, Mahamud Mia | 2019-09-07 | NQ1003 | 12.8 | 126 | 12.8 | 127 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6792 | 1967.9997 | 134.867
HBG-1.RR.245.1 | 24180179131102 | Bahubal, Mirpur, Kachuyadi, Siddike Ali | 2019-09-07 | NQ1003 | 9.3 | 128 | 9.3 | 129 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6792 | 1967.9997 | 97.9893
HBG-1.RR.246.1 | 24180099131100 | Bahubal, Mirpur, Kachuyadi, Shajul Islam | 2019-09-07 | NQ1003 | 11 | 130 | 10.7 | 131 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6792 | 1967.9997 | 112.7403
HBG-1.RR.247.1 | 24175359131064 | Bahubal, Mirpur, Ejjot Nagar, Edris Ali | 2019-09-07 | NQ1003 | 11.7 | 132 | 11.7 | 133 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6792 | 1967.9997 | 123.2768
HBG-1.RR.248.1 | 24174899131062 | Bahubal, Mirpur, Ejjot Nagar, Afdal Membar | 2019-09-07 | NQ1003 | 9.6 | 134 | 9.6 | 135 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6792 | 1967.9997 | 101.1502
HBG-1.RR.249.1 | 24175199131007 | Bahubal, Mirpur, Baniya Gaon, Harun Mia | 2019-09-07 | NQ1003 | 9.1 | 136 | 9.1 | 137 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6792 | 1967.9997 | 95.882
HBG-1.RR.250.1 | 24175329130594 | Bahubal, Mirpur, Baniya Gaon, Rahomot Ali | 2019-09-07 | NQ1003 | 8.9 | 138 | 8.9 | 139 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6792 | 1967.9997 | 93.7747
HBG-1.RR.251.1 | 24162419128124 | Shaistaganj, Old Bazar, Upohata, MD. Abdul Huq | 2019-09-01 | NQ1003 | 9.5 | 566 | 9.5 | 567 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6816 | 1943.9997 | 100.0966
HBG-1.RR.252.1 | 24162419128124 | Shaistaganj, Old Bazar, Upohata, Nasir Uddin | 2019-09-01 | NQ1003 | 9.9 | 568 | 9.9 | 569 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6816 | 1943.9997 | 104.3112
HBG-1.RR.253.1 | 24162359128122 | Shaistaganj, Old Bazar, Upohata, Suruj Ali | 2019-09-01 | NQ1003 | 11.7 | 570 | 11.7 | 571 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6816 | 1943.9997 | 123.2768
HBG-1.RR.254.1 | 24161969128111 | Shaistaganj, Old Bazar, Upohata, Oliul Rahman | 2019-09-01 | NQ1003 | 14.7 | 572 | 14.7 | 573 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6816 | 1943.9997 | 154.8863
HBG-1.RR.255.1 | 24162509128131 | Shaistaganj, Old Bazar, Upohata, Nanu Molla | 2019-09-01 | NQ1003 | 9.9 | 574 | 9.9 | 575 | 2022-01-01 | 2022-10-12 | NQ1007 | 1.6 | 65 | 1.6 | 66 | 2022-10-12 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6816 | 1943.9997
HBG-1.RR.256.1 | 24162109128147 | Shaistaganj, Old Bazar, Upohata, Fatama Villa, Rahana Akter | 2019-09-01 | NQ1003 | 5.1 | 576 | 5.1 | 577 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6816 | 1943.9997 | 53.7361
HBG-1.RR.257.1 | 24162109128147 | Shaistaganj, Old Bazar, Upohata, Arju Mia | 2019-09-01 | NQ1003 | 11.3 | 578 | 11.3 | 579 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6816 | 1943.9997 | 119.0622
HBG-1.RR.258.1 | 24162109128147 | Shaistaganj, Old Bazar, Upohata, Masum Ahmed | 2019-09-01 | NQ1003 | 9.6 | 580 | 9.6 | 581 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6816 | 1943.9997 | 101.1502
HBG-1.RR.259.1 | 24162359128179 | Shaistaganj, Old Bazar, Upohata, Sofia | 2019-09-01 | NQ1003 | 20.6 | 582 | 20.6 | 583 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 20.6 | 20.6 | 1.236 | 1.236 | 0.0007168 | 100% | 0% | 1.236 | 1.236 | 0.0011869 | 28 | 0.024778 | 0.024778 |  | 0 | 0 | 6816 | 1943.9997 | 217.0515
HBG-1.RR.260.1 | 24162229128173 | Shaistaganj, Old Bazar, Upohata, Hazi Abdul Goni | 2019-09-01 | NQ1003 | 15 | 584 | 15 | 585 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6816 | 1943.9997 | 158.0472
HBG-1.RR.261.1 | 24162199128151 | Shaistaganj, Old Bazar, Upohata, Hazi Abdul Roshid | 2019-09-01 | NQ1003 | 8.5 | 586 | 8.5 | 587 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6816 | 1943.9997 | 89.5601
HBG-1.RR.262.1 | 24162579128185 | Shaistaganj, Old Bazar, Lanja Para, Abdul Salam | 2019-09-01 | NQ1003 | 12.1 | 588 | 12.1 | 589 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6816 | 1943.9997 | 127.4914
HBG-1.RR.263.1 | 24120659131085 | Chunarughat, North Bazar, Sayed Nurul Alam | 2019-09-02 | NQ1003 | 8.9 | 626 | 8.3 | 627 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6456 | 2303.9997 | 87.4528
HBG-1.RR.264.1 | 24112839131104 | Chunarughat, Chnnorgram, Beauty | 2019-09-02 | NQ1003 | 10.8 | 632 | 10.8 | 633 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6456 | 2303.9997 | 113.794
HBG-1.RR.265.1 | 24113239131082 | Chunarughat, Hatunda, Collage Road, Mamunur Roshid | 2019-09-02 | NQ1003 | 10.7 | 634 | 10.7 | 635 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6456 | 2303.9997 | 112.7403
HBG-1.RR.266.1 | 24113239131036 | Chunarughat, Hatunda, Collage Road, Teredav Jotir Pal | 2019-09-02 | NQ1003 | 7.4 | 636 | 7.4 | 637 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6456 | 2303.9997 | 77.97
HBG-1.RR.267.1 | 24111329130493 | Chunarughat, Dayoargas, Taher Mia | 2019-09-02 | NQ1003 | 9.8 | 640 | 9.4 | 641 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6456 | 2303.9997 | 99.0429
HBG-1.RR.268.1 | 24111249130491 | Chunarughat, Dayoargas, Abdul Hamid | 2019-09-02 | NQ1003 | 8.4 | 642 | 8.4 | 643 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6456 | 2303.9997 | 88.5064
HBG-1.RR.269.1 | 24105949130390 | Chunarughat, Dayoargas, Abdur Shaid | 2019-09-02 | NQ1003 | 10.3 | 644 | 10.3 | 645 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6456 | 2303.9997 | 108.5258
HBG-1.RR.270.1 | 24202379132133 | Hobigong, Bahobal, Hospital Area, 50 bad Hospital Upozala Health Complex | 2019-09-03 | NQ1003 | 13.1 | 18 | 13.1 | 19 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6312 | 2447.9997 | 138.0279
HBG-1.RR.271.1 | 24202299132133 | Hobigong, Bahobal, Hospital Area, 50 bad Hospital Upozala Health Complex | 2019-09-03 | NQ1003 | 9.8 | 20 | 9.8 | 21 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6312 | 2447.9997 | 103.2575
HBG-1.RR.271.2 | 24202299132133 | Hobigong, Bahobal, Hospital Area, 50 bad Hospital Upozala Health Complex | 2021-01-10 | MN1032 | 11.6 | 1 | 11.6 | 2 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6312 | 2447.9997 | 122.2232
HBG-1.RR.272.1 | 24202299132133 | Hobigong, Bahobal, Hospital Area, 50 bad Hospital Upozala Health Complex | 2019-09-03 | NQ1003 | 10.2 | 22 | 10.2 | 23 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6312 | 2447.9997 | 107.4721
HBG-1.RR.273.1 | 24202219132043 | Hobigong, Bahobal, Hospital Area, Collage Road, Rahima Akter Momota | 2019-09-03 | NQ1003 | 11 | 27 | 11 | 28 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6312 | 2447.9997 | 115.9013
HBG-1.RR.274.1 | 24201099132167 | Hobigong, Bahobal, Hospital Area, Jangaliea, Jalal Uddin | 2019-09-03 | NQ1003 | 10.6 | 29 | 10.6 | 30 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6312 | 2447.9997 | 111.6867
HBG-1.RR.275.1 | 24201099132167 | Hobigong, Bahobal, Hospital Area, Jangaliea, Jazir Uddin | 2019-09-03 | NQ1003 | 9.5 | 31 | 9.5 | 32 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6312 | 2447.9997 | 100.0966
HBG-1.RR.276.1 | 24201059132086 | Hobigong, Bahobal, Hospital Area, Jangaliea, Abdul Kalam | 2019-09-03 | NQ1003 | 12.1 | 34 | 12.1 | 35 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6312 | 2447.9997 | 127.4914
HBG-1.RR.277.1 | 24201119132075 | Hobigong, Bahobal, Hospital Area, Jangaliea, Abdul Hai | 2019-09-03 | NQ1003 | 4.9 | 36 | 4.9 | 37 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6312 | 2447.9997 | 51.6288
HBG-1.RR.278.1 | 24241559133496 | Bahubal, Putijuri, NoyaPara, Atur Rahman | 2019-09-04 | NQ1003 | 10 | 56 | 10 | 57 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6312 | 2447.9997 | 105.3648
HBG-1.RR.279.1 | 24241559133496 | Bahubal, Putijuri, NoyaPara, Rabeya Begum | 2019-09-04 | NQ1003 | 12.6 | 58 | 12.5 | 59 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6312 | 2447.9997 | 131.706
HBG-1.RR.280.1 | 24241349133552 | Bahubal, Putijuri, Jadabpur, Jillur Rahman | 2019-09-04 | NQ1003 | 13.3 | 60 | 13.3 | 61 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6312 | 2447.9997 | 140.1352
HBG-1.RR.281.1 | 24241349133552 | Bahubal, Putijuri, Jadabpur, Ansar Mia | 2019-09-04 | NQ1003 | 15.1 | 62 | 15.1 | 63 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6312 | 2447.9997 | 159.1009
HBG-1.RR.282.1 | 24241269133551 | Bahubal, Putijuri, Jadabpur, Sazid Mia | 2019-09-04 | NQ1003 | 12 | 67 | 12 | 68 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6312 | 2447.9997 | 126.4378
HBG-1.RR.283.1 | 24241269133551 | Bahubal, Putijuri, Jadabpur, Abdul Aual | 2019-09-04 | NQ1003 | 10.1 | 69 | 10.1 | 70 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6312 | 2447.9997 | 106.4185
HBG-1.RR.284.1 | 24242639133583 | Bahubal, Putijuri, Miearpara, Sonai Mia | 2019-09-04 | NQ1003 | 9.2 | 71 | 8.7 | 72 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6312 | 2447.9997 | 91.6674
HBG-1.RR.285.1 | 24242539133581 | Bahubal, Putijuri, Miearpara, Sayed Zakir Hossain | 2019-09-04 | NQ1003 | 16.1 | 73 | 15.7 | 74 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 6312 | 2447.9997 | 165.4228
HBG-1.RR.286.1 | 24242449133583 | Bahubal, Putijuri, Miearpara, Johan Mia | 2019-09-04 | NQ1003 | 11.2 | 75 | 11.2 | 76 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6312 | 2447.9997 | 118.0086
HBG-1.RR.287.1 | 24242259133583 | Bahubal, Putijuri, Miearpara, Atik Mia | 2019-09-04 | NQ1003 | 19.7 | 77 | 19.7 | 78 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 19.7 | 19.7 | 1.182 | 1.182 | 0.0007168 | 100% | 0% | 1.182 | 1.182 | 0.0011869 | 28 | 0.023695 | 0.023695 |  | 0 | 0 | 6312 | 2447.9997 | 207.5687
HBG-1.RR.288.1 | 24244419133523 | Bahubal, Lama Putijuri, Pal Bari | 2019-09-04 | NQ1003 | 10.6 | 79 | 10.6 | 80 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6312 | 2447.9997 | 111.6867
HBG-1.RR.289.1 | 24244419133523 | Bahubal, Lama Putijuri, Pal Bari | 2019-09-04 | NQ1003 | 11.9 | 81 | 11.9 | 82 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6312 | 2447.9997 | 125.3841
HBG-1.RR.290.1 | 24163429127566 | Shaistagong, South Langa Para, Md. Abdul Khalak | 2019-09-05 | NQ1003 | 10.9 | 93 | 10.9 | 94 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6816 | 1943.9997 | 114.8476
HBG-1.RR.290.2 | 24163429127566 | Shaistagong, South Langa Para, Md. Abdul Khalak | 2021-01-12 | MN1032 | 7.1 | 19 | 7.1 | 20 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6816 | 1943.9997 | 74.809
HBG-1.RR.291.1 | 24163369127578 | Shaistagong, South Langa Para, Auib Ali | 2019-09-05 | NQ1003 | 22.9 | 96 | 22.9 | 97 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 22.9 | 22.9 | 1.374 | 1.374 | 0.0007168 | 100% | 0% | 1.374 | 1.374 | 0.0011869 | 28 | 0.027544 | 0.027544 |  | 0 | 0 | 6816 | 1943.9997 | 241.2854
HBG-1.RR.292.1 | 24162869128022 | Shaistagong, Sabaspur, Asa Foundation | 2019-09-05 | NQ1003 | 4.7 | 100 | 4.7 | 101 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6816 | 1943.9997 | 49.5215
HBG-1.RR.293.1 | 24175439130561 | Bahubal, Mirpur Bazar, UP Road, Dorbas Ali | 2019-09-05 | NQ1003 | 11.3 | 102 | 11.3 | 103 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6792 | 1967.9997 | 119.0622
HBG-1.RR.294.1 | 24175419130573 | Bahubal, Mirpur Bazar, UP Road, Atar Ali | 2019-09-05 | NQ1003 | 9.7 | 106 | 9.7 | 107 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6792 | 1967.9997 | 102.2039
HBG-1.RR.295.1 | 24174729131019 | Bahubal, Mirpur, Ijjet Nagor, South Para, Abdul Hai | 2019-09-07 | NQ1003 | 7.8 | 142 | 7.9 | 143 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6792 | 1967.9997 | 83.2382
HBG-1.RR.296.1 | 24174289131015 | Bahubal, Mirpur, Ijjet Nagor, South Para, Junaid Ahmed | 2019-09-07 | NQ1003 | 10.7 | 144 | 10.7 | 145 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6792 | 1967.9997 | 112.7403
HBG-1.RR.297.1 | 24183029131095 | Bahubal, Mirpur, Khmargao, Rojob Ali | 2019-09-07 | NQ1003 | 13.6 | 146 | 13.6 | 147 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6792 | 1967.9997 | 143.2961
HBG-1.RR.298.1 | 24232389124337 | Hobigong, Bogla Bazar, Drbosilpaloi | 2019-09-08 | NQ1003 | 11.1 | 174 | 11.1 | 175 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6384 | 2375.9997 | 116.9549
HBG-1.RR.299.1 | 24232389124337 | Hobigong, Bogla Bazar, Pinake | 2019-09-08 | NQ1003 | 13.1 | 176 | 13 | 177 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6384 | 2375.9997 | 136.9743
HBG-1.RR.300.1 | 24232389124337 | Hobigong, Bogla Bazar, Sompod | 2019-09-08 | NQ1003 | 9.1 | 180 | 9.1 | 181 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6384 | 2375.9997 | 95.882
HBG-1.RR.301.1 | 24163249127215 | Shayestaganj, Station Road, Mohlul Sunam R/A, Jaudge Villa, M.A. Wahab | 2019-08-31 | NQ1011 | 18.9 | 405 | 18.9 | 406 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6624 | 2135.9997 | 199.1395
HBG-1.RR.301.2 | 24163249127215 | Shayestaganj, Station Road, Mohlul Sunam R/A, Jaudge Villa, M.A. Wahab | 2021-09-04 | LX1011 | 15.1 | 207 | 15.1 | 208 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6624 | 2135.9997 | 159.1009
HBG-1.RR.302.1 | 24163249127215 | Shayestaganj, Station Road, Mohlul Sunam R/A, Jaudge Villa, M.A. Wahab | 2019-08-31 | NQ1011 | 10.5 | 407 | 10.5 | 408 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6624 | 2135.9997 | 110.6331
HBG-1.RR.302.2 | 24163249127215 | Shayestaganj, Station Road, Mohlul Sunam R/A, Jaudge Villa, M.A. Wahab | 2021-01-11 | MN1032 | 3 | 9 | 3 | 10 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6624 | 2135.9997 | 31.6094
HBG-1.RR.303.1 | 24163249127215 | Shayestaganj, Station Road, Mohlul Sunam R/A, Jaudge Villa, M.A. Wahab | 2019-08-31 | NQ1011 | 4.5 | 409 | 4.5 | 410 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6624 | 2135.9997 | 47.4142
HBG-1.RR.304.1 | 24162199127507 | Shayestaganj, West Lenjapara, Sohel | 2019-09-01 | NQ1011 | 12.8 | 433 | 12.8 | 434 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6816 | 1943.9997 | 134.867
HBG-1.RR.305.1 | 24162199127507 | Shayestaganj, West Lenjapara, Rahima begum | 2019-09-01 | NQ1011 | 14.9 | 435 | 14.9 | 436 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6816 | 1943.9997 | 156.9936
HBG-1.RR.306.1 | 24162389127507 | Shayestaganj, West Lenjapara, yusuf | 2019-09-01 | NQ1011 | 21.8 | 437 | 21.8 | 438 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 21.8 | 21.8 | 1.308 | 1.308 | 0.0007168 | 100% | 0% | 1.308 | 1.308 | 0.0011869 | 28 | 0.026221 | 0.026221 |  | 0 | 0 | 6816 | 1943.9997 | 229.6953
HBG-1.RR.307.1 | 24162639127483 | Shayestaganj, South Lenjapara, Selim Bhuiya | 2019-09-01 | NQ1011 | 11.8 | 439 | 11.8 | 440 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6816 | 1943.9997 | 124.3305
HBG-1.RR.308.1 | 24162489127431 | Shayestaganj, South Lenjapara, Abul Khayer | 2019-09-01 | NQ1011 | 11.6 | 441 | 11.6 | 442 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6816 | 1943.9997 | 122.2232
HBG-1.RR.309.1 | 24162489127431 | Shayestaganj, South Lenjapara, Ahad Ali | 2019-09-01 | NQ1011 | 18.6 | 443 | 18.6 | 444 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 6816 | 1943.9997 | 195.9786
HBG-1.RR.310.1 | 24162289127424 | Shayestaganj, South Lenjapara, Moti Mia | 2019-09-01 | NQ1011 | 11.7 | 445 | 11.9 | 446 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6816 | 1943.9997 | 125.3841
HBG-1.RR.311.1 | 24162119127468 | Shayestaganj, South Lenjapara, Nannu Talukdar | 2019-09-01 | NQ1011 | 14.7 | 447 | 14.7 | 448 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6816 | 1943.9997 | 154.8863
HBG-1.RR.312.1 | 24161769127460 | Shayestaganj, South Lenjapara, Ali Mia | 2019-09-01 | NQ1011 | 11.5 | 449 | 11.5 | 450 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6816 | 1943.9997 | 121.1695
HBG-1.RR.312.2 | 24161769127460 | Shayestaganj, South Lenjapara, Ali Mia | 2020-10-12 | NQ1003 | 11.2 | 24 | 11.2 | 25 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6816 | 1943.9997 | 118.0086
HBG-1.RR.313.1 | 24161679127450 | Shayestaganj, East Biramchor, Fazal Mia | 2019-09-01 | NQ1011 | 10.9 | 451 | 11 | 452 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6816 | 1943.9997 | 115.9013
HBG-1.RR.314.1 | 24161679127520 | Shayestaganj, East Biramchor, Shamim Mia | 2019-09-01 | NQ1011 | 21.1 | 453 | 20.9 | 454 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 20.9 | 20.9 | 1.254 | 1.254 | 0.0007168 | 100% | 0% | 1.254 | 1.254 | 0.0011869 | 28 | 0.025138 | 0.025138 |  | 0 | 0 | 6816 | 1943.9997 | 220.2125
HBG-1.RR.315.1 | 24161679127520 | Shayestaganj, East Biramchor, Abdullah Sarder | 2019-09-01 | NQ1011 | 17.6 | 455 | 17.5 | 456 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6816 | 1943.9997 | 184.3884
HBG-1.RR.316.1 | 24161679127520 | Shayestaganj, East Biramchor, Sohrab | 2019-09-01 | NQ1011 | 11.2 | 457 | 11.2 | 458 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6816 | 1943.9997 | 118.0086
HBG-1.RR.317.1 | 24155949128410 | Shayestaganj, Notun Bridge, Chunarughat Road, Shafiq Mia | 2019-09-01 | NQ1011 | 16.4 | 459 | 16.4 | 460 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6816 | 1943.9997 | 172.7983
HBG-1.RR.318.1 | 24155949128410 | Shayestaganj, Notun Bridge, Chunarughat Road, Abdul Goni | 2019-09-01 | NQ1011 | 11.8 | 461 | 11.8 | 462 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6816 | 1943.9997 | 124.3305
HBG-1.RR.319.1 | 24113389131202 | Chunarughat, Balla Road, Bijoya Bithi, Hemendro Deb | 2019-09-02 | NQ1011 | 10.9 | 505 | 11.3 | 506 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6456 | 2303.9997 | 119.0622
HBG-1.RR.320.1 | 24113429131201 | Chunarughat, Balla Road, Mintu Dev | 2019-09-02 | NQ1011 | 23.8 | 507 | 23.5 | 508 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 23.5 | 23.5 | 1.41 | 1.41 | 0.0007168 | 100% | 0% | 1.41 | 1.41 | 0.0011869 | 28 | 0.028266 | 0.028266 |  | 0 | 0 | 6456 | 2303.9997 | 247.6073
HBG-1.RR.321.1 | 24113199131207 | Chunarughat, Balla Road, Shamsul Islam | 2019-09-02 | NQ1011 | 11.4 | 509 | 11.4 | 510 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6456 | 2303.9997 | 120.1159
HBG-1.RR.322.1 | 24112419131026 | Chunarughat, College Road, Hatunda, Mortuza Ali Khan | 2019-09-02 | NQ1011 | 22.6 | 511 | 22.6 | 512 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 22.6 | 22.6 | 1.356 | 1.356 | 0.0007168 | 100% | 0% | 1.356 | 1.356 | 0.0011869 | 28 | 0.027183 | 0.027183 |  | 0 | 0 | 6456 | 2303.9997 | 238.1245
HBG-1.RR.323.1 | 24112529131032 | Chunarughat, College Road, Hatunda, Harun Rashid | 2019-09-02 | NQ1011 | 61.3 | 513 | 61.3 | 514 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 61.3 | 61.3 | 3.678 | 3.678 | 0.0007168 | 100% | 0% | 3.678 | 3.678 | 0.0011869 | 28 | 0.073731 | 0.073731 |  | 0 | 0 | 6456 | 2303.9997 | 645.8863
HBG-1.RR.324.1 | 24112349130591 | Chunarughat, College Road, Hatunda, Afiya Begum | 2019-09-02 | NQ1011 | 13.4 | 515 | 13.4 | 516 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6456 | 2303.9997 | 141.1888
HBG-1.RR.325.1 | 24112189130578 | Chunarughat, Oppsite of Chunarughat Govt. College, A. Razzak Villa | 2019-09-02 | NQ1011 | 13.3 | 517 | 13.3 | 518 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6456 | 2303.9997 | 140.1352
HBG-1.RR.326.1 | 24112229130565 | Chunarughat, College Road, OM Cottage | 2019-09-02 | NQ1011 | 11.2 | 519 | 11.2 | 520 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6456 | 2303.9997 | 118.0086
HBG-1.RR.327.1 | 24112249130547 | Chunarughat, College Road, Shafiqur Rahman | 2019-09-02 | NQ1011 | 14.1 | 521 | 13.8 | 522 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6456 | 2303.9997 | 145.4034
HBG-1.RR.328.1 | 24202789132223 | Bahuball, Girls High School Road, Abdul Baset Chowdhury | 2019-09-03 | NQ1011 | 12.9 | 11 | 12.9 | 12 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6312 | 2447.9997 | 135.9206
HBG-1.RR.329.1 | 24202779132232 | Bahuball, Girls High School Road, Abdur Rahman | 2019-09-03 | NQ1011 | 10.4 | 13 | 10.4 | 14 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6312 | 2447.9997 | 109.5794
HBG-1.RR.330.1 | 24202969132203 | Bahuball, Hospital Road, Iqbal Hossain | 2019-09-03 | NQ1011 | 18.6 | 15 | 18.7 | 16 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6312 | 2447.9997 | 197.0322
HBG-1.RR.330.2 | 24202969132203 | Bahuball, Hospital Road, Iqbal Hossain | 2019-09-03 | NQ1011 | 10.1 | 17 | 10.2 | 18 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6312 | 2447.9997 | 107.4721
HBG-1.RR.331.1 | 24203289132253 | Bahuball, Hospital Road, Shamsul Islam | 2019-09-03 | NQ1011 | 14.6 | 19 | 14.6 | 20 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6312 | 2447.9997 | 153.8326
HBG-1.RR.332.1 | 24203289132253 | Bahuball, Hospital Road, Nurul Islam | 2019-09-03 | NQ1011 | 9.9 | 21 | 9.9 | 22 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6312 | 2447.9997 | 104.3112
HBG-1.RR.333.1 | 24203289132253 | Bahuball, Hospital Road, Shahadat Ali | 2019-09-03 | NQ1011 | 19.6 | 23 | 19.3 | 24 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 6312 | 2447.9997 | 203.3541
HBG-1.RR.334.1 | 24203309132261 | Bahuball, Hospital Road, Abdul odud | 2019-09-03 | NQ1011 | 11.8 | 25 | 11.8 | 26 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6312 | 2447.9997 | 124.3305
HBG-1.RR.335.1 | 24204309132211 | Bahuball, Thana Road, Beside Of Union Bank Ltd., Shamim | 2019-09-03 | NQ1011 | 8.3 | 27 | 8.3 | 28 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6312 | 2447.9997 | 87.4528
HBG-1.RR.336.1 | 24204869132198 | Bahuball Bazar, Islamabad Road, Nazmul Islam | 2019-09-04 | NQ1002 | 10 | 25 | 10 | 26 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6312 | 2447.9997 | 105.3648
HBG-1.RR.337.1 | 24204859132198 | Bahuball Bazar, Islamabad Road, Abidur Rahman | 2019-09-04 | NQ1002 | 13.7 | 27 | 13.7 | 28 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6312 | 2447.9997 | 144.3498
HBG-1.RR.338.1 | 24204799132190 | Bahuball Bazar, Islamabad Road, Farid Mia | 2019-09-04 | NQ1002 | 52.7 | 29 | 52.7 | 30 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 52.7 | 52.7 | 3.162 | 3.162 | 0.0007168 | 100% | 0% | 3.162 | 3.162 | 0.0011869 | 28 | 0.063387 | 0.063387 |  | 0 | 0 | 6312 | 2447.9997 | 555.2726
HBG-1.RR.339.1 | 24204739132194 | Bahuball Bazar, Islamabad Road, Abdur Shahid | 2019-09-04 | NQ1002 | 17.9 | 31 | 17.9 | 32 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 6312 | 2447.9997 | 188.603
HBG-1.RR.339.2 | 24204739132194 | Bahuball Bazar, Islamabad Road, Abdur Shahid | 2022-03-13 | LU1001 | 2.9 | 48 | 2.9 | 49 | 2022-03-13 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 4608 | 2447.9997 | 24.6121
HBG-1.RR.340.1 | 24204819132183 | Bahuball, Islamabad, Sirajul Islam | 2019-09-04 | NQ1002 | 7.2 | 33 | 7.2 | 34 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6312 | 2447.9997 | 75.8627
HBG-1.RR.341.1 | 24204839132175 | Bahuball, Islamabad, Yusuf | 2019-09-04 | NQ1002 | 9.1 | 35 | 9.1 | 36 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6312 | 2447.9997 | 95.882
HBG-1.RR.342.1 | 24204879132155 | Bahuball, Islamabad, Munim Chowdhury | 2019-09-04 | NQ1002 | 8 | 37 | 8.1 | 38 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6312 | 2447.9997 | 85.3455
HBG-1.RR.343.1 | 24204759132145 | Bahuball, Islamabad, M.A. Jalil Talukdar | 2019-09-04 | NQ1002 | 8.1 | 39 | 8.1 | 40 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6312 | 2447.9997 | 85.3455
HBG-1.RR.344.1 | 24204569132139 | Bahuball, Islamabad, Nur Hossain | 2019-09-04 | NQ1002 | 11.3 | 41 | 11.3 | 42 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6312 | 2447.9997 | 119.0622
HBG-1.RR.345.1 | 24204569132139 | Bahuball, Islamabad, Mowlad Hossain | 2019-09-04 | NQ1002 | 11.3 | 43 | 11.3 | 44 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6312 | 2447.9997 | 119.0622
HBG-1.RR.346.1 | 24241799133554 | Bahuball, Putijuri, Jadobpur, Abdul Shahid | 2019-09-04 | NQ1002 | 26.1 | 45 | 25 | 46 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 25 | 25 | 1.5 | 1.5 | 0.0007168 | 100% | 0% | 1.5 | 1.5 | 0.0011869 | 28 | 0.03007 | 0.03007 |  | 0 | 0 | 6312 | 2447.9997 | 263.412
HBG-1.RR.346.2 | 24241799133554 | Bahuball, Putijuri, Jadobpur, Abdul Shahid | 2019-09-04 | NQ1002 | 107 | 47 | 107 | 48 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 107 | 107 | 6.42 | 6.42 | 0.0007168 | 100% | 0% | 6.42 | 6.42 | 0.0011869 | 28 | 0.1287 | 0.1287 |  | 0 | 0 | 6312 | 2447.9997 | 1127.4035
HBG-1.RR.347.1 | 24240929134059 | Bahuball, Putijuri, Jadobpur, Golap Mia | 2019-09-04 | NQ1002 | 10.6 | 49 | 10.6 | 50 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6312 | 2447.9997 | 111.6867
HBG-1.RR.347.2 | 24240929134059 | Bahuball, Putijuri, Jadobpur, Golap Mia | 2022-03-13 | LU1001 | 11.6 | 46 | 11.6 | 47 | 2022-03-13 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 4608 | 2447.9997 | 98.4483
HBG-1.RR.348.1 | 24163369127564 | Shayestaganj, South Lenjapara, Station Road, Biswajit Chandro | 2019-09-05 | NQ1002 | 8.7 | 59 | 8.7 | 60 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6816 | 1943.9997 | 91.6674
HBG-1.RR.349.1 | 24163369127564 | Shayestaganj, South Lenjapara, Station Road, Sontosh Chandro | 2019-09-05 | NQ1002 | 18.1 | 61 | 18.5 | 62 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6816 | 1943.9997 | 194.9249
HBG-1.RR.349.2 | 24163369127564 | Shayestaganj, South Lenjapara, Station Road, Sontosh Chandro | 2020-10-12 | NQ1003 | 2.2 | 26 | 2.2 | 27 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6816 | 1943.9997 | 23.1803
HBG-1.RR.350.1 | 24163309127565 | Shayestaganj, South Lenjapara, Station Road, Kanu Shekh | 2019-09-05 | NQ1002 | 11.6 | 63 | 11.6 | 64 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6816 | 1943.9997 | 122.2232
HBG-1.RR.351.1 | 24163209127471 | Saistaganj, Station Road, Worksop Area, Hazi Ashraf Mia | 2019-09-01 | NQ1011 | 15.3 | 463 | 15.3 | 464 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6816 | 1943.9997 | 161.2082
HBG-1.RR.352.1 | 24163209127471 | Saistaganj, Station Road, Worksop Area, Jamal Talukdar | 2019-09-01 | NQ1011 | 10.4 | 465 | 10.4 | 466 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6816 | 1943.9997 | 109.5794
HBG-1.RR.353.1 | 24163179127482 | Saistaganj, Station Road, Worksop Area, Shamol | 2019-09-01 | NQ1011 | 11.5 | 467 | 11.5 | 468 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 4536 | 0 | 2280 | 1943.9997 | 58.427
HBG-1.RR.354.1 | 24163149127497 | Saistaganj, Station Road, Worksop Area, Esha Motors | 2019-09-01 | NQ1011 | 6.8 | 469 | 6.8 | 470 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6816 | 1943.9997 | 71.6481
HBG-1.RR.355.1 | 24163099127542 | Saistaganj, Station Road, Worksop Area, Azim C.N.G | 2019-09-01 | NQ1011 | 10.2 | 471 | 10.2 | 472 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6816 | 1943.9997 | 107.4721
HBG-1.RR.356.1 | 24162739127554 | Saistaganj, Sabaspur, Boga mia | 2019-09-01 | NQ1011 | 1.5 | 473 | 1.5 | 474 | 2022-01-01 | [9 empty] | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 | 2022-01-01 12:00 | 0 | 0
HBG-1.RR.357.1 | 24114929130582 | Chunarghat, Shotong Road, Uttor Hatunda, Mosharof | 2019-09-01 | NQ1011 | 8.7 | 475 | 8.7 | 476 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6456 | 2303.9997 | 91.6674
HBG-1.RR.358.1 | 24115489131128 | Chunarughat Bazer, Ram Pal | 2019-09-02 | NQ1011 | 19.1 | 477 | 19.1 | 478 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 6456 | 2303.9997 | 201.2468
HBG-1.RR.359.1 | 24115489131128 | Chunarughat Bazer, Gopal Deb | 2019-09-02 | NQ1011 | 20.4 | 479 | 19.9 | 480 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0 | 6456 | 2303.9997 | 209.676
HBG-1.RR.360.1 | 24115569131125 | Chunarughat Bazer, Abdul Khalek | 2019-09-02 | NQ1011 | 10.7 | 481 | 10.7 | 482 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6456 | 2303.9997 | 112.7403
HBG-1.RR.361.1 | 24120459131031 | Chunarughat Bazer, Borail, Jalal mia | 2019-09-02 | NQ1011 | 13.9 | 483 | 14.6 | 484 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6456 | 2303.9997 | 153.8326
HBG-1.RR.362.1 | 24120639131017 | Chunarughat Bazer, Borail, Samsul Ali | 2019-09-02 | NQ1011 | 7.4 | 485 | 7.4 | 486 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6456 | 2303.9997 | 77.97
HBG-1.RR.363.1 | 24120639130575 | Chunarughat Bazer, Borail, Faruk Uddin | 2019-09-02 | NQ1011 | 11 | 487 | 11.1 | 488 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6456 | 2303.9997 | 116.9549
HBG-1.RR.364.1 | 24120639130575 | Chunarughat Bazer, Borail, Shahanamaz | 2019-09-02 | NQ1011 | 10.6 | 489 | 10.7 | 490 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6456 | 2303.9997 | 112.7403
HBG-1.RR.365.1 | 24120629130594 | Chunarughat Bazer, Borail, Ali Neaj | 2019-09-02 | NQ1011 | 13.9 | 491 | 13.9 | 492 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6456 | 2303.9997 | 146.4571
HBG-1.RR.367.1 | 24120509130592 | Chunarughat Bazer, Borail, Didar Mia | 2019-09-02 | NQ1011 | 13.6 | 493 | 13.6 | 494 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6456 | 2303.9997 | 143.2961
HBG-1.RR.368.1 | 24115919131077 | Chunarughat Bazer, Borail, Mokles Mia | 2019-09-02 | NQ1011 | 8 | 495 | 8 | 496 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6456 | 2303.9997 | 84.2919
HBG-1.RR.369.1 | 24115929131017 | Chunarughat Bazer, Borail, Kadir | 2019-09-02 | NQ1011 | 9.8 | 497 | 9.8 | 498 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6456 | 2303.9997 | 103.2575
HBG-1.RR.370.1 | 24120159131008 | Chunarughat Bazer, Borail, Abdul Ohab Salim | 2019-09-02 | NQ1011 | 8.4 | 499 | 8.4 | 500 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6456 | 2303.9997 | 88.5064
HBG-1.RR.371.1 | 24115979130594 | Chunarughat Bazer, Borail, Nur Jahan | 2019-09-02 | NQ1011 | 3 | 501 | 3 | 502 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6456 | 2303.9997 | 31.6094
HBG-1.RR.372.1 | 24115319131013 | Chunarughat Bazer, Borail, Mohommadia R/A, Kajol | 2019-09-02 | NQ1011 | 10.5 | 503 | 10.6 | 504 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6456 | 2303.9997 | 111.6867
HBG-1.RR.373.1 | 24125049130180 | Chunarughat, Gugaura, Ward # 1, Tojamul Huda | 2019-09-03 | NQ1011 | 11.4 | 1 | 11.4 | 2 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6456 | 2303.9997 | 120.1159
HBG-1.RR.374.1 | 24125049130180 | Chunarughat, Gugaura, Ward # 1, Fakrul Islam Chy. | 2019-09-03 | NQ1011 | 8.7 | 3 | 8.5 | 4 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6456 | 2303.9997 | 89.5601
HBG-1.RR.375.1 | 24125049130180 | Chunarughat, Gugaura, Ward # 1, Shahjahan Chy. | 2019-09-03 | NQ1011 | 15.3 | 5 | 15.3 | 6 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6456 | 2303.9997 | 161.2082
HBG-1.RR.376.1 | 24125049130180 | Chunarughat, Gugaura, Ward # 1, Farid Chy. | 2019-09-03 | NQ1011 | 7.8 | 7 | 7.8 | 8 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6456 | 2303.9997 | 82.1846
HBG-1.RR.377.1 | 24125259130180 | Chunarughat, Gugaura, Ward # 1, Tota Mia Chy. | 2019-09-03 | NQ1011 | 14 | 9 | 14 | 10 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6456 | 2303.9997 | 147.5107
HBG-1.RR.378.1 | 24205279132144 | Bahubol, Kabirpur Road, Sundor Ali | 2019-09-04 | NQ1002 | 5.4 | 1 | 5.4 | 2 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6312 | 2447.9997 | 56.897
HBG-1.RR.379.1 | 24205279132144 | Bahubol, Kabirpur Road, Kashem Ali | 2019-09-04 | NQ1002 | 5.2 | 3 | 5.2 | 4 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6312 | 2447.9997 | 54.7897
HBG-1.RR.380.1 | 24205339132122 | Bahubol, Kabirpur Road, Monaf Mia | 2019-09-04 | NQ1002 | 6.1 | 5 | 6.1 | 6 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6312 | 2447.9997 | 64.2725
HBG-1.RR.381.1 | 24205339132122 | Bahubol, Kabirpur Road, Abdul Korim | 2019-09-04 | NQ1002 | 5.4 | 7 | 5.4 | 8 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6312 | 2447.9997 | 56.897
HBG-1.RR.382.1 | 24205339132122 | Bahubol, Kabirpur Road, Afroz mia | 2019-09-04 | NQ1002 | 4.1 | 9 | 4.1 | 10 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6312 | 2447.9997 | 43.1996
HBG-1.RR.383.1 | 24205339132122 | Bahubol, Kabirpur Road, Abdul Haq | 2019-09-04 | NQ1002 | 3.7 | 11 | 3.8 | 12 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6312 | 2447.9997 | 40.0386
HBG-1.RR.383.2 | 24205339132122 | Bahubol, Kabirpur Road, Abdul Haq | 2021-08-24 | LX1011 | 21.4 | 41 | 21.4 | 42 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 6312 | 2447.9997 | 225.4807
HBG-1.RR.384.1 | 24205339132122 | Bahubol, Kabirpur Road, Abdur Nur | 2019-09-04 | NQ1002 | 2 | 13 | 2 | 14 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6312 | 2447.9997 | 21.073
HBG-1.RR.385.1 | 24205069132219 | Bahubol, Bazar, Main Road, Sadia Store | 2019-09-04 | NQ1002 | 10.8 | 15 | 10.8 | 16 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6312 | 2447.9997 | 113.794
HBG-1.RR.386.1 | 24205079132243 | Bahubol, Vitorer Bazar, Izazur Traders | 2019-09-04 | NQ1002 | 7.5 | 17 | 7.5 | 18 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6312 | 2447.9997 | 79.0236
HBG-1.RR.387.1 | 24204759132091 | Bahubol, Islamabad R/A, Abdul Kayum | 2019-09-04 | NQ1002 | 11.1 | 19 | 11.1 | 20 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6312 | 2447.9997 | 116.9549
HBG-1.RR.388.1 | 24204759132119 | Bahubol, Islamabad R/A, Abdul Kayum | 2019-09-04 | NQ1002 | 23.6 | 21 | 23.6 | 22 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 23.6 | 23.6 | 1.416 | 1.416 | 0.0007168 | 100% | 0% | 1.416 | 1.416 | 0.0011869 | 28 | 0.028386 | 0.028386 |  | 0 | 0 | 6312 | 2447.9997 | 248.661
HBG-1.RR.389.1 | 24204759132119 | Bahubol, Islamabad R/A, Shafiq | 2019-09-04 | NQ1002 | 3.7 | 23 | 3.7 | 24 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6312 | 2447.9997 | 38.985
HBG-1.RR.390.1 | 24115379131058 | Hbiganj, Chunarughat, Thana, Officer in Charge House | 2019-09-05 | NQ1002 | 54.4 | 51 | 54.2 | 52 | 2022-01-01 | [9 empty] | 54.2 | 54.2 | 3.252 | 3.252 | 0.0007168 | 100% | 0% | 3.252 | 3.252 | 0.0011869 | 28 | 0.065191 | 0.065191 |  | 0 | 0
HBG-1.RR.391.1 | 24115379131058 | Hbiganj, Chunarughat, Thana, Officer in Charge House | 2019-09-05 | NQ1002 | 15.1 | 53 | 15.1 | 54 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6456 | 2303.9997 | 159.1009
HBG-1.RR.392.1 | 24140799130087 | Chunarughat, Sreekutta, Abdul Kayum | 2019-09-05 | NQ1002 | 12.4 | 55 | 12.7 | 56 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6456 | 2303.9997 | 133.8133
HBG-1.RR.392.2 | 24140799130087 | Chunarughat, Sreekutta, Abdul Kayum | 2022-03-12 | LU1001 | 5.6 | 38 | 5.6 | 39 | 2022-03-12 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 4776 | 2303.9997 | 47.6884
HBG-1.RR.393.1 | 24140799130087 | Chunarughat, Sreekutta, Baser Chy | 2019-09-05 | NQ1002 | 24.7 | 57 | 24.7 | 58 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 24.7 | 24.7 | 1.482 | 1.482 | 0.0007168 | 100% | 0% | 1.482 | 1.482 | 0.0011869 | 28 | 0.029709 | 0.029709 |  | 0 | 0 | 6456 | 2303.9997 | 260.2511
HBG-1.RR.394.1 | 24175459130423 | Habiganj, Bahubol, Mirpur, Abdus Samad | 2019-09-07 | NQ1002 | 4.3 | 75 | 4.5 | 76 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6792 | 1967.9997 | 47.4142
HBG-1.RR.395.1 | 24180249130475 | Habiganj, Bahubol, Mirpur, Sujog Saha | 2019-09-07 | NQ1002 | 11.5 | 77 | 11.5 | 78 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6792 | 1967.9997 | 121.1695
HBG-1.RR.396.1 | 24180249130475 | Habiganj, Bahubol, Mirpur, Sonjoy Saha | 2019-09-07 | NQ1002 | 14 | 79 | 14 | 80 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6792 | 1967.9997 | 147.5107
HBG-1.RR.397.1 | 24180199130469 | Habiganj, Bahubol, Mirpur, Sudhir Chandra Kaur | 2019-09-07 | NQ1002 | 11.3 | 81 | 11.3 | 82 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6792 | 1967.9997 | 119.0622
HBG-1.RR.398.1 | 24180199130469 | Habiganj, Bahubol, Mirpur, Liton Chandra Deb | 2019-09-07 | NQ1002 | 8.6 | 83 | 8.6 | 84 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6792 | 1967.9997 | 90.6137
HBG-1.RR.399.1 | 24174769131132 | Mirpur, Sreemongol Road, Ijjotpur, Joinullah | 2019-09-07 | NQ1002 | 29.3 | 85 | 29.3 | 86 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 29.3 | 29.3 | 1.758 | 1.758 | 0.0007168 | 100% | 0% | 1.758 | 1.758 | 0.0011869 | 28 | 0.035242 | 0.035242 |  | 0 | 0 | 6792 | 1967.9997 | 308.7189
HBG-1.RR.400.1 | 24174889131133 | Mirpur, Sreemongol Road, Ijjotpur, Modina Nibas | 2019-09-07 | NQ1002 | 23.2 | 87 | 23.2 | 88 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 23.2 | 23.2 | 1.392 | 1.392 | 0.0007168 | 100% | 0% | 1.392 | 1.392 | 0.0011869 | 28 | 0.027905 | 0.027905 |  | 0 | 0 | 6792 | 1967.9997 | 244.4464
HBG-1.RR.401.1 | 24231559124359 | Habiganj, Ghatia Para, Jothirmoy Pal | 2019-09-08 | MP1006 | 3.8 | 159 | 3.8 | 160 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6336 | 2423.9997 | 40.0386
HBG-1.RR.402.1 | 24231619124385 | Habigonj, Ghatia Para, Upendra Vhoumik | 2019-09-09 | MP1006 | 13.5 | 161 | 13.5 | 162 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6336 | 2423.9997 | 142.2425
HBG-1.RR.403.1 | 24231619124385 | Habigonj, Ghatia Para, Naraion Madok | 2019-09-09 | MP1006 | 11.5 | 163 | 11.5 | 164 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6336 | 2423.9997 | 121.1695
HBG-1.RR.404.1 | 24231559124360 | Habigonj, Ghatia Para, Upendra Vhoumik | 2019-09-09 | MP1006 | 4.5 | 165 | 4.5 | 166 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6336 | 2423.9997 | 47.4142
HBG-1.RR.405.1 | 24231979124391 | Habigonj, Ghatia Para, Makhon Lal Das | 2019-09-09 | MP1006 | 45.5 | 167 | 45.7 | 168 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 45.7 | 45.7 | 2.742 | 2.742 | 0.0007168 | 100% | 0% | 2.742 | 2.742 | 0.0011869 | 28 | 0.054968 | 0.054968 |  | 0 | 0 | 6336 | 2423.9997 | 481.5172
HBG-1.RR.406.1 | 24231999124398 | Habigonj, Ghatia Para, Subrato Sarker | 2019-09-09 | MP1006 | 19.4 | 169 | 18.8 | 170 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 6336 | 2423.9997 | 198.0858
HBG-1.RR.407.1 | 24232049124405 | Habigonj, Ghatia Para, Bimol Sarker | 2019-09-09 | MP1006 | 6.2 | 171 | 6.2 | 172 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6336 | 2423.9997 | 65.3262
HBG-1.RR.408.1 | 24232049124405 | Habigonj, Ghatia Para, Bimol Sarker | 2019-09-09 | MP1006 | 13.7 | 173 | 13.7 | 174 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6336 | 2423.9997 | 144.3498
HBG-1.RR.409.1 | 24232049124405 | Habigonj, Ghatia Para, Nilu Roy | 2019-09-09 | MP1006 | 12.1 | 175 | 12.1 | 176 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6336 | 2423.9997 | 127.4914
HBG-1.RR.410.1 | 24232049124405 | Habigonj, Ghatia Para, Muhit Roy | 2019-09-09 | MP1006 | 4.1 | 177 | 4.1 | 178 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6336 | 2423.9997 | 43.1996
HBG-1.RR.411.1 | 24232049124405 | Habigonj, Ghatia Para, Horipoda | 2019-09-09 | MP1006 | 8.7 | 179 | 8.7 | 180 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6336 | 2423.9997 | 91.6674
HBG-1.RR.412.1 | 24232049124405 | Habigonj, Ghatia Para, Chiengo Roy | 2019-09-09 | MP1006 | 12.3 | 181 | 12.3 | 182 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6336 | 2423.9997 | 129.5987
HBG-1.RR.413.1 | 24232049124405 | Habigonj, Ghatia Para, Chandro Kisor | 2019-09-09 | MP1006 | 11 | 183 | 11 | 184 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6336 | 2423.9997 | 115.9013
HBG-1.RR.413.2 | 24232049124405 | Habigonj, Ghatia Para, Chandro Kisor | 2021-08-28 | LX1011 | 12.2 | 82 | 12.2 | 83 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6336 | 2423.9997 | 128.5451
HBG-1.RR.414.1 | 24232159124414 | Habigonj, Ghatia Para, Liton Das | 2019-09-09 | MP1006 | 7.3 | 187 | 7.3 | 188 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6336 | 2423.9997 | 76.9163
HBG-1.RR.415.1 | 24232159124414 | Habigonj, Ghatia Para, Liton Das | 2019-09-09 | MP1006 | 2.4 | 189 | 2.4 | 190 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6336 | 2423.9997 | 25.2876
HBG-1.RR.416.1 | 24232159124414 | Habigonj, Ghatia Para, Liton Das | 2019-09-09 | MP1006 | 11.5 | 191 | 11.5 | 192 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6336 | 2423.9997 | 121.1695
HBG-1.RR.417.1 | 24232159124414 | Habigonj, Ghatia Para, Liton Das | 2019-09-09 | MP1006 | 6.3 | 193 | 6.3 | 194 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6336 | 2423.9997 | 66.3798
HBG-1.RR.418.1 | 24232159124429 | Habiganj, Ghatiya Bazar, Aziz Market, Setara Begum | 2019-09-11 | MP1006 | 12.3 | 221 | 12.3 | 222 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6336 | 2423.9997 | 129.5987
HBG-1.RR.419.1 | 24232069124447 | Habiganj, Moha Provu Akhra Quarter, Adom Ali | 2019-09-11 | MP1006 | 6.8 | 223 | 6.8 | 224 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6336 | 2423.9997 | 71.6481
HBG-1.RR.420.1 | 24232069124447 | Habiganj, Moha Provu Akhra Quarter, Adom Ali | 2019-09-11 | MP1006 | 10.3 | 225 | 10.3 | 226 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6336 | 2423.9997 | 108.5258
HBG-1.RR.421.1 | 24232069124447 | Habiganj, Moha Provu Akhra Quarter, H # 3382 | 2019-09-11 | MP1006 | 10.7 | 227 | 10.7 | 228 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6336 | 2423.9997 | 112.7403
HBG-1.RR.422.1 | 24231839124431 | Habiganj, Ghatiya Bazar, R.K. Mission Road, H # 3425 | 2019-09-11 | MP1006 | 13.9 | 229 | 14 | 230 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6336 | 2423.9997 | 147.5107
HBG-1.RR.423.1 | 24231839124431 | Habiganj, Ghatiya Bazar, R.K. Mission Road, H # 3423 | 2019-09-11 | MP1006 | 6.3 | 231 | 6.3 | 232 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6336 | 2423.9997 | 66.3798
HBG-1.RR.424.1 | 24231839124431 | Habiganj, Ghatiya Bazar, R.K. Mission Road, H # 3421 | 2019-09-11 | MP1006 | 11.5 | 233 | 11.5 | 234 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6336 | 2423.9997 | 121.1695
HBG-1.RR.425.1 | 24231839124431 | Habiganj, Ghatiya Bazar, R.K. Mission Road, H # 3422 | 2019-09-11 | MP1006 | 4.7 | 235 | 4.7 | 236 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6336 | 2423.9997 | 49.5215
HBG-1.RR.426.1 | 24231549124415 | Habiganj, Ghatiya Bazar, R.K. Mission Road, Manik Pal | 2019-09-11 | MP1006 | 3 | 237 | 3 | 238 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6408 | 2351.9997 | 31.6094
HBG-1.RR.427.1 | 24231349124415 | Habiganj, Ghatiya Bazar, R.K. Mission Road, Bikas Chandra Pal | 2019-09-11 | MP1006 | 30.6 | 239 | 30.6 | 240 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 30.6 | 30.6 | 1.836 | 1.836 | 0.0007168 | 100% | 0% | 1.836 | 1.836 | 0.0011869 | 28 | 0.036806 | 0.036806 |  | 0 | 0 | 6408 | 2351.9997 | 322.4163
HBG-1.RR.428.1 | 24230339124408 | Habiganj, PTI Road, H # 3577 | 2019-09-11 | MP1006 | 18.8 | 241 | 18.8 | 242 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 6408 | 2351.9997 | 198.0858
HBG-1.RR.428.2 | 24230339124408 | Habiganj, PTI Road, H # 3577 | 2019-09-11 | MP1006 | 8.7 | 243 | 8.7 | 244 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6408 | 2351.9997 | 91.6674
HBG-1.RR.429.1 | 24225999124413 | Habiganj, PTI Road, Mouchak, Sayed Abidur | 2019-09-12 | MP1006 | 13.4 | 281 | 12.8 | 282 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6408 | 2351.9997 | 134.867
HBG-1.RR.430.1 | 24224939124403 | Habiganj, Rajnagar, Mohila College Road, Md. Salekuddin Ahmed | 2019-09-12 | MP1006 | 5.1 | 284 | 5.1 | 285 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6504 | 2255.9997 | 53.7361
HBG-1.RR.431.1 | 24224819124382 | Habiganj, Rajnagar, Mohila College Road, H # 51 | 2019-09-12 | MP1006 | 1.8 | 286 | 1.8 | 287 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6504 | 2255.9997 | 18.9657
HBG-1.RR.432.1 | 24224819124382 | Habiganj, Rajnagar, Mohila College Road, Harunur Roshid | 2019-09-12 | MP1006 | 14.3 | 288 | 14.3 | 289 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6504 | 2255.9997 | 150.6717
HBG-1.RR.433.1 | 24224619124388 | Habiganj, Rajnagar, Mohila College Road, H # 5271/1 | 2019-09-12 | MP1006 | 8.8 | 290 | 8.8 | 291 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6504 | 2255.9997 | 92.721
HBG-1.RR.434.1 | 24224619124388 | Habiganj, Rajnagar, Mohila College Road, Salim | 2019-09-12 | MP1006 | 11 | 292 | 11 | 293 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6504 | 2255.9997 | 115.9013
HBG-1.RR.435.1 | 24224649124376 | Habiganj, Rajnagar, Mohila College Road, H # 5338/2 | 2019-09-12 | MP1006 | 5.1 | 294 | 5.1 | 295 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6504 | 2255.9997 | 53.7361
HBG-1.RR.435.2 | 24224649124376 | Habiganj, Rajnagar, Mohila College Road, H # 5338/2 | 2020-10-10 | NQ1008 | 11 | 100 | 11 | 101 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6504 | 2255.9997 | 115.9013
HBG-1.RR.436.1 | 24224669124341 | Habiganj, Rajnagar, Kaborstan Road, Mutaleb | 2019-09-12 | MP1006 | 21.8 | 297 | 21.8 | 298 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 21.8 | 21.8 | 1.308 | 1.308 | 0.0007168 | 100% | 0% | 1.308 | 1.308 | 0.0011869 | 28 | 0.026221 | 0.026221 |  | 0 | 0 | 6504 | 2255.9997 | 229.6953
HBG-1.RR.437.1 | 24224669124341 | Habiganj, Rajnagar, Kaborstan Road, Sofiul Alom | 2019-09-12 | MP1006 | 3.4 | 299 | 3.4 | 300 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6504 | 2255.9997 | 35.824
HBG-1.RR.438.1 | 24224689124328 | Habiganj, Rajnagar, Kaborstan Road, Sazzadur Rahman | 2019-09-12 | MP1006 | 5.8 | 303 | 5.8 | 304 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6504 | 2255.9997 | 61.1116
HBG-1.RR.439.1 | 24224689124328 | Habiganj, Rajnagar, Kaborstan Road, Abdul Malek | 2019-09-12 | MP1006 | 11.1 | 305 | 11.1 | 306 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6504 | 2255.9997 | 116.9549
HBG-1.RR.440.1 | 24224689124328 | Habiganj, Rajnagar, Kaborstan Road, Abul Kalam | 2019-09-12 | MP1006 | 10.7 | 307 | 10.7 | 308 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6504 | 2255.9997 | 112.7403
HBG-1.RR.441.1 | 24224779124329 | Habiganj, Rajnagar, Kaborstan Road, Nure Alom | 2019-09-14 | MP1006 | 11.4 | 334 | 11.4 | 335 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6504 | 2255.9997 | 120.1159
HBG-1.RR.442.1 | 24224989124342 | Habiganj, Rajnagar, Kaborstan Road, Mannan Villa | 2019-09-14 | MP1006 | 4.8 | 336 | 4.8 | 337 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6504 | 2255.9997 | 50.5751
HBG-1.RR.443.1 | 24225059124353 | Habiganj, Rajnagar, Kaborstan Road, Beside of Mannan Villa | 2019-09-14 | MP1006 | 10.4 | 338 | 10.4 | 339 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6504 | 2255.9997 | 109.5794
HBG-1.RR.444.1 | 24224639124330 | Habiganj, Rajnagar, Primary School Road, Nurul Gazi | 2019-09-14 | MP1006 | 9.8 | 340 | 9.8 | 341 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6504 | 2255.9997 | 103.2575
HBG-1.RR.445.1 | 24224439124357 | Habiganj, Rajnagar, Primary School Road, Abdur Rahaman | 2019-09-14 | MP1006 | 8.4 | 342 | 8.5 | 343 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6504 | 2255.9997 | 89.5601
HBG-1.RR.446.1 | 24224409124357 | Habiganj, Rajnagar, Primary School Road, Golam Rahaman | 2019-09-14 | MP1006 | 6.9 | 344 | 6.9 | 345 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6504 | 2255.9997 | 72.7017
HBG-1.RR.447.1 | 24224409124357 | Habiganj, Rajnagar, Primary School Road, Miraj Mia | 2019-09-14 | MP1006 | 3.1 | 346 | 3.1 | 347 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6504 | 2255.9997 | 32.6631
HBG-1.RR.448.1 | 24224319124358 | Habiganj, Rajnagar, Primary School Road, Eklas | 2019-09-14 | MP1006 | 10.7 | 348 | 10.7 | 349 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6504 | 2255.9997 | 112.7403
HBG-1.RR.449.1 | 24224319124358 | Habiganj, Rajnagar, Primary School Road, Hasan | 2019-09-14 | MP1006 | 7.5 | 350 | 7.5 | 351 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6504 | 2255.9997 | 79.0236
HBG-1.RR.450.1 | 24224139124328 | Habiganj, Rajnagar, Jaduge Goly, Mizba Uddin | 2019-09-14 | MP1006 | 6.5 | 352 | 6.5 | 353 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6504 | 2255.9997 | 68.4871
HBG-1.RR.451.1 | 24231289124309 | Habiganj, Kaligachtola Road, Robindro Das | 2019-09-08 | MP1006 | 3.7 | 89 | 3.7 | 90 | 2022-01-01 | [9 empty] | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0
HBG-1.RR.452.1 | 24231549124406 | Habiganj, Ghatiya, Bidhan Dav | 2019-09-08 | MP1006 | 3.3 | 91 | 3.3 | 92 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6408 | 2351.9997 | 34.7704
HBG-1.RR.453.1 | 24231549124406 | Habiganj, Ghatiya, Bidhan Dav | 2019-09-08 | MP1006 | 13.2 | 93 | 13.2 | 94 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6408 | 2351.9997 | 139.0816
HBG-1.RR.453.2 | 24231549124406 | Habiganj, Ghatiya, Bidhan Dav | 2021-01-18 | LU1001 | 4 | 33 | 4 | 34 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6408 | 2351.9997 | 42.1459
HBG-1.RR.454.1 | 24231549124390 | Habiganj, Garning Park R/A, Tahera kunjo | 2019-09-08 | MP1006 | 3.5 | 95 | 3.5 | 96 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6408 | 2351.9997 | 36.8777
HBG-1.RR.455.1 | 24231289124387 | Habiganj, Garning Park R/A, Monmohon Das | 2019-09-08 | MP1006 | 9.1 | 97 | 9.1 | 98 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6408 | 2351.9997 | 95.882
HBG-1.RR.456.1 | 24231249124387 | Habiganj, Garning Park R/A, Abu Bakher Loskor | 2019-09-08 | MP1006 | 11.8 | 99 | 11.8 | 100 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6408 | 2351.9997 | 124.3305
HBG-1.RR.457.1 | 24231249124387 | Habiganj, Garning Park R/A, Bimol Das | 2019-09-08 | MP1006 | 3 | 101 | 3 | 102 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6408 | 2351.9997 | 31.6094
HBG-1.RR.458.1 | 24231169124395 | Habiganj, Garning Park R/A, Bekas | 2019-09-08 | MP1006 | 15.2 | 103 | 15.4 | 104 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6408 | 2351.9997 | 162.2618
HBG-1.RR.459.1 | 24231079124400 | Habiganj, Garning Park R/A, Eshi Kesh Saha | 2019-09-08 | MP1006 | 11.2 | 105 | 11.2 | 106 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6408 | 2351.9997 | 118.0086
HBG-1.RR.460.1 | 24231079124400 | Habiganj, Garning Park R/A, Eshi Kesh Saha | 2019-09-08 | MP1006 | 11.6 | 107 | 11.6 | 108 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6408 | 2351.9997 | 122.2232
HBG-1.RR.461.1 | 24230759124418 | Habiganj, B. Jaman Road, Onirban, Chowdhiry Monjil | 2019-09-09 | MP1006 | 11.6 | 195 | 11.3 | 196 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6408 | 2351.9997 | 119.0622
HBG-1.RR.462.1 | 24230769124449 | Habiganj, B. Jaman Road, Onirban, Golam Ali | 2019-09-09 | MP1006 | 11.4 | 197 | 11.4 | 198 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6408 | 2351.9997 | 120.1159
HBG-1.RR.463.1 | 24230769124449 | Habiganj, B. Jaman Road, Onirban, Samsuddin | 2019-09-09 | MP1006 | 11.8 | 199 | 11.6 | 200 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6408 | 2351.9997 | 122.2232
HBG-1.RR.464.1 | 24230349124447 | Habiganj, B. Jaman Road, Onirban, Abdul Wahid | 2019-09-09 | MP1006 | 5.3 | 201 | 5.4 | 202 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6408 | 2351.9997 | 56.897
HBG-1.RR.465.1 | 24230649124461 | Habiganj, B. Jaman Road, Onirban, Monnan Shoping Moll | 2019-09-09 | MP1006 | 7.8 | 203 | 7.8 | 204 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6408 | 2351.9997 | 82.1846
HBG-1.RR.466.1 | 24230599124426 | Habiganj, P.T.I Road, Jombir Kumer | 2019-09-09 | MP1006 | 5.2 | 205 | 5.2 | 206 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6408 | 2351.9997 | 54.7897
HBG-1.RR.467.1 | 24230439124424 | Habiganj, P.T.I Road, Sojol Rai | 2019-09-09 | MP1006 | 8.8 | 209 | 8.8 | 210 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6408 | 2351.9997 | 92.721
HBG-1.RR.468.1 | 24230439124424 | Habiganj, P.T.I Road, Sojol Rai | 2019-09-09 | MP1006 | 18 | 211 | 18 | 212 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 18 | 18 | 1.08 | 1.08 | 0.0007168 | 100% | 0% | 1.08 | 1.08 | 0.0011869 | 28 | 0.02165 | 0.02165 |  | 0 | 0 | 6408 | 2351.9997 | 189.6567
HBG-1.RR.469.1 | 24230419124413 | Habiganj, P.T.I Road, Krishno Babu | 2019-09-09 | MP1006 | 5.9 | 213 | 5.9 | 214 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6408 | 2351.9997 | 62.1652
HBG-1.RR.470.1 | 24230419124413 | Habiganj, P.T.I Road, Sonjoy Roy | 2019-09-09 | MP1006 | 8.8 | 215 | 8.8 | 216 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6408 | 2351.9997 | 92.721
HBG-1.RR.471.1 | 24230419124413 | Habiganj, P.T.I Road, Sonjoy Roy | 2019-09-09 | MP1006 | 11.1 | 219 | 11.1 | 220 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6408 | 2351.9997 | 116.9549
HBG-1.RR.472.1 | 24230209124433 | Habiganj, P.T.I Road, Anirban, Jabed Ali | 2019-09-11 | MP1006 | 9.2 | 245 | 9.2 | 246 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6408 | 2351.9997 | 96.9356
HBG-1.RR.473.1 | 24230209124433 | Habiganj, P.T.I Road, Anirban, Masuk Ali | 2019-09-11 | MP1006 | 6.1 | 247 | 6.1 | 248 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6408 | 2351.9997 | 64.2725
HBG-1.RR.474.1 | 24230209124433 | Habiganj, P.T.I Road, Anirban, Mubassir Mia | 2019-09-11 | MP1006 | 12.5 | 249 | 12.5 | 250 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6408 | 2351.9997 | 131.706
HBG-1.RR.475.1 | 24230219124433 | Habiganj, P.T.I Road, Anirban, GLDB Office | 2019-09-11 | MP1006 | 10.9 | 251 | 10.9 | 252 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6408 | 2351.9997 | 114.8476
HBG-1.RR.476.1 | 24230139124433 | Habiganj, P.T.I Road, Anirban, Ataur Rahman | 2019-09-11 | MP1006 | 10.3 | 256 | 10.3 | 257 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6408 | 2351.9997 | 108.5258
HBG-1.RR.477.1 | 24225759124409 | Habiganj, Kalibari Cross Road, Beauty Touch Beauty Parlour | 2019-09-11 | MP1006 | 3.8 | 258 | 3.8 | 259 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6480 | 2279.9997 | 40.0386
HBG-1.RR.478.1 | 24225759124421 | Habiganj, Kalibari Cross Road, Lutfa Begom | 2019-09-11 | MP1006 | 15.8 | 260 | 15.6 | 261 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6480 | 2279.9997 | 164.3691
HBG-1.RR.479.1 | 24225759124421 | Habiganj, Kalibari Cross Road, Mizan | 2019-09-11 | MP1006 | 11.8 | 262 | 11.8 | 263 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6480 | 2279.9997 | 124.3305
HBG-1.RR.480.1 | 24225659124437 | Habiganj, Kalibari Cross Road, Salia Begum | 2019-09-11 | MP1006 | 5.5 | 264 | 5.5 | 265 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6480 | 2279.9997 | 57.9506
HBG-1.RR.480.2 | 24225659124437 | Habiganj, Kalibari Cross Road, Salia Begum | 2019-09-11 | MP1006 | 6.5 | 266 | 6.5 | 267 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6480 | 2279.9997 | 68.4871
HBG-1.RR.481.1 | 24225749124448 | Habiganj, Kalibari Cross Road, Pronom Kumar Rai | 2019-09-11 | MP1006 | 7.4 | 268 | 7.4 | 269 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6480 | 2279.9997 | 77.97
HBG-1.RR.482.1 | 24225649124460 | Habiganj, Mohila College Road, Bijon Kumarkar | 2019-09-11 | MP1006 | 10.9 | 270 | 11 | 271 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6480 | 2279.9997 | 115.9013
HBG-1.RR.483.1 | 24225419124406 | Habiganj, Mohila College Road, Tofil Mia Talukdar | 2019-09-11 | MP1006 | 11.2 | 272 | 11.3 | 273 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6480 | 2279.9997 | 119.0622
HBG-1.RR.483.2 | 24225419124406 | Habiganj, Mohila College Road, Tofil Mia Talukdar | 2022-03-22 | LU1001 | 3.8 | 66 | 3.8 | 67 | 2022-03-22 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 4560 | 2279.9997 | 31.263
HBG-1.RR.484.1 | 24225419124406 | Habiganj, Mohila College Road, Tohema Talukdar | 2019-09-11 | MP1006 | 4.5 | 274 | 4.5 | 275 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6480 | 2279.9997 | 47.4142
HBG-1.RR.485.1 | 24225419124406 | Habiganj, Mohila College Road, Rofiq Mia | 2019-09-11 | MP1006 | 4.7 | 279 | 4.7 | 280 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6480 | 2279.9997 | 49.5215
HBG-1.RR.485.2 | 24225419124406 | Habiganj, Mohila College Road, Rofiq Mia | 2022-03-22 | LU1001 | 11.8 | 68 | 12 | 69 | 2022-03-22 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 4560 | 2279.9997 | 98.7254
HBG-1.RR.486.1 | 24224699124321 | Habiganj, Rajnagor, Koborsthan Road, Shamim | 2019-09-12 | MP1006 | 12.3 | 309 | 12.3 | 310 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6504 | 2255.9997 | 129.5987
HBG-1.RR.487.1 | 24224689124320 | Habiganj, Rajnagor, Koborsthan Road, Lotifur Rahman Anu | 2019-09-12 | MP1006 | 7.7 | 311 | 7.1 | 312 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6504 | 2255.9997 | 74.809
HBG-1.RR.488.1 | 24224739124320 | Habiganj, Rajnagor, Koborsthan Road, Azad Vila | 2019-09-12 | MP1006 | 17.3 | 314 | 17.3 | 315 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 6504 | 2255.9997 | 182.2811
HBG-1.RR.489.1 | 24224669124312 | Habiganj, Rajnagor, Koborsthan Road, Motiur Rahman | 2019-09-12 | MP1006 | 1.7 | 316 | 1.7 | 317 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6504 | 2255.9997 | 17.912
HBG-1.RR.490.1 | 24224649124314 | Habiganj, Rajnagor, Koborsthan Road, Ujjal/Fojilur Rahman | 2019-09-12 | MP1006 | 8.5 | 318 | 8.5 | 319 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6504 | 2255.9997 | 89.5601
HBG-1.RR.491.1 | 24224569124311 | Habiganj, Rajnagor, Koborsthan Road, Abdur Rahman | 2019-09-12 | MP1006 | 4.3 | 320 | 4.3 | 321 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6504 | 2255.9997 | 45.3069
HBG-1.RR.492.1 | 24224459124329 | Habiganj, Rajnagor, Koborsthan Road, Abdul Motin | 2019-09-12 | MP1006 | 3 | 322 | 3 | 323 | 2022-01-01 | [9 empty] | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0
HBG-1.RR.493.1 | 24224459124329 | Habiganj, Rajnagor, Koborsthan Road, Md. Rahman | 2019-09-12 | MP1006 | 3.8 | 324 | 3.8 | 325 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6504 | 2255.9997 | 40.0386
HBG-1.RR.494.1 | 24224409124323 | Habiganj, Rajnagor, Koborsthan Road, Abdul Hakim | 2019-09-12 | MP1006 | 5 | 328 | 5 | 329 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6504 | 2255.9997 | 52.6824
HBG-1.RR.495.1 | 24224409124323 | Habiganj, Rajnagor, Koborsthan Road, Abdul Hakim | 2019-09-12 | MP1006 | 3.9 | 330 | 3.9 | 331 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6504 | 2255.9997 | 41.0923
HBG-1.RR.496.1 | 24225439124417 | Habiganj, Mohila College Road, Nazmul Hasan | 2019-09-12 | MP1006 | 21.1 | 332 | 21.2 | 333 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 21.2 | 21.2 | 1.272 | 1.272 | 0.0007168 | 100% | 0% | 1.272 | 1.272 | 0.0011869 | 28 | 0.025499 | 0.025499 |  | 0 | 0 | 6480 | 2279.9997 | 223.3734
HBG-1.RR.497.1 | 24223219124491 | Habiganj, Jail Road, Musabbir Monjil | 2019-09-14 | MP1006 | 8.4 | 362 | 8.4 | 363 | 2022-01-01 | [9 empty] | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0
HBG-1.RR.497.2 | 24223219124491 | Habiganj, Jail Road, Musabbir Monjil | 2021-01-16 | NQ1007 | 3.3 | 21 | 3.2 | 22 | 2022-01-01 | [9 empty] | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0
HBG-1.RR.498.1 | 24223149124498 | Habiganj, Jail Road, Soiyod Abdul Hamid | 2019-09-14 | MP1006 | 11.6 | 364 | 11.6 | 365 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6576 | 2183.9997 | 122.2232
HBG-1.RR.499.1 | 24223339124504 | Habiganj, Press Club Road, Prosonno Sondha Nir | 2019-09-14 | MP1006 | 11 | 366 | 10.3 | 367 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6576 | 2183.9997 | 108.5258
HBG-1.RR.500.1 | 24223099124504 | Habiganj, Press Club Road, Ameer | 2019-09-14 | MP1006 | 7.3 | 368 | 7.4 | 369 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6576 | 2183.9997 | 77.97
HBG-1.RR.501.1 | 24175179130573 | Bahubal, Mirpur, Baniya Gaon, Monsur Ali | 2019-09-07 | NQ1003 | 9.9 | 140 | 9.9 | 141 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6792 | 1967.9997 | 104.3112
HBG-1.RR.502.1 | 24232349124294 | Habiganj, Bagla Bazar, Fajor Ali | 2019-09-08 | NQ1003 | 6 | 148 | 6 | 149 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6384 | 2375.9997 | 63.2189
HBG-1.RR.503.1 | 24232269124291 | Habiganj, Bagla Bazar, Abdul Hamid | 2019-09-08 | NQ1003 | 7.3 | 150 | 7.3 | 151 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6384 | 2375.9997 | 76.9163
HBG-1.RR.504.1 | 24232309124318 | Habiganj, Bagla Bazar, Horidas Sen | 2019-09-08 | NQ1003 | 12 | 152 | 11.9 | 153 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6384 | 2375.9997 | 125.3841
HBG-1.RR.505.1 | 24232339124326 | Habiganj, Bagla Bazar, Chandan Sen | 2019-09-08 | NQ1003 | 9 | 154 | 9 | 155 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6384 | 2375.9997 | 94.8283
HBG-1.RR.506.1 | 24232549124326 | Habiganj, Bagla Bazar, Sabur | 2019-09-08 | NQ1003 | 10.5 | 156 | 10.5 | 157 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6384 | 2375.9997 | 110.6331
HBG-1.RR.507.1 | 24232729124316 | Habiganj, Bagla Bazar, Tajuddin | 2019-09-08 | NQ1003 | 5.8 | 158 | 5.8 | 159 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6384 | 2375.9997 | 61.1116
HBG-1.RR.508.1 | 24232689124324 | Habiganj, Bagla Bazar, Kamrhapur, Sumi Aktar | 2019-09-08 | NQ1003 | 9.1 | 160 | 9.1 | 161 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6384 | 2375.9997 | 95.882
HBG-1.RR.509.1 | 24232769124353 | Habiganj, Bagla Bazar, Kamrhapur, Susanto Kuri | 2019-09-08 | NQ1003 | 5.1 | 162 | 5.1 | 163 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6384 | 2375.9997 | 53.7361
HBG-1.RR.510.1 | 24232769124353 | Habiganj, Bagla Bazar, Kamrhapur, Jamuna Kuri | 2019-09-08 | NQ1003 | 7.5 | 164 | 7.5 | 165 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6384 | 2375.9997 | 79.0236
HBG-1.RR.511.1 | 24232649124310 | Habiganj, Bagla Bazar, Kamrhapur, Sheikh Abdul Awal | 2019-09-08 | NQ1003 | 6.4 | 166 | 6.4 | 167 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6384 | 2375.9997 | 67.4335
HBG-1.RR.512.1 | 24232599124310 | Habiganj, Bagla Bazar, Kamrhapur, Samsul Haque | 2019-09-08 | NQ1003 | 17.6 | 168 | 17.6 | 169 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 6384 | 2375.9997 | 185.4421
HBG-1.RR.513.1 | 24232599124310 | Habiganj, Bagla Bazar, Kamrhapur, Harun Mia | 2019-09-08 | NQ1003 | 10.1 | 170 | 10.1 | 171 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6384 | 2375.9997 | 106.4185
HBG-1.RR.514.1 | 24232739124299 | Habiganj, Bagla Bazar, Kamrhapur, Mokam Bari, Farida Begum | 2019-09-08 | NQ1003 | 8.5 | 172 | 8.5 | 173 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6384 | 2375.9997 | 89.5601
HBG-1.RR.515.1 | 24232899124520 | Habiganj, Chowdhury Bazar, Abdul Basir | 2019-09-09 | NQ1003 | 7.1 | 257 | 7.1 | 258 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6336 | 2423.9997 | 74.809
HBG-1.RR.516.1 | 24232659124512 | Habiganj, Chowdhury Bazar, Puratun Khuyay Road, Abdul Jalal | 2019-09-09 | NQ1003 | 11.5 | 259 | 11.5 | 260 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6336 | 2423.9997 | 121.1695
HBG-1.RR.517.1 | 24232659124512 | Habiganj, Chowdhury Bazar, Puratun Khuyay Road, Abdul Jalal | 2019-09-09 | NQ1003 | 7.1 | 261 | 7.1 | 262 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6336 | 2423.9997 | 74.809
HBG-1.RR.518.1 | 24232739124514 | Habiganj, Chowdhury Bazar, Puratun Khuyay Road, Amir Ali Chowdhury | 2019-09-09 | NQ1003 | 11.1 | 263 | 10.8 | 264 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6336 | 2423.9997 | 113.794
HBG-1.RR.519.1 | 24232529124508 | Habiganj, Chowdhury Bazar, Puratun Khuyay Road, Abdul Jalal Doctor | 2019-09-09 | NQ1003 | 4.5 | 265 | 4.5 | 266 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6336 | 2423.9997 | 47.4142
HBG-1.RR.520.1 | 24232529124508 | Habiganj, Chowdhury Bazar, Puratun Khuyay Road, Mahid Chowdhury | 2019-09-09 | NQ1003 | 8.2 | 267 | 8.2 | 268 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6336 | 2423.9997 | 86.3991
HBG-1.RR.521.1 | 24232409124532 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Anan | 2019-09-09 | NQ1003 | 6.5 | 269 | 6.5 | 270 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6336 | 2423.9997 | 68.4871
HBG-1.RR.522.1 | 24232409124532 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Mortuj Ali | 2019-09-09 | NQ1003 | 8.5 | 271 | 8.5 | 272 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6336 | 2423.9997 | 89.5601
HBG-1.RR.522.2 | 24232409124532 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Mortuj Ali | 2021-01-18 | NQ1007 | 11 | 31 | 11 | 32 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6336 | 2423.9997 | 115.9013
HBG-1.RR.523.1 | 24232449124532 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Abdul Motin | 2019-09-09 | NQ1003 | 7.7 | 273 | 7.1 | 274 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6336 | 2423.9997 | 74.809
HBG-1.RR.524.1 | 24232449124532 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Siddik Ali | 2019-09-09 | NQ1003 | 8.6 | 275 | 8.6 | 276 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6336 | 2423.9997 | 90.6137
HBG-1.RR.525.1 | 24232439124539 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Abdul Khalek | 2019-09-09 | NQ1003 | 23.1 | 277 | 23.1 | 278 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 23.1 | 23.1 | 1.386 | 1.386 | 0.0007168 | 100% | 0% | 1.386 | 1.386 | 0.0011869 | 28 | 0.027785 | 0.027785 |  | 0 | 0 | 6336 | 2423.9997 | 243.3927
HBG-1.RR.526.1 | 24232439124539 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Julhaj Mia | 2019-09-09 | NQ1003 | 13.8 | 279 | 13.7 | 280 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6336 | 2423.9997 | 144.3498
HBG-1.RR.527.1 | 24232499124535 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Abdul Awal | 2019-09-09 | NQ1003 | 14.3 | 281 | 14.2 | 282 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6336 | 2423.9997 | 149.618
HBG-1.RR.528.1 | 24232489124544 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Abdul Ahad | 2019-09-09 | NQ1003 | 11.6 | 283 | 11.6 | 284 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6336 | 2423.9997 | 122.2232
HBG-1.RR.529.1 | 24232569124551 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Farjana Begum | 2019-09-09 | NQ1003 | 12.9 | 285 | 12.9 | 286 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6336 | 2423.9997 | 135.9206
HBG-1.RR.530.1 | 24232179124543 | Habiganj, Chowdhury Bazar, Nathirabadh R/A, Safiqul Haque | 2019-09-09 | NQ1003 | 6.8 | 287 | 6.8 | 288 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6408 | 2351.9997 | 71.6481
HBG-1.RR.531.1 | 24231879124575 | Habiganj, Nathirabadh R/A, Shipon | 2019-09-11 | NQ1003 | 12.3 | 317 | 12.3 | 318 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6432 | 2327.9997 | 129.5987
HBG-1.RR.532.1 | 24231879124575 | Habiganj, Nathirabadh R/A, Tutul | 2019-09-11 | NQ1003 | 9.5 | 319 | 8.9 | 320 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6432 | 2327.9997 | 93.7747
HBG-1.RR.533.1 | 24231759124558 | Habiganj, Nathirabadh R/A, Gopinathpur, Horidon Pal | 2019-09-11 | NQ1003 | 15.6 | 321 | 15.1 | 322 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6432 | 2327.9997 | 159.1009
HBG-1.RR.534.1 | 24231679124571 | Habiganj, Nathirabadh R/A, Gopinathpur, Sibu Ray | 2019-09-11 | NQ1003 | 18.5 | 323 | 18.1 | 324 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6432 | 2327.9997 | 190.7103
HBG-1.RR.535.1 | 24231679124571 | Habiganj, Nathirabadh R/A, Gopinathpur, Kajol Ranjon Ray | 2019-09-11 | NQ1003 | 10.5 | 325 | 10.5 | 326 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6432 | 2327.9997 | 110.6331
HBG-1.RR.536.1 | 24231529124575 | Habiganj, Nathirabadh R/A, Gopinathpur, Shashi Mahan | 2019-09-11 | NQ1003 | 7.5 | 327 | 7.5 | 328 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6432 | 2327.9997 | 79.0236
HBG-1.RR.537.1 | 24231519124571 | Habiganj, Nathirabadh R/A, Gopinathpur, Sudir Sutrodhar | 2019-09-11 | NQ1003 | 7.2 | 329 | 7.2 | 330 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6432 | 2327.9997 | 75.8627
HBG-1.RR.538.1 | 24231469124571 | Habiganj, Nathirabadh R/A, Gopinathpur, Gopal Bonik | 2019-09-11 | NQ1003 | 7.9 | 331 | 7.4 | 332 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6432 | 2327.9997 | 77.97
HBG-1.RR.539.1 | 24231449124569 | Habiganj, Nathirabadh R/A, Gopinathpur, Dipok Sutrodhar | 2019-09-11 | NQ1003 | 7.7 | 335 | 7.7 | 336 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6432 | 2327.9997 | 81.1309
HBG-1.RR.540.1 | 24231319124592 | Habiganj, Gopinathpur, Jitandro Das | 2019-09-11 | NQ1003 | 11 | 337 | 11 | 338 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6432 | 2327.9997 | 115.9013
HBG-1.RR.541.1 | 24231319124598 | Habiganj, Gopinathpur, Harendro Chandro Ray | 2019-09-11 | NQ1003 | 10.6 | 339 | 10.6 | 340 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6432 | 2327.9997 | 111.6867
HBG-1.RR.542.1 | 24231269125002 | Habiganj, Gopinathpur, Gautom Bashu | 2019-09-11 | NQ1003 | 4.8 | 341 | 4.8 | 342 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6432 | 2327.9997 | 50.5751
HBG-1.RR.543.1 | 24231499124525 | Habiganj, Gopinathpur(Chirakandi), Sema Pal (Suresh Bhaban) | 2019-09-12 | NQ1003 | 9.6 | 367 | 9.6 | 368 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6408 | 2351.9997 | 101.1502
HBG-1.RR.544.1 | 24231229124548 | Habiganj, Gopinathpur(Chirakandi), Jane Palace | 2019-09-12 | NQ1003 | 6.4 | 369 | 6.4 | 370 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6408 | 2351.9997 | 67.4335
HBG-1.RR.545.1 | 24231229124548 | Habiganj, Gopinathpur(Chirakandi), Samim Ahmed | 2019-09-12 | NQ1003 | 11.5 | 371 | 11.5 | 372 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6408 | 2351.9997 | 121.1695
HBG-1.RR.546.1 | 24231409124547 | Habiganj, Gopinathpur(Chirakandi), Orun Kumar Das | 2019-09-12 | NQ1003 | 7.3 | 373 | 7.3 | 374 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6408 | 2351.9997 | 76.9163
HBG-1.RR.547.1 | 24231449124539 | Habiganj, Gopinathpur(Chirakandi), Alpona | 2019-09-12 | NQ1003 | 10.7 | 375 | 10.7 | 376 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6408 | 2351.9997 | 112.7403
HBG-1.RR.548.1 | 24231029124545 | Habiganj, Gopinathpur(Chirakandi), Shajahan | 2019-09-12 | NQ1003 | 7.3 | 377 | 7.3 | 378 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6408 | 2351.9997 | 76.9163
HBG-1.RR.548.2 | 24231029124545 | Habiganj, Gopinathpur(Chirakandi), Shajahan | 2021-01-17 | NQ1003 | 11.4 | 51 | 11.4 | 52 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6408 | 2351.9997 | 120.1159
HBG-1.RR.549.1 | 24230919124544 | Habiganj, Gopinathpur(Chirakandi), H # 45/C | 2019-09-12 | NQ1003 | 11.2 | 381 | 11.2 | 382 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6408 | 2351.9997 | 118.0086
HBG-1.RR.550.1 | 24230989124555 | Habiganj, Gopinathpur(Chirakandi), Anamul Haque Sardar | 2019-09-12 | NQ1003 | 7.5 | 383 | 7.5 | 384 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6408 | 2351.9997 | 79.0236
HBG-1.RR.551.1 | 24232379124347 | Hobigong, Bogla Bazar, Ashor Ali | 2019-09-08 | NQ1003 | 7.8 | 182 | 7.8 | 183 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6384 | 2375.9997 | 82.1846
HBG-1.RR.552.1 | 24232379124347 | Hobigong, Bogla Bazar, Pretos Deb | 2019-09-08 | NQ1003 | 5.3 | 184 | 5.3 | 185 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6384 | 2375.9997 | 55.8434
HBG-1.RR.553.1 | 24232379124347 | Hobigong, Bogla Bazar, Lontu Deb | 2019-09-08 | NQ1003 | 10.7 | 186 | 10.7 | 187 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6384 | 2375.9997 | 112.7403
HBG-1.RR.554.1 | 24232399124349 | Hobigong, Bogla Bazar, Bkas Deb | 2019-09-08 | NQ1003 | 32.9 | 188 | 32.9 | 189 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 32.9 | 32.9 | 1.974 | 1.974 | 0.0007168 | 100% | 0% | 1.974 | 1.974 | 0.0011869 | 28 | 0.039572 | 0.039572 |  | 0 | 0 | 6384 | 2375.9997 | 346.6502
HBG-1.RR.555.1 | 24232599124364 | Hobigong, Bogla Bazar, Sofiq Mia | 2019-09-08 | NQ1003 | 11.3 | 190 | 12 | 191 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6384 | 2375.9997 | 126.4378
HBG-1.RR.556.1 | 24232599124364 | Hobigong, Bogla Bazar, Angura Khatun | 2019-09-08 | NQ1003 | 14.5 | 192 | 14.5 | 193 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 6384 | 2375.9997 | 152.779
HBG-1.RR.557.1 | 24232599124364 | Hobigong, Bogla Bazar, Hafiza Khatun | 2019-09-08 | NQ1003 | 16.4 | 194 | 16 | 195 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6384 | 2375.9997 | 168.5837
HBG-1.RR.558.1 | 24232629124382 | Hobigong, Old Bazar, Omullo Muduk | 2019-09-08 | NQ1003 | 8.3 | 196 | 8.3 | 197 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6384 | 2375.9997 | 87.4528
HBG-1.RR.559.1 | 24232629124382 | Hobigong, Old Bazar, Nipondo Dav | 2019-09-08 | NQ1003 | 19.2 | 198 | 19.2 | 199 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 19.2 | 19.2 | 1.152 | 1.152 | 0.0007168 | 100% | 0% | 1.152 | 1.152 | 0.0011869 | 28 | 0.023094 | 0.023094 |  | 0 | 0 | 6384 | 2375.9997 | 202.3004
HBG-1.RR.560.1 | 24232629124382 | Hobigong, Old Bazar, Bablu | 2019-09-08 | NQ1003 | 10.9 | 200 | 10.9 | 201 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6384 | 2375.9997 | 114.8476
HBG-1.RR.561.1 | 24232509124386 | Hobigong, Old Bazar, Haldar Kutir | 2019-09-08 | NQ1003 | 11.1 | 202 | 10.7 | 203 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6384 | 2375.9997 | 112.7403
HBG-1.RR.562.1 | 24232509124386 | Hobigong, Old Bazar, Osok Rai | 2019-09-08 | NQ1003 | 6.3 | 204 | 6.3 | 205 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 4464 | 0 | 1920 | 2375.9997 | 32.5534
HBG-1.RR.563.1 | 24232369124385 | Hobigong, Old Bazar, Bollove Bonik | 2019-09-08 | NQ1003 | 12.7 | 206 | 12.7 | 207 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6384 | 2375.9997 | 133.8133
HBG-1.RR.564.1 | 24232259124445 | Hobigong, Choudury Bazar, Sazidur Rahman | 2019-09-08 | NQ1003 | 12.3 | 208 | 11.9 | 209 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6336 | 2423.9997 | 125.3841
HBG-1.RR.565.1 | 24232259124445 | Hobigong, Choudury Bazar, Sukumar Rai | 2019-09-08 | NQ1003 | 10.7 | 210 | 10.4 | 211 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6336 | 2423.9997 | 109.5794
HBG-1.RR.566.1 | 24232039124369 | Hobigong, Natirpur, Md. Jomsar Ali | 2019-09-08 | NQ1003 | 9.1 | 214 | 8.7 | 215 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6384 | 2375.9997 | 91.6674
HBG-1.RR.567.1 | 24232039124369 | Hobigong, Natirpur, Dulal Mia | 2019-09-08 | NQ1003 | 6.4 | 216 | 6.4 | 217 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6384 | 2375.9997 | 67.4335
HBG-1.RR.568.1 | 24232079124368 | Hobigong, Natirpur, Monpor Ali | 2019-09-09 | NQ1003 | 14.1 | 218 | 14.1 | 219 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6384 | 2375.9997 | 148.5644
HBG-1.RR.569.1 | 24232079124368 | Hobigong, Natirpur, Abdul Monraf | 2019-09-09 | NQ1003 | 10 | 220 | 10 | 221 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6384 | 2375.9997 | 105.3648
HBG-1.RR.570.1 | 24232019124365 | Hobigong, Natirpur, Siddik Rahman | 2019-09-09 | NQ1003 | 12.7 | 224 | 12.7 | 225 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6384 | 2375.9997 | 133.8133
HBG-1.RR.571.1 | 24232019124365 | Hobigong, Natirpur, Sisu Mia | 2019-09-09 | NQ1003 | 9.6 | 226 | 9.6 | 227 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6384 | 2375.9997 | 101.1502
HBG-1.RR.572.1 | 24232019124365 | Hobigong, Natirpur, Al Amin | 2019-09-09 | NQ1003 | 14.2 | 228 | 13.4 | 229 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6384 | 2375.9997 | 141.1888
HBG-1.RR.573.1 | 24231959124366 | Hobigong, Natirpur, Babul Mia | 2019-09-09 | NQ1003 | 8.7 | 230 | 8.7 | 231 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6384 | 2375.9997 | 91.6674
HBG-1.RR.574.1 | 24231959124366 | Hobigong, Natirpur, Shaib Ali | 2019-09-09 | NQ1003 | 10.7 | 233 | 10.7 | 234 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6384 | 2375.9997 | 112.7403
HBG-1.RR.575.1 | 24231909124361 | Hobigong, Natirpur, Dudu Mia | 2019-09-09 | NQ1003 | 10.1 | 235 | 10.1 | 236 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6384 | 2375.9997 | 106.4185
HBG-1.RR.576.1 | 24231869124357 | Hobigong, Natirpur, Sohel | 2019-09-09 | NQ1003 | 2.3 | 239 | 2.3 | 240 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6384 | 2375.9997 | 24.2339
HBG-1.RR.577.1 | 24232329124461 | Hobigong, Chowdury Bazar, Rai Brothers | 2019-09-09 | NQ1003 | 8.6 | 241 | 8.6 | 242 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6336 | 2423.9997 | 90.6137
HBG-1.RR.578.1 | 24232329124461 | Hobigong, Chowdury Bazar, Noman Mia | 2019-09-09 | NQ1003 | 4.2 | 243 | 4.2 | 244 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6336 | 2423.9997 | 44.2532
HBG-1.RR.579.1 | 24232279124484 | Hobigong, Chowdury Bazar, Makun Chondro Bonik | 2019-09-09 | NQ1003 | 12.2 | 245 | 12.2 | 246 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6336 | 2423.9997 | 128.5451
HBG-1.RR.580.1 | 24232279124484 | Hobigong, Chowdury Bazar, Rupun Store | 2019-09-09 | NQ1003 | 10.3 | 247 | 10.3 | 248 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6336 | 2423.9997 | 108.5258
HBG-1.RR.581.1 | 24232269124490 | Hobigong, Chowdury Bazar, Abdul Jolil | 2019-09-09 | NQ1003 | 7.1 | 249 | 7.1 | 250 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6336 | 2423.9997 | 74.809
HBG-1.RR.582.1 | 24232269124490 | Hobigong, Chowdury Bazar, Taizur Rahman | 2019-09-09 | NQ1003 | 12.5 | 251 | 12 | 252 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6336 | 2423.9997 | 126.4378
HBG-1.RR.583.1 | 24232279124495 | Hobigong, Chowdury Bazar, Kamal Ahmed | 2019-09-09 | NQ1003 | 10.1 | 253 | 10.1 | 254 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6336 | 2423.9997 | 106.4185
HBG-1.RR.584.1 | 24232279124500 | Hobigong, Chowdury Bazar, Hazi Abdul Ali Chowdury Store | 2019-09-09 | NQ1003 | 12.9 | 255 | 12.9 | 256 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6336 | 2423.9997 | 135.9206
HBG-1.RR.585.1 | 24232049124542 | Habiganj, Chowdhury Bazar, Natirabad R/A, Md. Abdul Kader | 2019-09-11 | NQ1003 | 4 | 289 | 4 | 290 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6408 | 2351.9997 | 42.1459
HBG-1.RR.586.1 | 24232049124542 | Habiganj, Chowdhury Bazar, Natirabad R/A, Md. Abdul Solem | 2019-09-11 | NQ1003 | 8.3 | 291 | 8.3 | 292 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6408 | 2351.9997 | 87.4528
HBG-1.RR.586.2 | 24232049124542 | Habiganj, Chowdhury Bazar, Natirabad R/A, Md. Abdul Solem | 2021-08-28 | LU1001 | 21.8 | 7 | 21.8 | 8 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 21.8 | 21.8 | 1.308 | 1.308 | 0.0007168 | 100% | 0% | 1.308 | 1.308 | 0.0011869 | 28 | 0.026221 | 0.026221 |  | 0 | 0 | 6408 | 2351.9997 | 229.6953
HBG-1.RR.587.1 | 24232039124563 | Habiganj, Chowdhury Bazar, Natirabad R/A, Totul Nibas | 2019-09-11 | NQ1003 | 22.8 | 293 | 22.8 | 294 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 22.8 | 22.8 | 1.368 | 1.368 | 0.0007168 | 100% | 0% | 1.368 | 1.368 | 0.0011869 | 28 | 0.027424 | 0.027424 |  | 0 | 0 | 6432 | 2327.9997 | 240.2318
HBG-1.RR.588.1 | 24232039124563 | Habiganj, Chowdhury Bazar, Natirabad R/A, Totul Nibas | 2019-09-11 | NQ1003 | 2.4 | 295 | 2.4 | 296 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6432 | 2327.9997 | 25.2876
HBG-1.RR.589.1 | 24232049124566 | Habiganj, Natirabad Road, Natirabad R/A, H # 3001/1 | 2019-09-11 | NQ1003 | 6.7 | 297 | 6.7 | 298 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6432 | 2327.9997 | 70.5944
HBG-1.RR.590.1 | 24232119124577 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Md. Eidu Mia | 2019-09-11 | NQ1003 | 12.9 | 299 | 12.9 | 300 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6432 | 2327.9997 | 135.9206
HBG-1.RR.591.1 | 24232229124584 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Md. Musaedur Rohoman | 2019-09-11 | NQ1003 | 12.7 | 301 | 12.7 | 302 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6432 | 2327.9997 | 133.8133
HBG-1.RR.592.1 | 24232229124584 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Md. Abdul Hamid | 2019-09-11 | NQ1003 | 2.9 | 303 | 2.8 | 304 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6432 | 2327.9997 | 29.5021
HBG-1.RR.593.1 | 24232239125003 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Md. Sofiqul Islam | 2019-09-11 | NQ1003 | 20.8 | 305 | 20.8 | 306 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 20.8 | 20.8 | 1.248 | 1.248 | 0.0007168 | 100% | 0% | 1.248 | 1.248 | 0.0011869 | 28 | 0.025018 | 0.025018 |  | 0 | 0 | 6432 | 2327.9997 | 219.1588
HBG-1.RR.594.1 | 24232239125003 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Md. Abdur Roshid | 2019-09-11 | NQ1003 | 11.7 | 307 | 11.7 | 308 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6432 | 2327.9997 | 123.2768
HBG-1.RR.595.1 | 24232199125015 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Md. Abdul Malek | 2019-09-11 | NQ1003 | 7.1 | 309 | 7.1 | 310 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6432 | 2327.9997 | 74.809
HBG-1.RR.596.1 | 24232199125015 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Nahar Villa | 2019-09-11 | NQ1003 | 8 | 311 | 8 | 312 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6432 | 2327.9997 | 84.2919
HBG-1.RR.597.1 | 24232319125012 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Rohoman Sanu | 2019-09-11 | NQ1003 | 13.2 | 313 | 12.7 | 314 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6432 | 2327.9997 | 133.8133
HBG-1.RR.598.1 | 24232319125012 | Habiganj, Natirabad Road, Ward # 04, Natirabad R/A, Rohoman Sanu | 2019-09-11 | NQ1003 | 11.5 | 315 | 11.5 | 316 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6432 | 2327.9997 | 121.1695
HBG-1.RR.599.1 | 24232149124481 | Habiganj, Nayeber Pukur Par, Gourango Banik | 2019-09-12 | NQ1003 | 18.5 | 343 | 18.5 | 344 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6336 | 2423.9997 | 194.9249
HBG-1.RR.600.1 | 24231859124499 | Habiganj, Radhan Nagar, Jonaki Villa | 2019-09-12 | NQ1003 | 10.4 | 347 | 10.4 | 348 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6408 | 2351.9997 | 109.5794
HBG-1.RR.601.1 | 24163309127565 | Shayestaganj, South Lenjapara, Station Road, Nikhil Chandro | 2019-09-05 | NQ1002 | 10.1 | 65 | 10.1 | 66 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6816 | 1943.9997 | 106.4185
HBG-1.RR.602.1 | 24162909128037 | Shayestaganj, Shahbashpur, Station Road, Chowdhury Plaza | 2019-09-05 | NQ1002 | 33.5 | 67 | 34.5 | 68 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 34.5 | 34.5 | 2.07 | 2.07 | 0.0007168 | 100% | 0% | 2.07 | 2.07 | 0.0011869 | 28 | 0.041496 | 0.041496 |  | 0 | 0 | 6816 | 1943.9997 | 363.5086
HBG-1.RR.602.2 | 24162909128037 | Shayestaganj, Shahbashpur, Station Road, Chowdhury Plaza | 2020-10-20 | NQ1009 | 11 | 976 | 10.9 | 977 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6816 | 1943.9997 | 114.8476
HBG-1.RR.603.1 | 24175429130438 | Bahuball, Mirpur Bazar, Dhuliakhal Road, Kusum Ali | 2019-09-05 | NQ1002 | 27.2 | 69 | 27.2 | 70 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 27.2 | 27.2 | 1.632 | 1.632 | 0.0007168 | 100% | 0% | 1.632 | 1.632 | 0.0011869 | 28 | 0.032716 | 0.032716 |  | 0 | 0 | 6792 | 1967.9997 | 286.5923
HBG-1.RR.604.1 | 24175429130438 | Bahuball, Mirpur Bazar, Dhuliakhal Road, Avimoy | 2019-09-05 | NQ1002 | 18.9 | 71 | 18.9 | 72 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6792 | 1967.9997 | 199.1395
HBG-1.RR.605.1 | 24175429130438 | Bahuball, Mirpur Bazar, Dhuliakhal Road, Shafiqul Islam | 2019-09-05 | NQ1002 | 11.8 | 73 | 11.8 | 74 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6792 | 1967.9997 | 124.3305
HBG-1.RR.606.1 | 24174919131080 | Bahuball, Mirpur, Ijjotnagar, Noni Gopal | 2019-09-07 | NQ1002 | 20.2 | 95 | 20.2 | 96 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 20.2 | 20.2 | 1.212 | 1.212 | 0.0007168 | 100% | 0% | 1.212 | 1.212 | 0.0011869 | 28 | 0.024296 | 0.024296 |  | 0 | 0 | 6792 | 1967.9997 | 212.8369
HBG-1.RR.607.1 | 24174949131088 | Bahuball, Mirpur, Ijjotnagar, Bikash sen | 2019-09-07 | NQ1002 | 8.9 | 97 | 8.9 | 98 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6792 | 1967.9997 | 93.7747
HBG-1.RR.608.1 | 24175009130565 | Bahuball, Mirpur Bazar, Alauddin Mia | 2019-09-07 | NQ1002 | 10.3 | 99 | 10.3 | 100 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6792 | 1967.9997 | 108.5258
HBG-1.RR.609.1 | 24174939130550 | Bahuball, Mirpur Bazar, Arzu Mia | 2019-09-07 | NQ1002 | 14.3 | 101 | 14.4 | 102 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6792 | 1967.9997 | 151.7253
HBG-1.RR.610.1 | 24174889130553 | Bahuball, Mirpur Bazar, Beauty Begum | 2019-09-07 | NQ1002 | 8.2 | 103 | 8.2 | 104 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6792 | 1967.9997 | 86.3991
HBG-1.RR.611.1 | 24174889130553 | Bahuball, Mirpur Bazar, Iqbal Ahmed | 2019-09-07 | NQ1002 | 20.8 | 105 | 20.8 | 106 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 20.8 | 20.8 | 1.248 | 1.248 | 0.0007168 | 100% | 0% | 1.248 | 1.248 | 0.0011869 | 28 | 0.025018 | 0.025018 |  | 0 | 0 | 6792 | 1967.9997 | 219.1588
HBG-1.RR.612.1 | 24173589132188 | Bahuball, Notun Bazar, near by Jalalabad gas T&D system, Ibrahim Khan | 2019-09-07 | NQ1002 | 7.4 | 107 | 7.4 | 108 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6792 | 1967.9997 | 77.97
HBG-1.RR.613.1 | 24175669130379 | Bahuball, Mirpur, Sornorake, Shafiq Mia | 2019-09-07 | NQ1002 | 8.9 | 109 | 8.9 | 110 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6792 | 1967.9997 | 93.7747
HBG-1.RR.614.1 | 24175879130380 | Bahuball, Mirpur, Sornorake, Abdul Manik | 2019-09-07 | NQ1002 | 17.9 | 111 | 17.9 | 112 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 6792 | 1967.9997 | 188.603
HBG-1.RR.615.1 | 24175939130370 | Bahuball, Mirpur, Sornorake, Ahmod Ali | 2019-09-07 | NQ1002 | 9.6 | 113 | 9.9 | 114 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6792 | 1967.9997 | 104.3112
HBG-1.RR.616.1 | 24231269124222 | Hobiganj, Joser Abda, Khaddo Gudam Road, Abdur Rouf | 2019-09-08 | NQ1002 | 20 | 149 | 20 | 150 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 6384 | 2375.9997 | 210.7296
HBG-1.RR.617.1 | 24231279124212 | Hobiganj, Joser Abda, Khaddo Gudam Road, Azman Mia | 2019-09-08 | NQ1002 | 13.8 | 151 | 13.8 | 152 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6384 | 2375.9997 | 145.4034
HBG-1.RR.618.1 | 24231279124212 | Hobiganj, Joser Abda, Khaddo Gudam Road, Nur Islam | 2019-09-08 | NQ1002 | 18.4 | 153 | 18.4 | 154 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6384 | 2375.9997 | 193.8713
HBG-1.RR.619.1 | 24231279124212 | Hobiganj, Joser Abda, Khaddo Gudam Road, Yusuf Ali | 2019-09-08 | NQ1002 | 7.7 | 155 | 7.7 | 156 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6384 | 2375.9997 | 81.1309
HBG-1.RR.620.1 | 24231269124222 | Hobiganj, Joser Abda, Khaddo Gudam Road, Mokhlesur Rahman | 2019-09-08 | NQ1002 | 11 | 157 | 11.3 | 158 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6384 | 2375.9997 | 119.0622
HBG-1.RR.621.1 | 24231029124206 | Hobiganj, Joser Abda, ward# 2, Girindro chandro | 2019-09-08 | NQ1002 | 6.9 | 159 | 6.9 | 160 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6288 | 2471.9997 | 72.7017
HBG-1.RR.621.2 | 24231029124206 | Hobiganj, Joser Abda, ward# 2, Girindro chandro | 2022-09-20 | NQ1007 | 11.5 | 3 | 11.5 | 4 | 2022-09-20 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 0 | 2471.9997 | 34.193
HBG-1.RR.622.1 | 24231029124206 | Hobiganj, Joser Abda, ward# 2, Romakanto chandro | 2019-09-08 | NQ1002 | 8.6 | 161 | 8.6 | 162 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6288 | 2471.9997 | 90.6137
HBG-1.RR.623.1 | 24230909124199 | Hobiganj, Joser Abda, ward# 2, Digendro Das | 2019-09-08 | NQ1002 | 5.2 | 163 | 5.2 | 164 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6288 | 2471.9997 | 54.7897
HBG-1.RR.624.1 | 24230889124202 | Hobiganj, Joser Abda, ward# 2, Subol Das | 2019-09-08 | NQ1002 | 11.6 | 165 | 11.6 | 166 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6288 | 2471.9997 | 122.2232
HBG-1.RR.625.1 | 24230889124202 | Hobiganj, Joser Abda, ward# 2, Orun Chandro | 2019-09-08 | NQ1002 | 13.9 | 167 | 13.9 | 168 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6288 | 2471.9997 | 146.4571
HBG-1.RR.626.1 | 24230889124202 | Hobiganj, Joser Abda, ward# 2, Horipod Sorkar | 2019-09-08 | NQ1002 | 12.3 | 169 | 12.3 | 170 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6288 | 2471.9997 | 129.5987
HBG-1.RR.627.1 | 24230889124202 | Hobiganj, Joser Abda, ward# 2, Gowrango Sorkar | 2019-09-08 | NQ1002 | 20.6 | 171 | 20.6 | 172 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 20.6 | 20.6 | 1.236 | 1.236 | 0.0007168 | 100% | 0% | 1.236 | 1.236 | 0.0011869 | 28 | 0.024778 | 0.024778 |  | 0 | 0 | 6288 | 2471.9997 | 217.0515
HBG-1.RR.628.1 | 24230699124212 | Hobiganj, Joser Abda, ward# 2, Amor Das | 2019-09-08 | NQ1002 | 8.4 | 173 | 8.4 | 174 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6288 | 2471.9997 | 88.5064
HBG-1.RR.629.1 | 24230699124212 | Hobiganj, Joser Abda, ward# 2, Ojit Sorkar | 2019-09-08 | NQ1002 | 5.4 | 175 | 5.4 | 176 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6288 | 2471.9997 | 56.897
HBG-1.RR.630.1 | 24230699124212 | Hobiganj, Joser Abda, ward# 2, Gopal Roy | 2019-09-08 | NQ1002 | 7.2 | 177 | 7.2 | 178 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6288 | 2471.9997 | 75.8627
HBG-1.RR.631.1 | 24230579124217 | Hobiganj, Joser Abda, ward# 2, Babul Ray | 2019-09-08 | NQ1002 | 9.3 | 179 | 9.2 | 180 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6288 | 2471.9997 | 96.9356
HBG-1.RR.632.1 | 24230579124217 | Hobiganj, Joser Abda, ward# 2, Nishi Kanto | 2019-09-08 | NQ1002 | 17.6 | 181 | 17.6 | 182 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 6288 | 2471.9997 | 185.4421
HBG-1.RR.633.1 | 24230579124217 | Hobiganj, Joser Abda, ward# 2, Babul Sorkar | 2019-09-08 | NQ1002 | 6.8 | 183 | 6.9 | 184 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6288 | 2471.9997 | 72.7017
HBG-1.RR.633.2 | 24230579124217 | Hobiganj, Joser Abda, ward# 2, Babul Sorkar | 2020-10-07 | NQ1008 | 11.1 | 69 | 11.1 | 70 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6288 | 2471.9997 | 116.9549
HBG-1.RR.634.1 | 24230489124212 | Hobiganj, Joser Abda, ward# 2, Ajit Pal | 2019-09-08 | NQ1002 | 10.1 | 185 | 10.1 | 186 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6288 | 2471.9997 | 106.4185
HBG-1.RR.635.1 | 24230489124212 | Hobiganj, Joser Abda, ward# 2, Aruna Kuthir | 2019-09-08 | NQ1002 | 5.9 | 187 | 5.9 | 188 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6288 | 2471.9997 | 62.1652
HBG-1.RR.636.1 | 24230429124215 | Hobiganj, Joser Abda, Ward# 2, Ashim deb | 2019-09-09 | NQ1002 | 22.2 | 189 | 22.2 | 190 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 22.2 | 22.2 | 1.332 | 1.332 | 0.0007168 | 100% | 0% | 1.332 | 1.332 | 0.0011869 | 28 | 0.026702 | 0.026702 |  | 0 | 0 | 6288 | 2471.9997 | 233.9099
HBG-1.RR.637.1 | 24230429124215 | Hobiganj, Joser Abda, Ward# 2, Prodip Shil | 2019-09-09 | NQ1002 | 13.2 | 191 | 13.2 | 192 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6288 | 2471.9997 | 139.0816
HBG-1.RR.638.1 | 24230429124215 | Hobiganj, Joser Abda, Ward# 2, Sajal Bonik | 2019-09-09 | NQ1002 | 6.8 | 193 | 6.8 | 194 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6288 | 2471.9997 | 71.6481
HBG-1.RR.639.1 | 24230429124215 | Hobiganj, Joser Abda, Ward# 2, Sonju Das | 2019-09-09 | NQ1002 | 10.3 | 195 | 10.3 | 196 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6288 | 2471.9997 | 108.5258
HBG-1.RR.640.1 | 24230429124215 | Hobiganj, Joser Abda, Ward# 2, Ronjit Das | 2019-09-09 | NQ1002 | 6 | 197 | 5.8 | 198 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6288 | 2471.9997 | 61.1116
HBG-1.RR.641.1 | 24230359124218 | Hobiganj, Joser Abda, Ward# 2, Prodesh | 2019-09-09 | NQ1002 | 11.5 | 199 | 11.9 | 200 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6288 | 2471.9997 | 125.3841
HBG-1.RR.642.1 | 24230359124218 | Hobiganj, Joser Abda, Ward# 2, Nibaron Chakroboti | 2019-09-09 | NQ1002 | 8.4 | 201 | 8.2 | 202 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6288 | 2471.9997 | 86.3991
HBG-1.RR.643.1 | 24230359124218 | Hobiganj, Joser Abda, Ward# 2, Ramlal Das | 2019-09-09 | NQ1002 | 12.5 | 203 | 12.5 | 204 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6288 | 2471.9997 | 131.706
HBG-1.RR.644.1 | 24230399124233 | Hobiganj, Noyahati R/A, Ward# 3, Abul Sorkar | 2019-09-09 | NQ1002 | 12.6 | 205 | 12.6 | 206 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6288 | 2471.9997 | 132.7597
HBG-1.RR.645.1 | 24230439124254 | Hobiganj, Noyahati R/A, Ward# 3, Onjon Pal | 2019-09-09 | NQ1002 | 11.8 | 207 | 11.8 | 208 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6288 | 2471.9997 | 124.3305
HBG-1.RR.646.1 | 24230429124245 | Hobiganj, Noyahati R/A, Ward# 3, Matri Kuthir, Robita madok | 2019-09-09 | NQ1002 | 8.8 | 209 | 8.8 | 210 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6288 | 2471.9997 | 92.721
HBG-1.RR.647.1 | 24230489124235 | Hobiganj, Noyahati R/A, Ward# 3, Gopendro Sorkar | 2019-09-09 | NQ1002 | 9.6 | 211 | 9.6 | 212 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6288 | 2471.9997 | 101.1502
HBG-1.RR.648.1 | 24230489124235 | Hobiganj, Noyahati R/A, Ward# 3, Pranesh Ghosh | 2019-09-09 | NQ1002 | 11.4 | 213 | 11.4 | 214 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6288 | 2471.9997 | 120.1159
HBG-1.RR.649.1 | 24230559124234 | Hobiganj, Noyahati R/A, Ward# 3, Ripon Sorkar | 2019-09-09 | NQ1002 | 22.6 | 215 | 22.6 | 216 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 22.6 | 22.6 | 1.356 | 1.356 | 0.0007168 | 100% | 0% | 1.356 | 1.356 | 0.0011869 | 28 | 0.027183 | 0.027183 |  | 0 | 0 | 6288 | 2471.9997 | 238.1245
HBG-1.RR.650.1 | 24230559124234 | Hobiganj, Noyahati R/A, Ward# 3, Chondon Sorkar | 2019-09-09 | NQ1002 | 24.1 | 217 | 24.1 | 218 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 24.1 | 24.1 | 1.446 | 1.446 | 0.0007168 | 100% | 0% | 1.446 | 1.446 | 0.0011869 | 28 | 0.028987 | 0.028987 |  | 0 | 0 | 6288 | 2471.9997 | 253.9292
HBG-1.RR.651.1 | 24174889131133 | Mirpur, Sreemongol Road, Ijjotpur, Md. Abdullah | 2019-09-07 | NQ1002 | 8.3 | 89 | 8.3 | 90 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6792 | 1967.9997 | 87.4528
HBG-1.RR.651.2 | 24174889131133 | Mirpur, Sreemongol Road, Ijjotpur, Md. Abdullah | 2021-08-25 | LU1001 | 27.4 | 5 | 27.4 | 6 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 27.4 | 27.4 | 1.644 | 1.644 | 0.0007168 | 100% | 0% | 1.644 | 1.644 | 0.0011869 | 28 | 0.032957 | 0.032957 |  | 0 | 0 | 6792 | 1967.9997 | 288.6996
HBG-1.RR.652.1 | 24174789131119 | Mirpur, Sreemongol Road, Ijjotpur, Hazi Rois Ullah | 2019-09-07 | NQ1002 | 19.4 | 91 | 18.9 | 92 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6792 | 1967.9997 | 199.1395
HBG-1.RR.653.1 | 24174699131105 | Mirpur, Sreemongol Road, Ijjotpur, Nipesh Chandra Kaur | 2019-09-07 | NQ1002 | 6.5 | 93 | 6.5 | 94 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6792 | 1967.9997 | 68.4871
HBG-1.RR.654.1 | 24232629124266 | Habiganj, Bypass Road, Nearby New Bridge, Kamrapur, Aktar Uddin Badol | 2019-09-08 | NQ1002 | 58.2 | 115 | 58.2 | 116 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 58.2 | 58.2 | 3.492 | 3.492 | 0.0007168 | 100% | 0% | 3.492 | 3.492 | 0.0011869 | 28 | 0.070003 | 0.070003 |  | 0 | 0 | 6384 | 2375.9997 | 613.2232
HBG-1.RR.655.1 | 24232629124266 | Habiganj, Bypass Road, Nearby New Bridge, Kamrapur, Taijuddin | 2019-09-08 | NQ1002 | 35.8 | 117 | 35.8 | 118 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 35.8 | 35.8 | 2.148 | 2.148 | 0.0007168 | 100% | 0% | 2.148 | 2.148 | 0.0011869 | 28 | 0.04306 | 0.04306 |  | 0 | 0 | 6384 | 2375.9997 | 377.206
HBG-1.RR.656.1 | 24232629124266 | Habiganj, Bypass Road, Nearby New Bridge, Kamrapur, Abu Taher | 2019-09-08 | NQ1002 | 12.2 | 119 | 12.2 | 120 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6384 | 2375.9997 | 128.5451
HBG-1.RR.657.1 | 24232629124266 | Habiganj, Bypass Road, Nearby New Bridge, Kamrapur, Milon | 2019-09-08 | NQ1002 | 8.9 | 121 | 8.9 | 122 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6384 | 2375.9997 | 93.7747
HBG-1.RR.658.1 | 24232629124266 | Habiganj, Bypass Road, Nearby New Bridge, Kamrapur, Tofayel Ahmed | 2019-09-08 | NQ1002 | 2.9 | 123 | 2.9 | 124 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6384 | 2375.9997 | 30.5558
HBG-1.RR.659.1 | 24232669124264 | Habiganj, Bypass Road, Nearby New Bridge, Kamrapur, Khorshed Ali | 2019-09-08 | NQ1002 | 11.1 | 125 | 11.1 | 126 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6384 | 2375.9997 | 116.9549
HBG-1.RR.660.1 | 24232629124266 | Habiganj, Bypass Road, Nearby New Bridge, Kamrapur, Tuhin Mia | 2019-09-08 | NQ1002 | 6.6 | 127 | 6.4 | 128 | 2022-01-01 | [9 empty] | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0
HBG-1.RR.661.1 | 24232189124272 | Habiganj, Khaddogudam Road, Boglabazar, Doyel | 2019-09-08 | NQ1002 | 5.2 | 129 | 5.2 | 130 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6384 | 2375.9997 | 54.7897
HBG-1.RR.662.1 | 24232279124264 | Habiganj, Khaddogudam Road, Boglabazar, Mir Ahmed | 2019-09-08 | NQ1002 | 4.2 | 131 | 4.2 | 132 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6384 | 2375.9997 | 44.2532
HBG-1.RR.663.1 | 24232349124234 | Habiganj, Khaddogudam Road, Boglabazar, Tajul Islam | 2019-09-08 | NQ1002 | 1.4 | 133 | 1.4 | 134 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6384 | 2375.9997 | 14.7511
HBG-1.RR.664.1 | 24232349124234 | Habiganj, Khaddogudam Road, Boglabazar, Ahad Mia | 2019-09-08 | NQ1002 | 4.8 | 135 | 4.8 | 136 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6384 | 2375.9997 | 50.5751
HBG-1.RR.665.1 | 24232349124234 | Habiganj, Khaddogudam Road, Boglabazar, Shahid | 2019-09-08 | NQ1002 | 10.2 | 137 | 10.2 | 138 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6384 | 2375.9997 | 107.4721
HBG-1.RR.666.1 | 24231889124219 | Habiganj, Khaddogudam Road, Boglabazar, Joshor Abda, Mir Jalal | 2019-09-08 | NQ1002 | 11.4 | 139 | 11.4 | 140 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6384 | 2375.9997 | 120.1159
HBG-1.RR.667.1 | 24231479124208 | Habiganj, Khaddogudam Road, Boglabazar, Joshor Abda, Yunus Mia | 2019-09-08 | NQ1002 | 12.9 | 141 | 12.9 | 142 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6384 | 2375.9997 | 135.9206
HBG-1.RR.668.1 | 24231479124208 | Habiganj, Khaddogudam Road, Boglabazar, Joshor Abda, Aziz Mia | 2019-09-08 | NQ1002 | 5.2 | 143 | 5.2 | 144 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6384 | 2375.9997 | 54.7897
HBG-1.RR.669.1 | 24231379124222 | Habiganj, Khaddogudam Road, Boglabazar, Joshor Abda, Alain Mia | 2019-09-08 | NQ1002 | 11 | 145 | 11 | 146 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6384 | 2375.9997 | 115.9013
HBG-1.RR.670.1 | 24231379124222 | Habiganj, Khaddogudam Road, Boglabazar, Joshor Abda, Rizu | 2019-09-08 | NQ1002 | 8 | 147 | 8 | 148 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6384 | 2375.9997 | 84.2919
HBG-1.RR.670.2 | 24231379124222 | Habiganj, Khaddogudam Road, Boglabazar, Joshor Abda, Rizu | 2021-01-19 | LU1001 | 4.6 | 41 | 4.6 | 42 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6384 | 2375.9997 | 48.4678
HBG-1.RR.671.1 | 24231409124275 | Habiganj, Noahati, Hamida Khatun | 2019-09-09 | NQ1002 | 35.8 | 231 | 35.8 | 232 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 35.8 | 35.8 | 2.148 | 2.148 | 0.0007168 | 100% | 0% | 2.148 | 2.148 | 0.0011869 | 28 | 0.04306 | 0.04306 |  | 0 | 0 | 6384 | 2375.9997 | 377.206
HBG-1.RR.672.1 | 24231249124258 | Habiganj, Noahati, Radhamdhobjir Akhra | 2019-09-09 | NQ1002 | 8 | 233 | 8 | 234 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6384 | 2375.9997 | 84.2919
HBG-1.RR.673.1 | 24231239124258 | Habiganj, Noahati, Sreekanto Deb | 2019-09-09 | NQ1002 | 11.5 | 235 | 11.5 | 236 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6384 | 2375.9997 | 121.1695
HBG-1.RR.674.1 | 24231239124258 | Habiganj, Noahati, Narayan Ray | 2019-09-09 | NQ1002 | 5.2 | 237 | 5.2 | 238 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6384 | 2375.9997 | 54.7897
HBG-1.RR.675.1 | 24231209124249 | Habiganj, Noahati, Maa Varitey Store | 2019-09-09 | NQ1002 | 8 | 239 | 8 | 240 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6384 | 2375.9997 | 84.2919
HBG-1.RR.676.1 | 24231232424007 | Noahati, Fakol Sonkor | 2019-09-11 | NQ1011 | 5.2 | 61 | 5.2 | 62 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6384 | 2375.9997 | 54.7897
HBG-1.RR.677.1 | 24231349124242 | Noahati, Uttom Kumar | 2019-09-11 | NQ1011 | 13.2 | 63 | 13.2 | 64 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6384 | 2375.9997 | 139.0816
HBG-1.RR.678.1 | 24231349124242 | Noahati, Nunu Somajpoti | 2019-09-11 | NQ1011 | 8.1 | 65 | 8.1 | 66 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6384 | 2375.9997 | 85.3455
HBG-1.RR.679.1 | 24231349124242 | Noahati, Ramendro Somajpoti | 2019-09-11 | NQ1011 | 11.8 | 67 | 11.8 | 68 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6384 | 2375.9997 | 124.3305
HBG-1.RR.679.2 | 24231349124242 | Noahati, Ramendro Somajpoti | 2021-01-19 | LU1001 | 6.7 | 39 | 6.7 | 40 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6384 | 2375.9997 | 70.5944
HBG-1.RR.680.1 | 24231349124242 | Noahati, Norendro Chondro Deb | 2019-09-11 | NQ1011 | 19.2 | 69 | 19.2 | 70 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 19.2 | 19.2 | 1.152 | 1.152 | 0.0007168 | 100% | 0% | 1.152 | 1.152 | 0.0011869 | 28 | 0.023094 | 0.023094 |  | 0 | 0 | 6384 | 2375.9997 | 202.3004
HBG-1.RR.681.1 | 24231349124242 | Noahati, Sumon Somajpoti | 2019-09-11 | NQ1011 | 5.1 | 71 | 5.1 | 72 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6384 | 2375.9997 | 53.7361
HBG-1.RR.682.1 | 24231349124242 | Noahati, Manik Sarkar | 2019-09-11 | NQ1011 | 9.5 | 73 | 9.5 | 74 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6384 | 2375.9997 | 100.0966
HBG-1.RR.683.1 | 24231159124231 | Noahati, Shoronjit Roy | 2019-09-11 | NQ1011 | 7.6 | 75 | 7 | 76 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6384 | 2375.9997 | 73.7554
HBG-1.RR.684.1 | 24231159124231 | Noahati, Jogay Chandra | 2019-09-11 | NQ1011 | 12.1 | 79 | 11.9 | 80 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6384 | 2375.9997 | 125.3841
HBG-1.RR.685.1 | 24231159124231 | Noahati, Oshio Roy | 2019-09-11 | NQ1011 | 4.2 | 81 | 4.2 | 82 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6384 | 2375.9997 | 44.2532
HBG-1.RR.686.1 | 24230979124220 | Noahati, Bidhan Bonik | 2019-09-11 | NQ1011 | 23.6 | 83 | 23.6 | 84 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 23.6 | 23.6 | 1.416 | 1.416 | 0.0007168 | 100% | 0% | 1.416 | 1.416 | 0.0011869 | 28 | 0.028386 | 0.028386 |  | 0 | 0 | 6384 | 2375.9997 | 248.661
HBG-1.RR.687.1 | 24230979124220 | Noahati, Pobitro Sarkar | 2019-09-11 | NQ1011 | 5.1 | 85 | 5.1 | 86 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6384 | 2375.9997 | 53.7361
HBG-1.RR.688.1 | 24230979124220 | Noahati, Sojol Roy | 2019-09-11 | NQ1011 | 4.3 | 87 | 4.3 | 88 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6384 | 2375.9997 | 45.3069
HBG-1.RR.689.1 | 24230979124220 | Noahati, Somiron Sarkar | 2019-09-11 | NQ1011 | 17.7 | 89 | 17.7 | 90 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 6384 | 2375.9997 | 186.4957
HBG-1.RR.690.1 | 24230979124220 | Noahati, Sochindro Sarkar | 2019-09-11 | NQ1011 | 10.9 | 91 | 10.9 | 92 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6384 | 2375.9997 | 114.8476
HBG-1.RR.691.1 | 24225519124155 | Narayanpur, Jogodish Gop | 2019-09-12 | NQ1011 | 18.2 | 117 | 18.2 | 118 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 6288 | 2471.9997 | 191.764
HBG-1.RR.692.1 | 24225519124155 | Narayanpur, Nironjon Gop | 2019-09-12 | NQ1011 | 5.7 | 119 | 5.7 | 120 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6288 | 2471.9997 | 60.0579
HBG-1.RR.693.1 | 24225749124156 | Narayanpur, Rekha Gop | 2019-09-12 | NQ1011 | 5.6 | 121 | 5.7 | 122 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6288 | 2471.9997 | 60.0579
HBG-1.RR.694.1 | 24230099124129 | Narayanpur, Monodir Gop | 2019-09-12 | NQ1011 | 19.4 | 123 | 19.5 | 124 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 19.5 | 19.5 | 1.17 | 1.17 | 0.0007168 | 100% | 0% | 1.17 | 1.17 | 0.0011869 | 28 | 0.023454 | 0.023454 |  | 0 | 0 | 6288 | 2471.9997 | 205.4614
HBG-1.RR.694.2 | 24230099124129 | Narayanpur, Monodir Gop | 2021-01-19 | NQ1007 | 5.1 | 37 | 5.1 | 38 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6288 | 2471.9997 | 53.7361
HBG-1.RR.695.1 | 24230099124129 | Narayanpur, Mordor Gop | 2019-09-12 | NQ1011 | 8.7 | 125 | 8.7 | 126 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6288 | 2471.9997 | 91.6674
HBG-1.RR.695.2 | 24230099124129 | Narayanpur, Mordor Gop | 2021-01-19 | NQ1007 | 12.2 | 35 | 12.2 | 36 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6288 | 2471.9997 | 128.5451
HBG-1.RR.696.1 | 24230159124138 | Narayanpur, Sojol Gop | 2019-09-12 | NQ1011 | 7.3 | 127 | 7.3 | 128 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6288 | 2471.9997 | 76.9163
HBG-1.RR.697.1 | 24230159124138 | Narayanpur, Sopon Gpo | 2019-09-12 | NQ1011 | 9.3 | 129 | 9.3 | 130 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6288 | 2471.9997 | 97.9893
HBG-1.RR.698.1 | 24230259124135 | Narayanpur, Monmohon Gop | 2019-09-12 | NQ1011 | 5.6 | 131 | 5.6 | 132 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6288 | 2471.9997 | 59.0043
HBG-1.RR.699.1 | 24232069125002 | Habiganj, Natirabad, Nuabad Road, Abdul Momin | 2019-09-14 | NQ1003 | 9.2 | 395 | 9.2 | 396 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6432 | 2327.9997 | 96.9356
HBG-1.RR.700.1 | 24232019125009 | Habiganj, Natirabad, Nuabad Road, Abdul Ali | 2019-09-14 | NQ1003 | 13 | 397 | 13 | 398 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6432 | 2327.9997 | 136.9743
HBG-1.RR.700.2 | 24232019125009 | Habiganj, Natirabad, Nuabad Road, Abdul Ali | 2022-09-26 | NQ1007 | 13.1 | 22 | 13.1 | 23 | 2022-09-26 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 0 | 2327.9997 | 36.6814
HBG-1.RR.701.1 | 24224139124328 | Habiganj, Rajnagar, Jaduge Goly, H # 5420/3 | 2019-09-14 | MP1006 | 10.9 | 354 | 11 | 355 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6504 | 2255.9997 | 115.9013
HBG-1.RR.702.1 | 24224379124381 | Habiganj, Rajnagar, Mohila College Road, Ahona Complex | 2019-09-14 | MP1006 | 6.9 | 356 | 6.9 | 357 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6504 | 2255.9997 | 72.7017
HBG-1.RR.703.1 | 24224379124401 | Habiganj, Rajnagar, Mohila College Road, Aulia Complex | 2019-09-14 | MP1006 | 6.8 | 358 | 6.8 | 359 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6504 | 2255.9997 | 71.6481
HBG-1.RR.704.1 | 24224549124401 | Habiganj, Rajnagar, Mohila College Road, Jahingir | 2019-09-14 | MP1006 | 20.4 | 360 | 20.4 | 361 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 20.4 | 20.4 | 1.224 | 1.224 | 0.0007168 | 100% | 0% | 1.224 | 1.224 | 0.0011869 | 28 | 0.024537 | 0.024537 |  | 0 | 0 | 6504 | 2255.9997 | 214.9442
HBG-1.RR.705.1 | 24224079124402 | Habiganj, Rajnagar, College Road, Nazrul Islam | 2019-09-15 | MP1006 | 18.1 | 386 | 18.1 | 387 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6504 | 2255.9997 | 190.7103
HBG-1.RR.706.1 | 24224079124453 | Habiganj, Rajnagar, Master Quarter, Hemandro Vottacharjo | 2019-09-15 | MP1006 | 14.9 | 388 | 14.9 | 389 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6504 | 2255.9997 | 156.9936
HBG-1.RR.707.1 | 24224079124453 | Habiganj, Rajnagar, Master Quarter, Hemandro Vottacharjo | 2019-09-15 | MP1006 | 4.9 | 390 | 4.9 | 391 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6504 | 2255.9997 | 51.6288
HBG-1.RR.708.1 | 24224099124465 | Habiganj, Master Quarter, Onik-10/1 | 2019-09-15 | MP1006 | 4.9 | 392 | 4.9 | 393 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6504 | 2255.9997 | 51.6288
HBG-1.RR.709.1 | 24224129124469 | Habiganj, Master Quarter, Onik-9 | 2019-09-15 | MP1006 | 14.2 | 394 | 14.2 | 395 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6504 | 2255.9997 | 149.618
HBG-1.RR.710.1 | 24224129124469 | Habiganj, Master Quarter, Onik-30 | 2019-09-15 | MP1006 | 3.5 | 396 | 3.5 | 397 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6504 | 2255.9997 | 36.8777
HBG-1.RR.710.2 | 24224129124469 | Habiganj, Master Quarter, Onik-30 | 2021-01-17 | LU1001 | 3 | 31 | 3 | 32 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6504 | 2255.9997 | 31.6094
HBG-1.RR.711.1 | 24224129124469 | Habiganj, Master Quarter, Onik-30 | 2019-09-15 | MP1006 | 5.2 | 400 | 5.2 | 401 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6504 | 2255.9997 | 54.7897
HBG-1.RR.712.1 | 24224199124487 | Habiganj, Master Quarter, Richi Habili | 2019-09-15 | MP1006 | 4.5 | 402 | 4.5 | 403 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6504 | 2255.9997 | 47.4142
HBG-1.RR.713.1 | 24223979124477 | Habiganj, Master Quarter, Onik-11 | 2019-09-15 | MP1006 | 15.3 | 404 | 15.3 | 405 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6504 | 2255.9997 | 161.2082
HBG-1.RR.714.1 | 24223939124478 | Habiganj, Master Quarter, Onik-15/3 | 2019-09-15 | MP1006 | 12.4 | 406 | 12.4 | 407 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6504 | 2255.9997 | 130.6524
HBG-1.RR.715.1 | 24223849124477 | Habiganj, Master Quarter, Onik-16 | 2019-09-15 | MP1006 | 5.5 | 408 | 5.5 | 409 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6504 | 2255.9997 | 57.9506
HBG-1.RR.716.1 | 24223849124477 | Habiganj, Master Quarter, Onik-18 | 2019-09-15 | MP1006 | 7.4 | 410 | 7.4 | 411 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6504 | 2255.9997 | 77.97
HBG-1.RR.717.1 | 24223849124477 | Habiganj, Master Quarter, Onik-19 | 2019-09-15 | MP1006 | 3.6 | 412 | 3.6 | 413 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6504 | 2255.9997 | 37.9313
HBG-1.RR.718.1 | 24222079124494 | Court Station Road North, Bismillah Restaurant | 2019-09-15 | NQ1011 | 7.4 | 221 | 7.4 | 222 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6552 | 2207.9997 | 77.97
HBG-1.RR.719.1 | 24222079124494 | Court Station Road North, Maa Medicine Corner | 2019-09-15 | NQ1011 | 10 | 223 | 10 | 224 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6552 | 2207.9997 | 105.3648
HBG-1.RR.720.1 | 24221949124468 | Court Station Road North, Somir Ghosh | 2019-09-15 | NQ1011 | 6.8 | 225 | 6.8 | 226 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6552 | 2207.9997 | 71.6481
HBG-1.RR.721.1 | 24221789124469 | Court Station Road North, Dinendro Kumar Roy | 2019-09-15 | NQ1011 | 16 | 227 | 16 | 228 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6552 | 2207.9997 | 168.5837
HBG-1.RR.722.1 | 24221789124469 | Court Station Road North, Sujit Kumar Deb | 2019-09-15 | NQ1011 | 26.6 | 229 | 26.6 | 230 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 26.6 | 26.6 | 1.596 | 1.596 | 0.0007168 | 100% | 0% | 1.596 | 1.596 | 0.0011869 | 28 | 0.031994 | 0.031994 |  | 0 | 0 | 6552 | 2207.9997 | 280.2704
HBG-1.RR.723.1 | 24221669124487 | Court Station Road South, Bisnupodo Gop | 2019-09-15 | NQ1011 | 15.2 | 231 | 14.9 | 232 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6552 | 2207.9997 | 156.9936
HBG-1.RR.724.1 | 24221589124509 | Mohonpur R/A, Ronoprosad Achy. | 2019-09-15 | NQ1011 | 5.2 | 233 | 5.2 | 234 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6552 | 2207.9997 | 54.7897
HBG-1.RR.725.1 | 24221589124509 | Mohonpur R/A, Sohel Ahmed | 2019-09-15 | NQ1011 | 8.9 | 235 | 8.9 | 236 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6552 | 2207.9997 | 93.7747
HBG-1.RR.725.2 | 24221589124509 | Mohonpur R/A, Sohel Ahmed | 2021-08-31 | NQ1007 | 10.8 | 3 | 10.8 | 4 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6552 | 2207.9997 | 113.794
HBG-1.RR.726.1 | 24220579124567 | Habiganj, Mohonpur R/A, Sahin | 2019-09-16 | MP1006 | 8.7 | 493 | 8.7 | 494 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6600 | 2159.9997 | 91.6674
HBG-1.RR.727.1 | 24220579124567 | Habiganj, Mohonpur R/A, Mamun | 2019-09-16 | MP1006 | 9.4 | 495 | 9.4 | 496 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6600 | 2159.9997 | 99.0429
HBG-1.RR.728.1 | 24220519124555 | Habiganj, Mohonpur R/A, Moinuddin | 2019-09-16 | MP1006 | 12.1 | 497 | 12.1 | 498 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6600 | 2159.9997 | 127.4914
HBG-1.RR.728.2 | 24220519124555 | Habiganj, Mohonpur R/A, Moinuddin | 2019-09-16 | MP1006 | 6.5 | 499 | 6.5 | 500 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6600 | 2159.9997 | 68.4871
HBG-1.RR.729.1 | 24220499124545 | Habiganj, Mohonpur R/A, Afia Khatun | 2019-09-16 | MP1006 | 10.7 | 503 | 10.7 | 504 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6600 | 2159.9997 | 112.7403
HBG-1.RR.730.1 | 24220499124538 | Habiganj, Mohonpur R/A, Suna Mia | 2019-09-16 | MP1006 | 2.7 | 505 | 2.7 | 506 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6600 | 2159.9997 | 28.4485
HBG-1.RR.731.1 | 24220509124513 | Habiganj, Mohonpur R/A, Kashem | 2019-09-16 | MP1006 | 5.9 | 507 | 5.9 | 508 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6600 | 2159.9997 | 62.1652
HBG-1.RR.732.1 | 24220639124518 | Habiganj, Mohonpur R/A, Forida | 2019-09-16 | MP1006 | 11.8 | 509 | 11.8 | 510 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6600 | 2159.9997 | 124.3305
HBG-1.RR.733.1 | 24220649124516 | Habiganj, Mohonpur R/A, Manna | 2019-09-16 | MP1006 | 15.3 | 511 | 15.6 | 512 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6600 | 2159.9997 | 164.3691
HBG-1.RR.734.1 | 24220649124516 | Habiganj, Mohonpur R/A, Nurul | 2019-09-16 | MP1006 | 10.7 | 513 | 10.7 | 514 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6600 | 2159.9997 | 112.7403
HBG-1.RR.735.1 | 24220799124501 | Habiganj, Mohonpur R/A, M.A. Motin | 2019-09-17 | MP1006 | 12.6 | 539 | 12.6 | 540 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6600 | 2159.9997 | 132.7597
HBG-1.RR.736.1 | 24220799124501 | Habiganj, Mohonpur R/A, Babor Ali | 2019-09-17 | MP1006 | 32.3 | 541 | 32.3 | 542 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 32.3 | 32.3 | 1.938 | 1.938 | 0.0007168 | 100% | 0% | 1.938 | 1.938 | 0.0011869 | 28 | 0.03885 | 0.03885 |  | 0 | 0 | 6600 | 2159.9997 | 340.3283
HBG-1.RR.737.1 | 24220889124486 | Habiganj, Mohonpur R/A, Babul | 2019-09-17 | MP1006 | 10.4 | 543 | 10.4 | 544 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6600 | 2159.9997 | 109.5794
HBG-1.RR.737.2 | 24220889124486 | Habiganj, Mohonpur R/A, Babul | 2021-09-01 | NQ1007 | 7.1 | 5 | 7 | 6 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6600 | 2159.9997 | 73.7554
HBG-1.RR.738.1 | 24220889124486 | Habiganj, Mohonpur R/A, Arju Mia | 2019-09-17 | MP1006 | 5.9 | 545 | 5.5 | 546 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6600 | 2159.9997 | 57.9506
HBG-1.RR.738.2 | 24220889124486 | Habiganj, Mohonpur R/A, Arju Mia | 2021-01-13 | NQ1003 | 12.5 | 23 | 12.5 | 24 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6600 | 2159.9997 | 131.706
HBG-1.RR.739.1 | 24220889124486 | Habiganj, Mohonpur R/A, Abdul Ali | 2019-09-17 | MP1006 | 11 | 547 | 10.7 | 548 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 1392 | 0 | 5208 | 2159.9997 | 94.8254
HBG-1.RR.740.1 | 24220889124486 | Habiganj, Mohonpur R/A, Momin | 2019-09-17 | MP1006 | 12.1 | 549 | 11.9 | 550 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6600 | 2159.9997 | 125.3841
HBG-1.RR.741.1 | 24220889124486 | Habiganj, Mohonpur R/A, Taijul | 2019-09-17 | MP1006 | 19.1 | 551 | 19.1 | 552 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 6600 | 2159.9997 | 201.2468
HBG-1.RR.742.1 | 24220999124474 | Habiganj, Mohonpur R/A, H # 6124 | 2019-09-17 | MP1006 | 12.7 | 553 | 12.7 | 554 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6600 | 2159.9997 | 133.8133
HBG-1.RR.743.1 | 24220829124459 | Habiganj, Mohonpur R/A, H # 6120 | 2019-09-17 | MP1006 | 5.7 | 555 | 5.7 | 556 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6600 | 2159.9997 | 60.0579
HBG-1.RR.744.1 | 24220829124459 | Habiganj, Mohonpur R/A, Joudge Ali | 2019-09-17 | MP1006 | 5.8 | 557 | 5.8 | 558 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6600 | 2159.9997 | 61.1116
HBG-1.RR.745.1 | 24213549125048 | Habiganj, Nort Bahula, Hoshen Villa | 2019-09-18 | MP1006 | 10.2 | 617 | 10.2 | 618 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6720 | 2039.9997 | 107.4721
HBG-1.RR.746.1 | 24213549125048 | Habiganj, Nort Bahula, Forid Mia | 2019-09-18 | MP1006 | 10.7 | 619 | 10.8 | 620 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6720 | 2039.9997 | 113.794
HBG-1.RR.747.1 | 24212969124579 | Habiganj, Nort Bahula, Saidul | 2019-09-18 | MP1006 | 12.6 | 621 | 12.6 | 622 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6720 | 2039.9997 | 132.7597
HBG-1.RR.748.1 | 24212969124579 | Habiganj, Nort Bahula, Nurul | 2019-09-18 | MP1006 | 8.8 | 625 | 8.2 | 626 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6720 | 2039.9997 | 86.3991
HBG-1.RR.749.1 | 24230789124296 | Habiganj, Ganivg Park, Gourango | 2019-09-18 | MP1006 | 3.6 | 627 | 3.6 | 628 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6336 | 2423.9997 | 37.9313
HBG-1.RR.750.1 | 24230789124296 | Habiganj, Ganivg Park, P.K. Nibas | 2019-09-18 | MP1006 | 7.7 | 629 | 7.7 | 630 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6336 | 2423.9997 | 81.1309
HBG-1.RR.751.1 | 24223059124521 | Habiganj, Press Club Road, Aone Nibas, Advocate Afraz | 2019-09-14 | MP1006 | 13.5 | 370 | 13.5 | 371 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6576 | 2183.9997 | 142.2425
HBG-1.RR.751.2 | 24223059124521 | Habiganj, Press Club Road, Aone Nibas, Advocate Afraz | 2020-10-10 | NQ1009 | 1.6 | 377 | 1.6 | 378 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6576 | 2183.9997 | 16.8584
HBG-1.RR.752.1 | 24223129124523 | Habiganj, Press Club Road, Sinha Cottage, Ambia Khatun | 2019-09-14 | MP1006 | 13.6 | 372 | 13.2 | 373 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6576 | 2183.9997 | 139.0816
HBG-1.RR.753.1 | 24224799124308 | Habiganj, Rajnagor, Koborsthan Road, Soman Munju Wali | 2019-09-14 | MP1006 | 12.8 | 378 | 12.6 | 379 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6504 | 2255.9997 | 132.7597
HBG-1.RR.754.1 | 24224859124309 | Habiganj, Rajnagor, Koborsthan Road, Akbor Hosen | 2019-09-14 | MP1006 | 11.1 | 380 | 11.1 | 381 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6504 | 2255.9997 | 116.9549
HBG-1.RR.755.1 | 24224359124484 | Habiganj, Tinkona Pukur Par, Lokesh | 2019-09-14 | MP1006 | 11.3 | 382 | 11.3 | 383 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6504 | 2255.9997 | 119.0622
HBG-1.RR.756.1 | 24224329124484 | Habiganj, Tinkona Pukur Par, Additional Police Super Office | 2019-09-14 | MP1006 | 11.4 | 384 | 11.4 | 385 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6504 | 2255.9997 | 120.1159
HBG-1.RR.757.1 | 24222049124522 | Habiganj, Baby Stand, Fire Service Road, Mortu Mia | 2019-09-15 | MP1006 | 13.8 | 414 | 14 | 415 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6552 | 2207.9997 | 147.5107
HBG-1.RR.758.1 | 24221819124536 | Habiganj, Fire Service Road, Roshon Ali Vila | 2019-09-15 | MP1006 | 14.1 | 416 | 13.7 | 417 | 2022-01-01 | [9 empty] | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0
HBG-1.RR.759.1 | 24221569124534 | Habiganj, Fire Service Road, Ghoshpara, Sri Sri Gopinath Giur Akhra | 2019-09-15 | MP1006 | 11.7 | 418 | 11.7 | 419 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6552 | 2207.9997 | 123.2768
HBG-1.RR.760.1 | 24221569124534 | Habiganj, Fire Service Road, Ghoshpara, Advocate Narod Chandra Gop | 2019-09-15 | MP1006 | 4.5 | 420 | 4.5 | 421 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6552 | 2207.9997 | 47.4142
HBG-1.RR.761.1 | 24221619124525 | Habiganj, Fire Service Road, Ghoshpara, Nisit Ronjon Bhattacharjo | 2019-09-15 | MP1006 | 13.7 | 422 | 13.5 | 423 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6552 | 2207.9997 | 142.2425
HBG-1.RR.762.1 | 24221619124525 | Habiganj, Fire Service Road, Ghoshpara, Nisit Ronjon Bhattacharjo, Nidi pal | 2019-09-15 | MP1006 | 11.5 | 426 | 11.5 | 427 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6552 | 2207.9997 | 121.1695
HBG-1.RR.763.1 | 24221689124518 | Habiganj, Fire Service Road, Ghoshpara, Raju | 2019-09-15 | MP1006 | 11 | 428 | 11 | 429 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6552 | 2207.9997 | 115.9013
HBG-1.RR.764.1 | 24221689124518 | Habiganj, Fire Service Road, Ghoshpara, Raju | 2019-09-15 | MP1006 | 6.5 | 432 | 6.5 | 433 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6552 | 2207.9997 | 68.4871
HBG-1.RR.765.1 | 24221499124553 | Habiganj, Fire Service Road, Ghoshpara, Advocate Chowdhury Abdul High | 2019-09-15 | MP1006 | 5.5 | 434 | 5.5 | 435 | 2022-01-01 | [9 empty] | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 | 2022-03-10 12:00 | 0 | 0
HBG-1.RR.766.1 | 24221299124551 | Habiganj, Fire Service Road, Ghoshpara, Birendra Chandra Gop | 2019-09-15 | MP1006 | 7.3 | 438 | 7.3 | 439 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6552 | 2207.9997 | 76.9163
HBG-1.RR.767.1 | 24221289124564 | Habiganj, Fire Service Road, Ghoshpara, Jannat Tara | 2019-09-15 | MP1006 | 8.7 | 440 | 8.7 | 441 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6552 | 2207.9997 | 91.6674
HBG-1.RR.768.1 | 24221289124564 | Habiganj, Fire Service Road, Ghoshpara, Nasrin | 2019-09-15 | MP1006 | 21 | 442 | 21 | 443 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 21 | 21 | 1.26 | 1.26 | 0.0007168 | 100% | 0% | 1.26 | 1.26 | 0.0011869 | 28 | 0.025259 | 0.025259 |  | 0 | 0 | 6552 | 2207.9997 | 221.2661
HBG-1.RR.769.1 | 24221289124564 | Habiganj, Fire Service Road, Ghoshpara, Ayesha | 2019-09-15 | MP1006 | 14.7 | 446 | 14.7 | 447 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6552 | 2207.9997 | 154.8863
HBG-1.RR.770.1 | 24221269124568 | Habiganj, Fire Service Road, Ghoshpara, Nizaz | 2019-09-15 | MP1006 | 19.1 | 448 | 19.1 | 449 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 6552 | 2207.9997 | 201.2468
HBG-1.RR.771.1 | 24221389124570 | Habiganj, Fire Service Road, Ghoshpara, Hadi | 2019-09-15 | MP1006 | 10.5 | 450 | 10.5 | 451 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6552 | 2207.9997 | 110.6331
HBG-1.RR.772.1 | 24221389124570 | Habiganj, Fire Service Road, Ghoshpara, Tuhin | 2019-09-15 | MP1006 | 12.8 | 453 | 12.8 | 454 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6552 | 2207.9997 | 134.867
HBG-1.RR.773.1 | 24221569124587 | Habiganj, Fire Service Road, H # 19, Jahera Vila | 2019-09-16 | MP1006 | 11.6 | 455 | 11.6 | 456 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6552 | 2207.9997 | 122.2232
HBG-1.RR.774.1 | 24221659124587 | Habiganj, Fire Service Road, Advocate: Abdul Musabbir | 2019-09-16 | MP1006 | 11.5 | 457 | 11.5 | 458 | 2022-01-01 | [9 empty] | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0
HBG-1.RR.775.1 | 24221659124587 | Habiganj, Fire Service Road, Mokles Muntasir | 2019-09-16 | MP1006 | 6.2 | 459 | 6.2 | 460 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6552 | 2207.9997 | 65.3262
HBG-1.RR.776.1 | 24221659124587 | Habiganj, Fire Service Road, Shohid Chowdhury | 2019-09-16 | MP1006 | 4.9 | 461 | 4.9 | 462 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6552 | 2207.9997 | 51.6288
HBG-1.RR.777.1 | 24221169124570 | Habiganj, Mohonpur R/A, Bacchu | 2019-09-16 | MP1006 | 12.5 | 463 | 12.4 | 464 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6552 | 2207.9997 | 130.6524
HBG-1.RR.778.1 | 24221169124570 | Habiganj, Mohonpur R/A, Rabeya Cottage | 2019-09-16 | MP1006 | 9.8 | 465 | 9 | 466 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6552 | 2207.9997 | 94.8283
HBG-1.RR.779.1 | 24221059124572 | Habiganj, Mohonpur R/A, Ayub Ali Vila | 2019-09-16 | MP1006 | 12.3 | 467 | 12.1 | 468 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6552 | 2207.9997 | 127.4914
HBG-1.RR.780.1 | 24220889124551 | Habiganj, Mohonpur R/A, Zillur Mia | 2019-09-16 | MP1006 | 17.6 | 469 | 17.3 | 470 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 6552 | 2207.9997 | 182.2811
HBG-1.RR.781.1 | 24220969124551 | Habiganj, Mohonpur R/A, Hazi Bari, Hazi Abdul Khalek | 2019-09-16 | MP1006 | 9.6 | 471 | 9.6 | 472 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6552 | 2207.9997 | 101.1502
HBG-1.RR.782.1 | 24220969124551 | Habiganj, Mohonpur R/A, Hazi Bari, Hazi Abdul Khalek | 2019-09-16 | MP1006 | 6.4 | 473 | 6.4 | 474 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6552 | 2207.9997 | 67.4335
HBG-1.RR.783.1 | 24220969124551 | Habiganj, Mohonpur R/A, Hazi Bari, Hazi Abdul Khalek | 2019-09-16 | MP1006 | 12.6 | 475 | 12.3 | 476 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6552 | 2207.9997 | 129.5987
HBG-1.RR.784.1 | 24221059124548 | Habiganj, Mohonpur R/A, Abdul Hamid | 2019-09-16 | MP1006 | 3.3 | 477 | 3.3 | 478 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6552 | 2207.9997 | 34.7704
HBG-1.RR.785.1 | 24221059124548 | Habiganj, Mohonpur R/A, Altaf Ahmed | 2019-09-16 | MP1006 | 4.9 | 481 | 4.9 | 482 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6552 | 2207.9997 | 51.6288
HBG-1.RR.786.1 | 24221059124548 | Habiganj, Mohonpur R/A, Sajahan Ali | 2019-09-16 | MP1006 | 11.5 | 483 | 12 | 484 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6552 | 2207.9997 | 126.4378
HBG-1.RR.787.1 | 24221059124548 | Habiganj, Mohonpur R/A, Achiya | 2019-09-16 | MP1006 | 6.3 | 485 | 6.3 | 486 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6552 | 2207.9997 | 66.3798
HBG-1.RR.788.1 | 24221049124541 | Habiganj, Mohonpur R/A, Shahana | 2019-09-16 | MP1006 | 6.6 | 487 | 6.6 | 488 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6552 | 2207.9997 | 69.5408
HBG-1.RR.789.1 | 24220809124508 | Habiganj, Mohonpur R/A, Opposite of Jamiya Madrasa, Jamal Mia | 2019-09-16 | MP1006 | 11.5 | 489 | 11.5 | 490 | 2022-01-01 | [9 empty] | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0
HBG-1.RR.790.1 | 24220939124524 | Habiganj, Mohonpur R/A, Amena | 2019-09-16 | MP1006 | 13.1 | 491 | 13.1 | 492 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6552 | 2207.9997 | 138.0279
HBG-1.RR.791.1 | 24220369124548 | Habiganj, Mohonpur R/A, Hazi Azizul Haque | 2019-09-17 | MP1006 | 10.4 | 515 | 10.4 | 516 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6600 | 2159.9997 | 109.5794
HBG-1.RR.792.1 | 24220349124539 | Habiganj, Middle Mohonpur R/A, Aksir Mia | 2019-09-17 | MP1006 | 12.4 | 517 | 12.4 | 518 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6600 | 2159.9997 | 130.6524
HBG-1.RR.793.1 | 24220229124538 | Habiganj, Middle Mohonpur R/A, Julekha Khatun | 2019-09-17 | MP1006 | 10.8 | 519 | 10.8 | 520 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6600 | 2159.9997 | 113.794
HBG-1.RR.794.1 | 24220229124538 | Habiganj, Middle Mohonpur R/A, Hazi Azizul Rahaman | 2019-09-17 | MP1006 | 16.1 | 521 | 16.1 | 522 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6600 | 2159.9997 | 169.6373
HBG-1.RR.795.1 | 24220299124533 | Habiganj, Middle Mohonpur R/A, Shohid | 2019-09-17 | MP1006 | 9.1 | 523 | 9.1 | 524 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6600 | 2159.9997 | 95.882
HBG-1.RR.796.1 | 24220329124551 | Habiganj, Middle Mohonpur R/A, Abdul Aziz Younus | 2019-09-17 | MP1006 | 8.8 | 525 | 9 | 526 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6600 | 2159.9997 | 94.8283
HBG-1.RR.797.1 | 24220329124551 | Habiganj, Middle Mohonpur R/A, Abdul Aziz Younus | 2019-09-17 | MP1006 | 11.4 | 527 | 11.4 | 528 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6600 | 2159.9997 | 120.1159
HBG-1.RR.798.1 | 24220319124556 | Habiganj, Middle Mohonpur R/A, Manik | 2019-09-17 | MP1006 | 4.4 | 529 | 4.7 | 530 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6600 | 2159.9997 | 49.5215
HBG-1.RR.799.1 | 24220179124557 | Habiganj, Middle Mohonpur R/A, Alomgir | 2019-09-17 | MP1006 | 10.4 | 531 | 9.8 | 532 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6600 | 2159.9997 | 103.2575
HBG-1.RR.800.1 | 24220269124572 | Habiganj, Middle Mohonpur R/A, Forid Mia | 2019-09-17 | MP1006 | 9.8 | 533 | 9.8 | 534 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6600 | 2159.9997 | 103.2575
HBG-1.RR.801.1 | 24230779124556 | Habiganj, Gopinathpur(Chirakandi), Syed Kamrul Hasan | 2019-09-12 | NQ1003 | 13.8 | 385 | 13.8 | 386 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6408 | 2351.9997 | 145.4034
HBG-1.RR.802.1 | 24230809124564 | Habiganj, Gopinathpur(Chirakandi), Chamed Villa | 2019-09-12 | NQ1003 | 10.3 | 387 | 10.3 | 388 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6408 | 2351.9997 | 108.5258
HBG-1.RR.803.1 | 24231179124577 | Habiganj, Chirakandi(Bagan Bari), Bijoy Kumar Ray | 2019-09-12 | NQ1003 | 10.2 | 389 | 10.2 | 390 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6432 | 2327.9997 | 107.4721
HBG-1.RR.804.1 | 24231039124585 | Habiganj, Chirakandi(Bagan Bari), Mukul Kanti Chowdhury | 2019-09-12 | NQ1003 | 7.1 | 391 | 7.1 | 392 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6432 | 2327.9997 | 74.809
HBG-1.RR.805.1 | 24231069124583 | Habiganj, Chirakandi(Bagan Bari), Utfol Kumar Das | 2019-09-12 | NQ1003 | 12.3 | 393 | 12.3 | 394 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 1368 | 0 | 5064 | 2327.9997 | 109.36
HBG-1.RR.806.1 | 24232359125061 | Habiganj, Horipur, Nathirabadh Kaborstan Road, Rabi Barmon | 2019-09-14 | NQ1003 | 11.4 | 429 | 11.3 | 430 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6432 | 2327.9997 | 119.0622
HBG-1.RR.807.1 | 24232359125061 | Habiganj, Horipur, Nathirabadh Kaborstan Road, Sulokkhon | 2019-09-14 | NQ1003 | 10.1 | 431 | 9.7 | 432 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6432 | 2327.9997 | 102.2039
HBG-1.RR.808.1 | 24232359125061 | Habiganj, Horipur, Nathirabadh Kaborstan Road, Tapos Ray | 2019-09-14 | NQ1003 | 7.1 | 433 | 7.1 | 434 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6432 | 2327.9997 | 74.809
HBG-1.RR.808.2 | 24232359125061 | Habiganj, Horipur, Nathirabadh Kaborstan Road, Tapos Ray | 2021-08-29 | MN1018 | 10.2 | 5 | 10.2 | 6 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6432 | 2327.9997 | 107.4721
HBG-1.RR.809.1 | 24232299125086 | Habiganj, Horipur, Nathirabadh Kaborstan Road, Abdur Rashid | 2019-09-14 | NQ1003 | 6.9 | 435 | 6.9 | 436 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6432 | 2327.9997 | 72.7017
HBG-1.RR.810.1 | 24232299125086 | Habiganj, Horipur, Nathirabadh Kaborstan Road, Abdur Rashid | 2019-09-14 | NQ1003 | 11.9 | 437 | 11.7 | 438 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6432 | 2327.9997 | 123.2768
HBG-1.RR.811.1 | 24231889125053 | Habiganj, Horipur R/A, Hazi Mohammad Jitu Mia | 2019-09-14 | NQ1003 | 8.2 | 439 | 7.6 | 440 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6432 | 2327.9997 | 80.0773
HBG-1.RR.811.2 | 24231889125053 | Habiganj, Horipur R/A, Hazi Mohammad Jitu Mia | 2022-03-21 | LU1001 | 7.9 | 57 | 7.9 | 58 | 2022-03-21 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 4536 | 2327.9997 | 65.2223
HBG-1.RR.812.1 | 24231659125100 | Habiganj, Horipur R/A, Mohammad Afjal Mia | 2019-09-14 | NQ1003 | 10.8 | 441 | 10.8 | 442 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6432 | 2327.9997 | 113.794
HBG-1.RR.813.1 | 24231789125097 | Habiganj, Horipur R/A, Md. Nannu Mia | 2019-09-14 | NQ1003 | 9.4 | 443 | 9.4 | 444 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6432 | 2327.9997 | 99.0429
HBG-1.RR.813.2 | 24231789125097 | Habiganj, Horipur R/A, Md. Nannu Mia | 2021-08-29 | MN1018 | 6.2 | 7 | 6.2 | 8 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6432 | 2327.9997 | 65.3262
HBG-1.RR.814.1 | 24231789125097 | Habiganj, Horipur R/A, Md. Alauddin | 2019-09-14 | NQ1003 | 5.5 | 445 | 5.5 | 446 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6432 | 2327.9997 | 57.9506
HBG-1.RR.815.1 | 24231859125095 | Habiganj, Horipur R/A, Amir Ali | 2019-09-14 | NQ1003 | 11.2 | 447 | 10.9 | 448 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6432 | 2327.9997 | 114.8476
HBG-1.RR.816.1 | 24231919125097 | Habiganj, Horipur R/A, Baro Bari, Jonab Ali | 2019-09-14 | NQ1003 | 4.9 | 449 | 4.9 | 450 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6432 | 2327.9997 | 51.6288
HBG-1.RR.817.1 | 24231439125096 | Habiganj, Horipur R/A, Islam Nagar, Turab Ali | 2019-09-14 | NQ1003 | 2.9 | 451 | 2.9 | 452 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6432 | 2327.9997 | 30.5558
HBG-1.RR.818.1 | 24231199125069 | Habiganj, Uttor Shamoli R/A, Prosanti | 2019-09-14 | NQ1003 | 7.1 | 453 | 7.1 | 454 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6432 | 2327.9997 | 74.809
HBG-1.RR.819.1 | 24231019124495 | Hahiganj, Commercial Area, Chirakandi Road, Rafi Villa | 2019-09-15 | NQ1003 | 5.2 | 489 | 5.2 | 490 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6408 | 2351.9997 | 54.7897
HBG-1.RR.820.1 | 24231109124504 | Hahiganj, Commercial Area, Chirakandi Road, Imran Cottage | 2019-09-15 | NQ1003 | 4.5 | 491 | 4.5 | 492 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6408 | 2351.9997 | 47.4142
HBG-1.RR.821.1 | 24231119124510 | Hahiganj, Commercial Area, Chirakandi Road, Nehar Mansion | 2019-09-15 | NQ1003 | 11.9 | 493 | 11.7 | 494 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6408 | 2351.9997 | 123.2768
HBG-1.RR.822.1 | 24231219124522 | Hahiganj, Commercial Area, Chirakandi Road, Abdul Awal Swapan | 2019-09-15 | NQ1003 | 7.8 | 495 | 7.8 | 496 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6408 | 2351.9997 | 82.1846
HBG-1.RR.823.1 | 24230839124523 | Habiganj, Puran Munsefi R/A, Advocate Asraf Uddin Ahmed | 2019-09-15 | NQ1003 | 4.5 | 497 | 4.5 | 498 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6408 | 2351.9997 | 47.4142
HBG-1.RR.824.1 | 24230629124557 | Habiganj, Puran Munsefi R/A, Monir Mia | 2019-09-15 | NQ1003 | 10.1 | 499 | 10 | 500 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6408 | 2351.9997 | 105.3648
HBG-1.RR.825.1 | 24230589124552 | Habiganj, Puran Munsefi R/A, Syed Nurujjaman(Baytun Nur) | 2019-09-15 | NQ1003 | 5.8 | 501 | 5.8 | 502 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6408 | 2351.9997 | 61.1116
HBG-1.RR.826.1 | 24230589124552 | Habiganj, Puran Munsefi R/A, Syed Nurujjaman(Baytun Nur) | 2019-09-15 | NQ1003 | 10.8 | 503 | 10.1 | 504 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6408 | 2351.9997 | 106.4185
HBG-1.RR.827.1 | 24230479124598 | Habiganj, Uttor Shamoli R/A, Atiqur Rahman | 2019-09-15 | NQ1003 | 8.4 | 505 | 8.4 | 506 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6432 | 2327.9997 | 88.5064
HBG-1.RR.828.1 | 24230479124598 | Habiganj, Uttor Shamoli R/A, Khan Monjil | 2019-09-15 | NQ1003 | 6.9 | 507 | 6.9 | 508 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6432 | 2327.9997 | 72.7017
HBG-1.RR.829.1 | 24230479124598 | Habiganj, Uttor Shamoli R/A, Khatija Begum | 2019-09-15 | NQ1003 | 8.7 | 509 | 8.7 | 510 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6432 | 2327.9997 | 91.6674
HBG-1.RR.830.1 | 24230419125006 | Habiganj, Uttor Shamoli R/A, Jasim Uddin | 2019-09-15 | NQ1003 | 5.8 | 511 | 5.8 | 512 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6432 | 2327.9997 | 61.1116
HBG-1.RR.831.1 | 24231399124483 | Habiganj, Main Dakghar Area, Muktar Villa | 2019-09-16 | NQ1003 | 8.4 | 513 | 8.4 | 514 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6408 | 2351.9997 | 88.5064
HBG-1.RR.832.1 | 24230219124522 | Habiganj, Puran Munsefi R/A, Adom Ali | 2019-09-16 | NQ1003 | 12.8 | 515 | 12.9 | 516 | 2022-01-01 | 2022-09-28 | NQ1007 | 2.3 | 24 | 2.3 | 25 | 2022-09-28 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6480 | 2279.9997
HBG-1.RR.833.1 | 24230219124522 | Habiganj, Puran Munsefi R/A, Adom Ali | 2019-09-16 | NQ1003 | 8.5 | 517 | 8.5 | 518 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6480 | 2279.9997 | 89.5601
HBG-1.RR.834.1 | 24230139124527 | Habiganj, Puran Munsefi R/A, H # 4/B | 2019-09-16 | NQ1003 | 10.5 | 519 | 10.5 | 520 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6480 | 2279.9997 | 110.6331
HBG-1.RR.835.1 | 24230069124536 | Habiganj, Puran Munsefi R/A, Rehana Begum | 2019-09-16 | NQ1003 | 2.9 | 521 | 2.9 | 522 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6480 | 2279.9997 | 30.5558
HBG-1.RR.836.1 | 24230039124525 | Habiganj, Puran Munsefi R/A, Ranjit Kumar Ray | 2019-09-16 | NQ1003 | 8.6 | 523 | 8.6 | 524 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6480 | 2279.9997 | 90.6137
HBG-1.RR.837.1 | 24230299124509 | Habiganj, Puran Munsefi R/A, Shahab Uddin | 2019-09-16 | NQ1003 | 12.4 | 525 | 11.7 | 526 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 1776 | 0 | 4704 | 2279.9997 | 98.2837
HBG-1.RR.838.1 | 24225999124510 | Habiganj, Puran Munsefi R/A, Khairul Islam | 2019-09-16 | NQ1003 | 11.1 | 527 | 11.1 | 528 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6480 | 2279.9997 | 116.9549
HBG-1.RR.839.1 | 24225989124503 | Habiganj, Puran Munsefi R/A, James House | 2019-09-16 | NQ1003 | 13.2 | 529 | 12.9 | 530 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6480 | 2279.9997 | 135.9206
HBG-1.RR.840.1 | 24230459124543 | Habiganj, Puran Munsefi R/A, Timir Baron Shutrodhar | 2019-09-16 | NQ1003 | 6 | 531 | 6 | 532 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6480 | 2279.9997 | 63.2189
HBG-1.RR.840.2 | 24230459124543 | Habiganj, Puran Munsefi R/A, Timir Baron Shutrodhar | 2021-08-29 | NQ1007 | 11.7 | 1 | 11.7 | 2 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6480 | 2279.9997 | 123.2768
HBG-1.RR.841.1 | 24225889124505 | Habiganj, Puran Munsefi R/A, Morhum Abdur Rouf | 2019-09-17 | NQ1003 | 5.2 | 565 | 5.2 | 566 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6480 | 2279.9997 | 54.7897
HBG-1.RR.842.1 | 24225769124513 | Habiganj, Puran Munsefi R/A, Jhilpar, Orijit Chakroborti | 2019-09-17 | NQ1003 | 8.8 | 567 | 8.8 | 568 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6480 | 2279.9997 | 92.721
HBG-1.RR.843.1 | 24225649124507 | Habiganj, Puran Munsefi R/A, Jhilpar, Nurunnahar Chowdhury | 2019-09-17 | NQ1003 | 24.3 | 569 | 24.3 | 570 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 24.3 | 24.3 | 1.458 | 1.458 | 0.0007168 | 100% | 0% | 1.458 | 1.458 | 0.0011869 | 28 | 0.029228 | 0.029228 |  | 0 | 0 | 6480 | 2279.9997 | 256.0365
HBG-1.RR.844.1 | 24225439124517 | Habiganj, Puran Munsefi R/A, Jhilpar, Manik Ray | 2019-09-17 | NQ1003 | 13 | 571 | 13 | 572 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6480 | 2279.9997 | 136.9743
HBG-1.RR.845.1 | 24225829124514 | Habiganj, Puran Munsefi R/A, Abul Monsur | 2019-09-17 | NQ1003 | 6.8 | 573 | 6.8 | 574 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6480 | 2279.9997 | 71.6481
HBG-1.RR.846.1 | 24225889124525 | Habiganj, Puran Munsefi R/A, Khan Mohammad Noushad | 2019-09-17 | NQ1003 | 7 | 575 | 7 | 576 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6480 | 2279.9997 | 73.7554
HBG-1.RR.847.1 | 24225869124528 | Habiganj, Puran Munsefi R/A, Nurunnabi Mintu | 2019-09-17 | NQ1003 | 13 | 577 | 13 | 578 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6480 | 2279.9997 | 136.9743
HBG-1.RR.848.1 | 24230209124572 | Habiganj, Shamoli R/A, Kamal Ahmed | 2019-09-17 | NQ1003 | 7.6 | 579 | 7.6 | 580 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6432 | 2327.9997 | 80.0773
HBG-1.RR.849.1 | 24230209124572 | Habiganj, Shamoli R/A, Ambia Khatun | 2019-09-17 | NQ1003 | 15.6 | 581 | 15.6 | 582 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6432 | 2327.9997 | 164.3691
HBG-1.RR.850.1 | 24225609124554 | Habiganj, Shamoli R/A, Raju Villa, H # 4479 | 2019-09-18 | NQ1003 | 12.5 | 609 | 12.5 | 610 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6480 | 2279.9997 | 131.706
HBG-1.RR.851.1 | 24231809124497 | Habiganj, Radhan Nagar, Chira Kandi, Golden House | 2019-09-12 | NQ1003 | 10.6 | 349 | 10.6 | 350 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6408 | 2351.9997 | 111.6867
HBG-1.RR.852.1 | 24231669124503 | Habiganj, Radhan Nagar, Chira Kandi, Bisno Podo Gop | 2019-09-12 | NQ1003 | 9.8 | 351 | 9.4 | 352 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6408 | 2351.9997 | 99.0429
HBG-1.RR.853.1 | 24231689124516 | Habiganj, Radhan Nagar, Chira Kandi, Ronjit Pal | 2019-09-12 | NQ1003 | 10.4 | 353 | 10.4 | 354 | 2022-01-01 | [9 empty] | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0
HBG-1.RR.854.1 | 24231709124555 | Habiganj, Gopinathpur, Chira Kandi, Horimol Sutrodhor | 2019-09-12 | NQ1003 | 7.2 | 355 | 7.2 | 356 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6408 | 2351.9997 | 75.8627
HBG-1.RR.855.1 | 24231709124555 | Habiganj, Gopinathpur, Chira Kandi, Horidas Sutrodhor | 2019-09-12 | NQ1003 | 9.1 | 357 | 9.1 | 358 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6408 | 2351.9997 | 95.882
HBG-1.RR.856.1 | 24231869124540 | Habiganj, Gopinathpur, Chira Kandi, Manik Gosh | 2019-09-12 | NQ1003 | 16 | 359 | 16 | 360 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6408 | 2351.9997 | 168.5837
HBG-1.RR.857.1 | 24231869124540 | Habiganj, Gopinathpur, Chira Kandi, Mohitosh Pal Gong | 2019-09-12 | NQ1003 | 11.5 | 361 | 11.4 | 362 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6408 | 2351.9997 | 120.1159
HBG-1.RR.858.1 | 24231539124531 | Habiganj, Gopinathpur, Chira Kandi, Bondhon Bari, Tania | 2019-09-12 | NQ1003 | 8.4 | 363 | 8.5 | 364 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6408 | 2351.9997 | 89.5601
HBG-1.RR.859.1 | 24231539124531 | Habiganj, Gopinathpur, Chira Kandi, Narayan Pal | 2019-09-12 | NQ1003 | 20.4 | 365 | 20.4 | 366 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 20.4 | 20.4 | 1.224 | 1.224 | 0.0007168 | 100% | 0% | 1.224 | 1.224 | 0.0011869 | 28 | 0.024537 | 0.024537 |  | 0 | 0 | 6408 | 2351.9997 | 214.9442
HBG-1.RR.860.1 | 24230949124470 | Hobigonj, Ahsanieamision, Md. Rafiq Ahmed Choduary | 2019-09-16 | NQ1003 | 12.1 | 533 | 12.1 | 534 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6408 | 2351.9997 | 127.4914
HBG-1.RR.861.1 | 24230949124470 | Hobigonj, Ahsanieamision, Md. Rafiq Ahmed Choduary | 2019-09-16 | NQ1003 | 14.9 | 535 | 14.9 | 536 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6408 | 2351.9997 | 156.9936
HBG-1.RR.862.1 | 24230949124470 | Hobigonj, Ahsanieamision, Md. Rafiq Ahmed Choduary | 2019-09-16 | NQ1003 | 9.8 | 539 | 9.8 | 540 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6408 | 2351.9997 | 103.2575
HBG-1.RR.863.1 | 24230819124465 | Hobigonj, Ahsanieamision, Hazi Masuk Mia | 2019-09-16 | NQ1003 | 9.4 | 541 | 9.4 | 542 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6408 | 2351.9997 | 99.0429
HBG-1.RR.864.1 | 24230819124465 | Hobigonj, Ahsanieamision, Hazi Mortaza Ali | 2019-09-16 | NQ1003 | 11.5 | 543 | 11.5 | 544 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6408 | 2351.9997 | 121.1695
HBG-1.RR.865.1 | 24230819124465 | Hobigonj, Ahsanieamision, Hazi Mortaza Ali | 2019-09-16 | NQ1003 | 4.5 | 545 | 4.6 | 546 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6408 | 2351.9997 | 48.4678
HBG-1.RR.866.1 | 24230909124454 | Hobigonj, Ahsanieamision, Upondro Condro Sutrodor | 2019-09-16 | NQ1003 | 5.9 | 547 | 5.7 | 548 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6408 | 2351.9997 | 60.0579
HBG-1.RR.867.1 | 24230909124454 | Hobigonj, Ahsanieamision, Sudhanso Talukdur | 2019-09-16 | NQ1003 | 30.7 | 549 | 30.7 | 550 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 30.7 | 30.7 | 1.842 | 1.842 | 0.0007168 | 100% | 0% | 1.842 | 1.842 | 0.0011869 | 28 | 0.036926 | 0.036926 |  | 0 | 0 | 6408 | 2351.9997 | 323.47
HBG-1.RR.868.1 | 24231059124443 | Hobigonj, Ahsanieamision, Heron Nibas | 2019-09-16 | NQ1003 | 17 | 551 | 17 | 552 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 6408 | 2351.9997 | 179.1202
HBG-1.RR.869.1 | 24231159124449 | Hobigonj, Ahsanieamision, Firoza Begum | 2019-09-16 | NQ1003 | 5 | 553 | 5 | 554 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6408 | 2351.9997 | 52.6824
HBG-1.RR.870.1 | 24230779124488 | Hobigonj, Banizzik Area, Ashim | 2019-09-16 | NQ1003 | 10.4 | 555 | 10.4 | 556 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6408 | 2351.9997 | 109.5794
HBG-1.RR.871.1 | 24230679124483 | Hobigonj, Banizzik Area, Khokon | 2019-09-16 | NQ1003 | 6 | 557 | 6 | 558 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6408 | 2351.9997 | 63.2189
HBG-1.RR.872.1 | 24230679124483 | Hobigonj, Banizzik Area, Sajon gold Silpaloi | 2019-09-16 | NQ1003 | 8.8 | 559 | 8.8 | 560 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6408 | 2351.9997 | 92.721
HBG-1.RR.873.1 | 24230369124489 | Hobigonj, Banizzik Area, Annando Sit House | 2019-09-16 | NQ1003 | 10.8 | 561 | 10.8 | 562 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6480 | 2279.9997 | 113.794
HBG-1.RR.874.1 | 24230369124489 | Hobigonj, Banizzik Area, Aminur Nasa Khatun | 2019-09-16 | NQ1003 | 3.7 | 563 | 3.7 | 564 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6480 | 2279.9997 | 38.985
HBG-1.RR.875.1 | 24225389124552 | Hobigonj, South Samoli, Joshim Uddin | 2019-09-17 | NQ1003 | 22.8 | 583 | 22.8 | 584 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 22.8 | 22.8 | 1.368 | 1.368 | 0.0007168 | 100% | 0% | 1.368 | 1.368 | 0.0011869 | 28 | 0.027424 | 0.027424 |  | 0 | 0 | 6480 | 2279.9997 | 240.2318
HBG-1.RR.876.1 | 24225509124565 | Hobigonj, South Samoli, Mashuk Mia | 2019-09-17 | NQ1003 | 11.2 | 585 | 11.2 | 586 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6480 | 2279.9997 | 118.0086
HBG-1.RR.877.1 | 24225719124580 | Hobigonj, Samoli R/A, Jahan Monjil, H # 49/132 | 2019-09-17 | NQ1003 | 9.4 | 587 | 9.8 | 588 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6432 | 2327.9997 | 103.2575
HBG-1.RR.878.1 | 24225779124594 | Hobigonj, Samoli R/A, Homandro Vobon | 2019-09-17 | NQ1003 | 11.5 | 589 | 11.5 | 590 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6432 | 2327.9997 | 121.1695
HBG-1.RR.879.1 | 24225779124594 | Hobigonj, Samoli R/A, Fahad Vila, Anower Hossain | 2019-09-17 | NQ1003 | 10.9 | 591 | 10.9 | 592 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6432 | 2327.9997 | 114.8476
HBG-1.RR.880.1 | 24225539124581 | Hobigonj, Samoli R/A, Mahmuda Villa | 2019-09-17 | NQ1003 | 12.3 | 593 | 12.3 | 594 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6432 | 2327.9997 | 129.5987
HBG-1.RR.881.1 | 24225479125005 | Hobigonj, Goshia Nagor R/A, Sukur Ronjon | 2019-09-17 | NQ1003 | 12.4 | 595 | 12.4 | 596 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6480 | 2279.9997 | 130.6524
HBG-1.RR.881.2 | 24225479125005 | Hobigonj, Goshia Nagor R/A, Sukur Ronjon | 2021-01-16 | LU1001 | 7.5 | 22 | 7.5 | 23 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6480 | 2279.9997 | 79.0236
HBG-1.RR.882.1 | 24225479125005 | Hobigonj, Goshia Nagor R/A, Sibu Rishe | 2019-09-17 | NQ1003 | 12.1 | 597 | 12.1 | 598 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6480 | 2279.9997 | 127.4914
HBG-1.RR.883.1 | 24225519125012 | Hobigonj, Goshia Nagor, Badhol Rishe | 2019-09-17 | NQ1003 | 25.3 | 599 | 25.3 | 600 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 25.3 | 25.3 | 1.518 | 1.518 | 0.0007168 | 100% | 0% | 1.518 | 1.518 | 0.0011869 | 28 | 0.030431 | 0.030431 |  | 0 | 0 | 6480 | 2279.9997 | 266.573
HBG-1.RR.884.1 | 24225639125016 | Hobigonj, Goshia Nagor, Prodip Kumar | 2019-09-17 | NQ1003 | 16.7 | 601 | 16.7 | 602 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 6480 | 2279.9997 | 175.9592
HBG-1.RR.885.1 | 24225669125016 | Hobigonj, Goshia Nagor, Rakes Babu | 2019-09-17 | NQ1003 | 11.8 | 603 | 11.8 | 604 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6480 | 2279.9997 | 124.3305
HBG-1.RR.886.1 | 24225719125020 | Hobigonj, Goshia Nagor, Joy Dev Rishe | 2019-09-17 | NQ1003 | 12.8 | 605 | 12.8 | 606 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6480 | 2279.9997 | 134.867
HBG-1.RR.887.1 | 24225299125020 | Hobigonj, South Samoli, Azizmia Gong | 2019-09-18 | NQ1003 | 14.3 | 641 | 14.3 | 642 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6480 | 2279.9997 | 150.6717
HBG-1.RR.887.2 | 24225299125020 | Hobigonj, South Samoli, Azizmia Gong | 2021-08-29 | LX1011 | 21.6 | 84 | 21.6 | 85 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 6480 | 2279.9997 | 227.588
HBG-1.RR.888.1 | 24225279125015 | Hobigonj, South Samoli, Rokaya Begum | 2019-09-18 | NQ1003 | 9.6 | 645 | 9.6 | 646 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6480 | 2279.9997 | 101.1502
HBG-1.RR.889.1 | 24225209125019 | Hobigonj, South Samoli, Mahafuz Ahmed | 2019-09-18 | NQ1003 | 13.6 | 647 | 13.6 | 648 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6480 | 2279.9997 | 143.2961
HBG-1.RR.889.2 | 24225209125019 | Hobigonj, South Samoli, Mahafuz Ahmed | 2021-08-29 | LX1011 | 15.7 | 86 | 15.3 | 87 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6480 | 2279.9997 | 161.2082
HBG-1.RR.890.1 | 24225209125019 | Hobigonj, South Samoli, Turab Ali | 2019-09-18 | NQ1003 | 11 | 649 | 11 | 650 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6480 | 2279.9997 | 115.9013
HBG-1.RR.891.1 | 24225249125026 | Hobigonj, South Samoli, Rohaman Villa, Motiur Rahman | 2019-09-18 | NQ1003 | 14.8 | 651 | 14.8 | 652 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6480 | 2279.9997 | 155.9399
HBG-1.RR.892.1 | 24225419125047 | Hobigonj, South Samoli, Md. Abu Tahar Mir | 2019-09-18 | NQ1003 | 16.8 | 653 | 16.8 | 654 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6480 | 2279.9997 | 177.0129
HBG-1.RR.893.1 | 24225509125043 | Hobigonj, East Samoli, Md. Moina Mia | 2019-09-18 | NQ1003 | 11.5 | 655 | 11.4 | 656 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6480 | 2279.9997 | 120.1159
HBG-1.RR.894.1 | 24225519125039 | Hobigonj, East Samoli, Samsur Nahar Begum | 2019-09-18 | NQ1003 | 10.1 | 657 | 10.1 | 658 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6480 | 2279.9997 | 106.4185
HBG-1.RR.895.1 | 24225669125033 | Hobigonj, East Samoli, Siddik Ali | 2019-09-18 | NQ1003 | 11.3 | 659 | 11.3 | 660 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6480 | 2279.9997 | 119.0622
HBG-1.RR.896.1 | 24225809125019 | Hobigonj, East Samoli, Md. Abdul Korim | 2019-09-18 | NQ1003 | 13.6 | 661 | 13.6 | 662 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6480 | 2279.9997 | 143.2961
HBG-1.RR.897.1 | 24230059125016 | Hobigonj, East Samoli, Md. Samsur Haq | 2019-09-18 | NQ1003 | 10 | 663 | 10 | 664 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6480 | 2279.9997 | 105.3648
HBG-1.RR.898.1 | 24225239125039 | Hobigonj, Goshaipur R/A, Haq Villa | 2019-09-19 | NQ1003 | 11.7 | 667 | 11.7 | 668 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6480 | 2279.9997 | 123.2768
HBG-1.RR.899.1 | 24225279125054 | Hobigonj, Goshaipur R/A, Md. Salak Mia | 2019-09-19 | NQ1003 | 3.9 | 669 | 3.9 | 670 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6480 | 2279.9997 | 41.0923
HBG-1.RR.899.2 | 24225279125054 | Hobigonj, Goshaipur R/A, Md. Salak Mia | 2022-03-22 | LU1001 | 22.4 | 61 | 22.4 | 62 | 2022-03-22 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 22.4 | 22.4 | 1.344 | 1.344 | 0.0007168 | 100% | 0% | 1.344 | 1.344 | 0.0011869 | 28 | 0.026943 | 0.026943 |  | 0 | 0 | 4560 | 2279.9997 | 184.2874
HBG-1.RR.900.1 | 24225249125066 | Hobigonj, Goshaipur R/A, Mostofa Ali | 2019-09-19 | NQ1003 | 6.3 | 671 | 6.3 | 672 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6480 | 2279.9997 | 66.3798
HBG-1.RR.901.1 | 24230649124230 | Hobiganj, Noyahati R/A, Ward# 3, Horidash Sorkar | 2019-09-09 | NQ1002 | 19.2 | 219 | 19.2 | 220 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 19.2 | 19.2 | 1.152 | 1.152 | 0.0007168 | 100% | 0% | 1.152 | 1.152 | 0.0011869 | 28 | 0.023094 | 0.023094 |  | 0 | 0 | 6288 | 2471.9997 | 202.3004
HBG-1.RR.902.1 | 24230649124230 | Hobiganj, Noyahati R/A, Ward# 3, Motilal Sorkar | 2019-09-09 | NQ1002 | 17.1 | 221 | 17.1 | 222 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 6288 | 2471.9997 | 180.1738
HBG-1.RR.902.2 | 24230649124230 | Hobiganj, Noyahati R/A, Ward# 3, Motilal Sorkar | 2022-09-20 | NQ1007 | 10.3 | 5 | 10.3 | 6 | 2022-09-20 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 0 | 2471.9997 | 30.6251
HBG-1.RR.903.1 | 24230729124226 | Hobiganj, Noyahati R/A, Ward# 3, Rubel | 2019-09-09 | NQ1002 | 6 | 223 | 6 | 224 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6288 | 2471.9997 | 63.2189
HBG-1.RR.904.1 | 24230729124226 | Hobiganj, Noyahati R/A, Ward# 3, Suleka Rani Das | 2019-09-09 | NQ1002 | 9.6 | 225 | 9.6 | 226 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6288 | 2471.9997 | 101.1502
HBG-1.RR.905.1 | 24230729124226 | Hobiganj, Noyahati R/A, Ward# 3, Girindro Sorkar | 2019-09-09 | NQ1002 | 8.1 | 227 | 8 | 228 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6288 | 2471.9997 | 84.2919
HBG-1.RR.905.2 | 24230729124226 | Hobiganj, Noyahati R/A, Ward# 3, Girindro Sorkar | 2022-09-20 | NQ1007 | 6.8 | 7 | 6.8 | 8 | 2022-09-20 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 0 | 2471.9997 | 20.2185
HBG-1.RR.906.1 | 24230729124226 | Hobiganj, Noyahati R/A, Ward# 3, Sonkor Sorkar | 2019-09-09 | NQ1002 | 11.7 | 229 | 11.7 | 230 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6288 | 2471.9997 | 123.2768
HBG-1.RR.907.1 | 24230509124242 | Hobiganj, Noyahati R/A, Ward #3, Sunil Kuthir | 2019-09-11 | NQ1011 | 23.4 | 29 | 22.8 | 30 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 22.8 | 22.8 | 1.368 | 1.368 | 0.0007168 | 100% | 0% | 1.368 | 1.368 | 0.0011869 | 28 | 0.027424 | 0.027424 |  | 0 | 0 | 6288 | 2471.9997 | 240.2318
HBG-1.RR.908.1 | 24230779124256 | Hobiganj, Noyahati R/A, Ward #3, Omio Prova Debi | 2019-09-11 | NQ1011 | 12.7 | 31 | 12.7 | 32 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6288 | 2471.9997 | 133.8133
HBG-1.RR.909.1 | 24230739124264 | Hobiganj, Noyahati R/A, Ward# 3, Shamol Kanti Biswas | 2019-09-11 | NQ1011 | 12.3 | 33 | 12.3 | 34 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6288 | 2471.9997 | 129.5987
HBG-1.RR.910.1 | 24230739124264 | Hobiganj, Noyahati R/A, Ward #3, Roma Kanto Das | 2019-09-11 | NQ1011 | 7.1 | 35 | 7 | 36 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6288 | 2471.9997 | 73.7554
HBG-1.RR.911.1 | 24230829124246 | Hobiganj, Noyahati R/A, Ward #3, Babul Shah | 2019-09-11 | NQ1011 | 15.1 | 37 | 15.1 | 38 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6288 | 2471.9997 | 159.1009
HBG-1.RR.911.2 | 24230829124246 | Hobiganj, Noyahati R/A, Ward #3, Babul Shah | 2019-09-11 | NQ1011 | 10 | 39 | 10 | 40 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6288 | 2471.9997 | 105.3648
HBG-1.RR.912.1 | 24230069124225 | Hobiganj, Anwarpur R/A, Ward #3, Kimmot Ali | 2019-09-11 | NQ1011 | 11 | 41 | 11 | 42 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6288 | 2471.9997 | 115.9013
HBG-1.RR.912.2 | 24230069124225 | Hobiganj, Anwarpur R/A, Ward #3, Kimmot Ali | 2021-01-19 | NQ1007 | 5.7 | 39 | 5.7 | 40 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6288 | 2471.9997 | 60.0579
HBG-1.RR.913.1 | 24225789124236 | Hobiganj, Anwarpur R/A, Ward #3, Awal Mia | 2019-09-11 | NQ1011 | 10.7 | 43 | 10.3 | 44 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6288 | 2471.9997 | 108.5258
HBG-1.RR.914.1 | 24225789124236 | Hobiganj, Anwarpur R/A, Ward #3, Sawal Mia | 2019-09-11 | NQ1011 | 13.4 | 45 | 13.4 | 46 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6288 | 2471.9997 | 141.1888
HBG-1.RR.915.1 | 24225789124236 | Hobiganj, Anowarpur R/A, Ward #3, Sufiyan | 2019-09-11 | NQ1011 | 5.7 | 47 | 5.7 | 48 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6288 | 2471.9997 | 60.0579
HBG-1.RR.916.1 | 24225709124238 | Hobiganj, Anwarpur R/A, Ward #3, Amir Ali | 2019-09-11 | NQ1011 | 14 | 49 | 14.9 | 50 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6288 | 2471.9997 | 156.9936
HBG-1.RR.917.1 | 24225799124248 | Hobiganj, Anwarpur R/A, Ward #3, Ansob Ali | 2019-09-11 | NQ1011 | 12.5 | 51 | 12.5 | 52 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6288 | 2471.9997 | 131.706
HBG-1.RR.918.1 | 24225799124248 | Hobiganj, Anwarpur R/A, Ward #3, Yaar Hossain | 2019-09-11 | NQ1011 | 10 | 53 | 10.1 | 54 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6288 | 2471.9997 | 106.4185
HBG-1.RR.919.1 | 24225799124248 | Hobiganj, Anwarpur R/A, Ward #3, Salek Ahmed | 2019-09-11 | NQ1011 | 12 | 55 | 12 | 56 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6288 | 2471.9997 | 126.4378
HBG-1.RR.920.1 | 24225799124248 | Hobiganj, Anwarpur R/A, Ward #3, Jewel Ahmed | 2019-09-11 | NQ1011 | 9.2 | 57 | 9.2 | 58 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6288 | 2471.9997 | 96.9356
HBG-1.RR.921.1 | 24225699124249 | Hobiganj, Anwarpur R/A, Ward #3, Abdul Ajit | 2019-09-11 | NQ1011 | 12.8 | 59 | 13.6 | 60 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6288 | 2471.9997 | 143.2961
HBG-1.RR.922.1 | 24225859124249 | Hobiganj, Anwarpur R/A, Ward # 3, A. Shahid | 2019-09-12 | NQ1011 | 11.8 | 93 | 11.8 | 94 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6288 | 2471.9997 | 124.3305
HBG-1.RR.923.1 | 24225739124260 | Hobiganj, Anwarpur R/A, Ward # 3, Hasan Ali | 2019-09-12 | NQ1011 | 14 | 95 | 14 | 96 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6288 | 2471.9997 | 147.5107
HBG-1.RR.924.1 | 24225739124260 | Hobiganj, Anwarpur R/A, Ward # 3, Kazal Mia | 2019-09-12 | NQ1011 | 6.4 | 97 | 6.4 | 98 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6288 | 2471.9997 | 67.4335
HBG-1.RR.925.1 | 24225659124208 | Hobiganj, Anwarpur R/A, Ward # 3, Ashraf Ali | 2019-09-12 | NQ1011 | 12.3 | 99 | 12.3 | 100 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6288 | 2471.9997 | 129.5987
HBG-1.RR.926.1 | 24225539124226 | Hobiganj, Anwarpur R/A, Ward # 3, Amir Hossain | 2019-09-12 | NQ1011 | 12 | 101 | 12 | 102 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6288 | 2471.9997 | 126.4378
HBG-1.RR.927.1 | 24225539124226 | Hobiganj, Anwarpur R/A, Ward # 3, Dengu Mia | 2019-09-12 | NQ1011 | 12.6 | 103 | 12.3 | 104 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6288 | 2471.9997 | 129.5987
HBG-1.RR.928.1 | 24225749124212 | Hobiganj, Anwarpur R/A, Ward # 3, Shukkur Ali | 2019-09-12 | NQ1011 | 11.1 | 105 | 11.1 | 106 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6288 | 2471.9997 | 116.9549
HBG-1.RR.929.1 | 24225799124198 | Hobiganj, Anwarpur R/A, Ward # 3, Abdul Malek | 2019-09-12 | NQ1011 | 8.5 | 107 | 8.5 | 108 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6288 | 2471.9997 | 89.5601
HBG-1.RR.930.1 | 24225889124192 | Hobiganj, Anwarpur R/A, Ward # 3, Shahabuddin | 2019-09-12 | NQ1011 | 21.6 | 109 | 21.6 | 110 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 6288 | 2471.9997 | 227.588
HBG-1.RR.931.1 | 24225979124182 | Hobiganj, Anwarpur R/A, Ward # 3, Sejul Ali | 2019-09-12 | NQ1011 | 11.3 | 111 | 11.3 | 112 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6288 | 2471.9997 | 119.0622
HBG-1.RR.932.1 | 24225979124182 | Hobiganj, Anwarpur R/A, Ward # 3, Awal Mia | 2019-09-12 | NQ1011 | 10.2 | 113 | 10.2 | 114 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6288 | 2471.9997 | 107.4721
HBG-1.RR.933.1 | 24225249124240 | Hobiganj, Jalalabad Road, Noyaigao, Munsi Villa, Minnot Ali | 2019-09-12 | NQ1011 | 12.8 | 115 | 12.8 | 116 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6288 | 2471.9997 | 134.867
HBG-1.RR.934.1 | 24224199124376 | Hobiganj, Rajnagar R/A, College Road, Sopno Bilash, Taus Mia | 2019-09-14 | NQ1011 | 6.7 | 133 | 6.7 | 134 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6504 | 2255.9997 | 70.5944
HBG-1.RR.935.1 | 24224199124363 | Hobiganj, Rajnagar R/A, College Road, Mizanur Rahman | 2019-09-14 | NQ1011 | 11.3 | 135 | 11.3 | 136 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6504 | 2255.9997 | 119.0622
HBG-1.RR.936.1 | 24224079124370 | Hobiganj, Rajnagar R/A, College Road, Tanvir Ahammed | 2019-09-14 | NQ1011 | 8.6 | 137 | 8.6 | 138 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6504 | 2255.9997 | 90.6137
HBG-1.RR.937.1 | 24224079124370 | Hobiganj, Rajnagar R/A, College Road, Tanvir Ahammed | 2019-09-14 | NQ1011 | 13.6 | 139 | 13.6 | 140 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6504 | 2255.9997 | 143.2961
HBG-1.RR.938.1 | 24223999124367 | Hobiganj, Rajnagar R/A, College Road, Abdul Awal | 2019-09-14 | NQ1011 | 11 | 143 | 11 | 144 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6504 | 2255.9997 | 115.9013
HBG-1.RR.939.1 | 24223839124381 | Hobiganj, Rajnagar R/A, College Road, Motaleb Mia | 2019-09-14 | NQ1011 | 12.5 | 145 | 12.9 | 146 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6504 | 2255.9997 | 135.9206
HBG-1.RR.940.1 | 24223839124381 | Hobiganj, Rajnagar R/A, College Road, Mujibur Rahman Dilu | 2019-09-14 | NQ1011 | 9.3 | 147 | 9.3 | 148 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6504 | 2255.9997 | 97.9893
HBG-1.RR.941.1 | 24223839124381 | Hobiganj, Rajnagar R/A, College Road, Siddikur Rahman | 2019-09-14 | NQ1011 | 12.4 | 149 | 12.3 | 150 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6504 | 2255.9997 | 129.5987
HBG-1.RR.942.1 | 24223839124381 | Hobiganj, Rajnagar R/A, College Road, Habibur Rahman | 2019-09-14 | NQ1011 | 12.6 | 151 | 12.5 | 152 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6504 | 2255.9997 | 131.706
HBG-1.RR.943.1 | 24223569124369 | Hobiganj, Rajnagar R/A, Yatimkhana Road, Mujibur Rahman | 2019-09-14 | NQ1011 | 17 | 153 | 17 | 154 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 6504 | 2255.9997 | 179.1202
HBG-1.RR.944.1 | 24223569124369 | Hobiganj, Rajnagar R/A, Yatimkhana Road, Dhonai Ullah | 2019-09-14 | NQ1011 | 15.6 | 155 | 15.6 | 156 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6504 | 2255.9997 | 164.3691
HBG-1.RR.944.2 | 24223569124369 | Hobiganj, Rajnagar R/A, Yatimkhana Road, Dhonai Ullah | 2019-09-14 | NQ1011 | 26.9 | 157 | 26.9 | 158 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 26.9 | 26.9 | 1.614 | 1.614 | 0.0007168 | 100% | 0% | 1.614 | 1.614 | 0.0011869 | 28 | 0.032355 | 0.032355 |  | 0 | 0 | 6504 | 2255.9997 | 283.4313
HBG-1.RR.945.1 | 24223519124357 | Hobiganj, Rajnagar R/A, Yatimkhana Road, Humayun Kabir | 2019-09-14 | NQ1011 | 4.9 | 159 | 4.9 | 160 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6504 | 2255.9997 | 51.6288
HBG-1.RR.946.1 | 24223519124357 | Hobiganj, Rajnagar R/A, Yatimkhana Road, Joshim Uddin | 2019-09-14 | NQ1011 | 4.2 | 161 | 4.2 | 162 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6504 | 2255.9997 | 44.2532
HBG-1.RR.946.2 | 24223519124357 | Hobiganj, Rajnagar R/A, Yatimkhana Road, Joshim Uddin | 2022-03-24 | LU1001 | 12.7 | 82 | 12.7 | 83 | 2022-03-24 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 4536 | 2255.9997 | 103.7511
HBG-1.RR.947.1 | 24223279124363 | Hobiganj, Rajnagar R/A, Yatimkhana Road, ATM Dolon | 2019-09-14 | NQ1011 | 11.2 | 163 | 11.2 | 164 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 4512 | 0 | 1992 | 2255.9997 | 57.2261
HBG-1.RR.948.1 | 24223279124363 | Hobiganj, Rajnagar R/A, Yatimkhana Road, Principle Jahanara | 2019-09-14 | NQ1011 | 3.6 | 165 | 3.6 | 166 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6504 | 2255.9997 | 37.9313
HBG-1.RR.949.1 | 24223149124367 | Hobiganj, Rajnagar R/A, Yatimkhana Road, A. Kader | 2019-09-14 | NQ1011 | 11.2 | 167 | 10.7 | 168 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6504 | 2255.9997 | 112.7403
HBG-1.RR.950.1 | 24223469124419 | Hobiganj, College Road, Birds KG School | 2019-09-15 | NQ1011 | 12 | 187 | 11.9 | 188 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6576 | 2183.9997 | 125.3841
HBG-1.RR.951.1 | 24231919125013 | Habiganj, Natirabad, Nuabad Road, Siddik | 2019-09-14 | NQ1003 | 14.1 | 399 | 14.1 | 400 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6432 | 2327.9997 | 148.5644
HBG-1.RR.952.1 | 24231919125012 | Habiganj, Natirabad, Nuabad Road, Jamil Ahmmed | 2019-09-14 | NQ1003 | 13.6 | 401 | 13.6 | 402 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6432 | 2327.9997 | 143.2961
HBG-1.RR.953.1 | 24231789125007 | Habiganj, Natirabad, Nuabad Road, Jalaluddin | 2019-09-14 | NQ1003 | 12.8 | 403 | 12.8 | 404 | 2022-01-01 | 2022-09-26 | NQ1007 | 1.9 | 20 | 1.9 | 21 | 2022-09-26 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6432 | 2327.9997
HBG-1.RR.954.1 | 24231659125010 | Habiganj, Natirabad, Nuabad Road, Jalaluddin | 2019-09-14 | NQ1003 | 14.3 | 405 | 14.3 | 406 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6432 | 2327.9997 | 150.6717
HBG-1.RR.955.1 | 24231659125010 | Habiganj, Natirabad, Nuabad Road, Mohid | 2019-09-14 | NQ1003 | 11.8 | 407 | 11.5 | 408 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6432 | 2327.9997 | 121.1695
HBG-1.RR.956.1 | 24231659125010 | Habiganj, Natirabad, Nuabad Road, Shahid | 2019-09-14 | NQ1003 | 10.5 | 409 | 10.5 | 410 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6432 | 2327.9997 | 110.6331
HBG-1.RR.957.1 | 24231659125010 | Habiganj, Natirabad, Nuabad Road, Abdul Korim | 2019-09-14 | NQ1003 | 11.1 | 411 | 10.8 | 412 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6432 | 2327.9997 | 113.794
HBG-1.RR.958.1 | 24231499125005 | Habiganj, Natirabad, Nuabad Road, Nurul Haque | 2019-09-14 | NQ1003 | 6.5 | 413 | 6.5 | 414 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6432 | 2327.9997 | 68.4871
HBG-1.RR.959.1 | 24231499125005 | Habiganj, Natirabad, Nuabad Road, Shohel | 2019-09-14 | NQ1003 | 11.4 | 415 | 11.6 | 416 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6432 | 2327.9997 | 122.2232
HBG-1.RR.960.1 | 24231499125005 | Habiganj, Natirabad, Nuabad Road, Abdullah Mia | 2019-09-14 | NQ1003 | 12.1 | 417 | 12.1 | 418 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6432 | 2327.9997 | 127.4914
HBG-1.RR.961.1 | 24231499125005 | Habiganj, Natirabad, Nuabad Road, Nozrul Islam | 2019-09-14 | NQ1003 | 13.1 | 419 | 13.1 | 420 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6432 | 2327.9997 | 138.0279
HBG-1.RR.962.1 | 24231499125005 | Habiganj, Natirabad, Nuabad Road, Nurul Islam | 2019-09-14 | NQ1003 | 11.1 | 421 | 11.1 | 422 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6432 | 2327.9997 | 116.9549
HBG-1.RR.963.1 | 24231559125017 | Habiganj, Natirabad, Nuabad Road, Hossen Ahmmed | 2019-09-14 | NQ1003 | 12.9 | 423 | 12.9 | 424 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6432 | 2327.9997 | 135.9206
HBG-1.RR.965.1 | 24232179125055 | Habiganj, Horipur R/A, Ward # 04, Nur Mohammad | 2019-09-14 | NQ1003 | 13.8 | 427 | 13.8 | 428 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6432 | 2327.9997 | 145.4034
HBG-1.RR.966.1 | 24223539124353 | Rajnogor, Etimkhana Road, Md. Saiful Haque | 2019-09-14 | NQ1011 | 3 | 169 | 3 | 170 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6504 | 2255.9997 | 31.6094
HBG-1.RR.966.2 | 24223539124353 | Rajnogor, Etimkhana Road, Md. Saiful Haque | 2022-03-24 | LU1001 | 9.9 | 84 | 9.9 | 85 | 2022-03-24 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 4536 | 2255.9997 | 80.8769
HBG-1.RR.967.1 | 24223709124324 | Rajnogor, Etimkhana Road, H # 5457, Sajedur Rahman | 2019-09-14 | NQ1011 | 6.3 | 171 | 6.3 | 172 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6504 | 2255.9997 | 66.3798
HBG-1.RR.968.1 | 24223709124324 | Rajnogor, Etimkhana Road, Mosaddek Raja | 2019-09-14 | NQ1011 | 17.8 | 173 | 17.8 | 174 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 6504 | 2255.9997 | 187.5494
HBG-1.RR.969.1 | 24223799124348 | Rajnogor, Etimkhana Road, Ataur Raman | 2019-09-14 | NQ1011 | 12.4 | 175 | 12.9 | 176 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6504 | 2255.9997 | 135.9206
HBG-1.RR.970.1 | 24223799124348 | Rajnogor, Etimkhana Road, Saiful Alam | 2019-09-14 | NQ1011 | 7 | 177 | 7 | 178 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6504 | 2255.9997 | 73.7554
HBG-1.RR.971.1 | 24223319124325 | Rajnogor, Etimkhana Road, Mortuj Ali | 2019-09-14 | NQ1011 | 17.8 | 179 | 17.8 | 180 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 6504 | 2255.9997 | 187.5494
HBG-1.RR.971.2 | 24223319124325 | Rajnogor, Etimkhana Road, Mortuj Ali | 2022-09-29 | NQ1007 | 3.7 | 26 | 3.7 | 27 | 2022-09-29 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 0 | 2255.9997 | 10.04
HBG-1.RR.972.1 | 24223319124325 | Rajnogor, Etimkhana Road, Mojib | 2019-09-14 | NQ1011 | 9.6 | 181 | 9.6 | 182 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6504 | 2255.9997 | 101.1502
HBG-1.RR.973.1 | 24223119124335 | Rajnogor, Etimkhana Road, Bina | 2019-09-14 | NQ1011 | 2 | 185 | 2 | 186 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6504 | 2255.9997 | 21.073
HBG-1.RR.974.1 | 24232239124456 | Chowdhury Bazar, Business Area, Surjo Kanto Mojumdar | 2019-09-15 | NQ1003 | 7.9 | 455 | 7.9 | 456 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6336 | 2423.9997 | 83.2382
HBG-1.RR.975.1 | 24232239124456 | Chowdhury Bazar, Business Area, Abdur Rohim | 2019-09-15 | NQ1003 | 10.5 | 457 | 10.5 | 458 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6336 | 2423.9997 | 110.6331
HBG-1.RR.976.1 | 24232089124457 | Chowdhury Bazar, Business Area, Robin Store | 2019-09-15 | NQ1003 | 9.2 | 459 | 8.7 | 460 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6336 | 2423.9997 | 91.6674
HBG-1.RR.977.1 | 24232089124457 | Chowdhury Bazar, Business Area, Nayem Store | 2019-09-15 | NQ1003 | 7.4 | 461 | 7.4 | 462 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6336 | 2423.9997 | 77.97
HBG-1.RR.978.1 | 24232029124458 | Chowdhury Bazar, Business Area, Habib Store | 2019-09-15 | NQ1003 | 10.9 | 463 | 10.9 | 464 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6336 | 2423.9997 | 114.8476
HBG-1.RR.979.1 | 24232029124458 | Chowdhury Bazar, Business Area, Khondokar Berger | 2019-09-15 | NQ1003 | 11.7 | 465 | 11.7 | 466 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6336 | 2423.9997 | 123.2768
HBG-1.RR.980.1 | 24231929124462 | Chowdhury Bazar, Business Area, Amirul Haque | 2019-09-15 | NQ1003 | 17.7 | 467 | 18.4 | 468 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6336 | 2423.9997 | 193.8713
HBG-1.RR.981.1 | 24231549124487 | Chowdhury Bazar, Business Area, Cherekandi R/A, H # 04 | 2019-09-15 | NQ1003 | 4.6 | 469 | 4.7 | 470 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6408 | 2351.9997 | 49.5215
HBG-1.RR.982.1 | 24231549124498 | Chowdhury Bazar, Business Area, Cherekandi R/A, Madhuri Sutrodhor | 2019-09-15 | NQ1003 | 16.4 | 471 | 16.4 | 472 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6408 | 2351.9997 | 172.7983
HBG-1.RR.983.1 | 24231549124498 | Chowdhury Bazar, Business Area, Cherekandi R/A, Roma Kanto Modak | 2019-09-15 | NQ1003 | 12.5 | 473 | 12.5 | 474 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6408 | 2351.9997 | 131.706
HBG-1.RR.984.1 | 24231549124510 | Chowdhury Bazar, Business Area, Cherekandi R/A, Topon Roy | 2019-09-15 | NQ1003 | 10.9 | 475 | 10.9 | 476 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6408 | 2351.9997 | 114.8476
HBG-1.RR.985.1 | 24231309124538 | Chowdhury Bazar, Business Area, Cherekandi R/A, Gurango Roy | 2019-09-15 | NQ1003 | 22.6 | 477 | 22.6 | 478 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 22.6 | 22.6 | 1.356 | 1.356 | 0.0007168 | 100% | 0% | 1.356 | 1.356 | 0.0011869 | 28 | 0.027183 | 0.027183 |  | 0 | 0 | 6408 | 2351.9997 | 238.1245
HBG-1.RR.986.1 | 24231219124540 | Chowdhury Bazar, Cherekandi R/A, Korunamoy Chokroborty | 2019-09-15 | NQ1003 | 12.5 | 479 | 12.5 | 480 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6408 | 2351.9997 | 131.706
HBG-1.RR.987.1 | 24231229124524 | Chowdhury Bazar,Cherekandi R/A, Enamul Haque | 2019-09-15 | NQ1003 | 12 | 481 | 12.5 | 482 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6408 | 2351.9997 | 131.706
HBG-1.RR.988.1 | 24231269124521 | Chowdhury Bazar, Cherekandi R/A, Probal Shaha | 2019-09-15 | NQ1003 | 6.5 | 483 | 6.5 | 484 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6408 | 2351.9997 | 68.4871
HBG-1.RR.989.1 | 24231269124521 | Chowdhury Bazar, Cherekandi R/A, Bipul Chondro Shaha | 2019-09-15 | NQ1003 | 4.4 | 485 | 4.4 | 486 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6408 | 2351.9997 | 46.3605
HBG-1.RR.990.1 | 24231269124521 | Chowdhury Bazar, Cherekandi R/A, Rakhal Modok | 2019-09-15 | NQ1003 | 11.4 | 487 | 11.4 | 488 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6408 | 2351.9997 | 120.1159
HBG-1.RR.991.1 | 24221429124518 | Habiganj, Station Road, Mohonpur R/A, Sinekdha Villa | 2019-09-16 | NQ1011 | 14 | 237 | 14 | 238 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6552 | 2207.9997 | 147.5107
HBG-1.RR.992.1 | 24221379124527 | Habiganj, Station Road, Mohonpur R/A, Shofiuddin | 2019-09-16 | NQ1011 | 16.4 | 239 | 16.4 | 240 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6552 | 2207.9997 | 172.7983
HBG-1.RR.993.1 | 24221269124526 | Habiganj, Station Road, Mohonpur R/A, Mohibur Rahman | 2019-09-16 | NQ1011 | 11.9 | 241 | 11.9 | 242 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6552 | 2207.9997 | 125.3841
HBG-1.RR.994.1 | 24221269124526 | Habiganj, Station Road, Mohonpur R/A, Robiul Islam | 2019-09-16 | NQ1011 | 7.5 | 243 | 7 | 244 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6552 | 2207.9997 | 73.7554
HBG-1.RR.994.2 | 24221269124526 | Habiganj, Station Road, Mohonpur R/A, Robiul Islam | 2022-03-27 | LU1001 | 21.4 | 90 | 21.4 | 91 | 2022-03-27 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 4512 | 2207.9997 | 172.9715
HBG-1.RR.995.1 | 24221249124532 | Habiganj, Station Road, Mohonpur R/A, Moshrob Ali | 2019-09-16 | NQ1011 | 15.4 | 245 | 15.4 | 246 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6552 | 2207.9997 | 162.2618
HBG-1.RR.996.1 | 24221249124532 | Habiganj, Station Road, Mohonpur R/A, Abdur Rohim | 2019-09-16 | NQ1011 | 10.7 | 247 | 10.7 | 248 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6552 | 2207.9997 | 112.7403
HBG-1.RR.997.1 | 24221199124523 | Habiganj, Station Road, Mohonpur R/A, Begum Chan | 2019-09-16 | NQ1011 | 12 | 249 | 12 | 250 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6552 | 2207.9997 | 126.4378
HBG-1.RR.998.1 | 24221199124523 | Habiganj, Station Road, Mohonpur R/A, Hamjab Ali | 2019-09-16 | NQ1011 | 4.3 | 251 | 4.3 | 252 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6552 | 2207.9997 | 45.3069
HBG-1.RR.999.1 | 24221269124526 | Habiganj, Station Road, Mohonpur R/A, Morjina Begum | 2019-09-16 | NQ1011 | 6.9 | 253 | 6.9 | 254 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6552 | 2207.9997 | 72.7017
HBG-1.RR.1000.1 | 24221299124517 | Habiganj, Station Road, Mohonpur R/A, Edu Mia | 2019-09-16 | NQ1011 | 11 | 255 | 11 | 256 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6552 | 2207.9997 | 115.9013
HBG-1.RR.1001.1 | 24225759124306 | Habiganj, Shoshanghat Road, Aminul Islam | 2019-09-18 | MP1006 | 7.6 | 631 | 7.7 | 632 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6480 | 2279.9997 | 81.1309
HBG-1.RR.1002.1 | 24225759124306 | Habiganj, Shoshanghat Road, Shajahan | 2019-09-18 | MP1006 | 12.5 | 633 | 12.5 | 634 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6480 | 2279.9997 | 131.706
HBG-1.RR.1003.1 | 24225879124340 | Habiganj, Uttara R/A, Jahan Villa | 2019-09-18 | MP1006 | 12.1 | 635 | 11.6 | 636 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6480 | 2279.9997 | 122.2232
HBG-1.RR.1004.1 | 24212469125075 | Habiganj, Baro Bahula, Md. Jahir Mia | 2019-09-19 | MP1006 | 15.5 | 637 | 14.9 | 638 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6720 | 2039.9997 | 156.9936
HBG-1.RR.1005.1 | 24212469125075 | Habiganj, Baro Bahula, Md. Jahir Mia | 2019-09-19 | MP1006 | 12.1 | 639 | 12.1 | 640 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6720 | 2039.9997 | 127.4914
HBG-1.RR.1006.1 | 24212469125075 | Habiganj, Baro Bahula, Tofiq Mia | 2019-09-19 | MP1006 | 6.1 | 641 | 6.1 | 642 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6720 | 2039.9997 | 64.2725
HBG-1.RR.1007.1 | 24212119125070 | Habiganj, Baro Bahula, Faruk | 2019-09-19 | MP1006 | 3.8 | 643 | 3.8 | 644 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6720 | 2039.9997 | 40.0386
HBG-1.RR.1008.1 | 24212119125070 | Habiganj, Baro Bahula, Taijul Islam | 2019-09-19 | MP1006 | 6.6 | 645 | 6.1 | 646 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6720 | 2039.9997 | 64.2725
HBG-1.RR.1009.1 | 24212119125070 | Habiganj, Baro Bahula, Lotif | 2019-09-19 | MP1006 | 11.1 | 650 | 11.1 | 651 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6720 | 2039.9997 | 116.9549
HBG-1.RR.1010.1 | 24211939125069 | Habiganj, Baro Bahula, Mostofa | 2019-09-19 | MP1006 | 10.9 | 652 | 10.8 | 653 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6720 | 2039.9997 | 113.794
HBG-1.RR.1011.1 | 24211939125069 | Habiganj, Baro Bahula, Samsul Haque | 2019-09-19 | MP1006 | 4 | 654 | 4 | 655 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6720 | 2039.9997 | 42.1459
HBG-1.RR.1012.1 | 24211939125069 | Habiganj, Baro Bahula, Kobir | 2019-09-19 | MP1006 | 3.1 | 656 | 3.1 | 657 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6720 | 2039.9997 | 32.6631
HBG-1.RR.1013.1 | 24211849125093 | Habiganj, Baro Bahula, Kayes | 2019-09-19 | MP1006 | 13.9 | 658 | 13.9 | 659 | 2022-01-01 | 2022-10-08 | NQ1007 | 12.2 | 47 | 12.2 | 48 | 2022-10-08 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 96 | 0 | 6624 | 2039.9997
HBG-1.RR.1013.2 | 24211849125093 | Habiganj, Baro Bahula, Kayes | 2020-10-18 | NQ1003 | 5.6 | 44 | 5.6 | 45 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 96 | 0 | 6624 | 2039.9997 | 58.3577
HBG-1.RR.1014.1 | 24211849125093 | Habiganj, Baro Bahula, Jalal | 2019-09-19 | MP1006 | 12 | 660 | 12 | 661 | 2022-01-01 | 2022-10-08 | NQ1007 |  |  | 0 | 50 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6720 | 2039.9997
HBG-1.RR.1015.1 | 24211849125104 | Habiganj, Baro Bahula, Noman | 2019-09-19 | MP1006 | 13.7 | 662 | 13.7 | 663 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6720 | 2039.9997 | 144.3498
HBG-1.RR.1016.1 | 24211869125104 | Habiganj, Baro Bahula, Masud Mia | 2019-09-19 | MP1006 | 11.6 | 664 | 11.6 | 665 | 2022-01-01 | 2022-10-08 | NQ1007 |  |  | 0 | 51 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6720 | 2039.9997
HBG-1.RR.1017.1 | 24211869125104 | Habiganj, Baro Bahula, Shamim | 2019-09-19 | MP1006 | 14.3 | 666 | 14.3 | 667 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6720 | 2039.9997 | 150.6717
HBG-1.RR.1018.1 | 24224009124534 | Habiganj, Old Hospital Road, Azizur Rahaman | 2019-09-21 | MP1006 | 21.6 | 706 | 21.6 | 707 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 6504 | 2255.9997 | 227.588
HBG-1.RR.1019.1 | 24224009124534 | Habiganj, Old Hospital Road, Shodesh Biswas | 2019-09-21 | MP1006 | 11.9 | 708 | 11.9 | 709 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6504 | 2255.9997 | 125.3841
HBG-1.RR.1019.2 | 24224009124534 | Habiganj, Old Hospital Road, Shodesh Biswas | 2021-01-17 | NQ1007 | 4.4 | 23 | 4.4 | 24 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6504 | 2255.9997 | 46.3605
HBG-1.RR.1020.1 | 24223469124517 | Habiganj, Old Hospital Road, Neaj Muhammed | 2019-09-21 | MP1006 | 6.7 | 710 | 6.7 | 711 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6576 | 2183.9997 | 70.5944
HBG-1.RR.1021.1 | 24223469124517 | Habiganj, Old Hospital Road, Sofia Kashem | 2019-09-21 | MP1006 | 11.4 | 712 | 11.4 | 713 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6576 | 2183.9997 | 120.1159
HBG-1.RR.1022.1 | 24223469124517 | Habiganj, Old Hospital Road, H # 34 | 2019-09-21 | MP1006 | 20.3 | 714 | 20 | 715 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 6576 | 2183.9997 | 210.7296
HBG-1.RR.1023.1 | 24223469124517 | Habiganj, Old Hospital Road, Prodip Bonik | 2019-09-21 | MP1006 | 4.6 | 716 | 4.6 | 717 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6576 | 2183.9997 | 48.4678
HBG-1.RR.1024.1 | 24221379125179 | Habiganj, South Anantapur, Shohel | 2019-09-22 | MP1006 | 9.4 | 742 | 9.4 | 743 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6600 | 2159.9997 | 99.0429
HBG-1.RR.1025.1 | 24221379125179 | Habiganj, South Anantapur, Modina Bhabon | 2019-09-22 | MP1006 | 12.8 | 744 | 12.9 | 745 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6600 | 2159.9997 | 135.9206
HBG-1.RR.1026.1 | 24221299125199 | Habiganj, Mahamudabad R/A, H # 6778 | 2019-09-22 | MP1006 | 11.3 | 746 | 11.3 | 747 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6600 | 2159.9997 | 119.0622
HBG-1.RR.1027.1 | 24221539125197 | Habiganj, Mahamudabad R/A, Shoriful Islam | 2019-09-22 | MP1006 | 11.1 | 748 | 11.1 | 749 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6600 | 2159.9997 | 116.9549
HBG-1.RR.1028.1 | 24221539125197 | Habiganj, Mahamudabad R/A, Kutubuddin | 2019-09-22 | MP1006 | 7.9 | 750 | 7.9 | 751 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6600 | 2159.9997 | 83.2382
HBG-1.RR.1029.1 | 24221519125209 | Habiganj, South Anantapur, Shanto Nir | 2019-09-22 | MP1006 | 5.5 | 752 | 5.5 | 753 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6600 | 2159.9997 | 57.9506
HBG-1.RR.1030.1 | 24221349125222 | Habiganj, South Anantapur, H # 6752 | 2019-09-22 | MP1006 | 2.5 | 754 | 2.5 | 755 | 2022-01-01 | [9 empty] | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0
HBG-1.RR.1031.1 | 24221349125222 | Habiganj, South Anantapur, Sadek Mia | 2019-09-22 | MP1006 | 12.8 | 756 | 12.3 | 757 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6600 | 2159.9997 | 129.5987
HBG-1.RR.1032.1 | 24221349125222 | Habiganj, South Anantapur, H # 6775/1 | 2019-09-22 | MP1006 | 3.6 | 760 | 3.6 | 761 | 2022-01-01 | [9 empty] | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0
HBG-1.RR.1033.1 | 24221499125229 | Habiganj, South Anantapur, Mofezzel Ali | 2019-09-22 | MP1006 | 12.9 | 762 | 12.9 | 763 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6600 | 2159.9997 | 135.9206
HBG-1.RR.1034.1 | 24221159125185 | Habiganj, Mahamudabad R/A, Mamunur Rashid | 2019-09-23 | MP1006 | 27.9 | 764 | 27.9 | 765 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 27.9 | 27.9 | 1.674 | 1.674 | 0.0007168 | 100% | 0% | 1.674 | 1.674 | 0.0011869 | 28 | 0.033558 | 0.033558 |  | 0 | 0 | 6600 | 2159.9997 | 293.9678
HBG-1.RR.1035.1 | 24221159125185 | Habiganj, Mahamudabad R/A, Altafuddin | 2019-09-23 | MP1006 | 12.6 | 766 | 12.6 | 767 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6600 | 2159.9997 | 132.7597
HBG-1.RR.1036.1 | 24221029125194 | Habiganj, Mahamudabad R/A, Opposite Hanif Mia | 2019-09-23 | MP1006 | 8 | 768 | 8 | 769 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6600 | 2159.9997 | 84.2919
HBG-1.RR.1037.1 | 24221029125194 | Habiganj, Mahamudabad R/A, Chudhary Nibas | 2019-09-23 | MP1006 | 10.3 | 770 | 10.3 | 771 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6600 | 2159.9997 | 108.5258
HBG-1.RR.1038.1 | 24220949125204 | Habiganj, Mahamudabad R/A, H # 6791/4 | 2019-09-23 | MP1006 | 6.6 | 772 | 6.6 | 773 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6600 | 2159.9997 | 69.5408
HBG-1.RR.1039.1 | 24220799125213 | Habiganj, Mahamudabad R/A, Hena Monjil | 2019-09-23 | MP1006 | 7 | 774 | 7 | 775 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6600 | 2159.9997 | 73.7554
HBG-1.RR.1040.1 | 24220799125213 | Habiganj, Mahamudabad R/A, Abdul Ahad | 2019-09-23 | MP1006 | 10.6 | 776 | 10.6 | 777 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6600 | 2159.9997 | 111.6867
HBG-1.RR.1041.1 | 24220949125223 | Habiganj, Mahamudabad R/A, Alomgir | 2019-09-23 | MP1006 | 6.9 | 778 | 6.3 | 779 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6600 | 2159.9997 | 66.3798
HBG-1.RR.1042.1 | 24220749125208 | Habiganj, Mahamudabad R/A, Alauddin | 2019-09-23 | MP1006 | 10.8 | 780 | 10.8 | 781 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6600 | 2159.9997 | 113.794
HBG-1.RR.1043.1 | 24220749125208 | Habiganj, Mahamudabad R/A, Asraful | 2019-09-23 | MP1006 | 30.1 | 782 | 30.1 | 783 | 2022-01-01 | [9 empty] | 30.1 | 30.1 | 1.806 | 1.806 | 0.0007168 | 100% | 0% | 1.806 | 1.806 | 0.0011869 | 28 | 0.036204 | 0.036204 |  | 0 | 0
HBG-1.RR.1044.1 | 24220749125208 | Habiganj, Mahamudabad R/A, Milon | 2019-09-23 | MP1006 | 15.1 | 784 | 13.9 | 785 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6600 | 2159.9997 | 146.4571
HBG-1.RR.1045.1 | 24220719125216 | Habiganj, Mahamudabad R/A, Boshir Ahmed | 2019-09-23 | MP1006 | 8.5 | 786 | 8 | 787 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6600 | 2159.9997 | 84.2919
HBG-1.RR.1046.1 | 24221409125337 | Habiganj, Machuliya, Mohammad Ali | 2019-09-24 | MP1006 | 5.3 | 802 | 5.3 | 803 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6768 | 1991.9997 | 55.8434
HBG-1.RR.1047.1 | 24221479125320 | Habiganj, Machuliya, Ali Ahmmed | 2019-09-24 | MP1006 | 9.5 | 804 | 9.5 | 805 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6768 | 1991.9997 | 100.0966
HBG-1.RR.1048.1 | 24221529125326 | Habiganj, Machuliya, Nazmul | 2019-09-24 | MP1006 | 12.6 | 806 | 12.2 | 807 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 4632 | 0 | 2136 | 1991.9997 | 60.5747
HBG-1.RR.1049.1 | 24221709125329 | Habiganj, Machuliya, Mittunjoy Pal | 2019-09-24 | MP1006 | 11.3 | 808 | 11.3 | 809 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6768 | 1991.9997 | 119.0622
HBG-1.RR.1050.1 | 24221069125365 | Habiganj, Shaistanagar, Nur Jahan | 2019-09-24 | MP1006 | 16.9 | 810 | 16.9 | 811 | 2022-01-01 | 2022-10-10 | NQ1007 |  |  | 0 | 58 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6768 | 1991.9997
HBG-1.RR.1051.1 | 24220269124572 | Habiganj, Middle Mohonpur R/A, Abdul Kashem | 2019-09-17 | MP1006 | 9.2 | 535 | 8.8 | 536 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6600 | 2159.9997 | 92.721
HBG-1.RR.1052.1 | 24220269124572 | Habiganj, Middle Mohonpur R/A, Hazi Saidul | 2019-09-17 | MP1006 | 9.3 | 537 | 8.8 | 538 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6600 | 2159.9997 | 92.721
HBG-1.RR.1053.1 | 24215019125003 | Habiganj, Gopaya, Boro Bohula, Shah Forid Ahmed | 2019-09-18 | MP1006 | 11.3 | 571 | 11.3 | 572 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6672 | 2087.9997 | 119.0622
HBG-1.RR.1054.1 | 24215019125003 | Habiganj, Gopaya, Boro Bohula, Shah Mahbub | 2019-09-18 | MP1006 | 12.3 | 575 | 12 | 576 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6672 | 2087.9997 | 126.4378
HBG-1.RR.1055.1 | 24215019125003 | Habiganj, Gopaya, Boro Bohula, Shah Yousuf Ali | 2019-09-18 | MP1006 | 12.4 | 577 | 11.9 | 578 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6672 | 2087.9997 | 125.3841
HBG-1.RR.1056.1 | 24215019125003 | Habiganj, Gopaya, Boro Bohula, Shah Shahin | 2019-09-18 | MP1006 | 12.6 | 579 | 12.5 | 580 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6672 | 2087.9997 | 131.706
HBG-1.RR.1057.1 | 24215049125032 | Habiganj, Gopaya, Boro Bohula, Shah Alom | 2019-09-18 | MP1006 | 11.3 | 581 | 11.3 | 582 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6672 | 2087.9997 | 119.0622
HBG-1.RR.1058.1 | 24215049125032 | Habiganj, Gopaya, Boro Bohula, Shah Romzan Ali | 2019-09-18 | MP1006 | 12.6 | 583 | 12.4 | 584 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6672 | 2087.9997 | 130.6524
HBG-1.RR.1058.2 | 24215049125032 | Habiganj, Gopaya, Boro Bohula, Shah Romzan Ali | 2021-01-13 | LU1001 | 11.8 | 16 | 11.8 | 17 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6672 | 2087.9997 | 124.3305
HBG-1.RR.1059.1 | 24214629125065 | Habiganj, Gopaya, Boro Bohula, Nimbor Ali | 2019-09-18 | MP1006 | 3.8 | 585 | 3.9 | 586 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6672 | 2087.9997 | 41.0923
HBG-1.RR.1059.2 | 24214629125065 | Habiganj, Gopaya, Boro Bohula, Nimbor Ali | 2022-03-31 | LU1001 | 18.9 | 104 | 18.9 | 105 | 2022-03-31 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 4536 | 2087.9997 | 150.5822
HBG-1.RR.1060.1 | 24214509125050 | Habiganj, Gopaya, Boro Bohula, Full Mia | 2019-09-18 | MP1006 | 12.6 | 587 | 12.6 | 588 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6672 | 2087.9997 | 132.7597
HBG-1.RR.1061.1 | 24214109125066 | Habiganj, Gopaya, Boro Bohula, Khadija | 2019-09-18 | MP1006 | 2.5 | 589 | 2.5 | 590 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6672 | 2087.9997 | 26.3412
HBG-1.RR.1062.1 | 24213999125065 | Habiganj, Gopaya, Boro Bohula, Jetu Mia | 2019-09-18 | MP1006 | 7.1 | 593 | 7.1 | 594 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6672 | 2087.9997 | 74.809
HBG-1.RR.1063.1 | 24213939125064 | Habiganj, Gopaya, Boro Bohula, Kodir Ali | 2019-09-18 | MP1006 | 10.5 | 595 | 10.5 | 596 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6672 | 2087.9997 | 110.6331
HBG-1.RR.1063.2 | 24213939125064 | Habiganj, Gopaya, Boro Bohula, Kodir Ali | 2022-03-31 | LU1001 | 12 | 102 | 12 | 103 | 2022-03-31 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 4536 | 2087.9997 | 95.6077
HBG-1.RR.1064.1 | 24213839125060 | Habiganj, Gopaya, Boro Bohula, Abul Hosen | 2019-09-18 | MP1006 | 12.1 | 599 | 12.1 | 600 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6672 | 2087.9997 | 127.4914
HBG-1.RR.1065.1 | 24213839125060 | Habiganj, Gopaya, Boro Bohula, Khalek | 2019-09-18 | MP1006 | 10.1 | 601 | 10.1 | 602 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6672 | 2087.9997 | 106.4185
HBG-1.RR.1066.1 | 24213769125061 | Habiganj, Gopaya, Boro Bohula, Masuda | 2019-09-18 | MP1006 | 9.5 | 603 | 9.5 | 604 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6672 | 2087.9997 | 100.0966
HBG-1.RR.1067.1 | 24213499125091 | Habiganj, Gopaya, Boro Bohula, Yeakub Ali | 2019-09-18 | MP1006 | 4.6 | 605 | 4.6 | 606 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6720 | 2039.9997 | 48.4678
HBG-1.RR.1068.1 | 24213429125085 | Habiganj, Gopaya, Boro Bohula, Younus Ali | 2019-09-18 | MP1006 | 12.5 | 613 | 12.4 | 614 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6720 | 2039.9997 | 130.6524
HBG-1.RR.1069.1 | 24213429125085 | Habiganj, Gopaya, Boro Bohula, Abdul Hamid | 2019-09-18 | MP1006 | 9.9 | 615 | 10.6 | 616 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6720 | 2039.9997 | 111.6867
HBG-1.RR.1070.1 | 24211599125074 | Habiganj, Gopaya, Boro Bohula, Romzan Ali | 2019-09-19 | MP1006 | 10.5 | 670 | 10.8 | 671 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6720 | 2039.9997 | 113.794
HBG-1.RR.1071.1 | 24211669125052 | Habiganj, Gopaya, Boro Bohula, Rois Ali | 2019-09-19 | MP1006 | 12.6 | 672 | 12.6 | 673 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6720 | 2039.9997 | 132.7597
HBG-1.RR.1072.1 | 24211669125052 | Habiganj, Gopaya, Boro Bohula, Rois Ali | 2019-09-19 | MP1006 | 5.9 | 676 | 5.5 | 677 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6720 | 2039.9997 | 57.9506
HBG-1.RR.1073.1 | 24211339125050 | Habiganj, Gopaya, Boro Bohula, Shahabuddin | 2019-09-19 | MP1006 | 6.4 | 678 | 6.4 | 679 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6720 | 2039.9997 | 67.4335
HBG-1.RR.1074.1 | 24211339125034 | Habiganj, Gopaya, Boro Bohula, Modhu Mia | 2019-09-19 | MP1006 | 13.5 | 680 | 13.5 | 681 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6720 | 2039.9997 | 142.2425
HBG-1.RR.1075.1 | 24211539125026 | Habiganj, Gopaya, Boro Bohula, Indrojeet | 2019-09-19 | MP1006 | 6.6 | 682 | 6.1 | 683 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6720 | 2039.9997 | 64.2725
HBG-1.RR.1076.1 | 24211089124585 | Habiganj, Gopaya, Boro Bohula, Helal Ahmed | 2019-09-19 | MP1006 | 11 | 684 | 11 | 685 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6720 | 2039.9997 | 115.9013
HBG-1.RR.1077.1 | 24211129125024 | Habiganj, Gopaya, Boro Bohula, Motiur Rahman | 2019-09-19 | MP1006 | 3.3 | 686 | 3.3 | 687 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6720 | 2039.9997 | 34.7704
HBG-1.RR.1078.1 | 24224659124496 | Habiganj, Tinkona Pukurpar, Victorius Kg and High School, Mahbub Vila | 2019-09-21 | MP1006 | 2.9 | 688 | 2.9 | 689 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6504 | 2255.9997 | 30.5558
HBG-1.RR.1079.1 | 24224539124503 | Habiganj, Tinkona Pukurpar, Modina Kg and High School, Ruhul Amin Chairman | 2019-09-21 | MP1006 | 10.6 | 690 | 10.4 | 691 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6504 | 2255.9997 | 109.5794
HBG-1.RR.1080.1 | 24224319124533 | Habiganj, Tinkona Pukurpar, Sub-Tax Commissioner's Office | 2019-09-21 | MP1006 | 12.3 | 692 | 12.6 | 693 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6504 | 2255.9997 | 132.7597
HBG-1.RR.1081.1 | 24224619124535 | Habiganj, Muslim Quarter, H # 13/1, Muktadir Khan | 2019-09-21 | MP1006 | 11.8 | 694 | 12.2 | 695 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6504 | 2255.9997 | 128.5451
HBG-1.RR.1082.1 | 24224089124552 | Habiganj, Old Hospital Road, Jahed Lodge | 2019-09-21 | MP1006 | 15.2 | 696 | 15.2 | 697 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6504 | 2255.9997 | 160.1545
HBG-1.RR.1082.2 | 24224089124552 | Habiganj, Old Hospital Road, Jahed Lodge | 2022-09-29 | NQ1007 | 4.5 | 28 | 4.5 | 29 | 2022-09-29 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 0 | 2255.9997 | 12.2108
HBG-1.RR.1083.1 | 24224089124552 | Habiganj, Old Hospital Road, Jahed Lodge | 2019-09-21 | MP1006 | 11.3 | 698 | 11.3 | 699 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6504 | 2255.9997 | 119.0622
HBG-1.RR.1084.1 | 24224029124550 | Habiganj, Old Hospital Road, Iqbal | 2019-09-21 | MP1006 | 10.8 | 700 | 10.8 | 701 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6504 | 2255.9997 | 113.794
HBG-1.RR.1085.1 | 24223979124561 | Habiganj, Sobugbag R/A, Old Hospital Road, Chowdhury Bhabon, H # 63 | 2019-09-21 | MP1006 | 11.2 | 702 | 11.2 | 703 | 2022-01-01 | 2022-09-29 | NQ1007 | 3.9 | 30 | 3.9 | 31 | 2022-09-29 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6504 | 2255.9997
HBG-1.RR.1085.2 | 24223979124561 | Habiganj, Sobugbag R/A, Old Hospital Road, Chowdhury Bhabon, H # 63 | 2022-09-29 | NQ1007 | 5.7 | 32 | 5.7 | 33 | 2022-09-29 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 0 | 2255.9997 | 15.467
HBG-1.RR.1086.1 | 24223959124573 | Habiganj, Sobugbag R/A, Old Hospital Road, Astar Jahan Chowdhury | 2019-09-21 | MP1006 | 22.7 | 704 | 22 | 705 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 22 | 22 | 1.32 | 1.32 | 0.0007168 | 100% | 0% | 1.32 | 1.32 | 0.0011869 | 28 | 0.026461 | 0.026461 |  | 0 | 0 | 6504 | 2255.9997 | 231.8026
HBG-1.RR.1087.1 | 24221929125133 | Habiganj, Ananthopur R/A, Ward # 9, Badsha Mia | 2019-09-22 | MP1006 | 3.3 | 718 | 3.4 | 719 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6600 | 2159.9997 | 35.824
HBG-1.RR.1088.1 | 24221759125143 | Habiganj, Ananthopur R/A, Ward # 9, Rabeya Khatun | 2019-09-22 | MP1006 | 11.5 | 720 | 11.5 | 721 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6600 | 2159.9997 | 121.1695
HBG-1.RR.1089.1 | 24221759125143 | Habiganj, Ananthopur R/A, Ward # 9, Jahir Mia | 2019-09-22 | MP1006 | 2.8 | 722 | 2.8 | 723 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6600 | 2159.9997 | 29.5021
HBG-1.RR.1090.1 | 24221799125172 | Habiganj, South Ananthopur R/A, Abdur Rajjak | 2019-09-22 | MP1006 | 4 | 724 | 4 | 725 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6600 | 2159.9997 | 42.1459
HBG-1.RR.1091.1 | 24221799125172 | Habiganj, South Ananthopur R/A, Rojob Ali | 2019-09-22 | MP1006 | 7.5 | 726 | 7.6 | 727 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6600 | 2159.9997 | 80.0773
HBG-1.RR.1092.1 | 24221689125133 | Habiganj, Ananthopur R/A, Sumita Dotto | 2019-09-22 | MP1006 | 14.7 | 728 | 14.7 | 729 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6600 | 2159.9997 | 154.8863
HBG-1.RR.1092.2 | 24221689125133 | Habiganj, Ananthopur R/A, Sumita Dotto | 2021-01-14 | NQ1003 | 7.2 | 31 | 6.7 | 32 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6600 | 2159.9997 | 70.5944
HBG-1.RR.1093.1 | 24221629125153 | Habiganj, Ananthopur R/A, Piyas | 2019-09-22 | MP1006 | 4.7 | 730 | 4.7 | 731 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6600 | 2159.9997 | 49.5215
HBG-1.RR.1094.1 | 24221629125170 | Habiganj, Ananthopur R/A, Arju Mia | 2019-09-22 | MP1006 | 8.4 | 732 | 7.7 | 733 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6600 | 2159.9997 | 81.1309
HBG-1.RR.1095.1 | 24221519125183 | Habiganj, South Ananthopur R/A, Hasna Nibas, Rofique Uddin Chowdhury | 2019-09-22 | MP1006 | 12.4 | 734 | 12.6 | 735 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6600 | 2159.9997 | 132.7597
HBG-1.RR.1096.1 | 24221559125184 | Habiganj, South Ananthopur R/A, Elahi Bhaban, Md. Wahid Mia | 2019-09-22 | MP1006 | 10.9 | 736 | 10.9 | 737 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6600 | 2159.9997 | 114.8476
HBG-1.RR.1097.1 | 24221559125184 | Habiganj, South Ananthopur R/A, Ema Bhaban, Md. Mortuz Ali(Chairman) | 2019-09-22 | MP1006 | 5.8 | 738 | 5.8 | 739 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6600 | 2159.9997 | 61.1116
HBG-1.RR.1098.1 | 24221559125184 | Habiganj, South Ananthopur R/A, Khosru | 2019-09-22 | MP1006 | 5.2 | 740 | 5.3 | 741 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6600 | 2159.9997 | 55.8434
HBG-1.RR.1099.1 | 24220839125241 | Habiganj, Mahmudabad R/A, Soiyod Miftah Uddin Ahmed | 2019-09-23 | MP1006 | 9.9 | 788 | 9.9 | 789 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6768 | 1991.9997 | 104.3112
HBG-1.RR.1100.1 | 24220799125263 | Habiganj, Mahmudabad R/A, Motahar Hosen, H # 6812/1 | 2019-09-23 | MP1006 | 8.6 | 790 | 8.6 | 791 | 2022-01-01 | [9 empty] | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0
HBG-1.RR.1101.1 | 24225699124560 | Habiganj, Shamoli R/A, Hazi Samsu Mia Cottage | 2019-09-18 | NQ1003 | 11.3 | 611 | 11.3 | 612 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6480 | 2279.9997 | 119.0622
HBG-1.RR.1102.1 | 24225659124554 | Habiganj, Shamoli R/A, Swadesh Banik (Pushpita Kutir) | 2019-09-18 | NQ1003 | 8.4 | 613 | 8.4 | 614 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6480 | 2279.9997 | 88.5064
HBG-1.RR.1103.1 | 24225579124535 | Habiganj, Shamoli R/A, Mokarom Hosen (Hossain Villa) | 2019-09-18 | NQ1003 | 8.5 | 615 | 8.5 | 616 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6480 | 2279.9997 | 89.5601
HBG-1.RR.1104.1 | 24225729124541 | Habiganj, Shamoli R/A, Rahman Kutir | 2019-09-18 | NQ1003 | 12.3 | 617 | 12.3 | 618 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6480 | 2279.9997 | 129.5987
HBG-1.RR.1105.1 | 24225709124528 | Habiganj, Shamoli R/A, Kabir Ahmed | 2019-09-18 | NQ1003 | 9.5 | 621 | 9.5 | 622 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6480 | 2279.9997 | 100.0966
HBG-1.RR.1106.1 | 24225669124530 | Habiganj, Shamoli R/A, Yeakub Ali | 2019-09-18 | NQ1003 | 5.6 | 623 | 5.6 | 624 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6480 | 2279.9997 | 59.0043
HBG-1.RR.1107.1 | 24225669124530 | Habiganj, Shamoli R/A, Abdur Rouf | 2019-09-18 | NQ1003 | 10.2 | 625 | 10.8 | 626 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6480 | 2279.9997 | 113.794
HBG-1.RR.1108.1 | 24230309124579 | Habiganj, Shamoli R/A, Advocate Ataur Rahman | 2019-09-18 | NQ1003 | 9.5 | 627 | 9 | 628 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6432 | 2327.9997 | 94.8283
HBG-1.RR.1109.1 | 24230359124585 | Habiganj, Shamoli R/A, Golap Uddin | 2019-09-18 | NQ1003 | 6.9 | 629 | 6.9 | 630 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6432 | 2327.9997 | 72.7017
HBG-1.RR.1110.1 | 24230729125000 | Habiganj, North Shamoli R/A, Mohammad Abu Sufiyan | 2019-09-18 | NQ1003 | 10.1 | 631 | 10.1 | 632 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6432 | 2327.9997 | 106.4185
HBG-1.RR.1111.1 | 24230579125006 | Habiganj, North Shamoli R/A, Anamul Haque | 2019-09-18 | NQ1003 | 9.1 | 633 | 9.1 | 634 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6432 | 2327.9997 | 95.882
HBG-1.RR.1112.1 | 24230579125006 | Habiganj, North Shamoli R/A, Talukdar Villa | 2019-09-18 | NQ1003 | 10.2 | 635 | 10.2 | 636 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6432 | 2327.9997 | 107.4721
HBG-1.RR.1113.1 | 24230679125044 | Habiganj, North Shamoli R/A, Guljar Hosen Babul | 2019-09-18 | NQ1003 | 12.4 | 637 | 12.7 | 638 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6432 | 2327.9997 | 133.8133
HBG-1.RR.1114.1 | 24230669125042 | Habiganj, North Shamoli R/A, Hossain Mohammad Pathan | 2019-09-18 | NQ1003 | 14 | 639 | 14 | 640 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6432 | 2327.9997 | 147.5107
HBG-1.RR.1115.1 | 24163739126579 | Saistaganj, South Borchor, talugary, Station Road, Hazi Safiqur Rahman | 2019-09-19 | NQ1003 | 12.5 | 665 | 12.5 | 666 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6624 | 2135.9997 | 131.706
HBG-1.RR.1116.1 | 24211439125089 | Habiganj, Habiganj Sadar, Baro Bohula, Khandokar Hiras Mia | 2019-09-19 | LX1011 | 11.1 | 177 | 11.1 | 178 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6720 | 2039.9997 | 116.9549
HBG-1.RR.1117.1 | 24211319125089 | Habiganj, Habiganj Sadar, Baro Bohula, Chowdhury Abdul Mohin | 2019-09-19 | LX1011 | 9 | 179 | 9 | 180 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6720 | 2039.9997 | 94.8283
HBG-1.RR.1118.1 | 24211099125104 | Habiganj, Habiganj Sadar, Baro Bohula, Mohammad Kutub Ali | 2019-09-19 | LX1011 | 11.1 | 181 | 11.1 | 182 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6720 | 2039.9997 | 116.9549
HBG-1.RR.1119.1 | 24211089125112 | Habiganj, Habiganj Sadar, Baro Bohula, Abdur Rahim | 2019-09-19 | LX1011 | 11.2 | 183 | 11.2 | 184 | 2022-01-01 | 2022-10-08 | NQ1007 | 0.7 | 45 | 0.7 | 46 | 2022-10-08 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 4368 | 0 | 2352 | 2039.9997
HBG-1.RR.1120.1 | 24211589125122 | Habiganj, Habiganj Sadar, Baro Bohula, Mohammad Hyder Ali | 2019-09-19 | LX1011 | 12.7 | 185 | 12.8 | 186 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6720 | 2039.9997 | 134.867
HBG-1.RR.1121.1 | 24211659125012 | Habiganj, Habiganj Sadar, Baro Bohula, Bohula Model Sarkari Prathomik Biddolay, Abdul Kuddus | 2019-09-19 | LX1011 | 10.3 | 187 | 9.9 | 188 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6720 | 2039.9997 | 104.3112
HBG-1.RR.1121.2 | 24211659125012 | Habiganj, Habiganj Sadar, Baro Bohula, Bohula Model Sarkari Prathomik Biddolay, Abdul Kuddus | 2021-09-02 | MN1018 | 11.4 | 14 | 11.4 | 15 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6720 | 2039.9997 | 120.1159
HBG-1.RR.1122.1 | 24211729124588 | Habiganj, Habiganj Sadar, Baro Bohula, Bohula Model Sarkari Prathomik Biddolay, Samsunnahar | 2019-09-19 | LX1011 | 14.6 | 189 | 14.6 | 190 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6720 | 2039.9997 | 153.8326
HBG-1.RR.1123.1 | 24224619125072 | Habiganj, Ghusaipur, New Muslim Quarter, Md. Tofayel Ahmed | 2019-09-21 | NQ1003 | 12.3 | 701 | 12.3 | 702 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6480 | 2279.9997 | 129.5987
HBG-1.RR.1124.1 | 24224719125072 | Habiganj, Ghusaipur, New Muslim Quarter, Abdul Hannan | 2019-09-21 | NQ1003 | 12.6 | 703 | 12.6 | 704 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6480 | 2279.9997 | 132.7597
HBG-1.RR.1125.1 | 24224489125039 | Habiganj, Ghusaipur, New Muslim Quarter, Niamul Haque Loskor | 2019-09-21 | NQ1003 | 14.6 | 705 | 14.6 | 706 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6480 | 2279.9997 | 153.8326
HBG-1.RR.1126.1 | 24224429125028 | Habiganj, Ghusaipur, New Muslim Quarter, Md. Rezaul Karim | 2019-09-21 | NQ1003 | 9.4 | 707 | 9.4 | 708 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6480 | 2279.9997 | 99.0429
HBG-1.RR.1127.1 | 24224279125009 | Habiganj, Ghusaipur, New Muslim Quarter, Sawkot Mia | 2019-09-21 | NQ1003 | 11.4 | 709 | 11.4 | 710 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6480 | 2279.9997 | 120.1159
HBG-1.RR.1128.1 | 24224279125005 | Habiganj, Ghusaipur, New Muslim Quarter, Hasan Sadek | 2019-09-21 | NQ1003 | 9.5 | 711 | 9.5 | 712 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6480 | 2279.9997 | 100.0966
HBG-1.RR.1129.1 | 24223519125014 | Habiganj. Inatabad, Inatabad Road, Md. Masud | 2019-09-22 | NQ1003 | 16.8 | 723 | 16.8 | 724 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6576 | 2183.9997 | 177.0129
HBG-1.RR.1130.1 | 24223259125051 | Habiganj, Anantapur, Beside of Stuff Quarter School, Md. Sukur Mahmud | 2019-09-22 | NQ1003 | 4.9 | 725 | 4.9 | 726 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6576 | 2183.9997 | 51.6288
HBG-1.RR.1131.1 | 24223189125049 | Habiganj, Anantapur, Beside of Stuff Quarter School, Md. Farid Mia | 2019-09-22 | NQ1003 | 6.6 | 727 | 6.6 | 728 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6576 | 2183.9997 | 69.5408
HBG-1.RR.1132.1 | 24223299125058 | Habiganj, South Anantapur, Stuff Quarter, Dilara Zaman | 2019-09-22 | NQ1003 | 11.5 | 729 | 11.5 | 730 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6576 | 2183.9997 | 121.1695
HBG-1.RR.1133.1 | 24223299125064 | Habiganj, South Anantapur, Stuff Quarter, Md. Mahbub | 2019-09-22 | NQ1003 | 6.5 | 731 | 6.5 | 732 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6576 | 2183.9997 | 68.4871
HBG-1.RR.1134.1 | 24223289125072 | Habiganj, South Anantapur, Md. Shahjahan | 2019-09-22 | NQ1003 | 8.6 | 733 | 8.6 | 734 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6576 | 2183.9997 | 90.6137
HBG-1.RR.1135.1 | 24223239125075 | Habiganj, South Anantapur, Ward # 09, H # 6505, Niloy | 2019-09-22 | NQ1003 | 11.2 | 735 | 11.2 | 736 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6576 | 2183.9997 | 118.0086
HBG-1.RR.1136.1 | 24223399125055 | Habiganj, South Anantapur, H # 6494, Amina Khatun | 2019-09-22 | NQ1003 | 20 | 737 | 20 | 738 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 6576 | 2183.9997 | 210.7296
HBG-1.RR.1137.1 | 24223699125115 | Habiganj, Inatabad R/A, Surui Islam | 2019-09-22 | NQ1003 | 9.4 | 739 | 9.4 | 740 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6576 | 2183.9997 | 99.0429
HBG-1.RR.1138.1 | 24223689125109 | Habiganj, Inatabad R/A, Shiekh Liton | 2019-09-22 | NQ1003 | 10.6 | 741 | 10.6 | 742 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6576 | 2183.9997 | 111.6867
HBG-1.RR.1139.1 | 24223879125118 | Habiganj, Inatabad R/A, Abdur Rahim | 2019-09-22 | NQ1003 | 10 | 743 | 9.9 | 744 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6576 | 2183.9997 | 104.3112
HBG-1.RR.1140.1 | 24224059125118 | Habiganj, Inatabad R/A, Haji Mortuz Ali | 2019-09-22 | NQ1003 | 8 | 745 | 8 | 746 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6576 | 2183.9997 | 84.2919
HBG-1.RR.1141.1 | 24223169125255 | Habiganj. North Masulia, Ward # 09, Siraj Monjil | 2019-09-23 | NQ1003 | 11.3 | 808 | 11.3 | 809 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6576 | 2183.9997 | 119.0622
HBG-1.RR.1142.1 | 24223209125256 | Habiganj. North Masulia, Ward # 09, Abdul Gofur | 2019-09-23 | NQ1003 | 1.8 | 810 | 1.8 | 811 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6576 | 2183.9997 | 18.9657
HBG-1.RR.1143.1 | 24223339125239 | Habiganj, Inatabad R/A, H # 4900. Abdul Mutlib | 2019-09-23 | NQ1003 | 11.9 | 812 | 12 | 813 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6576 | 2183.9997 | 126.4378
HBG-1.RR.1144.1 | 24223349125233 | Habiganj, Inatabad R/A, H # 4917/1, Md. Abdul Hamid | 2019-09-23 | NQ1003 | 11.5 | 814 | 11.5 | 815 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6576 | 2183.9997 | 121.1695
HBG-1.RR.1144.2 | 24223349125233 | Habiganj, Inatabad R/A, H # 4917/1, Md. Abdul Hamid | 2021-01-14 | MN1032 | 16 | 21 | 16 | 22 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6576 | 2183.9997 | 168.5837
HBG-1.RR.1145.1 | 24223849125346 | Habiganj, Jangle Bahula, Akhra Road. Mujibar Rahman | 2019-09-23 | NQ1003 | 10.3 | 816 | 9.7 | 817 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6576 | 2183.9997 | 102.2039
HBG-1.RR.1146.1 | 24223929125345 | Habiganj, Jangle Bahula, Akhra Road. Nazma Akhter Parul | 2019-09-23 | NQ1003 | 10.5 | 820 | 10.5 | 821 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6576 | 2183.9997 | 110.6331
HBG-1.RR.1147.1 | 24223929125345 | Habiganj, Jangle Bahula, Akhra Road, Afil Uddin | 2019-09-23 | NQ1003 | 10.9 | 822 | 10.9 | 823 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6576 | 2183.9997 | 114.8476
HBG-1.RR.1148.1 | 24224039125338 | Habiganj, Jangle Bahula, H # 4824/1, Hossen Ahmed Chowdhury | 2019-09-23 | NQ1003 | 10.7 | 824 | 10.7 | 825 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6576 | 2183.9997 | 112.7403
HBG-1.RR.1149.1 | 24224009125278 | Habiganj, Jangle Bahula, Taher Mia | 2019-09-23 | NQ1003 | 6.3 | 826 | 6.3 | 827 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6576 | 2183.9997 | 66.3798
HBG-1.RR.1150.1 | 24223999125243 | Habiganj, East Inatabad R/A (Jungle Bahula), Md. Nanu Mia | 2019-09-23 | NQ1003 | 10.4 | 828 | 10.4 | 829 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6576 | 2183.9997 | 109.5794
HBG-1.RR.1151.1 | 24225169125072 | Hobigonj, Goshaipur R/A, Sayed Kamrul Islam | 2019-09-19 | NQ1003 | 10.5 | 675 | 10.5 | 676 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6480 | 2279.9997 | 110.6331
HBG-1.RR.1152.1 | 24225139125087 | Hobigonj, Goshaipur R/A, Nur Hossain | 2019-09-19 | NQ1003 | 11.5 | 677 | 11.5 | 678 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6480 | 2279.9997 | 121.1695
HBG-1.RR.1153.1 | 24225139125087 | Hobigonj, Goshaipur R/A, Nur Hossain | 2019-09-19 | NQ1003 | 14.6 | 679 | 14.7 | 680 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6480 | 2279.9997 | 154.8863
HBG-1.RR.1154.1 | 24225169125051 | Hobigonj, Goshaipur R/A, Kutub Chan | 2019-09-19 | NQ1003 | 5.8 | 681 | 5.8 | 682 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6480 | 2279.9997 | 61.1116
HBG-1.RR.1155.1 | 24224959125043 | Hobigonj, Goshaipur R/A, Hafsa | 2019-09-19 | NQ1003 | 12.5 | 683 | 12.4 | 684 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6480 | 2279.9997 | 130.6524
HBG-1.RR.1156.1 | 24224899125046 | Hobigonj, Goshaipur R/A, Rashida Khanom | 2019-09-19 | NQ1003 | 16 | 685 | 16 | 686 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6480 | 2279.9997 | 168.5837
HBG-1.RR.1157.1 | 24224899125046 | Hobigonj, Goshaipur R/A, Amina Begum | 2019-09-19 | NQ1003 | 10.3 | 687 | 10.3 | 688 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6480 | 2279.9997 | 108.5258
HBG-1.RR.1158.1 | 24224829125049 | Hobigonj, Goshaipur R/A, Md. Abdul Kuddse | 2019-09-19 | NQ1003 | 11.6 | 689 | 11.7 | 690 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6480 | 2279.9997 | 123.2768
HBG-1.RR.1159.1 | 24224759125027 | Hobigonj, Goshaipur, New Muslim Quter, Dr. Mahmudul Rahman Khan | 2019-09-19 | NQ1003 | 6.7 | 691 | 6.7 | 692 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6480 | 2279.9997 | 70.5944
HBG-1.RR.1160.1 | 24224869125018 | Hobigonj, Goshaipur, New Muslim Quter, Abdul Hakim | 2019-09-19 | NQ1003 | 12.7 | 693 | 12 | 694 | 2022-01-01 | [9 empty] | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0
HBG-1.RR.1161.1 | 24224749125005 | Hobigonj, Goshaipur, New Muslim Quter, Md. Nasir Uddin | 2019-09-19 | NQ1003 | 14.2 | 695 | 14.2 | 696 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6480 | 2279.9997 | 149.618
HBG-1.RR.1162.1 | 24224749124582 | Hobigonj, Goshaipur, New Muslim Quter, Janntul Nasa | 2019-09-19 | NQ1003 | 12.4 | 697 | 12.4 | 698 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6480 | 2279.9997 | 130.6524
HBG-1.RR.1163.1 | 24224749124582 | Hobigonj, Goshaipur, New Muslim Quter, Aloy Member | 2019-09-19 | NQ1003 | 12.5 | 699 | 12.5 | 700 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6480 | 2279.9997 | 131.706
HBG-1.RR.1164.1 | 24224489124568 | Hobigonj, New Muslim Quter, Mosarof Talukdar | 2019-09-21 | NQ1003 | 14.9 | 713 | 14.2 | 714 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6480 | 2279.9997 | 149.618
HBG-1.RR.1165.1 | 24224769124571 | Hobigonj, New Muslim Quter, Maria Garden, H # 4664 | 2019-09-21 | NQ1003 | 15 | 715 | 15 | 716 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6480 | 2279.9997 | 158.0472
HBG-1.RR.1165.2 | 24224769124571 | Hobigonj, New Muslim Quter, Maria Garden, H # 4664 | 2022-03-22 | LU1001 | 7.8 | 64 | 7.8 | 65 | 2022-03-22 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 4560 | 2279.9997 | 64.1715
HBG-1.RR.1166.1 | 24224799124572 | Hobigonj, New Muslim Quter, Morirom Chan | 2019-09-21 | NQ1003 | 10 | 717 | 10 | 718 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6480 | 2279.9997 | 105.3648
HBG-1.RR.1167.1 | 24225009124594 | Hobigonj, New Muslim Quter, Abu Mia | 2019-09-21 | NQ1003 | 6.1 | 719 | 6.1 | 720 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6480 | 2279.9997 | 64.2725
HBG-1.RR.1168.1 | 24225009124594 | Hobigonj, New Muslim Quter, Md. Yakub Ali | 2019-09-21 | NQ1003 | 11.2 | 721 | 11.2 | 722 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6480 | 2279.9997 | 118.0086
HBG-1.RR.1169.1 | 24223629125150 | Hobigonj, Enatabadh, Sohel Mia | 2019-09-22 | NQ1003 | 11.3 | 747 | 11.3 | 748 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6576 | 2183.9997 | 119.0622
HBG-1.RR.1169.2 | 24223629125150 | Hobigonj, Enatabadh, Sohel Mia | 2020-10-17 | NQ1003 | 45.1 | 38 | 45.1 | 39 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 45.1 | 45.1 | 2.706 | 2.706 | 0.0007168 | 100% | 0% | 2.706 | 2.706 | 0.0011869 | 28 | 0.054246 | 0.054246 |  | 0 | 0 | 6576 | 2183.9997 | 475.1953
HBG-1.RR.1170.1 | 24223599125170 | Hobigonj, Enatabadh, Arju Villa | 2019-09-22 | NQ1003 | 5.9 | 749 | 5.9 | 750 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6576 | 2183.9997 | 62.1652
HBG-1.RR.1170.2 | 24223599125170 | Hobigonj, Enatabadh, Arju Villa | 2021-01-14 | LU1001 | 9.9 | 18 | 9.9 | 19 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6576 | 2183.9997 | 104.3112
HBG-1.RR.1171.1 | 24223549125178 | Hobigonj, Enatabadh, Sayada Koijon Nesa | 2019-09-22 | NQ1003 | 7 | 751 | 7.1 | 752 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6576 | 2183.9997 | 74.809
HBG-1.RR.1172.1 | 24223529125133 | Hobigonj, Enatabadh, Hazi Abdul Nur | 2019-09-22 | NQ1003 | 11.7 | 753 | 11.5 | 754 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6576 | 2183.9997 | 121.1695
HBG-1.RR.1173.1 | 24225089124589 | Hobigonj, New Muslim Quter, Bulbul Choduary | 2019-09-22 | NQ1003 | 7.2 | 755 | 7.2 | 756 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6480 | 2279.9997 | 75.8627
HBG-1.RR.1174.1 | 24225209124587 | Hobigonj, New Muslim Quter, Hiron Mia | 2019-09-22 | NQ1003 | 8.5 | 757 | 8.5 | 758 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6480 | 2279.9997 | 89.5601
HBG-1.RR.1175.1 | 24225209124587 | Hobigonj, New Muslim Quter, Sayada Ambia Villa | 2019-09-22 | NQ1003 | 10.2 | 759 | 10.2 | 760 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6480 | 2279.9997 | 107.4721
HBG-1.RR.1176.1 | 24223589125067 | Hobigonj, New Muslim Quter, Gov. Staff Quter | 2019-09-22 | NQ1003 | 10.5 | 761 | 10.5 | 762 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6576 | 2183.9997 | 110.6331
HBG-1.RR.1177.1 | 24223589125067 | Hobigonj, New Muslim Quter, Gov. Staff Quter | 2019-09-22 | NQ1003 | 5.9 | 763 | 5.4 | 764 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6576 | 2183.9997 | 56.897
HBG-1.RR.1178.1 | 24223539125192 | Hobigonj, Enatabadh, Md Kutab Ali | 2019-09-22 | NQ1003 | 9.5 | 765 | 9.1 | 766 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6576 | 2183.9997 | 95.882
HBG-1.RR.1179.1 | 24223539125192 | Hobigonj, Enatabadh, S M Abdul Alower | 2019-09-22 | NQ1003 | 4.2 | 767 | 4.2 | 768 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6576 | 2183.9997 | 44.2532
HBG-1.RR.1180.1 | 24223649125197 | Hobigonj, Enatabadh, Md . Mohi Uddin | 2019-09-22 | NQ1003 | 4.6 | 769 | 4.6 | 770 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6576 | 2183.9997 | 48.4678
HBG-1.RR.1181.1 | 24223649125197 | Hobigonj, Enatabadh, Parvin Akter Chowdary | 2019-09-22 | NQ1003 | 10.9 | 771 | 10.9 | 772 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6576 | 2183.9997 | 114.8476
HBG-1.RR.1181.2 | 24223649125197 | Hobigonj, Enatabadh, Parvin Akter Chowdary | 2021-01-14 | LU1001 | 22.8 | 20 | 22.8 | 21 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 22.8 | 22.8 | 1.368 | 1.368 | 0.0007168 | 100% | 0% | 1.368 | 1.368 | 0.0011869 | 28 | 0.027424 | 0.027424 |  | 0 | 0 | 6576 | 2183.9997 | 240.2318
HBG-1.RR.1182.1 | 24223439125181 | Hobigonj, Enatabadh, Sayed Sukrana Masud | 2019-09-22 | NQ1003 | 16.4 | 773 | 16.4 | 774 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6576 | 2183.9997 | 172.7983
HBG-1.RR.1183.1 | 24223469125141 | Hobigonj, Enatabadh, 36 Probaho, Sitol House | 2019-09-23 | NQ1003 | 16 | 775 | 16 | 776 | 2022-01-01 | [9 empty] | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 | 2022-09-12 12:00 | 0 | 0
HBG-1.RR.1184.1 | 24223159125141 | Hobigonj, Enatabadh, Nur Mohammad Complex | 2019-09-23 | NQ1003 | 10.1 | 777 | 10.1 | 778 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6576 | 2183.9997 | 106.4185
HBG-1.RR.1185.1 | 24223159125141 | Hobigonj, Enatabadh, Anando Nikaton | 2019-09-23 | NQ1003 | 11.8 | 779 | 11.8 | 780 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6576 | 2183.9997 | 124.3305
HBG-1.RR.1186.1 | 24222899125174 | Hobigonj, Anantopur R/A, Apurbo Dav | 2019-09-23 | NQ1003 | 11.6 | 781 | 11.6 | 782 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6576 | 2183.9997 | 122.2232
HBG-1.RR.1187.1 | 24222899125160 | Hobigonj, Anantopur R/A, Aiet Ali | 2019-09-23 | NQ1003 | 4.4 | 786 | 4.4 | 787 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6576 | 2183.9997 | 46.3605
HBG-1.RR.1188.1 | 24222939125165 | Hobigonj, Anantopur R/A, Md. Abdul Salam | 2019-09-23 | NQ1003 | 4 | 788 | 4 | 789 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6576 | 2183.9997 | 42.1459
HBG-1.RR.1189.1 | 24222869125140 | Hobigonj, Anantopur R/A, Runu Bibi | 2019-09-23 | NQ1003 | 13.6 | 790 | 13.6 | 791 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6576 | 2183.9997 | 143.2961
HBG-1.RR.1190.1 | 24222869125140 | Hobigonj, Anantopur R/A, Idris Mia | 2019-09-23 | NQ1003 | 12 | 792 | 12 | 793 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6576 | 2183.9997 | 126.4378
HBG-1.RR.1191.1 | 24222759125127 | Hobigonj, Anantopur R/A, Kazi Abdul Salak, Kazi Nibas | 2019-09-23 | NQ1003 | 10.7 | 794 | 10.7 | 795 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6576 | 2183.9997 | 112.7403
HBG-1.RR.1192.1 | 24222459125126 | Hobigonj, Anantopur R/A, Raju Gosh | 2019-09-23 | NQ1003 | 7.8 | 796 | 7.8 | 797 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6576 | 2183.9997 | 82.1846
HBG-1.RR.1193.1 | 24222459125126 | Hobigonj, Anantopur R/A, Razzak | 2019-09-23 | NQ1003 | 4.2 | 798 | 4.8 | 799 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6576 | 2183.9997 | 50.5751
HBG-1.RR.1194.1 | 24223109125196 | Hobigonj, Enatabadh, H # 4914/2, Hossain House | 2019-09-23 | NQ1003 | 10.7 | 800 | 10.7 | 801 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6576 | 2183.9997 | 112.7403
HBG-1.RR.1195.1 | 24222939125208 | Hobigonj, Enatabadh, Ayesha Siddiqua | 2019-09-23 | NQ1003 | 16 | 802 | 16 | 803 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6576 | 2183.9997 | 168.5837
HBG-1.RR.1196.1 | 24223069125243 | Hobigonj, Enatabadh, H # 6993/1, Hazi Ayub ali | 2019-09-23 | NQ1003 | 11 | 804 | 10.7 | 805 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6576 | 2183.9997 | 112.7403
HBG-1.RR.1196.2 | 24223069125243 | Hobigonj, Enatabadh, H # 6993/1, Hazi Ayub ali | 2021-09-01 | MN1018 | 20.2 | 12 | 19.9 | 13 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0 | 6576 | 2183.9997 | 209.676
HBG-1.RR.1197.1 | 24223069125243 | Hobigonj, Enatabadh, Abdul High | 2019-09-23 | NQ1003 | 8 | 806 | 8 | 807 | 2022-01-01 | [9 empty] | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0
HBG-1.RR.1198.1 | 24215489125107 | Hobigonj, Eidgha Road, Lucky Engineering Work Shop, Abdul Jobbar | 2019-09-24 | NQ1003 | 4.3 | 830 | 4.3 | 831 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6720 | 2039.9997 | 45.3069
HBG-1.RR.1199.1 | 24214989125131 | Hobigonj, S.P Office | 2019-09-24 | NQ1003 | 5 | 832 | 5 | 833 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6720 | 2039.9997 | 52.6824
HBG-1.RR.1200.1 | 24214769125140 | Hobigonj, 2 No Pool, Md Abdul Ali, Thana Sikka Officer | 2019-09-24 | NQ1003 | 7.5 | 834 | 7.5 | 835 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6720 | 2039.9997 | 79.0236
HBG-1.RR.1200.2 | 24214769125140 | Hobigonj, 2 No Pool, Md Abdul Ali, Thana Sikka Officer | 2021-01-13 | LU1001 | 12.2 | 14 | 12.2 | 15 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6720 | 2039.9997 | 128.5451
HBG-1.RR.1201.1 | 24223279124435 | Hobiganj, College Quarter, Ayub Ali | 2019-09-15 | NQ1011 | 12 | 189 | 12 | 190 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6576 | 2183.9997 | 126.4378
HBG-1.RR.1202.1 | 24223089124439 | Hobiganj, College Quarter, Titli Villa | 2019-09-15 | NQ1011 | 10.4 | 191 | 10.4 | 192 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6576 | 2183.9997 | 109.5794
HBG-1.RR.1203.1 | 24223129124424 | Hobiganj, College Quarter, Ayesha Siddika | 2019-09-15 | NQ1011 | 12.5 | 193 | 12.5 | 194 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6576 | 2183.9997 | 131.706
HBG-1.RR.1204.1 | 24223129124424 | Hobiganj, College Quarter, Maleka Khatun | 2019-09-15 | NQ1011 | 12.7 | 195 | 12.7 | 196 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6576 | 2183.9997 | 133.8133
HBG-1.RR.1205.1 | 24223069124420 | Hobiganj, College Quarter, Kazal Das | 2019-09-15 | NQ1011 | 15.9 | 197 | 15.9 | 198 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6576 | 2183.9997 | 167.5301
HBG-1.RR.1206.1 | 24223069124420 | Hobiganj, College Quarter, Abdul Kadir | 2019-09-15 | NQ1011 | 7.4 | 199 | 7.4 | 200 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6576 | 2183.9997 | 77.97
HBG-1.RR.1207.1 | 24222979124432 | Hobiganj, College Quarter, Taus Maldar | 2019-09-15 | NQ1011 | 5.7 | 201 | 5.7 | 202 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6576 | 2183.9997 | 60.0579
HBG-1.RR.1208.1 | 24222979124432 | Hobiganj, College Quarter, Abdul Hai | 2019-09-15 | NQ1011 | 12 | 203 | 12.1 | 204 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6576 | 2183.9997 | 127.4914
HBG-1.RR.1209.1 | 24222999124442 | Hobiganj, College Quarter, Rupa Villa | 2019-09-15 | NQ1011 | 4.4 | 207 | 4.4 | 208 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6576 | 2183.9997 | 46.3605
HBG-1.RR.1210.1 | 24221819124498 | Hobiganj, Ghoshpara R/A, Kamini Bhaban, Priyobashi Goap | 2019-09-15 | NQ1011 | 10 | 209 | 10.6 | 210 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6552 | 2207.9997 | 111.6867
HBG-1.RR.1211.1 | 24221819124498 | Hobiganj, Ghoshpara R/A, Swapan Bhattacharjo | 2019-09-15 | NQ1011 | 11.9 | 211 | 11.9 | 212 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6552 | 2207.9997 | 125.3841
HBG-1.RR.1212.1 | 24221739124514 | Hobiganj, Ghoshpara R/A, Moni | 2019-09-15 | NQ1011 | 8.9 | 213 | 8.9 | 214 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6552 | 2207.9997 | 93.7747
HBG-1.RR.1213.1 | 24221739124514 | Hobiganj, Ghoshpara R/A, Arun Kumar Bhattacharjo | 2019-09-15 | NQ1011 | 6.6 | 219 | 6.6 | 220 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6552 | 2207.9997 | 69.5408
HBG-1.RR.1214.1 | 24220359125036 | Habiganj, Shayestanagar, Mohonpur R/A, Parvez House | 2019-09-16 | NQ1011 | 11.5 | 268 | 11.5 | 269 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6672 | 2087.9997 | 121.1695
HBG-1.RR.1215.1 | 24220359125036 | Habiganj, Shayestanagar, Mohonpur R/A, Arif & Fayez Villa | 2019-09-16 | NQ1011 | 8.9 | 274 | 8.4 | 275 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6672 | 2087.9997 | 88.5064
HBG-1.RR.1216.1 | 24220279125024 | Habiganj, Shayestanagar, Mohonpur R/A, Nurul Amin | 2019-09-16 | NQ1011 | 15.8 | 276 | 15.8 | 277 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6672 | 2087.9997 | 166.4764
HBG-1.RR.1217.1 | 24220249125041 | Habiganj, Shayestanagar, Mohonpur R/A, Abdul Hai | 2019-09-16 | NQ1011 | 12.9 | 278 | 12.9 | 279 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6672 | 2087.9997 | 135.9206
HBG-1.RR.1218.1 | 24220199125033 | Habiganj, Shayestanagar, Mohonpur R/A, Abdul Kuddus | 2019-09-16 | NQ1011 | 5 | 280 | 5 | 281 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6672 | 2087.9997 | 52.6824
HBG-1.RR.1219.1 | 24220139125022 | Habiganj, South Mohonpur, Moskot Khan | 2019-09-16 | NQ1011 | 11.5 | 282 | 11.5 | 283 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6672 | 2087.9997 | 121.1695
HBG-1.RR.1220.1 | 24220139125022 | Habiganj, South Mohonpur, Anowara Begum | 2019-09-16 | NQ1011 | 10.7 | 284 | 10.7 | 285 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6672 | 2087.9997 | 112.7403
HBG-1.RR.1221.1 | 24220139125022 | Habiganj, South Mohonpur, Korfunnesa | 2019-09-16 | NQ1011 | 9.4 | 286 | 9.4 | 287 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6672 | 2087.9997 | 99.0429
HBG-1.RR.1222.1 | 24220049124587 | Habiganj, South Mohonpur, Moksed Ali | 2019-09-16 | NQ1011 | 7.2 | 288 | 7.2 | 289 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6600 | 2159.9997 | 75.8627
HBG-1.RR.1223.1 | 24220159124592 | Habiganj, South Mohonpur, Anam | 2019-09-16 | NQ1011 | 11.8 | 290 | 11.8 | 291 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6600 | 2159.9997 | 124.3305
HBG-1.RR.1224.1 | 24220159124592 | Habiganj, South Mohonpur, Sazid | 2019-09-16 | NQ1011 | 23.2 | 292 | 23.2 | 293 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 23.2 | 23.2 | 1.392 | 1.392 | 0.0007168 | 100% | 0% | 1.392 | 1.392 | 0.0011869 | 28 | 0.027905 | 0.027905 |  | 0 | 0 | 6600 | 2159.9997 | 244.4464
HBG-1.RR.1225.1 | 24220109124574 | Habiganj, South Mohonpur, Talukdar Bari | 2019-09-16 | NQ1011 | 11.3 | 294 | 11.3 | 295 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6600 | 2159.9997 | 119.0622
HBG-1.RR.1226.1 | 24220089124570 | Habiganj, South Mohonpur, Moinuddin | 2019-09-16 | NQ1011 | 9.4 | 296 | 9.4 | 297 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 6144 | 0 | 456 | 2159.9997 | 29.5772
HBG-1.RR.1227.1 | 24215969124557 | Habiganj, South Mohonpur, Nahar Cottage | 2019-09-16 | NQ1011 | 17.2 | 298 | 17.2 | 299 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 6600 | 2159.9997 | 181.2275
HBG-1.RR.1227.2 | 24215969124557 | Habiganj, South Mohonpur, Nahar Cottage | 2020-10-12 | NQ1003 | 4.6 | 16 | 4.6 | 17 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6600 | 2159.9997 | 48.4678
HBG-1.RR.1228.1 | 24221459124373 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Mortuza Ali | 2019-09-17 | NQ1011 | 18.1 | 331 | 17.2 | 332 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 6552 | 2207.9997 | 181.2275
HBG-1.RR.1229.1 | 24221449124365 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Tanvir Villa | 2019-09-17 | NQ1011 | 11.8 | 334 | 11.8 | 335 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6552 | 2207.9997 | 124.3305
HBG-1.RR.1230.1 | 24221459124357 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Abdul Kaiyum | 2019-09-17 | NQ1011 | 3.2 | 336 | 3.2 | 337 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6552 | 2207.9997 | 33.7167
HBG-1.RR.1231.1 | 24221299124363 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Foridur Rahman | 2019-09-17 | MP1006 | 12.3 | 559 | 12.3 | 560 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6552 | 2207.9997 | 129.5987
HBG-1.RR.1232.1 | 24221259124337 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Yakub Ali | 2019-09-17 | MP1006 | 15 | 561 | 15 | 562 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6552 | 2207.9997 | 158.0472
HBG-1.RR.1233.1 | 24221149124310 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Abdul Wahed | 2019-09-17 | MP1006 | 8.5 | 563 | 7.9 | 564 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6552 | 2207.9997 | 83.2382
HBG-1.RR.1234.1 | 24221149124310 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Saheb Ali | 2019-09-17 | MP1006 | 10.8 | 565 | 10.8 | 566 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6552 | 2207.9997 | 113.794
HBG-1.RR.1235.1 | 24221149124310 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Somir Mia | 2019-09-17 | MP1006 | 16.1 | 567 | 16.1 | 568 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6552 | 2207.9997 | 169.6373
HBG-1.RR.1236.1 | 24221149124310 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Siddik Mia | 2019-09-17 | MP1006 | 8.6 | 569 | 8.6 | 570 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6552 | 2207.9997 | 90.6137
HBG-1.RR.1237.1 | 24220999124293 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Tenu Mia | 2019-09-18 | LX1011 | 13.3 | 92 | 13.3 | 93 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6552 | 2207.9997 | 140.1352
HBG-1.RR.1238.1 | 24220999124293 | Habiganj, Sultan Mahmudpur, Dakkhinpara, Samsu | 2019-09-18 | LX1011 | 11.5 | 94 | 11.5 | 95 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6552 | 2207.9997 | 121.1695
HBG-1.RR.1239.1 | 24221159124276 | Habiganj, Sultan Mahmudpur, Shahabuddin | 2019-09-18 | LX1011 | 13.3 | 96 | 13.3 | 97 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6552 | 2207.9997 | 140.1352
HBG-1.RR.1239.2 | 24221159124276 | Habiganj, Sultan Mahmudpur, Shahabuddin | 2022-10-01 | NQ1007 | 7.1 | 36 | 7.1 | 37 | 2022-10-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 0 | 2207.9997 | 18.856
HBG-1.RR.1240.1 | 24221219124263 | Habiganj, Sultan Mahmudpur, Mohidur Ali | 2019-09-18 | LX1011 | 13.1 | 98 | 12.5 | 99 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6552 | 2207.9997 | 131.706
HBG-1.RR.1241.1 | 24221219124263 | Habiganj, Sultan Mahmudpur, Farid Mia | 2019-09-18 | LX1011 | 4.4 | 100 | 4.4 | 101 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6552 | 2207.9997 | 46.3605
HBG-1.RR.1242.1 | 24221199124256 | Habiganj, Sultan Mahmudpur, Didar Ali | 2019-09-18 | LX1011 | 15.1 | 102 | 14.8 | 103 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6552 | 2207.9997 | 155.9399
HBG-1.RR.1243.1 | 24221199124256 | Habiganj, Sultan Mahmudpur, Siddik Ali | 2019-09-18 | LX1011 | 11.3 | 104 | 11.3 | 105 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6552 | 2207.9997 | 119.0622
HBG-1.RR.1243.2 | 24221199124256 | Habiganj, Sultan Mahmudpur, Siddik Ali | 2022-10-01 | NQ1007 | 11.8 | 34 | 11.8 | 35 | 2022-10-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 0 | 2207.9997 | 31.3381
HBG-1.RR.1244.1 | 24221199124256 | Habiganj, Sultan Mahmudpur, Gofur Hazi | 2019-09-18 | LX1011 | 11.7 | 106 | 11.8 | 107 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6552 | 2207.9997 | 124.3305
HBG-1.RR.1245.1 | 24221199124256 | Habiganj, Sultan Mahmudpur, Jalal Uddin | 2019-09-18 | LX1011 | 17.5 | 108 | 17.5 | 109 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6552 | 2207.9997 | 184.3884
HBG-1.RR.1246.1 | 24221199124256 | Habiganj, Sultan Mahmudpur, Abdus Salam | 2019-09-18 | LX1011 | 11.7 | 110 | 11.7 | 111 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6552 | 2207.9997 | 123.2768
HBG-1.RR.1247.1 | 24221199124256 | Habiganj, Sultan Mahmudpur, Kajol | 2019-09-18 | LX1011 | 65.5 | 112 | 65.5 | 113 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 65.5 | 65.5 | 3.93 | 3.93 | 0.0007168 | 100% | 0% | 3.93 | 3.93 | 0.0011869 | 28 | 0.078783 | 0.078783 |  | 0 | 0 | 6552 | 2207.9997 | 690.1395
HBG-1.RR.1248.1 | 24221329124276 | Habiganj, Sultan Mahmudpur, Ujjol | 2019-09-18 | LX1011 | 12.6 | 114 | 12.6 | 115 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6552 | 2207.9997 | 132.7597
HBG-1.RR.1249.1 | 24221399124275 | Habiganj, Sultan Mahmudpur, Firoz Ali | 2019-09-18 | LX1011 | 8.8 | 116 | 8.8 | 117 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6552 | 2207.9997 | 92.721
HBG-1.RR.1250.1 | 24221339124304 | Habiganj, Sultan Mahmudpur, Jamshed Ali | 2019-09-18 | LX1011 | 12.4 | 118 | 12.4 | 119 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6552 | 2207.9997 | 130.6524
HBG-1.RR.1251.1 | 24221549124441 | Habiganj, Court Station Road, Mohonpur,Samsuddin | 2019-09-16 | NQ1011 | 10.7 | 257 | 10.7 | 258 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6552 | 2207.9997 | 112.7403
HBG-1.RR.1252.1 | 24221499124448 | Habiganj, Court Station Road, Mohonpur, Afsana Rohoman | 2019-09-16 | NQ1011 | 4.6 | 260 | 4.6 | 261 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6552 | 2207.9997 | 48.4678
HBG-1.RR.1253.1 | 24221469124438 | Habiganj, Court Station Road, Mohonpur, Richi Optic | 2019-09-16 | NQ1011 | 2.8 | 262 | 2.8 | 263 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6552 | 2207.9997 | 29.5021
HBG-1.RR.1254.1 | 24221449124432 | Habiganj, Court Station Road, Mohonpur, Abdul Ohab | 2019-09-16 | NQ1011 | 3.6 | 264 | 3.7 | 265 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6552 | 2207.9997 | 38.985
HBG-1.RR.1255.1 | 24221449124432 | Habiganj, Court Station Road, Mohonpur, Shahadat Monjil | 2019-09-16 | NQ1011 | 9.2 | 266 | 9.2 | 267 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6552 | 2207.9997 | 96.9356
HBG-1.RR.1256.1 | 24215669124592 | Habiganj, Bypass Road, South Mohonpur R/A, Abdur Rohoman | 2019-09-17 | NQ1011 | 7.1 | 300 | 7.1 | 301 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6672 | 2087.9997 | 74.809
HBG-1.RR.1257.1 | 24215669124592 | Habiganj, Bypass Road, South Mohonpur R/A, Muktadir Hossen | 2019-09-17 | NQ1011 | 9.4 | 302 | 9.4 | 303 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6672 | 2087.9997 | 99.0429
HBG-1.RR.1258.1 | 24215709125003 | Habiganj, Bypass Road, South Mohonpur R/A, Abdul Khalek | 2019-09-17 | NQ1011 | 11.6 | 304 | 11.6 | 305 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6672 | 2087.9997 | 122.2232
HBG-1.RR.1259.1 | 24215709125003 | Habiganj, Bypass Road, South Mohonpur R/A, Abdur Nur | 2019-09-17 | NQ1011 | 7.8 | 306 | 7.8 | 307 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6672 | 2087.9997 | 82.1846
HBG-1.RR.1260.1 | 24215629124599 | Habiganj, Bypass Road, South Mohonpur R/A, Nazrul | 2019-09-17 | NQ1011 | 6.2 | 308 | 6.2 | 309 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6672 | 2087.9997 | 65.3262
HBG-1.RR.1261.1 | 24215629124599 | Habiganj, Bypass Road, South Mohonpur R/A, Amir Hossen | 2019-09-17 | NQ1011 | 5.2 | 311 | 5.2 | 312 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6672 | 2087.9997 | 54.7897
HBG-1.RR.1262.1 | 24215629124599 | Habiganj, Bypass Road, South Mohonpur R/A, Fojor Mia | 2019-09-17 | NQ1011 | 6.8 | 315 | 6.8 | 316 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6672 | 2087.9997 | 71.6481
HBG-1.RR.1262.2 | 24215629124599 | Habiganj, Bypass Road, South Mohonpur R/A, Fojor Mia | 2021-01-13 | NQ1007 | 7.7 | 13 | 7.7 | 14 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6672 | 2087.9997 | 81.1309
HBG-1.RR.1263.1 | 24215639125000 | Habiganj, Bypass Road, South Mohonpur R/A, Rofiq Mia | 2019-09-17 | NQ1011 | 5.7 | 317 | 5.7 | 318 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6672 | 2087.9997 | 60.0579
HBG-1.RR.1264.1 | 24215639125000 | Habiganj, Bypass Road, South Mohonpur R/A, Ashraf Ali | 2019-09-17 | NQ1011 | 7.5 | 319 | 7.5 | 320 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6672 | 2087.9997 | 79.0236
HBG-1.RR.1265.1 | 24215639125000 | Habiganj, Bypass Road, South Mohonpur R/A, Jafor Ali | 2019-09-17 | NQ1011 | 8.8 | 321 | 8.8 | 322 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6672 | 2087.9997 | 92.721
HBG-1.RR.1266.1 | 24215619125036 | Habiganj, Bypass Road, South Mohonpur R/A, Faruk | 2019-09-17 | NQ1011 | 10.3 | 323 | 10.3 | 324 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6672 | 2087.9997 | 108.5258
HBG-1.RR.1267.1 | 24215629125027 | Habiganj, Bypass Road, South Mohonpur R/A, Ruma | 2019-09-17 | NQ1011 | 7.5 | 325 | 7.5 | 326 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6672 | 2087.9997 | 79.0236
HBG-1.RR.1268.1 | 24215809125065 | Habiganj, Bypass Road, South Mohonpur R/A, Abul | 2019-09-17 | NQ1011 | 8.7 | 327 | 8.7 | 328 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6672 | 2087.9997 | 91.6674
HBG-1.RR.1269.1 | 24215809125065 | Habiganj, Bypass Road, South Mohonpur R/A, Helal | 2019-09-17 | NQ1011 | 10 | 329 | 10 | 330 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6672 | 2087.9997 | 105.3648
HBG-1.RR.1270.1 | 24221639124358 | Sultan Mahmudpur, North Para, Abdul Basar Jumon | 2019-09-18 | LX1011 | 3.1 | 120 | 3.1 | 121 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6552 | 2207.9997 | 32.6631
HBG-1.RR.1271.1 | 24221599124359 | Sultan Mahmudpur, Uttorpara, Hurmoj Ali | 2019-09-18 | LX1011 | 11.3 | 122 | 11.3 | 123 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 1800 | 0 | 4752 | 2207.9997 | 94.5974
HBG-1.RR.1271.2 | 24221599124359 | Sultan Mahmudpur, Uttorpara, Hurmoj Ali | 2022-10-01 | NQ1007 | 16.7 | 38 | 16.7 | 39 | 2022-10-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 0 | 2207.9997 | 44.3514
HBG-1.RR.1272.1 | 24221669124346 | Sultan Mahmudpur, Uttorpara, Sohid Chowdhury | 2019-09-18 | LX1011 | 16.3 | 124 | 16.3 | 125 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 6552 | 2207.9997 | 171.7446
HBG-1.RR.1273.1 | 24221609124344 | Sultan Mahmudpur, Uttorpara, Abdul Monaf | 2019-09-18 | LX1011 | 11.1 | 126 | 11.1 | 127 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6552 | 2207.9997 | 116.9549
HBG-1.RR.1274.1 | 24221629124342 | Sultan Mahmudpur, Uttorpara, Siddik Ali | 2019-09-18 | LX1011 | 3.1 | 128 | 3.1 | 129 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6552 | 2207.9997 | 32.6631
HBG-1.RR.1275.1 | 24221609124340 | Sultan Mahmudpur, Uttorpara, Abdur Razzak | 2019-09-18 | LX1011 | 8.1 | 130 | 8.1 | 131 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6552 | 2207.9997 | 85.3455
HBG-1.RR.1276.1 | 24221569124325 | Sultan Mahmudpur, Uttorpara, Aysa Akter | 2019-09-18 | LX1011 | 8 | 132 | 8 | 133 | 2022-01-01 | [9 empty] | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0
HBG-1.RR.1277.1 | 24221429124326 | Sultan Mahmudpur, Uttorpara, Abdul Kayum | 2019-09-18 | LX1011 | 11.9 | 135 | 12.6 | 136 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6552 | 2207.9997 | 132.7597
HBG-1.RR.1278.1 | 24221429124316 | Sultan Mahmudpur, Uttorpara, Jakir Hossen | 2019-09-18 | LX1011 | 7.8 | 139 | 7.8 | 140 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6552 | 2207.9997 | 82.1846
HBG-1.RR.1278.2 | 24221429124316 | Sultan Mahmudpur, Uttorpara, Jakir Hossen | 2022-03-27 | LU1001 | 48.8 | 86 | 48.8 | 87 | 2022-03-27 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 48.8 | 48.8 | 2.928 | 2.928 | 0.0007168 | 100% | 0% | 2.928 | 2.928 | 0.0011869 | 28 | 0.058696 | 0.058696 |  | 0 | 0 | 4512 | 2207.9997 | 394.4397
HBG-1.RR.1279.1 | 24221489124275 | Sultan Mahmudpur, Uttorpara, Didar Ali | 2019-09-18 | LX1011 | 3.7 | 141 | 3.7 | 142 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6552 | 2207.9997 | 38.985
HBG-1.RR.1280.1 | 24221339124296 | Sultan Mahmudpur, Uttorpara, Nazrul Islam | 2019-09-18 | LX1011 | 11.1 | 143 | 10.6 | 144 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6552 | 2207.9997 | 111.6867
HBG-1.RR.1281.1 | 24221279124300 | Sultan Mahmudpur, Uttorpara, Johura khatun | 2019-09-18 | LX1011 | 15.5 | 145 | 15.5 | 146 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 6552 | 2207.9997 | 163.3155
HBG-1.RR.1282.1 | 24221279124300 | Sultan Mahmudpur, Uttorpara, Fojor Ali | 2019-09-18 | LX1011 | 11.1 | 147 | 11.1 | 148 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6552 | 2207.9997 | 116.9549
HBG-1.RR.1283.1 | 24221279124300 | Sultan Mahmudpur, Uttorpara, Maju Mia | 2019-09-18 | LX1011 | 5.8 | 149 | 5.8 | 150 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6552 | 2207.9997 | 61.1116
HBG-1.RR.1284.1 | 24212579125081 | Habiganj, Boro Bohula, Ward #02, Arfan | 2019-09-19 | LX1011 | 17 | 151 | 16.6 | 152 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 6720 | 2039.9997 | 174.9056
HBG-1.RR.1285.1 | 24212579125081 | Habiganj, Boro Bohula, Ward #02, Nur Islam | 2019-09-19 | LX1011 | 6.8 | 153 | 6.8 | 154 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6720 | 2039.9997 | 71.6481
HBG-1.RR.1286.1 | 24212999125077 | Habiganj, Boro Bohula, Ward #02, Abu Fojor | 2019-09-19 | LX1011 | 11.3 | 155 | 11.3 | 156 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6720 | 2039.9997 | 119.0622
HBG-1.RR.1287.1 | 24212999125077 | Habiganj, Boro Bohula, Ward #02, Nurul Haque | 2019-09-19 | LX1011 | 8.7 | 157 | 8.7 | 158 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6720 | 2039.9997 | 91.6674
HBG-1.RR.1288.1 | 24212839125036 | Habiganj, Boro Bohula, Ward #02, Ful mia | 2019-09-19 | LX1011 | 12.4 | 159 | 12.4 | 160 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6720 | 2039.9997 | 130.6524
HBG-1.RR.1289.1 | 24212839125036 | Habiganj, Boro Bohula, Ward #02, Motin | 2019-09-19 | LX1011 | 9 | 161 | 9 | 162 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6720 | 2039.9997 | 94.8283
HBG-1.RR.1290.1 | 24213059125050 | Habiganj, Boro Bohula, Ward #02, Runa Khatun | 2019-09-19 | LX1011 | 11.6 | 163 | 11.6 | 164 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6720 | 2039.9997 | 122.2232
HBG-1.RR.1291.1 | 24213059125050 | Habiganj, Boro Bohula, Ward #02, Chan mia | 2019-09-19 | LX1011 | 5.8 | 165 | 5.8 | 166 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6720 | 2039.9997 | 61.1116
HBG-1.RR.1292.1 | 24212639125039 | Habiganj, Boro Bohula, Ward #02, Ali Hossen | 2019-09-19 | LX1011 | 14.8 | 167 | 14.8 | 168 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6720 | 2039.9997 | 155.9399
HBG-1.RR.1293.1 | 24212359125012 | Habiganj, Boro Bohula, Ward #02, Siddik | 2019-09-19 | LX1011 | 9.4 | 169 | 8.7 | 170 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6720 | 2039.9997 | 91.6674
HBG-1.RR.1294.1 | 24212529125038 | Habiganj, Boro Bohula, Ward #02, Salim | 2019-09-19 | LX1011 | 17.5 | 171 | 17.5 | 172 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6720 | 2039.9997 | 184.3884
HBG-1.RR.1295.1 | 24212379125034 | Habiganj, Boro Bohula, Ward #02, Motaleb | 2019-09-19 | LX1011 | 10.3 | 175 | 10.3 | 176 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6720 | 2039.9997 | 108.5258
HBG-1.RR.1296.1 | 24224879124505 | Habiganj, Cinema Hall Road, Takdia Begum | 2019-09-21 | LX1011 | 20.7 | 191 | 20.7 | 192 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 20.7 | 20.7 | 1.242 | 1.242 | 0.0007168 | 100% | 0% | 1.242 | 1.242 | 0.0011869 | 28 | 0.024898 | 0.024898 |  | 0 | 0 | 6504 | 2255.9997 | 218.1052
HBG-1.RR.1297.1 | 24224979124498 | Habiganj, Cinema Hall Road, Kamrul Islam | 2019-09-21 | LX1011 | 11.6 | 193 | 11.6 | 194 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6504 | 2255.9997 | 122.2232
HBG-1.RR.1298.1 | 24224969124510 | Habiganj, Cinema Hall Road, Helth Care Hospital | 2019-09-21 | LX1011 | 11.2 | 195 | 11.4 | 196 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6504 | 2255.9997 | 120.1159
HBG-1.RR.1299.1 | 24222709125045 | Kurcsh Nogur R/A, Ward # 09, Porisonkhan Office | 2019-09-21 | LX1011 | 10.8 | 197 | 10.8 | 198 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6576 | 2183.9997 | 113.794
HBG-1.RR.1300.1 | 24223059125053 | Kurcsh Nogur R/A, Ward # 09, Habibur Rohoman | 2019-09-21 | LX1011 | 14.6 | 199 | 14.6 | 200 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6576 | 2183.9997 | 153.8326
HBG-1.RR.1301.1 | 24215859125091 | Habiganj, Shaistanagar, Saya Nir | 2019-09-24 | MP1006 | 6.5 | 812 | 6.5 | 813 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6672 | 2087.9997 | 68.4871
HBG-1.RR.1302.1 | 24215929125079 | Habiganj, Shaistanagar, Md. Ali Reza | 2019-09-24 | MP1006 | 9.2 | 814 | 9.2 | 815 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6672 | 2087.9997 | 96.9356
HBG-1.RR.1303.1 | 24220899125062 | Habiganj, Shaistanagar, Trafic Point, Abdul Hannan | 2019-09-24 | MP1006 | 15.6 | 816 | 15.6 | 817 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6672 | 2087.9997 | 164.3691
HBG-1.RR.1304.1 | 24220749125084 | Habiganj, Shaistanagar, Abdul | 2019-09-24 | MP1006 | 7.8 | 818 | 7.8 | 819 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6672 | 2087.9997 | 82.1846
HBG-1.RR.1305.1 | 24220729125086 | Habiganj, Shaistanagar, Md. Salahuddin | 2019-09-24 | MP1006 | 6.4 | 820 | 6.4 | 821 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6672 | 2087.9997 | 67.4335
HBG-1.RR.1306.1 | 24220789125102 | Habiganj, Shaistanagar, Shahed Mia | 2019-09-24 | MP1006 | 11.9 | 822 | 11.9 | 823 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6672 | 2087.9997 | 125.3841
HBG-1.RR.1307.1 | 24220799125119 | Habiganj,Shaistanagar, Mizan | 2019-09-26 | MP1006 | 14.9 | 824 | 14.9 | 825 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6672 | 2087.9997 | 156.9936
HBG-1.RR.1308.1 | 24220759125134 | Habiganj,Shaistanagar, Abdur Rashid | 2019-09-26 | MP1006 | 6.8 | 826 | 6.8 | 827 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6672 | 2087.9997 | 71.6481
HBG-1.RR.1309.1 | 24220759125134 | Habiganj,Shaistanagar, Shofiqul Haque | 2019-09-26 | MP1006 | 8.2 | 828 | 8.2 | 829 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6672 | 2087.9997 | 86.3991
HBG-1.RR.1310.1 | 24221059125075 | Habiganj,Shaistanagar, Md. Abdul Haque | 2019-09-26 | MP1006 | 12.6 | 830 | 12.7 | 831 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6672 | 2087.9997 | 133.8133
HBG-1.RR.1311.1 | 24220189125078 | Habiganj,Shaistanagar, Arif Manson | 2019-09-26 | MP1006 | 10.5 | 832 | 10.5 | 833 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6672 | 2087.9997 | 110.6331
HBG-1.RR.1312.1 | 24223699124524 | Habiganj, Old Hospital Road, Abu Jahir | 2019-09-26 | MP1006 | 9.8 | 836 | 9.8 | 837 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6576 | 2183.9997 | 103.2575
HBG-1.RR.1313.1 | 24225809124371 | Habiganj, Shosanghat Road, Asica Garden | 2019-09-26 | MP1006 | 15.1 | 838 | 15.1 | 839 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6480 | 2279.9997 | 159.1009
HBG-1.RR.1314.1 | 24220799124470 | Habiganj, Mohonpur R/A, Rehena Parven | 2019-09-28 | MP1006 | 15.2 | 860 | 15.2 | 861 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6600 | 2159.9997 | 160.1545
HBG-1.RR.1315.1 | 24220869124440 | Habiganj, Mohonpur R/A, Mojid Mia | 2019-09-28 | MP1006 | 14.2 | 862 | 14.2 | 863 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6600 | 2159.9997 | 149.618
HBG-1.RR.1316.1 | 24220869124440 | Habiganj, Mohonpur R/A, Mojid Mia | 2019-09-28 | MP1006 | 8.8 | 864 | 8.8 | 865 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6600 | 2159.9997 | 92.721
HBG-1.RR.1317.1 | 24220869124440 | Habiganj, Mohonpur R/A, Altaf Chowdhury | 2019-09-28 | MP1006 | 14.1 | 866 | 13.7 | 867 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6600 | 2159.9997 | 144.3498
HBG-1.RR.1318.1 | 24201139126264 | Habiganj, Tatoya, Shamim | 2019-09-28 | MP1006 | 11.6 | 868 | 11.6 | 869 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6768 | 1991.9997 | 122.2232
HBG-1.RR.1319.1 | 24201139126264 | Habiganj, Tatoya, Sahin | 2019-09-28 | MP1006 | 11.3 | 870 | 10.7 | 871 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6768 | 1991.9997 | 112.7403
HBG-1.RR.1320.1 | 24201479126274 | Habiganj, Tatoya, Ayub Ali | 2019-09-28 | MP1006 | 12.8 | 872 | 12.8 | 873 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6768 | 1991.9997 | 134.867
HBG-1.RR.1321.1 | 24221699125405 | Habiganj, Machuliya R/A, Mamun | 2019-09-29 | MP1006 | 19.9 | 892 | 19.9 | 893 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0 | 6768 | 1991.9997 | 209.676
HBG-1.RR.1322.1 | 24222079125350 | Habiganj, Machuliya R/A, Olydev | 2019-09-29 | MP1006 | 10.9 | 894 | 10.9 | 895 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6768 | 1991.9997 | 114.8476
HBG-1.RR.1323.1 | 24222319125347 | Habiganj, Machuliya R/A, Uzzal Mia | 2019-09-29 | MP1006 | 6.1 | 896 | 6.1 | 897 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6768 | 1991.9997 | 64.2725
HBG-1.RR.1324.1 | 24222319125347 | Habiganj, Machuliya R/A, Shofik Mia | 2019-09-29 | MP1006 | 6.4 | 898 | 6.4 | 899 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6768 | 1991.9997 | 67.4335
HBG-1.RR.1325.1 | 24170059125178 | Shaistaganj, Nosrotpur Railgate, Fokrul | 2019-10-07 | MN1032 | 9.9 | 207 | 9.9 | 208 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6624 | 2135.9997 | 104.3112
HBG-1.RR.1326.1 | 24170019125209 | Shaistaganj, Nosrotpur Railgate, Kalu Mia | 2019-10-07 | MN1032 | 8.1 | 209 | 8.1 | 210 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6624 | 2135.9997 | 85.3455
HBG-1.RR.1327.1 | 24165889125199 | Shaistaganj, Nosrotpur Railgate, Seraj Mia | 2019-10-07 | MN1032 | 12.1 | 211 | 12.1 | 212 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6624 | 2135.9997 | 127.4914
HBG-1.RR.1351.1 | 24220499125252 | Habiganj, Mahmudabad R/A, Abdul Motin | 2019-09-23 | MP1006 | 12.4 | 792 | 12.1 | 793 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6768 | 1991.9997 | 127.4914
HBG-1.RR.1352.1 | 24220689125269 | Habiganj, Mahmudabad R/A, Rofique | 2019-09-23 | MP1006 | 12.9 | 794 | 13 | 795 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6768 | 1991.9997 | 136.9743
HBG-1.RR.1353.1 | 24220909125283 | Habiganj, Mahmudabad R/A, Abdul Aziz | 2019-09-23 | MP1006 | 12.1 | 796 | 12.1 | 797 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6768 | 1991.9997 | 127.4914
HBG-1.RR.1354.1 | 24221239125298 | Habiganj, Mahmudabad R/A, Subid Ali | 2019-09-23 | MP1006 | 13 | 798 | 13 | 799 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6768 | 1991.9997 | 136.9743
HBG-1.RR.1355.1 | 24220889125319 | Habiganj, Mahmudabad R/A, Salamot Ali | 2019-09-23 | MP1006 | 8.5 | 800 | 8.5 | 801 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6768 | 1991.9997 | 89.5601
HBG-1.RR.1356.1 | 24204239126025 | Habiganj, West Vadoi, Nurul Islam | 2019-09-26 | MP1006 | 13.7 | 840 | 13.7 | 841 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6768 | 1991.9997 | 144.3498
HBG-1.RR.1357.1 | 24204149126004 | Habiganj, West Vadoi, Mannan | 2019-09-26 | MP1006 | 5.6 | 844 | 5.6 | 845 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6768 | 1991.9997 | 59.0043
HBG-1.RR.1358.1 | 24204459125545 | Habiganj, West Vadoi, Shahjahan | 2019-09-26 | MP1006 | 11.1 | 846 | 10.9 | 847 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6768 | 1991.9997 | 114.8476
HBG-1.RR.1359.1 | 24204579125523 | Habiganj, West Vadoi, Noman Mia | 2019-09-26 | MP1006 | 11.4 | 848 | 11.4 | 849 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6768 | 1991.9997 | 120.1159
HBG-1.RR.1360.1 | 24204579125523 | Habiganj, West Vadoi, Sadek Mia | 2019-09-26 | MP1006 | 12.1 | 850 | 12.1 | 851 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6768 | 1991.9997 | 127.4914
HBG-1.RR.1361.1 | 24204759125543 | Habiganj, West Vadoi, Odud Mia | 2019-09-26 | MP1006 | 17.5 | 852 | 17.5 | 853 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6768 | 1991.9997 | 184.3884
HBG-1.RR.1361.2 | 24204759125543 | Habiganj, West Vadoi, Odud Mia | 2021-01-12 | NQ1007 | 14.1 | 9 | 14.1 | 10 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6768 | 1991.9997 | 148.5644
HBG-1.RR.1362.1 | 24204899125538 | Habiganj, West Vadoi, Abdul Houque | 2019-09-26 | MP1006 | 8.5 | 854 | 8.5 | 855 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6768 | 1991.9997 | 89.5601
HBG-1.RR.1363.1 | 24204899125538 | Habiganj, West Vadoi, Abdul Kayom | 2019-09-26 | MP1006 | 10.9 | 856 | 10.9 | 857 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6768 | 1991.9997 | 114.8476
HBG-1.RR.1364.1 | 24204769125401 | Habiganj, Bhangapool, Vadoi, Golam Mohammad Manik | 2019-09-26 | MP1006 | 13 | 858 | 13 | 859 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6768 | 1991.9997 | 136.9743
HBG-1.RR.1365.1 | 24231589124309 | Habiganj, Batirpur R/A, Shibenro Roy | 2019-09-28 | MP1006 | 12.8 | 874 | 12.8 | 875 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6384 | 2375.9997 | 134.867
HBG-1.RR.1366.1 | 24231639124326 | Habiganj, Batirpur R/A, Anil Rai | 2019-09-28 | MP1006 | 12.9 | 876 | 13 | 877 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6384 | 2375.9997 | 136.9743
HBG-1.RR.1367.1 | 24231629124337 | Habiganj, Batirpur R/A, Devbroto Bonik | 2019-09-28 | MP1006 | 6.2 | 878 | 6.2 | 879 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6384 | 2375.9997 | 65.3262
HBG-1.RR.1368.1 | 24231629124337 | Habiganj, Batirpur R/A, Mohadeb Rai | 2019-09-28 | MP1006 | 13 | 880 | 13 | 881 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6384 | 2375.9997 | 136.9743
HBG-1.RR.1369.1 | 24231629124337 | Habiganj, Batirpur R/A, Shibudev | 2019-09-28 | MP1006 | 12.7 | 884 | 12.7 | 885 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6384 | 2375.9997 | 133.8133
HBG-1.RR.1370.1 | 24231629124337 | Habiganj, Batirpur R/A, Bhanu Bonik | 2019-09-28 | MP1006 | 5.5 | 886 | 5.5 | 887 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6384 | 2375.9997 | 57.9506
HBG-1.RR.1371.1 | 24231729124345 | Habiganj, Batirpur R/A, Subol Sorkar | 2019-09-28 | MP1006 | 4.7 | 888 | 4.7 | 889 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6384 | 2375.9997 | 49.5215
HBG-1.RR.1372.1 | 24231729124345 | Habiganj, Batirpur R/A, Jhontu Sorkar | 2019-09-28 | MP1006 | 7.8 | 890 | 7.8 | 891 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6384 | 2375.9997 | 82.1846
HBG-1.RR.1372.2 | 24231729124345 | Habiganj, Batirpur R/A, Jhontu Sorkar | 2021-01-19 | MN1032 | 5.5 | 33 | 5.4 | 34 | 2022-01-01 | 2022-09-24 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6384 | 2375.9997 | 56.897
HBG-1.RR.1401.1 | 24214089125192 | Habiganj, Thagoria R/A, Md. Shahin | 2019-09-24 | NQ1003 | 5.7 | 856 | 5.7 | 857 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6720 | 2039.9997 | 60.0579
HBG-1.RR.1402.1 | 24214129125203 | Habiganj, Thagoria R/A, H # 5790, Nur Bhaban | 2019-09-24 | NQ1003 | 12.7 | 858 | 12.7 | 859 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6720 | 2039.9997 | 133.8133
HBG-1.RR.1403.1 | 24214209125233 | Habiganj, Thagoria R/A, Jahanara Begum | 2019-09-24 | NQ1003 | 5.2 | 860 | 5.2 | 861 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6720 | 2039.9997 | 54.7897
HBG-1.RR.1404.1 | 24213859125239 | Habiganj, Thagoria R/A, Samsul Islam | 2019-09-24 | NQ1003 | 11.1 | 862 | 11.1 | 863 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6720 | 2039.9997 | 116.9549
HBG-1.RR.1405.1 | 24213969125247 | Habiganj, Thagoria R/A, Sahed Ali | 2019-09-24 | NQ1003 | 9.2 | 864 | 9.2 | 865 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6720 | 2039.9997 | 96.9356
HBG-1.RR.1406.1 | 24213969125247 | Habiganj, Thagoria R/A, Abdul Hamid | 2019-09-24 | NQ1003 | 5.5 | 866 | 5.5 | 867 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6720 | 2039.9997 | 57.9506
HBG-1.RR.1407.1 | 24213859125204 | Habiganj, Thagoria R/A, Bhi Bhi Villa | 2019-09-24 | NQ1003 | 4.6 | 868 | 4.6 | 869 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6720 | 2039.9997 | 48.4678
HBG-1.RR.1408.1 | 24213679125217 | Habiganj, Thagoria R/A, Siraj Mia | 2019-09-24 | NQ1003 | 3 | 870 | 3 | 871 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6720 | 2039.9997 | 31.6094
HBG-1.RR.1409.1 | 24204229126015 | Habiganj, West Badoi, H # 44, Jahanara Begum | 2019-09-26 | NQ1003 | 4 | 28 | 4 | 29 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6768 | 1991.9997 | 42.1459
HBG-1.RR.1410.1 | 24204319125575 | Habiganj, West Badoi, Abdul Gofur | 2019-09-26 | NQ1003 | 14.5 | 30 | 14.6 | 31 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6768 | 1991.9997 | 153.8326
HBG-1.RR.1411.1 | 24204379125577 | Habiganj, West Badoi, Akram Hossain | 2019-09-26 | NQ1003 | 11.2 | 32 | 11.2 | 33 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6768 | 1991.9997 | 118.0086
HBG-1.RR.1412.1 | 24204479126017 | Habiganj, West Badoi, Abdul Hay | 2019-09-26 | NQ1003 | 8.1 | 34 | 8.1 | 35 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6768 | 1991.9997 | 85.3455
HBG-1.RR.1413.1 | 24204479126017 | Habiganj, West Badoi, Moinul Haque Sumon | 2019-09-26 | NQ1003 | 12.7 | 36 | 12.7 | 37 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6768 | 1991.9997 | 133.8133
HBG-1.RR.1414.1 | 24204489126028 | Habiganj, West Badoi, Fazlur Rahman | 2019-09-26 | NQ1003 | 8.7 | 38 | 8.7 | 39 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6768 | 1991.9997 | 91.6674
HBG-1.RR.1415.1 | 24204649125535 | Habiganj, West Badoi, Tareq Mia | 2019-09-26 | NQ1003 | 10.9 | 40 | 10.9 | 41 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6768 | 1991.9997 | 114.8476
HBG-1.RR.1416.1 | 24204799125528 | Habiganj, West Badoi, Abdul Khalek | 2019-09-26 | NQ1003 | 7.6 | 42 | 7.6 | 43 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6768 | 1991.9997 | 80.0773
HBG-1.RR.1417.1 | 24203369125498 | Habiganj, West Badoi, Front of Forest Office, Muslim Uddin | 2019-09-26 | NQ1003 | 11.8 | 44 | 11.8 | 45 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6768 | 1991.9997 | 124.3305
HBG-1.RR.1418.1 | 24203179125486 | Habiganj, West Badoi, Front of Forest Office, A.K.M Abdul Malek | 2019-09-26 | NQ1003 | 4.5 | 46 | 4.5 | 47 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6768 | 1991.9997 | 47.4142
HBG-1.RR.1419.1 | 24230839124595 | Habiganj, North Shamoli R/A, Mamun Mia | 2019-09-28 | NQ1003 | 13 | 72 | 13.1 | 73 | 2022-01-01 | [9 empty] | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0
HBG-1.RR.1420.1 | 24230939125017 | Habiganj, North Shamoli R/A, Faysal Ahmed Chowdhury | 2019-09-28 | NQ1003 | 5.8 | 76 | 5.8 | 77 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6432 | 2327.9997 | 61.1116
HBG-1.RR.1421.1 | 24230999125028 | Habiganj, North Shamoli R/A, Shahidul Hasan | 2019-09-28 | NQ1003 | 12.4 | 78 | 12.4 | 79 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6432 | 2327.9997 | 130.6524
HBG-1.RR.1422.1 | 24231049125034 | Habiganj, North Shamoli R/A, Monirul Islam | 2019-09-28 | NQ1003 | 6.9 | 80 | 6.9 | 81 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6432 | 2327.9997 | 72.7017
HBG-1.RR.1423.1 | 24230949125039 | Habiganj, North Shamoli R/A, Amir Hosen | 2019-09-28 | NQ1003 | 13.2 | 82 | 13.2 | 83 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6432 | 2327.9997 | 139.0816
HBG-1.RR.1424.1 | 24230929125041 | Habiganj, North Shamoli R/A, Halima Khanom | 2019-09-28 | NQ1003 | 6.7 | 84 | 6.7 | 85 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6432 | 2327.9997 | 70.5944
HBG-1.RR.1425.1 | 24230929125041 | Habiganj, North Shamoli R/A, Arju Mia | 2019-09-28 | NQ1003 | 10.3 | 86 | 10.3 | 87 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6432 | 2327.9997 | 108.5258
HBG-1.RR.1426.1 | 24230809125051 | Habiganj, North Shamoli R/A, Sawyed Abdul Hai | 2019-09-28 | NQ1003 | 7.5 | 88 | 7.5 | 89 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6432 | 2327.9997 | 79.0236
HBG-1.RR.1427.1 | 24231169125055 | Habiganj, North Shamoli R/A, Ridoy (Khaja Bhaban) | 2019-09-28 | NQ1003 | 121 | 90 | 121 | 91 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 121 | 121 | 7.26 | 7.26 | 0.0007168 | 100% | 0% | 7.26 | 7.26 | 0.0011869 | 28 | 0.14554 | 0.14554 |  | 0 | 0 | 6432 | 2327.9997 | 1274.9142
HBG-1.RR.1428.1 | 24231009125062 | Habiganj, North Shamoli R/A, Shorifa Cottage | 2019-09-28 | NQ1003 | 10.1 | 92 | 10.1 | 93 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6432 | 2327.9997 | 106.4185
HBG-1.RR.1451.1 | 24214769125140 | Hobigonj, 2 No Pool, Eidgah Road, Sayed Boshir Ahmed, Ahmed Cottage | 2019-09-24 | NQ1003 | 7.4 | 838 | 6.7 | 839 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6720 | 2039.9997 | 70.5944
HBG-1.RR.1452.1 | 24214649125141 | Hobigonj, 2 No Pool, Eidgah Road, Mojjafor Villa | 2019-09-24 | NQ1003 | 11.5 | 841 | 11.1 | 842 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6720 | 2039.9997 | 116.9549
HBG-1.RR.1452.2 | 24214649125141 | Hobigonj, 2 No Pool, Eidgah Road, Mojjafor Villa | 2022-04-02 | LU1001 | 10.8 | 106 | 10.6 | 107 | 2022-04-02 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 4536 | 2039.9997 | 83.8415
HBG-1.RR.1453.1 | 24214329125185 | Hobigonj, Tagoriya R/A, London Bari | 2019-09-24 | NQ1003 | 10.1 | 843 | 10.1 | 844 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6720 | 2039.9997 | 106.4185
HBG-1.RR.1454.1 | 24214339125203 | Hobigonj, Tagoriya R/A, Nur Villa | 2019-09-24 | NQ1003 | 6.9 | 847 | 6.9 | 848 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6720 | 2039.9997 | 72.7017
HBG-1.RR.1455.1 | 24214339125230 | Hobigonj, Tagoriya R/A, Foraig Villa | 2019-09-24 | NQ1003 | 15.3 | 849 | 15.3 | 850 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6720 | 2039.9997 | 161.2082
HBG-1.RR.1456.1 | 24214509125230 | Hobigonj, Tagoriya R/A, Monnan | 2019-09-24 | NQ1003 | 18.4 | 852 | 18.4 | 853 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6720 | 2039.9997 | 193.8713
HBG-1.RR.1457.1 | 24214509125230 | Hobigonj, Tagoriya R/A, Alhaz Md Ileas Uddin, Sopnar Nir | 2019-09-24 | NQ1003 | 10.2 | 854 | 10.2 | 855 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6720 | 2039.9997 | 107.4721
HBG-1.RR.1458.1 | 24225819124483 | Hobigonj, Kali Bari Road, Omni | 2019-09-26 | NQ1003 | 15.6 | 1 | 15.6 | 2 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6480 | 2279.9997 | 164.3691
HBG-1.RR.1459.1 | 24225819124483 | Hobigonj, Kali Bari Road, Apex | 2019-09-26 | NQ1003 | 9.8 | 3 | 9.8 | 4 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6480 | 2279.9997 | 103.2575
HBG-1.RR.1460.1 | 24225819124483 | Hobigonj, Kali Bari Road, Dutch-Bangla Bank Limited | 2019-09-26 | NQ1003 | 11.3 | 5 | 11.3 | 6 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6480 | 2279.9997 | 119.0622
HBG-1.RR.1462.1 | 24225489124471 | Hobigonj, Kali Bari Road, Wahidul Mamun | 2019-09-26 | NQ1003 | 9.6 | 9 | 9.6 | 10 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6480 | 2279.9997 | 101.1502
HBG-1.RR.1463.1 | 24225489124471 | Hobigonj, Kali Bari Road, Abdul Malak | 2019-09-26 | NQ1003 | 7.1 | 11 | 7.1 | 12 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6480 | 2279.9997 | 74.809
HBG-1.RR.1464.1 | 24225369124470 | Hobigong, Town hall Road, Anando Electrick | 2019-09-26 | NQ1003 | 10.2 | 13 | 10.3 | 14 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6480 | 2279.9997 | 108.5258
HBG-1.RR.1465.1 | 24224909124461 | Hobigong, Town hall Road, Kazi Muksud | 2019-09-26 | NQ1003 | 10.8 | 15 | 10.8 | 16 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6504 | 2255.9997 | 113.794
HBG-1.RR.1466.1 | 24224909124461 | Hobigong, Town hall Road, Kazi Muksud | 2019-09-26 | NQ1003 | 13.4 | 17 | 13.2 | 18 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6504 | 2255.9997 | 139.0816
HBG-1.RR.1467.1 | 24224829124471 | Hobigong, Town hall Road, Asma Khatun | 2019-09-26 | NQ1003 | 7.2 | 20 | 7.2 | 21 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6504 | 2255.9997 | 75.8627
HBG-1.RR.1468.1 | 24224889124448 | Hobigong, Town hall Road, Sibu Condro Dav | 2019-09-26 | NQ1003 | 12.2 | 22 | 12.2 | 23 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6504 | 2255.9997 | 128.5451
HBG-1.RR.1469.1 | 24224889124448 | Hobigong, Town hall Road, Autul Chondro Rai | 2019-09-26 | NQ1003 | 10.6 | 24 | 10.6 | 25 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6504 | 2255.9997 | 111.6867
HBG-1.RR.1470.1 | 24224889124448 | Hobigong, Town hall Road, Dijandro Lal | 2019-09-26 | NQ1003 | 8.3 | 26 | 8.3 | 27 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6504 | 2255.9997 | 87.4528
HBG-1.RR.1471.1 | 24221039124389 | Hobigonj, Kod Station Road South, Md Abdul Ahad Baccu | 2019-09-28 | NQ1003 | 12.8 | 48 | 12.3 | 49 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 120 | 0 | 6432 | 2207.9997 | 127.8234
HBG-1.RR.1472.1 | 24221039124389 | Hobigonj, Kod Station Road South, Md Abdul Ahad Baccu | 2019-09-28 | NQ1003 | 10.8 | 50 | 10.8 | 51 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6552 | 2207.9997 | 113.794
HBG-1.RR.1472.2 | 24221039124389 | Hobigonj, Kod Station Road South, Md Abdul Ahad Baccu | 2021-08-31 | LX1011 | 18.1 | 90 | 18.2 | 91 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 6552 | 2207.9997 | 191.764
HBG-1.RR.1473.1 | 24220919124373 | Hobigonj, Kod Station Road South, Moksudur Rahman | 2019-09-28 | NQ1003 | 8.7 | 52 | 8.7 | 53 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6552 | 2207.9997 | 91.6674
HBG-1.RR.1474.1 | 24221129124379 | Hobigonj, Kod Station Road South, Nozrul Islam | 2019-09-28 | NQ1003 | 13.9 | 56 | 13.9 | 57 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6552 | 2207.9997 | 146.4571
HBG-1.RR.1475.1 | 24221069124379 | Hobigonj, Kod Station Road South, Salma | 2019-09-28 | NQ1003 | 10.3 | 58 | 10.3 | 59 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6552 | 2207.9997 | 108.5258
HBG-1.RR.1476.1 | 24221069124379 | Hobigonj, Kod Station Road South, Firoz Mia | 2019-09-28 | NQ1003 | 9.7 | 60 | 9.7 | 61 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6552 | 2207.9997 | 102.2039
HBG-1.RR.1477.1 | 24201459126198 | Hobigong, Tatuia, Doctor Bari Jama Mosjid Road, Abdul Nur | 2019-09-28 | NQ1003 | 8.6 | 62 | 8.6 | 63 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6768 | 1991.9997 | 90.6137
HBG-1.RR.1478.1 | 24201469126207 | Hobigong, Tatuia, Doctor Bari Jama Mosjid Road, Master Villa | 2019-09-28 | NQ1003 | 10.6 | 64 | 10.6 | 65 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6768 | 1991.9997 | 111.6867
HBG-1.RR.1479.1 | 24201469126207 | Hobigong, Tatuia, Doctor Bari Jama Mosjid Road, Kismot Ali | 2019-09-28 | NQ1003 | 11.1 | 66 | 11.1 | 67 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6768 | 1991.9997 | 116.9549
HBG-1.RR.1479.2 | 24201469126207 | Hobigong, Tatuia, Doctor Bari Jama Mosjid Road, Kismot Ali | 2021-01-12 | NQ1007 | 12.2 | 5 | 12.2 | 6 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6768 | 1991.9997 | 128.5451
HBG-1.RR.1480.1 | 24200769126039 | Hobigonj, Dulia Khal, Md Amir Ali | 2019-09-28 | NQ1003 | 10 | 68 | 10 | 69 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6768 | 1991.9997 | 105.3648
HBG-1.RR.1481.1 | 24200769126039 | Hobigonj, Dulia Khal, Faruk | 2019-09-28 | NQ1003 | 7.1 | 70 | 7.1 | 71 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6768 | 1991.9997 | 74.809
HBG-1.RR.1482.1 | 24221279125399 | Hobigonj, Masuliea R/A, Sonkor Pal | 2019-09-29 | NQ1003 | 13.1 | 94 | 13.1 | 95 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6768 | 1991.9997 | 138.0279
HBG-1.RR.1482.2 | 24221279125399 | Hobigonj, Masuliea R/A, Sonkor Pal | 2022-03-30 | LU1001 | 12.8 | 98 | 12.8 | 99 | 2022-03-30 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 4656 | 1991.9997 | 102.3511
HBG-1.RR.1483.1 | 24221299125382 | Hobigonj, Masuliea R/A, Ojit Pal | 2019-09-29 | NQ1003 | 10.8 | 96 | 10.8 | 97 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6768 | 1991.9997 | 113.794
HBG-1.RR.1484.1 | 24221299125382 | Hobigonj, Masuliea R/A, Suruj Datta | 2019-09-29 | NQ1003 | 15.5 | 98 | 15.5 | 99 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 6768 | 1991.9997 | 163.3155
HBG-1.RR.1501.1 | 24222579125062 | Habiganj, Anantopur R/A, Shahedul Haq | 2019-09-21 | LX1011 | 11.1 | 211 | 11.1 | 212 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6576 | 2183.9997 | 116.9549
HBG-1.RR.1502.1 | 24222579125062 | Habiganj, Anantopur R/A, Ajmal Uddin Nibash | 2019-09-21 | LX1011 | 3.5 | 213 | 3.5 | 214 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6576 | 2183.9997 | 36.8777
HBG-1.RR.1503.1 | 24222579125070 | Habiganj, Anantopur R/A, Sayed Ali | 2019-09-21 | LX1011 | 11.7 | 215 | 11.7 | 216 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6576 | 2183.9997 | 123.2768
HBG-1.RR.1504.1 | 24222579125070 | Habiganj, Anantopur R/A, Razzaq Ali | 2019-09-21 | LX1011 | 9.3 | 217 | 9.3 | 218 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6576 | 2183.9997 | 97.9893
HBG-1.RR.1505.1 | 24222579125070 | Habiganj, Anantopur R/A, Romij Ali | 2019-09-21 | LX1011 | 13.4 | 219 | 13.4 | 220 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6576 | 2183.9997 | 141.1888
HBG-1.RR.1506.1 | 24222569125078 | Habiganj, Anantopur R/A, Faysal Hossain | 2019-09-21 | LX1011 | 12.5 | 221 | 12.5 | 222 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6576 | 2183.9997 | 131.706
HBG-1.RR.1506.2 | 24222569125078 | Habiganj, Anantopur R/A, Faysal Hossain | 2020-10-12 | NQ1009 | 13.3 | 461 | 13.3 | 462 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6576 | 2183.9997 | 140.1352
HBG-1.RR.1507.1 | 24222569125078 | Habiganj, Anantopur R/A, Afiya Akter | 2019-09-21 | LX1011 | 12 | 223 | 11.5 | 224 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6576 | 2183.9997 | 121.1695
HBG-1.RR.1508.1 | 24222749125087 | Habiganj, Anantopur R/A, Taher Mia | 2019-09-21 | LX1011 | 15.2 | 225 | 14.6 | 226 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6576 | 2183.9997 | 153.8326
HBG-1.RR.1509.1 | 24222749125087 | Habiganj, Anantopur R/A, Alkas Mia | 2019-09-21 | LX1011 | 13.7 | 227 | 13.7 | 228 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6576 | 2183.9997 | 144.3498
HBG-1.RR.1510.1 | 24221559125039 | Habiganj, Shaistanagar R/A, Hasna Monjil | 2019-09-22 | LX1011 | 12.3 | 249 | 12.3 | 250 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6672 | 2087.9997 | 129.5987
HBG-1.RR.1511.1 | 24221629125055 | Habiganj, Shaistanagar R/A, Sayeda Monowara | 2019-09-22 | LX1011 | 13.4 | 251 | 13.4 | 252 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6672 | 2087.9997 | 141.1888
HBG-1.RR.1512.1 | 24221459125069 | Habiganj, Shaistanagar R/A, Mortuza Cottage, Lal Mia | 2019-09-22 | LX1011 | 22.2 | 253 | 22.3 | 254 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 6672 | 2087.9997 | 234.9635
HBG-1.RR.1513.1 | 24221509125077 | Habiganj, Shaistanagar R/A, Golam Mahmud | 2019-09-22 | LX1011 | 15.9 | 255 | 15.8 | 256 | 2022-01-01 | [9 empty] | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0
HBG-1.RR.1514.1 | 24221509125077 | Habiganj, Shaistanagar R/A, Bulbul Ahmed | 2019-09-22 | LX1011 | 11.3 | 257 | 11.3 | 258 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6672 | 2087.9997 | 119.0622
HBG-1.RR.1515.1 | 24221509125077 | Habiganj, Shaistanagar R/A, Tania Akter Keya | 2019-09-22 | LX1011 | 9.5 | 259 | 9.6 | 260 | 2022-01-01 | [9 empty] | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0
HBG-1.RR.1516.1 | 24221339125082 | Habiganj, Shaistanagar R/A, Golam Mohit | 2019-09-22 | LX1011 | 13.2 | 261 | 13.2 | 262 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6672 | 2087.9997 | 139.0816
HBG-1.RR.1517.1 | 24221339125082 | Habiganj, Shaistanagar R/A, Bulbul Mia | 2019-09-22 | LX1011 | 19 | 263 | 18.3 | 264 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 18.3 | 18.3 | 1.098 | 1.098 | 0.0007168 | 100% | 0% | 1.098 | 1.098 | 0.0011869 | 28 | 0.022011 | 0.022011 |  | 0 | 0 | 6672 | 2087.9997 | 192.8176
HBG-1.RR.1518.1 | 24221329125057 | Habiganj, Shaistanagar R/A, Abdul Haq | 2019-09-22 | LX1011 | 13.9 | 265 | 13.9 | 266 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6672 | 2087.9997 | 146.4571
HBG-1.RR.1519.1 | 24221329125057 | Habiganj, Shaistanagar R/A, Sundor Ali | 2019-09-22 | LX1011 | 7.1 | 267 | 7.1 | 268 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6672 | 2087.9997 | 74.809
HBG-1.RR.1520.1 | 24221329125057 | Habiganj, Shaistanagar R/A, Ambia Khatun | 2019-09-22 | LX1011 | 18.1 | 269 | 18.1 | 270 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6672 | 2087.9997 | 190.7103
HBG-1.RR.1521.1 | 24221169125061 | Habiganj, Shaistanagar R/A, Jaynullah Mia | 2019-09-22 | LX1011 | 12.6 | 271 | 12.6 | 272 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 4776 | 0 | 1896 | 2087.9997 | 60.3784
HBG-1.RR.1522.1 | 24221339125106 | Habiganj, Shaistanagar R/A, Abdul Ahad | 2019-09-23 | LX1011 | 9.5 | 273 | 9.1 | 274 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6672 | 2087.9997 | 95.882
HBG-1.RR.1523.1 | 24220909125123 | Habiganj, Shaistanagar R/A, Wahedur Rahman, H# 54 | 2019-09-23 | LX1011 | 11.4 | 275 | 11.4 | 276 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6672 | 2087.9997 | 120.1159
HBG-1.RR.1524.1 | 24220909125123 | Habiganj, Shaistanagar R/A, Soikot Ahmed | 2019-09-23 | LX1011 | 20.3 | 277 | 20.3 | 278 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 20.3 | 20.3 | 1.218 | 1.218 | 0.0007168 | 100% | 0% | 1.218 | 1.218 | 0.0011869 | 28 | 0.024417 | 0.024417 |  | 0 | 0 | 6672 | 2087.9997 | 213.8906
HBG-1.RR.1525.1 | 24220909125123 | Habiganj, Shaistanagar R/A, Shah Habibur Rahman | 2019-09-23 | LX1011 | 11.1 | 279 | 11.1 | 280 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6672 | 2087.9997 | 116.9549
HBG-1.RR.1526.1 | 24220909125123 | Habiganj, Shaistanagar R/A, Abdul Bahar | 2019-09-23 | LX1011 | 14.8 | 281 | 14.8 | 282 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6672 | 2087.9997 | 155.9399
HBG-1.RR.1527.1 | 24221039125122 | Habiganj, Shaistanagar R/A, Saiyod Renu Mia | 2019-09-23 | LX1011 | 12.3 | 283 | 11.5 | 284 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6672 | 2087.9997 | 121.1695
HBG-1.RR.1528.1 | 24221199125128 | Habiganj, Shaistanagar R/A, Kazi Nilufar Akter | 2019-09-23 | LX1011 | 22.4 | 285 | 22.4 | 286 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 22.4 | 22.4 | 1.344 | 1.344 | 0.0007168 | 100% | 0% | 1.344 | 1.344 | 0.0011869 | 28 | 0.026943 | 0.026943 |  | 0 | 0 | 6672 | 2087.9997 | 236.0172
HBG-1.RR.1529.1 | 24221219125154 | Habiganj, Shaistanagar R/A, Abul Fazal | 2019-09-23 | LX1011 | 20.7 | 287 | 20.9 | 288 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 20.9 | 20.9 | 1.254 | 1.254 | 0.0007168 | 100% | 0% | 1.254 | 1.254 | 0.0011869 | 28 | 0.025138 | 0.025138 |  | 0 | 0 | 6672 | 2087.9997 | 220.2125
HBG-1.RR.1530.1 | 24221209125157 | Habiganj, Shaistanagar R/A, Moynul Haq | 2019-09-23 | LX1011 | 18.9 | 289 | 19 | 290 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 6672 | 2087.9997 | 200.1931
HBG-1.RR.1531.1 | 24221069125164 | Habiganj, Shaistanagar R/A, Suruj Mia | 2019-09-23 | LX1011 | 16.9 | 291 | 17 | 292 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 6672 | 2087.9997 | 179.1202
HBG-1.RR.1531.2 | 24221069125164 | Habiganj, Shaistanagar R/A, Suruj Mia | 2022-10-06 | NQ1007 | 29.4 | 42 | 29.4 | 43 | 2022-10-06 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 29.4 | 29.4 | 1.764 | 1.764 | 0.0007168 | 100% | 0% | 1.764 | 1.764 | 0.0011869 | 28 | 0.035362 | 0.035362 |  | 0 | 0 | 0 | 2087.9997 | 73.8362
HBG-1.RR.1532.1 | 24220989125158 | Habiganj, Shaistanagar R/A, M.A. Jalil | 2019-09-23 | LX1011 | 15.1 | 293 | 15.3 | 294 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6672 | 2087.9997 | 161.2082
HBG-1.RR.1533.1 | 24220989125158 | Habiganj, Shaistanagar R/A, Shohagjul Islam | 2019-09-23 | LX1011 | 10.1 | 295 | 10.1 | 296 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6672 | 2087.9997 | 106.4185
HBG-1.RR.1534.1 | 24220409125188 | Habiganj, Shaistanagar R/A, Koborsthan Road, Regia Begum | 2019-09-23 | LX1011 | 12.6 | 297 | 12.3 | 298 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6768 | 1991.9997 | 129.5987
HBG-1.RR.1534.2 | 24220409125188 | Habiganj, Shaistanagar R/A, Koborsthan Road, Regia Begum | 2020-10-12 | NQ1003 | 6.4 | 20 | 6.4 | 21 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6768 | 1991.9997 | 67.4335
HBG-1.RR.1535.1 | 24220409125188 | Habiganj, Shaistanagar R/A, Koborsthan Road, Khondokar Villa | 2019-09-23 | LX1011 | 19.5 | 299 | 18.8 | 300 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 6768 | 1991.9997 | 198.0858
HBG-1.RR.1536.1 | 24220319125199 | Habiganj, Shaistanagar R/A, Koborsthan Road, Forid Mia | 2019-09-23 | LX1011 | 14.5 | 301 | 14 | 302 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6768 | 1991.9997 | 147.5107
HBG-1.RR.1537.1 | 24220319125199 | Habiganj, Shaistanagar R/A, Koborsthan Road, Moinuddin | 2019-09-23 | LX1011 | 18.5 | 303 | 17.8 | 304 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 6768 | 1991.9997 | 187.5494
HBG-1.RR.1538.1 | 24220389125171 | Habiganj, Shaistanagar R/A, Koborsthan Road, Nur Hossain | 2019-09-24 | LX1011 | 15.4 | 337 | 15.4 | 338 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6768 | 1991.9997 | 162.2618
HBG-1.RR.1539.1 | 24220389125171 | Habiganj, Shaistanagar R/A, Koborsthan Road, Dulal Mia | 2019-09-24 | LX1011 | 9 | 339 | 9 | 340 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6768 | 1991.9997 | 94.8283
HBG-1.RR.1540.1 | 24220419125165 | Habiganj, Shaistanagar R/A, Koborsthan Road, Abdullah | 2019-09-24 | LX1011 | 10.4 | 341 | 10.4 | 342 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6768 | 1991.9997 | 109.5794
HBG-1.RR.1541.1 | 24220459125167 | Habiganj, Shaistanagar R/A, Koborsthan Road, Wahid | 2019-09-24 | LX1011 | 11.3 | 343 | 11.2 | 344 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6768 | 1991.9997 | 118.0086
HBG-1.RR.1542.1 | 24220409125148 | Habiganj, Shaistanagar R/A, Koborsthan Road, Shah Alam | 2019-09-24 | LX1011 | 17 | 345 | 17 | 346 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 6672 | 2087.9997 | 179.1202
HBG-1.RR.1543.1 | 24220409125148 | Habiganj, Shaistanagar R/A, Koborsthan Road, Shah House | 2019-09-24 | LX1011 | 10.3 | 349 | 10.3 | 350 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6672 | 2087.9997 | 108.5258
HBG-1.RR.1543.2 | 24220409125148 | Habiganj, Shaistanagar R/A, Koborsthan Road, Shah House | 2022-10-06 | NQ1007 | 10 | 40 | 9.9 | 41 | 2022-10-06 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 0 | 2087.9997 | 24.8632
HBG-1.RR.1544.1 | 24220419125132 | Habiganj, Shaistanagar R/A, Koborsthan Road, Abdul Kaiyum | 2019-09-24 | LX1011 | 15.9 | 351 | 15.9 | 352 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6672 | 2087.9997 | 167.5301
HBG-1.RR.1545.1 | 24220419125132 | Habiganj, Shaistanagar R/A, Koborsthan Road, Azman | 2019-09-24 | LX1011 | 13.7 | 353 | 13.7 | 354 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6672 | 2087.9997 | 144.3498
HBG-1.RR.1546.1 | 24220419125132 | Habiganj, Shaistanagar R/A, Koborsthan Road, Kobir | 2019-09-24 | LX1011 | 11.8 | 355 | 11.8 | 356 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6672 | 2087.9997 | 124.3305
HBG-1.RR.1547.1 | 24220469125115 | Habiganj, Shaistanagar R/A, Koborsthan Road, Kamal Ahmed | 2019-09-24 | LX1011 | 18.7 | 360 | 18.7 | 361 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6672 | 2087.9997 | 197.0322
HBG-1.RR.1548.1 | 24220469125115 | Habiganj, Shaistanagar R/A, Koborsthan Road, Shanti Niketon, Joshim | 2019-09-24 | LX1011 | 14.6 | 362 | 14.5 | 363 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 6672 | 2087.9997 | 152.779
HBG-1.RR.1549.1 | 24220469125115 | Habiganj, Shaistanagar R/A, Koborsthan Road, Serajul Islam | 2019-09-24 | LX1011 | 11.1 | 364 | 11.8 | 365 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6672 | 2087.9997 | 124.3305
HBG-1.RR.1550.1 | 24220299125106 | Habiganj, Shaistanagar R/A, Koborsthan Road, Sohan | 2019-09-24 | LX1011 | 15.4 | 366 | 15.4 | 367 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6672 | 2087.9997 | 162.2618
HBG-1.RR.1551.1 | 24223059125053 | Kurcsh Nogur R/A, Ward # 09, Harun Mia | 2019-09-21 | LX1011 | 13.3 | 201 | 13.3 | 202 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6576 | 2183.9997 | 140.1352
HBG-1.RR.1552.1 | 24223049125067 | Kurcsh Nogur R/A, Ward # 09, Md. Nur Mia | 2019-09-21 | LX1011 | 10.9 | 203 | 10.9 | 204 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6576 | 2183.9997 | 114.8476
HBG-1.RR.1553.1 | 24222659125064 | Kurcsh Nogur R/A, Ward # 09, Hona Mia | 2019-09-21 | LX1011 | 10.9 | 205 | 10.9 | 206 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6576 | 2183.9997 | 114.8476
HBG-1.RR.1554.1 | 24222659125064 | Kurcsh Nogur R/A, Ward # 09, Abdul Hamid | 2019-09-21 | LX1011 | 36.3 | 207 | 36.3 | 208 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 36.3 | 36.3 | 2.178 | 2.178 | 0.0007168 | 100% | 0% | 2.178 | 2.178 | 0.0011869 | 28 | 0.043661 | 0.043661 |  | 0 | 0 | 6576 | 2183.9997 | 382.4743
HBG-1.RR.1555.1 | 24222659125064 | Kurcsh Nogur R/A, Ward # 09, Dulal | 2019-09-21 | LX1011 | 8.7 | 209 | 8.7 | 210 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6576 | 2183.9997 | 91.6674
HBG-1.RR.1556.1 | 24222239125034 | Habigamj, Hospital Gate, Hospital Road, Amir Hossen Chowdhury | 2019-09-22 | LX1011 | 11.1 | 229 | 11.1 | 230 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6576 | 2183.9997 | 116.9549
HBG-1.RR.1557.1 | 24222139125090 | Habigamj, Hospital Gate, Onontopur R/A,Alfu Mia | 2019-09-22 | LX1011 | 11.5 | 231 | 10.9 | 232 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6600 | 2159.9997 | 114.8476
HBG-1.RR.1558.1 | 24222139125090 | Habigamj, Hospital Gate, Onontopur R/A, Forid Mia | 2019-09-22 | LX1011 | 18.4 | 233 | 18.4 | 234 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6600 | 2159.9997 | 193.8713
HBG-1.RR.1559.1 | 24222159125090 | Habigamj, Hospital Gate, Onontopur R/A, Maksud Mia | 2019-09-22 | LX1011 | 6 | 235 | 6 | 236 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6600 | 2159.9997 | 63.2189
HBG-1.RR.1560.1 | 24221959125108 | Habigamj, Hospital Gate, Onontopur R/A, Abdus Salam | 2019-09-22 | LX1011 | 3.1 | 237 | 3.1 | 238 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6600 | 2159.9997 | 32.6631
HBG-1.RR.1561.1 | 24221959125108 | Habigamj, Hospital Gate, Onontopur R/A, Al-Khaj | 2019-09-22 | LX1011 | 5.9 | 239 | 5.9 | 240 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6600 | 2159.9997 | 62.1652
HBG-1.RR.1562.1 | 24221829125112 | Habigamj, Hospital Gate, Onontopur R/A, Ruhul Amin | 2019-09-22 | LX1011 | 15.2 | 241 | 15.2 | 242 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6600 | 2159.9997 | 160.1545
HBG-1.RR.1563.1 | 24221879125074 | Habiganj, Circuit House road, Anowara Khatun | 2019-09-22 | LX1011 | 10.9 | 243 | 10.9 | 244 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6672 | 2087.9997 | 114.8476
HBG-1.RR.1564.1 | 24221709125067 | Habiganj, Circuit House road, Alim Kotage | 2019-09-22 | LX1011 | 10.6 | 245 | 10.6 | 246 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6672 | 2087.9997 | 111.6867
HBG-1.RR.1564.2 | 24221709125067 | Habiganj, Circuit House road, Alim Kotage | 2020-10-12 | NQ1009 | 8.6 | 424 | 8.6 | 425 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6672 | 2087.9997 | 90.6137
HBG-1.RR.1565.1 | 24222029125036 | Habiganj, Circuit House road, Abdul Mojid | 2019-09-22 | LX1011 | 14.8 | 247 | 14.7 | 248 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6672 | 2087.9997 | 154.8863
HBG-1.RR.1565.2 | 24222029125036 | Habiganj, Circuit House road, Abdul Mojid | 2020-10-12 | NQ1009 | 3 | 413 | 3 | 414 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6672 | 2087.9997 | 31.6094
HBG-1.RR.1566.1 | 24220359125298 | Habiganj, Poil Road, Shaistanagar, Siddik | 2019-09-23 | LX1011 | 21.8 | 305 | 21.8 | 306 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 21.8 | 21.8 | 1.308 | 1.308 | 0.0007168 | 100% | 0% | 1.308 | 1.308 | 0.0011869 | 28 | 0.026221 | 0.026221 |  | 0 | 0 | 6768 | 1991.9997 | 229.6953
HBG-1.RR.1567.1 | 24220359125298 | Habiganj, Poil Road, Shaistanagar, Kalam | 2019-09-23 | LX1011 | 7.3 | 307 | 7.3 | 308 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6768 | 1991.9997 | 76.9163
HBG-1.RR.1568.1 | 24220449125307 | Habiganj, Poil Road, Shaistanagar, Kuddus Mia | 2019-09-23 | LX1011 | 22 | 309 | 22 | 310 | 2022-01-01 | 2022-10-10 | NQ1007 | 1.4 | 59 | 1.4 | 60 | 2022-10-10 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6768 | 1991.9997
HBG-1.RR.1569.1 | 24220589125342 | Habiganj, Poil Road, Shaistanagar, Jahir Uddin | 2019-09-23 | LX1011 | 14.7 | 311 | 14.7 | 312 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6768 | 1991.9997 | 154.8863
HBG-1.RR.1570.1 | 24220629125358 | Habiganj, Poil Road, Shaistanagar, Abdul Bosir | 2019-09-23 | LX1011 | 17.3 | 313 | 17.3 | 314 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 6768 | 1991.9997 | 182.2811
HBG-1.RR.1571.1 | 24220229125264 | Habiganj, Poil Road, Shaistanagar, Abdur Nur | 2019-09-23 | LX1011 | 14.3 | 315 | 14.3 | 316 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6768 | 1991.9997 | 150.6717
HBG-1.RR.1572.1 | 24220229125264 | Habiganj, Poil Road, Shaistanagar, Nur Alom | 2019-09-23 | LX1011 | 13.6 | 317 | 13.5 | 318 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6768 | 1991.9997 | 142.2425
HBG-1.RR.1572.2 | 24220229125264 | Habiganj, Poil Road, Shaistanagar, Nur Alom | 2022-03-30 | LU1001 | 2.3 | 100 | 2.3 | 101 | 2022-03-30 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 4656 | 1991.9997 | 18.3912
HBG-1.RR.1573.1 | 24220239125238 | Habiganj, Poil Road, Shaistanagar, Abdul Ohab | 2019-09-23 | LX1011 | 12.5 | 319 | 12.5 | 320 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6600 | 2159.9997 | 131.706
HBG-1.RR.1574.1 | 24220239125238 | Habiganj, Poil Road, Shaistanagar, Raja Mia | 2019-09-23 | LX1011 | 11 | 321 | 11 | 322 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6600 | 2159.9997 | 115.9013
HBG-1.RR.1575.1 | 24220239125238 | Habiganj, Poil Road, Shaistanagar, Cherag Ali | 2019-09-23 | LX1011 | 10.9 | 323 | 10.9 | 324 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6600 | 2159.9997 | 114.8476
HBG-1.RR.1576.1 | 24220209125186 | Habiganj, Poil Road, Shaistanagar, Abdul Mozid | 2019-09-23 | LX1011 | 14.2 | 325 | 14.2 | 326 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6768 | 1991.9997 | 149.618
HBG-1.RR.1577.1 | 24220209125186 | Habiganj, Poil Road, Shaistanagar, Brac Office | 2019-09-23 | LX1011 | 6.9 | 327 | 6.9 | 328 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6768 | 1991.9997 | 72.7017
HBG-1.RR.1578.1 | 24220169125163 | Habiganj, Poil Road, Shaistanagar, Talibuddin | 2019-09-23 | LX1011 | 11.7 | 329 | 11.7 | 330 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6768 | 1991.9997 | 123.2768
HBG-1.RR.1579.1 | 24220309125108 | Habiganj, Poil Road, Shaistanagar, Abdul Kuddus | 2019-09-23 | LX1011 | 7.2 | 335 | 7.2 | 336 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6672 | 2087.9997 | 75.8627
HBG-1.RR.1580.1 | 24213099125207 | Habiganjj, Tagunia R/A, Ayub Ali | 2019-09-24 | LX1011 | 12.6 | 374 | 12.6 | 375 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6720 | 2039.9997 | 132.7597
HBG-1.RR.1581.1 | 24213079125220 | Habiganjj, Tagunia R/A, Sayful Islam | 2019-09-24 | LX1011 | 12.5 | 376 | 12.5 | 377 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6720 | 2039.9997 | 131.706
HBG-1.RR.1582.1 | 24213079125220 | Habiganjj, Tagunia R/A, Darul Alom | 2019-09-24 | LX1011 | 13.1 | 378 | 13.1 | 379 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6720 | 2039.9997 | 138.0279
HBG-1.RR.1582.2 | 24213079125220 | Habiganjj, Tagunia R/A, Darul Alom | 2020-10-12 | NQ1009 | 5.4 | 385 | 5.4 | 386 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6720 | 2039.9997 | 56.897
HBG-1.RR.1583.1 | 24213079125220 | Habiganjj, Tagunia R/A, Mojib Ali | 2019-09-24 | LX1011 | 9.5 | 380 | 9.5 | 381 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6720 | 2039.9997 | 100.0966
HBG-1.RR.1584.1 | 24213039125237 | Habiganjj, Tagunia R/A, Sayful Islam | 2019-09-24 | LX1011 | 13.9 | 382 | 13.9 | 383 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6720 | 2039.9997 | 146.4571
HBG-1.RR.1585.1 | 24213029125244 | Habiganjj, Tagunia R/A, Younus Ali | 2019-09-24 | LX1011 | 12.6 | 384 | 12.6 | 385 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6720 | 2039.9997 | 132.7597
HBG-1.RR.1586.1 | 24213029125244 | Habiganjj, Tagunia R/A, Maksud Rahman | 2019-09-24 | LX1011 | 11.6 | 386 | 11.6 | 387 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6720 | 2039.9997 | 122.2232
HBG-1.RR.1587.1 | 24213029125244 | Habiganjj, Tagunia R/A, Oliur Rohoman | 2019-09-24 | LX1011 | 10.9 | 388 | 10.9 | 389 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6720 | 2039.9997 | 114.8476
HBG-1.RR.1588.1 | 24213159125249 | Habiganjj, Tagunia R/A, Didar Hossen | 2019-09-24 | LX1011 | 13 | 390 | 13 | 391 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6720 | 2039.9997 | 136.9743
HBG-1.RR.1589.1 | 24213159125249 | Habiganjj, Tagunia R/A, Salek | 2019-09-24 | LX1011 | 12 | 392 | 12 | 393 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6720 | 2039.9997 | 126.4378
HBG-1.RR.1590.1 | 24213159125249 | Habiganjj, Tagunia R/A, Kajol Mia | 2019-09-24 | LX1011 | 6.7 | 394 | 6.2 | 395 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6720 | 2039.9997 | 65.3262
HBG-1.RR.1591.1 | 24213039125189 | Habiganj, Upazila Rooad,Abdul Jolil | 2019-09-24 | LX1011 | 24.2 | 396 | 24.2 | 397 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 24.2 | 24.2 | 1.452 | 1.452 | 0.0007168 | 100% | 0% | 1.452 | 1.452 | 0.0011869 | 28 | 0.029108 | 0.029108 |  | 0 | 0 | 6720 | 2039.9997 | 254.9828
HBG-1.RR.1591.2 | 24213039125189 | Habiganj, Upazila Rooad,Abdul Jolil | 2022-04-02 | LU1001 | 30 | 112 | 29.6 | 113 | 2022-04-02 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 29.6 | 29.6 | 1.776 | 1.776 | 0.0007168 | 100% | 0% | 1.776 | 1.776 | 0.0011869 | 28 | 0.035603 | 0.035603 |  | 0 | 0 | 4536 | 2039.9997 | 234.1235
HBG-1.RR.1592.1 | 24212849125214 | Habiganj, Upazila Rooad,Water Development Board | 2019-09-24 | LX1011 | 12.5 | 398 | 12.6 | 399 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6720 | 2039.9997 | 132.7597
HBG-1.RR.1593.1 | 24212709125242 | Habiganj, Upazila Rooad,Water Development Board | 2019-09-24 | LX1011 | 9.3 | 400 | 9.3 | 401 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6720 | 2039.9997 | 97.9893
HBG-1.RR.1594.1 | 24222759125012 | Habiganj, Koreshnagor R/A, Ward # 09,Amzad Monzil | 2019-09-26 | LX1011 | 26.6 | 1 | 26.6 | 2 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 26.6 | 26.6 | 1.596 | 1.596 | 0.0007168 | 100% | 0% | 1.596 | 1.596 | 0.0011869 | 28 | 0.031994 | 0.031994 |  | 0 | 0 | 6576 | 2183.9997 | 280.2704
HBG-1.RR.1594.2 | 24222759125012 | Habiganj, Koreshnagor R/A, Ward # 09,Amzad Monzil | 2019-09-26 | LX1011 | 7.6 | 3 | 7 | 4 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6576 | 2183.9997 | 73.7554
HBG-1.RR.1595.1 | 24211809125232 | Habiganj, Upazila Gate, Poddarbari, Cherag Ali | 2019-09-26 | LX1011 | 14.4 | 5 | 14.4 | 6 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6720 | 2039.9997 | 151.7253
HBG-1.RR.1596.1 | 24210569125279 | Habiganj, Upazila Road, Vadoy, Sohid | 2019-09-26 | LX1011 | 17.9 | 7 | 17.8 | 8 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 6720 | 2039.9997 | 187.5494
HBG-1.RR.1597.1 | 24210619125326 | Habiganj, Upazila Road, West Vadoy, Sukkur Ali | 2019-09-26 | LX1011 | 23.7 | 9 | 23.7 | 10 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 23.7 | 23.7 | 1.422 | 1.422 | 0.0007168 | 100% | 0% | 1.422 | 1.422 | 0.0011869 | 28 | 0.028506 | 0.028506 |  | 0 | 0 | 6720 | 2039.9997 | 249.7146
HBG-1.RR.1598.1 | 24210619125326 | Habiganj, Upazila Road, West Vadoy, Md. Arju Mia | 2019-09-26 | LX1011 | 11.8 | 11 | 11.8 | 12 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6720 | 2039.9997 | 124.3305
HBG-1.RR.1599.1 | 24210709125342 | Habiganj, Upazila Road, West Vadoy, Saschu Mia | 2019-09-26 | LX1011 | 13.4 | 13 | 13.5 | 14 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6720 | 2039.9997 | 142.2425
HBG-1.RR.1600.1 | 24210879125337 | Habiganj, Upazila Road, West Vadoy, Anu Master | 2019-09-26 | LX1011 | 17.9 | 15 | 17.9 | 16 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 6720 | 2039.9997 | 188.603
HBG-1.RR.1801.1 | 24220289125089 | Habiganj, Shaistanagar R/A, Julhash Mia | 2019-09-24 | LX1011 | 6.5 | 368 | 6.5 | 369 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6672 | 2087.9997 | 68.4871
HBG-1.RR.1802.1 | 24220349125105 | Habiganj, Shaistanagar R/A, Saleha Bhaban, Mahmudur Rahman | 2019-09-24 | LX1011 | 10.9 | 370 | 10.9 | 371 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6672 | 2087.9997 | 114.8476
HBG-1.RR.1803.1 | 24220649125126 | Habiganj, Shaistanagar R/A, Abdul Haque | 2019-09-24 | LX1011 | 14.1 | 372 | 14.1 | 373 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6672 | 2087.9997 | 148.5644
HBG-1.RR.1804.1 | 24210359125276 | Habiganj, West Vadei, near by Gas office, Romij Hazi | 2019-09-26 | LX1011 | 21.3 | 33 | 21.3 | 34 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 6720 | 2039.9997 | 224.4271
HBG-1.RR.1805.1 | 24210209125265 | Habiganj, West Vadei, Siddik Ali | 2019-09-26 | LX1011 | 14.4 | 35 | 14.5 | 36 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 6720 | 2039.9997 | 152.779
HBG-1.RR.1806.1 | 24210059125248 | Habiganj, West Vadei, Ronokul Islam | 2019-09-26 | LX1011 | 12.3 | 37 | 12.3 | 38 | 2022-01-01 | 2022-10-08 | NQ1007 |  |  | 0 | 55 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6720 | 2039.9997
HBG-1.RR.1807.1 | 24210049125261 | Habiganj, West Vadei, Sharifullah | 2019-09-26 | LX1011 | 12.9 | 43 | 12.9 | 44 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6720 | 2039.9997 | 135.9206
HBG-1.RR.1808.1 | 24205829125263 | Habiganj, West Vadei, Sufia House, Hazi Maruf | 2019-09-26 | LX1011 | 13.6 | 45 | 13.6 | 46 | 2022-01-01 | 2022-10-08 | NQ1007 |  |  | 0 | 56 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6720 | 2039.9997
HBG-1.RR.1809.1 | 24210379125257 | Habiganj, West Vadei, Romjan Mia | 2019-09-26 | LX1011 | 8.5 | 47 | 8.5 | 48 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6720 | 2039.9997 | 89.5601
HBG-1.RR.1810.1 | 24210369125249 | Habiganj, West Vadei, Rojob Ali | 2019-09-26 | LX1011 | 10.7 | 49 | 10.7 | 50 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6720 | 2039.9997 | 112.7403
HBG-1.RR.1811.1 | 24205249125374 | Habiganj, West Vadei, Ziaur Rahman | 2019-09-26 | LX1011 | 22.1 | 51 | 21.8 | 52 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 21.8 | 21.8 | 1.308 | 1.308 | 0.0007168 | 100% | 0% | 1.308 | 1.308 | 0.0011869 | 28 | 0.026221 | 0.026221 |  | 0 | 0 | 6768 | 1991.9997 | 229.6953
HBG-1.RR.1812.1 | 24205049125375 | Habiganj, West Vadei, Abdul Kaiyum | 2019-09-26 | LX1011 | 5.8 | 53 | 5.8 | 54 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6768 | 1991.9997 | 61.1116
HBG-1.RR.1812.2 | 24205049125375 | Habiganj, West Vadei, Abdul Kaiyum | 2021-01-12 | NQ1003 | 9.3 | 19 | 9.3 | 20 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6768 | 1991.9997 | 97.9893
HBG-1.RR.1813.1 | 24204959125393 | Habiganj, West Vadei, Vangapul, Abdul Hamid | 2019-09-26 | LX1011 | 13.9 | 55 | 13.9 | 56 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6768 | 1991.9997 | 146.4571
HBG-1.RR.1814.1 | 24204819125340 | Habiganj, West Vadei, Vangapul, Hafizur Rahman | 2019-09-26 | LX1011 | 16.4 | 57 | 16.4 | 58 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6768 | 1991.9997 | 172.7983
HBG-1.RR.1815.1 | 24204889125377 | Habiganj, West Vadei, Vangapul, A.K.M. Tajul Islam | 2019-09-26 | LX1011 | 16.7 | 59 | 16.4 | 60 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6768 | 1991.9997 | 172.7983
HBG-1.RR.1816.1 | 24220989124397 | Habiganj, Baipas West Court Station Road, Rasheda Begum | 2019-09-28 | LX1011 | 15.9 | 61 | 15.9 | 62 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6552 | 2207.9997 | 167.5301
HBG-1.RR.1817.1 | 24220989124397 | Habiganj, Baipas West Court Station Road, Abdul Mojid Nunu Mia | 2019-09-28 | LX1011 | 4.8 | 63 | 4.8 | 64 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6552 | 2207.9997 | 50.5751
HBG-1.RR.1817.2 | 24220989124397 | Habiganj, Baipas West Court Station Road, Abdul Mojid Nunu Mia | 2021-08-31 | LX1011 | 12.9 | 92 | 12.9 | 93 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6552 | 2207.9997 | 135.9206
HBG-1.RR.1818.1 | 24221029124381 | Habiganj, Baipas West Court Station Road, Hamida Akter | 2019-09-28 | LX1011 | 10.3 | 65 | 10.3 | 66 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6552 | 2207.9997 | 108.5258
HBG-1.RR.1819.1 | 24221009124367 | Habiganj, Sultan Mahmudpur, West Court Station Road, Tajul Islam | 2019-09-28 | LX1011 | 11 | 67 | 11 | 68 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6552 | 2207.9997 | 115.9013
HBG-1.RR.1820.1 | 24201459126154 | Habiganj, Tetaya, Ward# 5, Abul Kalam | 2019-09-28 | LX1011 | 9.4 | 69 | 9.4 | 70 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6768 | 1991.9997 | 99.0429
HBG-1.RR.1821.1 | 24201449126166 | Habiganj, Tetaya, Ward# 5, Rafiq Mia | 2019-09-28 | LX1011 | 13.1 | 71 | 13.1 | 72 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6768 | 1991.9997 | 138.0279
HBG-1.RR.1821.2 | 24201449126166 | Habiganj, Tetaya, Ward# 5, Rafiq Mia | 2022-04-02 | LU1001 | 7.2 | 110 | 7.2 | 111 | 2022-04-02 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 4584 | 1991.9997 | 56.949
HBG-1.RR.1822.1 | 24201119126089 | Habiganj, Tetaya, Ward# 5, Abdus Shahid | 2019-09-28 | LX1011 | 18.7 | 73 | 18.7 | 74 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6768 | 1991.9997 | 197.0322
HBG-1.RR.1823.1 | 24221389125397 | Habiganj, Masulia R/A, Debendro Pal | 2019-09-29 | LX1011 | 13.5 | 99 | 13.5 | 100 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6768 | 1991.9997 | 142.2425
HBG-1.RR.1823.2 | 24221389125397 | Habiganj, Masulia R/A, Debendro Pal | 2022-03-30 | LU1001 | 6.3 | 94 | 6.3 | 95 | 2022-03-30 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 4656 | 1991.9997 | 50.3759
HBG-1.RR.1824.1 | 24221549125389 | Habiganj, Masulia R/A, Amitav Chowdhury Choyon | 2019-09-29 | LX1011 | 15.5 | 101 | 15.5 | 102 | 2022-01-01 | [9 empty] | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0
HBG-1.RR.1824.2 | 24221549125389 | Habiganj, Masulia R/A, Amitav Chowdhury Choyon | 2022-03-30 | LU1001 | 12.9 | 92 | 12.9 | 93 | 2022-03-30 | [9 empty] | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0
HBG-1.RR.1825.1 | 24221589125395 | Habiganj, Masulia R/A, Sipra Rani Das | 2019-09-29 | LX1011 | 12.4 | 103 | 11.9 | 104 | 2022-01-01 | 2022-10-10 | NQ1007 |  |  | 0 | 57 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6768 | 1991.9997
HBG-1.RR.1826.1 | 24222269125374 | Habiganj, Masulia R/A, Abdur Rashid | 2019-09-29 | LX1011 | 12.7 | 105 | 12.7 | 106 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6768 | 1991.9997 | 133.8133
HBG-1.RR.1827.1 | 24222269125374 | Habiganj, Masulia R/A, Shah Newaz Selim | 2019-09-29 | LX1011 | 6.8 | 107 | 6.8 | 108 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6768 | 1991.9997 | 71.6481
HBG-1.RR.1851.1 | 24210879125337 | Habiganj, Upazila Road, West Vadoy, Ami Hossen | 2019-09-26 | LX1011 | 9 | 17 | 9 | 18 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6720 | 2039.9997 | 94.8283
HBG-1.RR.1851.2 | 24210879125337 | Habiganj, Upazila Road, West Vadoy, Ami Hossen | 2022-10-08 | NQ1007 | 2.1 | 52 | 2.1 | 53 | 2022-10-08 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 0 | 2039.9997 | 5.1528
HBG-1.RR.1852.1 | 24210879125337 | Habiganj, Upazila Road, West Vadoy, Mokbul Mia | 2019-09-26 | LX1011 | 6.7 | 19 | 6.7 | 20 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6720 | 2039.9997 | 70.5944
HBG-1.RR.1853.1 | 24210559125364 | Habiganj, Upazila Road, West Vadoy, Tenu Mia | 2019-09-26 | LX1011 | 11.7 | 21 | 11.7 | 22 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6720 | 2039.9997 | 123.2768
HBG-1.RR.1854.1 | 24210559125364 | Habiganj, Upazila Road, West Vadoy, Safu Mia | 2019-09-26 | LX1011 | 16.1 | 23 | 16.1 | 24 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6720 | 2039.9997 | 169.6373
HBG-1.RR.1855.1 | 24210379125353 | Habiganj, Upazila Road, West Vadoy, Aymena Begum | 2019-09-26 | LX1011 | 13.1 | 25 | 13.1 | 26 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6720 | 2039.9997 | 138.0279
HBG-1.RR.1856.1 | 24210379125353 | Habiganj, Upazila Road, West Vadoy, Mollah | 2019-09-26 | LX1011 | 9 | 27 | 9 | 28 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6720 | 2039.9997 | 94.8283
HBG-1.RR.1857.1 | 24210339125376 | Habiganj, Upazila Road, West Vadoy, Salamot | 2019-09-26 | LX1011 | 11.7 | 29 | 11.7 | 30 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6720 | 2039.9997 | 123.2768
HBG-1.RR.1858.1 | 24210339125376 | Habiganj, Upazila Road, West Vadoy, Shahana | 2019-09-26 | LX1011 | 15.6 | 31 | 15.6 | 32 | 2022-01-01 | 2022-10-08 | NQ1007 |  |  | 0 | 54 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6720 | 2039.9997
HBG-1.RR.1859.1 | 24195599126091 | Habiganj,, Dhuliakhal, Mirpur Road, Abidur Khan | 2019-09-28 | LX1011 | 11.3 | 75 | 11.3 | 76 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6768 | 1991.9997 | 119.0622
HBG-1.RR.1860.1 | 24195429126126 | Habiganj,, Dhuliakhal, Mirpur Road, Mizanur Rohoman | 2019-09-28 | LX1011 | 15.8 | 77 | 15.2 | 78 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6768 | 1991.9997 | 160.1545
HBG-1.RR.1861.1 | 24195179126159 | Habiganj,, Dhuliakhal, Mirpur Road, Md Sohel Khan | 2019-09-28 | LX1011 | 10.7 | 79 | 10.7 | 80 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6768 | 1991.9997 | 112.7403
HBG-1.RR.1862.1 | 24194959126187 | Habiganj,, Dhuliakhal, Mirpur Road, Md Faruk Mia | 2019-09-28 | LX1011 | 11.4 | 81 | 11.4 | 82 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6768 | 1991.9997 | 120.1159
HBG-1.RR.1863.1 | 24194859126179 | Habiganj,, Dhuliakhal, Mirpur Road, Toyeb Ali | 2019-09-28 | LX1011 | 14.2 | 83 | 14.3 | 84 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6768 | 1991.9997 | 150.6717
HBG-1.RR.1864.1 | 24194859126179 | Habiganj,, Dhuliakhal, Mirpur Road, Salek Ali | 2019-09-28 | LX1011 | 14.9 | 85 | 14.9 | 86 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6768 | 1991.9997 | 156.9936
HBG-1.RR.1865.1 | 24195189126234 | Habiganj,, Dhuliakhal, Mirpur Road, Md Salam | 2019-09-28 | LX1011 | 19.9 | 87 | 19.1 | 88 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 6768 | 1991.9997 | 201.2468
HBG-1.RR.1866.1 | 24195149126325 | Habiganj,, Dhuliakhal, Mirpur Road, Belal Chatrabas | 2019-09-28 | LX1011 | 11.5 | 89 | 11.5 | 90 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 3000 | 0 | 3768 | 1991.9997 | 79.6731
HBG-1.RR.1867.1 | 24195149126325 | Habiganj,, Dhuliakhal, Mirpur Road, Forid | 2019-09-28 | LX1011 | 18.7 | 91 | 18.7 | 92 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6768 | 1991.9997 | 197.0322
HBG-1.RR.1868.1 | 24194839126339 | Habiganj,, Dhuliakhal, Mirpur Road, Abduul Amin | 2019-09-28 | LX1011 | 10.7 | 93 | 10.7 | 94 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6768 | 1991.9997 | 112.7403
HBG-1.RR.1869.1 | 24194719126373 | Habiganj,, Dhuliakhal, Mirpur Road, Tanu Mia | 2019-09-28 | LX1011 | 12.4 | 95 | 12.4 | 96 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6768 | 1991.9997 | 130.6524
HBG-1.RR.1870.1 | 24194719126373 | Habiganj,, Dhuliakhal, Mirpur Road, Zalal Mia | 2019-09-28 | LX1011 | 7.1 | 97 | 7.1 | 98 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6768 | 1991.9997 | 74.809
HBG-3.RR.1.1 | 24112509121130 | Madhobpur, Karara, Sanu | 2019-09-30 | MN1032 | 6.2 | 1 | 6.2 | 2 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6072 | 2687.9997 | 65.3262
HBG-3.RR.2.1 | 24112509121130 | Madhobpur, Karara, Faruk | 2019-09-30 | MN1032 | 11.5 | 3 | 11.5 | 4 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6072 | 2687.9997 | 121.1695
HBG-3.RR.2.2 | 24112509121130 | Madhobpur, Karara, Faruk | 2021-01-20 | NQ1003 | 7.5 | 75 | 7.5 | 76 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6072 | 2687.9997 | 79.0236
HBG-3.RR.3.1 | 24111739121138 | Madhobpur, Karara, Hamidur | 2019-09-30 | MN1032 | 21.4 | 5 | 21.6 | 6 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 6072 | 2687.9997 | 227.588
HBG-3.RR.4.1 | 24111739121138 | Madhobpur, Karara, Nur Alom | 2019-09-30 | MN1032 | 15.9 | 7 | 15.3 | 8 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6072 | 2687.9997 | 161.2082
HBG-3.RR.5.1 | 24111739121138 | Madhobpur, Karara, Shofiq | 2019-09-30 | MN1032 | 16.9 | 9 | 16.9 | 10 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 6072 | 2687.9997 | 178.0665
HBG-3.RR.5.2 | 24111739121138 | Madhobpur, Karara, Shofiq | 2020-10-17 | NQ1009 | 8.6 | 753 | 8.6 | 754 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6072 | 2687.9997 | 90.6137
HBG-3.RR.6.1 | 24111739121138 | Madhobpur, Karara, Serizul Islam | 2019-09-30 | MN1032 | 7.4 | 11 | 7.4 | 12 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6072 | 2687.9997 | 77.97
HBG-3.RR.7.1 | 24111899121142 | Madhobpur, Karara, Jhanu Mia | 2019-09-30 | MN1032 | 13.7 | 13 | 13.7 | 14 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6072 | 2687.9997 | 144.3498
HBG-3.RR.8.1 | 24111899121142 | Madhobpur, Karara, Jhanu Mia | 2019-09-30 | MN1032 | 10.7 | 15 | 10.4 | 16 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6072 | 2687.9997 | 109.5794
HBG-3.RR.9.1 | 24111309121074 | Madhobpur, Karara, Mofizur Rahman | 2019-09-30 | MN1032 | 12.4 | 17 | 12.4 | 18 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6072 | 2687.9997 | 130.6524
HBG-3.RR.10.1 | 24054199117033 | Madhabpur, Katiara Dhakkin Pata, Santos Kumar Das | 2019-10-06 | MN1032 | 8.2 | 183 | 8.2 | 184 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6168 | 2591.9997 | 86.3991
HBG-3.RR.11.1 | 24054429117029 | Madhabpur, Katiara Dhakkin Pata, Asu Das | 2019-10-06 | MN1032 | 5.5 | 185 | 5.5 | 186 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6168 | 2591.9997 | 57.9506
HBG-3.RR.12.1 | 24054429117015 | Madhabpur, Katiara Dhakkin Pata, Sunil Chakrabarti | 2019-10-06 | MN1032 | 12 | 187 | 11.6 | 188 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6168 | 2591.9997 | 122.2232
HBG-3.RR.13.1 | 24054649117064 | Madhabpur, Katiara Dhakkin Pata, Sribash Chandra Biswas | 2019-10-06 | MN1032 | 4.6 | 189 | 4.6 | 190 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6168 | 2591.9997 | 48.4678
HBG-3.RR.14.1 | 24054709117037 | Madhabpur, Katiara Uttar Pata, Sentu Das | 2019-10-06 | MN1032 | 7.9 | 191 | 7.7 | 192 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6168 | 2591.9997 | 81.1309
HBG-3.RR.15.1 | 24054709117037 | Madhabpur, Katiara Uttar Pata, Topon Das | 2019-10-06 | MN1032 | 9.7 | 193 | 9.7 | 194 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6168 | 2591.9997 | 102.2039
HBG-3.RR.16.1 | 24054679117024 | Madhabpur, Katiara Uttar Pata, Rati Ranjan Das | 2019-10-06 | MN1032 | 5.8 | 195 | 5.8 | 196 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6168 | 2591.9997 | 61.1116
HBG-3.RR.17.1 | 24054679117024 | Madhabpur, Katiara Uttar Pata, Noresh | 2019-10-06 | MN1032 | 18.3 | 197 | 18.3 | 198 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 18.3 | 18.3 | 1.098 | 1.098 | 0.0007168 | 100% | 0% | 1.098 | 1.098 | 0.0011869 | 28 | 0.022011 | 0.022011 |  | 0 | 0 | 6168 | 2591.9997 | 192.8176
HBG-3.RR.18.1 | 24054679117007 | Madhabpur, Katiara Uttar Pata, Sonkor Kumar Das | 2019-10-06 | MN1032 | 18.9 | 199 | 18.5 | 200 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6168 | 2591.9997 | 194.9249
HBG-3.RR.19.1 | 24054739117078 | Madhabpur, Katiara North Para, Shoshi Mohon Sarkar | 2019-10-07 | MN1032 | 9.3 | 201 | 9 | 202 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6168 | 2591.9997 | 94.8283
HBG-3.RR.20.1 | 24054559117089 | Madhabpur, Katiara East Para, Sukomal Roy | 2019-10-07 | MN1032 | 11.6 | 203 | 11.6 | 204 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6168 | 2591.9997 | 122.2232
HBG-3.RR.21.1 | 24054569117100 | Madhabpur, Katiara North Para, Bhoktoram Pal | 2019-10-07 | MN1032 | 11.6 | 205 | 11.6 | 206 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6168 | 2591.9997 | 122.2232
HBG-3.RR.51.1 | 24121269121228 | Madhabpur, North Nowapara, Ward # 9, Chanu Mia | 2019-09-30 | MP1006 | 13.4 | 900 | 13.4 | 901 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6072 | 2687.9997 | 141.1888
HBG-3.RR.52.1 | 24121429121218 | Madhabpur, North Nowapara, Ward # 9, Abdul Hekim | 2019-09-30 | MP1006 | 7.7 | 902 | 8 | 903 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6072 | 2687.9997 | 84.2919
HBG-3.RR.53.1 | 24120529121231 | Madhabpur, North Nowapara, Ward # 9, Rokeya Begom | 2019-09-30 | MP1006 | 6.6 | 904 | 6.1 | 905 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6072 | 2687.9997 | 64.2725
HBG-3.RR.53.2 | 24120529121231 | Madhabpur, North Nowapara, Ward # 9, Rokeya Begom | 2020-10-17 | NQ1009 | 14.7 | 801 | 14.7 | 802 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6072 | 2687.9997 | 154.8863
HBG-3.RR.54.1 | 24120349121146 | Madhabpur, North Nowapara, Ward # 9, Doctor Alauddin | 2019-09-30 | MP1006 | 10.6 | 906 | 10.6 | 907 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6072 | 2687.9997 | 111.6867
HBG-3.RR.55.1 | 24120179121146 | Madhabpur, North Nowapara, Ward # 9, Abdul Motalib | 2019-09-30 | MP1006 | 10 | 908 | 10 | 909 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6072 | 2687.9997 | 105.3648
HBG-3.RR.56.1 | 24120519121127 | Madhabpur, North Nowapara, Ward # 9, Korim | 2019-09-30 | MP1006 | 11.6 | 910 | 11.6 | 911 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6072 | 2687.9997 | 122.2232
HBG-3.RR.57.1 | 24120519121127 | Madhabpur, North Nowapara, Ward # 9, Asraf | 2019-09-30 | MP1006 | 10.6 | 912 | 10.2 | 913 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6072 | 2687.9997 | 107.4721
HBG-3.RR.58.1 | 24103949121192 | Madhabpur, Noyapara, Kashipur, Mahbubur Rahman | 2019-10-01 | MN1032 | 11.1 | 19 | 11.1 | 20 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6144 | 2615.9997 | 116.9549
HBG-3.RR.59.1 | 24103909121169 | Madhabpur, Noyapara, Kashipur, Abdul Aowal Khan | 2019-10-01 | MN1032 | 25 | 21 | 25.2 | 22 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 25.2 | 25.2 | 1.512 | 1.512 | 0.0007168 | 100% | 0% | 1.512 | 1.512 | 0.0011869 | 28 | 0.03031 | 0.03031 |  | 0 | 0 | 6144 | 2615.9997 | 265.5193
HBG-3.RR.60.1 | 24103659121219 | Madhabpur, Noyapara, Kashipur, Advocate Emam Ullah | 2019-10-01 | MN1032 | 9.2 | 23 | 9.2 | 24 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6144 | 2615.9997 | 96.9356
HBG-3.RR.61.1 | 24103509121193 | Madhabpur, Noyapara, Kashipur, Sabu Mia | 2019-10-01 | MN1032 | 15.8 | 25 | 15.8 | 26 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6096 | 2663.9997 | 166.4764
HBG-3.RR.62.1 | 24103509121193 | Madhabpur, Noyapara, Kashipur, Nijam Uddin | 2019-10-01 | MN1032 | 18.4 | 27 | 17.7 | 28 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 6096 | 2663.9997 | 186.4957
HBG-3.RR.63.1 | 24102659121189 | Madhabpur, Nowapara, Murapara, Sohel | 2019-10-02 | MN1032 | 18.5 | 29 | 18.5 | 30 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6144 | 2615.9997 | 194.9249
HBG-3.RR.64.1 | 24102589121186 | Madhabpur, Nowapara, Murapara, Lal Shah | 2019-10-02 | MN1032 | 14.2 | 31 | 14.2 | 32 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6144 | 2615.9997 | 149.618
HBG-3.RR.65.1 | 24102589121186 | Madhabpur, Nowapara, Murapara, Alom Shah | 2019-10-02 | MN1032 | 10.7 | 33 | 10.7 | 34 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6144 | 2615.9997 | 112.7403
HBG-3.RR.66.1 | 24095069121171 | Madhabpur, Nowapara, Mirzapur, Abdul Roshid | 2019-10-02 | MN1032 | 17.5 | 37 | 17.5 | 38 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6096 | 2663.9997 | 184.3884
HBG-3.RR.67.1 | 24094599121163 | Madhabpur, Nowapara, Mirzapur, Jodge Mia | 2019-10-02 | MN1032 | 12 | 39 | 12 | 40 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6096 | 2663.9997 | 126.4378
HBG-3.RR.68.1 | 24093369121094 | Madhabpur, Itakhola, Charabhanga Saheb Bari, Soiyod Salauddin Mahbub | 2019-10-02 | MN1032 | 16.1 | 41 | 16.1 | 42 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6144 | 2615.9997 | 169.6373
HBG-3.RR.69.1 | 24092729121141 | Madhabpur, Jogodishpur, Sri Ganga Sutradhar | 2019-10-03 | MN1032 | 10.3 | 43 | 10.3 | 44 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6096 | 2663.9997 | 108.5258
HBG-3.RR.70.1 | 24092949121156 | Madhabpur, Jogodishpur, Komol Ronjon Shil | 2019-10-03 | MN1032 | 11.8 | 45 | 11.8 | 46 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6096 | 2663.9997 | 124.3305
HBG-3.RR.71.1 | 24093429121196 | Madhabpur, Jogodishpur, Charabhanga, Alfaz Mia | 2019-10-03 | MN1032 | 14.3 | 47 | 13.7 | 48 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6096 | 2663.9997 | 144.3498
HBG-3.RR.72.1 | 24092439121139 | Madhabpur, Jogodishpur, Jallal Uddin | 2019-10-03 | MN1032 | 17.7 | 49 | 17.8 | 50 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 6096 | 2663.9997 | 187.5494
HBG-3.RR.73.1 | 24092439121139 | Madhabpur, Jogodishpur, Sorif Uddin | 2019-10-03 | MN1032 | 13 | 51 | 13 | 52 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6096 | 2663.9997 | 136.9743
HBG-3.RR.74.1 | 24092439121139 | Madhabpur, Jogodishpur, Luqman Uddin | 2019-10-03 | MN1032 | 10.4 | 53 | 10.4 | 54 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6096 | 2663.9997 | 109.5794
HBG-3.RR.75.1 | 24092439121139 | Madhabpur, Jogodishpur, Tofile Khan | 2019-10-03 | MN1032 | 6.2 | 55 | 6.2 | 56 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6096 | 2663.9997 | 65.3262
HBG-3.RR.76.1 | 24092439121139 | Madhabpur, Jogodishpur, Ayub Khan | 2019-10-03 | MN1032 | 5 | 57 | 5 | 58 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6096 | 2663.9997 | 52.6824
HBG-3.RR.77.1 | 24092489121093 | Madhabpur, Jogodishpur, Kajol | 2019-10-03 | MN1032 | 4.6 | 59 | 4.6 | 60 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6144 | 2615.9997 | 48.4678
HBG-3.RR.78.1 | 24061989117579 | Madhabpur, Kacharipara, School Road, Mojnu Mia | 2019-10-03 | MN1032 | 13.1 | 67 | 13.1 | 68 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6216 | 2543.9997 | 138.0279
HBG-3.RR.79.1 | 24062019117589 | Madhabpur, Kacharipara, School Road, Kanai Mollik | 2019-10-03 | MN1032 | 25.3 | 69 | 24 | 70 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 24 | 24 | 1.44 | 1.44 | 0.0007168 | 100% | 0% | 1.44 | 1.44 | 0.0011869 | 28 | 0.028867 | 0.028867 |  | 0 | 0 | 6216 | 2543.9997 | 252.8756
HBG-3.RR.80.1 | 24062119117592 | Madhabpur, Kacharipara, School Road, Kanu Mollik | 2019-10-03 | MN1032 | 33.8 | 71 | 32.6 | 72 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 32.6 | 32.6 | 1.956 | 1.956 | 0.0007168 | 100% | 0% | 1.956 | 1.956 | 0.0011869 | 28 | 0.039211 | 0.039211 |  | 0 | 0 | 6216 | 2543.9997 | 343.4893
HBG-3.RR.81.1 | 24062279118038 | Madhabpur, Chowdhury Para, Ward # 2, Rosmot Ali | 2019-10-03 | MN1032 | 13.7 | 73 | 12.7 | 74 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6216 | 2543.9997 | 133.8133
HBG-3.RR.82.1 | 24062279118038 | Madhabpur, Chowdhury Para, Ward # 2, Foju Rahaman | 2019-10-03 | MN1032 | 6.3 | 76 | 6.3 | 77 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6216 | 2543.9997 | 66.3798
HBG-3.RR.83.1 | 24062279118038 | Madhabpur, Chowdhury Para, Ward # 2, Ohab Mia | 2019-10-03 | MN1032 | 7 | 78 | 7 | 79 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6216 | 2543.9997 | 73.7554
HBG-3.RR.84.1 | 24062319118045 | Madhabpur, Chowdhury Para, Ward # 2, Kajol Mia | 2019-10-03 | MN1032 | 11.1 | 80 | 11.1 | 81 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6216 | 2543.9997 | 116.9549
HBG-3.RR.85.1 | 24061799118053 | Madhabpur, Bonik Para, Porimol Bonik | 2019-10-03 | MN1032 | 3.6 | 82 | 3.6 | 83 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6216 | 2543.9997 | 37.9313
HBG-3.RR.85.2 | 24061799118053 | Madhabpur, Bonik Para, Porimol Bonik | 2021-01-21 | NQ1007 | 3.1 | 52 | 3.1 | 53 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6216 | 2543.9997 | 32.6631
HBG-3.RR.86.1 | 24061799118053 | Madhabpur, Bonik Para, Krisno Bonik | 2019-10-03 | MN1032 | 11.6 | 84 | 11.6 | 85 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6216 | 2543.9997 | 122.2232
HBG-3.RR.87.1 | 24061719118056 | Madhabpur, Bonik Para, Gridhon Bonik | 2019-10-03 | MN1032 | 7.9 | 96 | 7.9 | 97 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6216 | 2543.9997 | 83.2382
HBG-3.RR.88.1 | 24061669118052 | Madhabpur, Bonik Para, Shyamol Bonik | 2019-10-03 | MN1032 | 13.3 | 98 | 13.3 | 99 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6216 | 2543.9997 | 140.1352
HBG-3.RR.89.1 | 24061669118052 | Madhabpur, Bonik Para, Bijoy Bonik | 2019-10-03 | MN1032 | 6.7 | 100 | 6.7 | 101 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6216 | 2543.9997 | 70.5944
HBG-3.RR.90.1 | 24061669118052 | Madhabpur, Bonik Para, Bimol Bonik | 2019-10-03 | MN1032 | 12.4 | 102 | 11.9 | 103 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6216 | 2543.9997 | 125.3841
HBG-3.RR.91.1 | 24061579118052 | Madhabpur, Bonik Para, Utpol Bonik | 2019-10-05 | MN1032 | 19.3 | 104 | 19.3 | 105 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 6216 | 2543.9997 | 203.3541
HBG-3.RR.92.1 | 24061579118052 | Madhabpur, Bonik Para, Nokol Bonik | 2019-10-05 | MN1032 | 13.4 | 106 | 13.4 | 107 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6216 | 2543.9997 | 141.1888
HBG-3.RR.93.1 | 24061579118052 | Madhabpur, Bonik Para, Shyamol Bonik | 2019-10-05 | MN1032 | 10 | 108 | 9.7 | 109 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6216 | 2543.9997 | 102.2039
HBG-3.RR.94.1 | 24061219118004 | Madhabpur, Raipara, Kajol Rai | 2019-10-05 | MN1032 | 12 | 110 | 12 | 111 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6216 | 2543.9997 | 126.4378
HBG-3.RR.94.2 | 24061219118004 | Madhabpur, Raipara, Kajol Rai | 2020-10-15 | NQ1003 | 5.3 | 34 | 5.1 | 35 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6216 | 2543.9997 | 53.7361
HBG-3.RR.95.1 | 24061079117596 | Madhabpur, Raipara, Gourdas | 2019-10-05 | MN1032 | 5.9 | 112 | 5.9 | 113 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6216 | 2543.9997 | 62.1652
HBG-3.RR.96.1 | 24060939118002 | Madhabpur, Raipara, Nikhil Rai | 2019-10-05 | MN1032 | 2.1 | 114 | 2.1 | 115 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6216 | 2543.9997 | 22.1266
HBG-3.RR.97.1 | 24061169117591 | Madhabpur, Raipara, Ronjeet Rai | 2019-10-05 | MN1032 | 11.5 | 117 | 11.5 | 118 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6216 | 2543.9997 | 121.1695
HBG-3.RR.98.1 | 24061169117591 | Madhabpur, Raipara, Ronjeet Rai | 2019-10-05 | MN1032 | 9.8 | 119 | 9.8 | 120 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6216 | 2543.9997 | 103.2575
HBG-3.RR.99.1 | 24061599117580 | Madhabpur, Raipara, Nipa Rai | 2019-10-05 | MN1032 | 11.6 | 121 | 11.4 | 122 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6216 | 2543.9997 | 120.1159
HBG-3.RR.100.1 | 24061559117582 | Madhabpur, Raipara, Anjon Rai | 2019-10-05 | MN1032 | 9.9 | 123 | 9.9 | 124 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6216 | 2543.9997 | 104.3112
HBG-3.RR.101.1 | 24115839121215 | Madhobpur, Noapara, Ratanpur, Gias Uddin | 2019-09-30 | NQ1003 | 13.9 | 100 | 13.9 | 101 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6072 | 2687.9997 | 146.4571
HBG-3.RR.102.1 | 24115969121194 | Madhobpur, Noapara, Ratanpur, Abdul Elem | 2019-09-30 | NQ1003 | 7.9 | 102 | 7.9 | 103 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6072 | 2687.9997 | 83.2382
HBG-3.RR.103.1 | 24115489121179 | Madhobpur, Noapara, Ratanpur, Abdur Rouf Mia | 2019-09-30 | NQ1003 | 14 | 106 | 14 | 107 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6072 | 2687.9997 | 147.5107
HBG-3.RR.104.1 | 24115189121205 | Madhobpur, Noapara, Ratanpur, Baccha Mia | 2019-09-30 | NQ1003 | 16.7 | 108 | 16.7 | 109 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 6072 | 2687.9997 | 175.9592
HBG-3.RR.105.1 | 24115089121203 | Madhobpur, Noapara, Ratanpur, Md. Runu Mia | 2019-09-30 | NQ1003 | 15.9 | 110 | 15.9 | 111 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6072 | 2687.9997 | 167.5301
HBG-3.RR.106.1 | 24115079121203 | Madhobpur, Noapara, Ratanpur, Md. Alfu Mia | 2019-09-30 | NQ1003 | 10.4 | 112 | 10.4 | 113 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6072 | 2687.9997 | 109.5794
HBG-3.RR.107.1 | 24114729121188 | Madhobpur, Noapara, Ratanpur, Abdur Rahim | 2019-09-30 | NQ1003 | 12.2 | 115 | 12.2 | 116 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6072 | 2687.9997 | 128.5451
HBG-3.RR.108.1 | 24114539121187 | Madhobpur, Noapara, Ratanpur, Abdur Jabbar | 2019-09-30 | NQ1003 | 10 | 117 | 10 | 118 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6072 | 2687.9997 | 105.3648
HBG-3.RR.109.1 | 24114489121189 | Madhobpur, Noapara, Ratanpur, Md. Alauddin | 2019-09-30 | NQ1003 | 8.3 | 119 | 7.8 | 120 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6072 | 2687.9997 | 82.1846
HBG-3.RR.110.1 | 24102469121196 | Madhobpur, Noapara, Murapara, Rajob Ali | 2019-10-02 | NQ1007 | 3.2 | 17 | 3.2 | 18 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6144 | 2615.9997 | 33.7167
HBG-3.RR.111.1 | 24102529121173 | Madhobpur, Noapara, Murapara, Motiur Rahman | 2019-10-02 | NQ1007 | 12.1 | 19 | 12.1 | 20 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6144 | 2615.9997 | 127.4914
HBG-3.RR.112.1 | 24102809121172 | Madhobpur, Noapara, Murapara, Lutfor Rahman | 2019-10-02 | NQ1007 | 7 | 21 | 7.1 | 22 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6144 | 2615.9997 | 74.809
HBG-3.RR.113.1 | 24102909121174 | Madhobpur, Noapara, Murapara, Salauddin | 2019-10-02 | NQ1007 | 9.8 | 23 | 9.8 | 24 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6144 | 2615.9997 | 103.2575
HBG-3.RR.114.1 | 24102519121132 | Madhobpur, Noapara, Murapara, Abdul Mannan Master | 2019-10-02 | NQ1007 | 11.7 | 25 | 11.7 | 26 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6144 | 2615.9997 | 123.2768
HBG-3.RR.115.1 | 24102309121032 | Madhobpur, Noapara, Eitakhola, Lal Shah | 2019-10-02 | NQ1007 | 6.5 | 27 | 6.5 | 28 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6096 | 2663.9997 | 68.4871
HBG-3.RR.116.1 | 24102329121034 | Madhobpur, Noapara, Eitakhola, Akkas Mia | 2019-10-02 | NQ1007 | 4.6 | 29 | 4.6 | 30 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6096 | 2663.9997 | 48.4678
HBG-3.RR.117.1 | 24102329121034 | Madhobpur, Noapara, Eitakhola, Akkas Mia | 2019-10-02 | NQ1007 | 5.2 | 31 | 5.2 | 32 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6096 | 2663.9997 | 54.7897
HBG-3.RR.118.1 | 24102329121034 | Madhobpur, Noapara, Eitakhola, Akkas Mia | 2019-10-02 | NQ1007 | 11.6 | 35 | 11.6 | 36 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6096 | 2663.9997 | 122.2232
HBG-3.RR.119.1 | 24102329121034 | Madhobpur, Noapara, Eitakhola, Akkas Mia | 2019-10-02 | NQ1007 | 7.8 | 37 | 7.8 | 38 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6096 | 2663.9997 | 82.1846
HBG-3.RR.120.1 | 24102589121035 | Madhobpur, Noapara, Eitakhola, Tajul Islam | 2019-10-02 | NQ1007 | 3.8 | 39 | 3.8 | 40 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6096 | 2663.9997 | 40.0386
HBG-3.RR.121.1 | 24102499121036 | Madhobpur, Noapara, Eitakhola, Jabed Mia | 2019-10-02 | NQ1007 | 4.7 | 41 | 4.7 | 42 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6096 | 2663.9997 | 49.5215
HBG-3.RR.122.1 | 24102529121073 | Madhobpur, Noapara, Eitakhola, Abdul Hamid | 2019-10-02 | NQ1007 | 12.7 | 45 | 12.7 | 46 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6096 | 2663.9997 | 133.8133
HBG-3.RR.123.1 | 24102709121071 | Madhobpur, Noapara, Eitakhola, Mizanur Rahman | 2019-10-02 | NQ1007 | 2.4 | 47 | 2.4 | 48 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6096 | 2663.9997 | 25.2876
HBG-3.RR.124.1 | 24102769121075 | Madhobpur, Noapara, Eitakhola, Sajahan | 2019-10-02 | NQ1007 | 3.1 | 49 | 3.1 | 50 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6096 | 2663.9997 | 32.6631
HBG-3.RR.125.1 | 24092129121174 | Madhobpur, Jagodispur, Avijit Das | 2019-10-03 | MN1032 | 9.1 | 61 | 9.1 | 62 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6096 | 2663.9997 | 95.882
HBG-3.RR.126.1 | 24092129121174 | Madhobpur, Jagodispur, Mohon Lal | 2019-10-03 | MN1032 | 4.3 | 63 | 4.3 | 64 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6096 | 2663.9997 | 45.3069
HBG-3.RR.127.1 | 24092049121171 | Madhobpur, Jagodispur, Anando Roy | 2019-10-03 | MN1032 | 4.7 | 65 | 4.7 | 66 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6096 | 2663.9997 | 49.5215
HBG-3.RR.128.1 | 24060909118157 | Madhobpur, East Madhobpur, Muslim Chairmaner Bari, Hazi Mahafuj Shah | 2019-10-05 | NQ1007 | 11.7 | 73 | 11.4 | 74 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6216 | 2543.9997 | 120.1159
HBG-3.RR.129.1 | 24060409118138 | Madhobpur, East Madhobpur, Shahid Miar Bari, Jarip Hosen | 2019-10-05 | NQ1007 | 5.1 | 75 | 5.1 | 76 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6216 | 2543.9997 | 53.7361
HBG-3.RR.129.2 | 24060409118138 | Madhobpur, East Madhobpur, Shahid Miar Bari, Jarip Hosen | 2021-01-21 | NQ1007 | 1.4 | 64 | 1.4 | 65 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6216 | 2543.9997 | 14.7511
HBG-3.RR.130.1 | 24060409118138 | Madhobpur, East Madhobpur, Shahid Miar Bari, Lou Hosen | 2019-10-05 | NQ1007 | 5.4 | 77 | 5.4 | 78 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6216 | 2543.9997 | 56.897
HBG-3.RR.131.1 | 24054219117275 | Madhobpur, Shantipara, Madhobpur Thana Road, Prodip Vorta Charjo | 2019-10-05 | NQ1007 | 6.4 | 79 | 6.4 | 80 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6168 | 2591.9997 | 67.4335
HBG-3.RR.132.1 | 24054079117290 | Madhobpur, Shantipara, Madhobpur Thana Road, Saiham Future Complex | 2019-10-05 | NQ1007 | 9.2 | 81 | 9.2 | 82 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6168 | 2591.9997 | 96.9356
HBG-3.RR.133.1 | 24054079117395 | Madhobpur, Shantipara, Madhobpur Thana Road, Shamol Baron Rishi | 2019-10-05 | NQ1007 | 6.3 | 83 | 6.3 | 84 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6168 | 2591.9997 | 66.3798
HBG-3.RR.133.2 | 24054079117395 | Madhobpur, Shantipara, Madhobpur Thana Road, Shamol Baron Rishi | 2021-08-22 | LX1011 | 9.5 | 2 | 9.5 | 3 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6168 | 2591.9997 | 100.0966
HBG-3.RR.134.1 | 24054229117411 | Madhobpur, Ganganagar, Rishipara, Madhobpur Thana Road, Manik Rishi | 2019-10-05 | NQ1007 | 25.5 | 85 | 25.5 | 86 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 25.5 | 25.5 | 1.53 | 1.53 | 0.0007168 | 100% | 0% | 1.53 | 1.53 | 0.0011869 | 28 | 0.030671 | 0.030671 |  | 0 | 0 | 6168 | 2591.9997 | 268.6803
HBG-3.RR.135.1 | 24054229117411 | Madhobpur, Ganganagar, Rishipara, Madhobpur Thana Road, Bimol Rishi | 2019-10-05 | NQ1007 | 13.4 | 87 | 13.4 | 88 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6168 | 2591.9997 | 141.1888
HBG-3.RR.136.1 | 24054209117407 | Madhobpur, Ganganagar, Rishipara, Madhobpur Thana Road, Jotish Rishi | 2019-10-05 | NQ1007 | 13.4 | 89 | 13.4 | 90 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6168 | 2591.9997 | 141.1888
HBG-3.RR.136.2 | 24054209117407 | Madhobpur, Ganganagar, Rishipara, Madhobpur Thana Road, Jotish Rishi | 2020-10-14 | NQ1009 | 6.3 | 613 | 6.3 | 614 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6168 | 2591.9997 | 66.3798
HBG-3.RR.137.1 | 24060879117467 | Madhobpur, West Madhobpur, Main Road, Badsha Mia | 2019-10-06 | NQ1007 | 11.3 | 136 | 11.3 | 137 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6216 | 2543.9997 | 119.0622
HBG-3.RR.138.1 | 24060879117467 | Madhobpur, West Madhobpur, Main Road, Abu Mia | 2019-10-06 | NQ1007 | 10.8 | 138 | 10.7 | 139 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6216 | 2543.9997 | 112.7403
HBG-3.RR.138.2 | 24060879117467 | Madhobpur, West Madhobpur, Main Road, Abu Mia | 2020-10-15 | NQ1009 | 13.1 | 723 | 13.1 | 724 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6216 | 2543.9997 | 138.0279
HBG-3.RR.139.1 | 24061459117428 | Madhobpur, West Madhobpur, New Bagh, Dipok | 2019-10-06 | NQ1007 | 7.1 | 140 | 7.1 | 141 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6216 | 2543.9997 | 74.809
HBG-3.RR.140.1 | 24061719117422 | Madhobpur, West Madhobpur, Ward # 3, Munsi Bari, Harunur Rashid | 2019-10-06 | NQ1007 | 9.4 | 142 | 9.4 | 143 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6216 | 2543.9997 | 99.0429
HBG-3.RR.141.1 | 24061859117429 | Madhobpur, West Madhobpur, Ward # 3, Munsi Bari, Nasir Uddin | 2019-10-06 | NQ1007 | 12.2 | 144 | 12.2 | 145 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6216 | 2543.9997 | 128.5451
HBG-3.RR.142.1 | 24061629117424 | Madhobpur, West Madhobpur, Ward # 3, Munsi Bari, Feroj Mia | 2019-10-06 | NQ1007 | 13.2 | 146 | 13.2 | 147 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6216 | 2543.9997 | 139.0816
HBG-3.RR.142.2 | 24061629117424 | Madhobpur, West Madhobpur, Ward # 3, Munsi Bari, Feroj Mia | 2021-01-21 | NQ1003 | 4.7 | 108 | 4.7 | 109 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6216 | 2543.9997 | 49.5215
HBG-3.RR.143.1 | 24061649117390 | Madhobpur, West Madhobpur, Ward # 3, Master Bari, Jinnot Ali | 2019-10-06 | NQ1007 | 11.3 | 148 | 11.3 | 149 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6216 | 2543.9997 | 119.0622
HBG-3.RR.144.1 | 24061629117424 | Madhobpur, West Madhobpur, Ward # 3, Master Bari, Kala Mia | 2019-10-06 | NQ1007 | 11.2 | 150 | 10.8 | 151 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6216 | 2543.9997 | 113.794
HBG-3.RR.145.1 | 24061779117388 | Madhobpur, West Madhobpur, Ward # 3, Master Bari, Abdul Mannan | 2019-10-06 | NQ1007 | 5.7 | 152 | 5.7 | 153 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6216 | 2543.9997 | 60.0579
HBG-3.RR.146.1 | 24061379117359 | Madhobpur, West Madhobpur, Ward # 3, Najir Bari, Lalu Mia | 2019-10-06 | NQ1007 | 15.1 | 154 | 15.1 | 155 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6216 | 2543.9997 | 159.1009
HBG-3.RR.146.2 | 24061379117359 | Madhobpur, West Madhobpur, Ward # 3, Najir Bari, Lalu Mia | 2022-03-06 | LU1001 | 5.9 | 22 | 5.9 | 23 | 2022-03-06 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 4680 | 2543.9997 | 51.265
HBG-3.RR.147.1 | 24060669117519 | Madhobpur, Tong Bari, Jadge Ali | 2019-10-07 | NQ1007 | 10.7 | 186 | 10.7 | 187 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6216 | 2543.9997 | 112.7403
HBG-3.RR.148.1 | 24060719117518 | Madhobpur, Tong Bari, Yousuf Ali | 2019-10-07 | NQ1007 | 11.9 | 188 | 11.6 | 189 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6216 | 2543.9997 | 122.2232
HBG-3.RR.149.1 | 24060909117513 | Madhobpur, Tong Bari, Nurul Islam | 2019-10-07 | NQ1007 | 9.2 | 190 | 8.7 | 191 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6216 | 2543.9997 | 91.6674
HBG-3.RR.150.1 | 24060909117513 | Madhobpur, Tong Bari, Rafik Mia | 2019-10-07 | NQ1007 | 8.3 | 192 | 8 | 193 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6216 | 2543.9997 | 84.2919
HBG-3.RR.151.1 | 24112719121161 | NoyaPara, Korora, Saiham Nogor, Ahmad Mia | 2019-09-30 | NQ1003 | 7.1 | 123 | 7.1 | 124 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6072 | 2687.9997 | 74.809
HBG-3.RR.152.1 | 24112749121151 | NoyaPara, Mothergora, Saiham Nogor, Nurul Islam | 2019-09-30 | NQ1003 | 9.1 | 125 | 9.1 | 126 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6072 | 2687.9997 | 95.882
HBG-3.RR.153.1 | 24112749121151 | NoyaPara, Korora, Saiham Nogor, Abdul Malak | 2019-09-30 | NQ1003 | 11.5 | 127 | 11.5 | 128 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6072 | 2687.9997 | 121.1695
HBG-3.RR.154.1 | 24112779121127 | NoyaPara, Korora, Saiham, Rofiqul | 2019-09-30 | NQ1003 | 10.5 | 129 | 10.5 | 130 | 2022-01-01 | [9 empty] | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0
HBG-3.RR.155.1 | 24112809121112 | NoyaPara, Mothergora, Saiham, Nipemdro Das | 2019-09-30 | NQ1003 | 8.7 | 131 | 8.7 | 132 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6072 | 2687.9997 | 91.6674
HBG-3.RR.156.1 | 24113069121116 | NoyaPara, Mothergora, Saiham, Nironjon Das | 2019-09-30 | NQ1003 | 11 | 133 | 11 | 134 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6072 | 2687.9997 | 115.9013
HBG-3.RR.157.1 | 24113839121126 | NoyaPara, Mothergora, Saiham, Morium | 2019-09-30 | NQ1003 | 7.7 | 135 | 7.7 | 136 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6072 | 2687.9997 | 81.1309
HBG-3.RR.157.2 | 24113839121126 | NoyaPara, Mothergora, Saiham, Morium | 2021-11-22 | MN1018 | 1.7 | 51 | 1.7 | 52 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6072 | 2687.9997 | 17.912
HBG-3.RR.158.1 | 24113719121081 | NoyaPara, Mothergora, Saiham, Mosarof Hossain | 2019-09-30 | NQ1003 | 15.8 | 137 | 15.8 | 138 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6072 | 2687.9997 | 166.4764
HBG-3.RR.158.2 | 24113719121081 | NoyaPara, Mothergora, Saiham, Mosarof Hossain | 2019-09-30 | NQ1003 | 8.7 | 139 | 8.7 | 140 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6072 | 2687.9997 | 91.6674
HBG-3.RR.159.1 | 24104559121135 | Noya Para, Kashipur, Abdul Kadir | 2019-10-01 | NQ1007 | 35.9 | 1 | 35.9 | 2 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 35.9 | 35.9 | 2.154 | 2.154 | 0.0007168 | 100% | 0% | 2.154 | 2.154 | 0.0011869 | 28 | 0.04318 | 0.04318 |  | 0 | 0 | 6072 | 2687.9997 | 378.2597
HBG-3.RR.160.1 | 24104669121115 | Noya Para, Bangduba, Hazi Abdur Rahman | 2019-10-01 | NQ1007 | 12.8 | 3 | 12.8 | 4 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6072 | 2687.9997 | 134.867
HBG-3.RR.161.1 | 24104669121115 | Noya Para, Bangduba, Abdul Khalak | 2019-10-01 | NQ1007 | 8.3 | 5 | 8.3 | 6 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6072 | 2687.9997 | 87.4528
HBG-3.RR.162.1 | 24104629121094 | Noya Para, Bangduba, Eklas | 2019-10-01 | NQ1007 | 11 | 7 | 11 | 8 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6072 | 2687.9997 | 115.9013
HBG-3.RR.163.1 | 24104629121094 | Noya Para, Bangduba, Turab Ali | 2019-10-01 | NQ1007 | 7.8 | 9 | 7.9 | 10 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6072 | 2687.9997 | 83.2382
HBG-3.RR.164.1 | 24104979121047 | Noya Para, Bangduba, Kalu Mia | 2019-10-01 | NQ1007 | 12.8 | 11 | 12.8 | 12 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6072 | 2687.9997 | 134.867
HBG-3.RR.165.1 | 24104989121070 | Noya Para, Bangduba, Abdul Ahad | 2019-10-01 | NQ1007 | 2.8 | 13 | 2.8 | 14 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6072 | 2687.9997 | 29.5021
HBG-3.RR.165.2 | 24104989121070 | Noya Para, Bangduba, Abdul Ahad | 2021-01-20 | NQ1007 | 4.6 | 47 | 4.6 | 48 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6072 | 2687.9997 | 48.4678
HBG-3.RR.166.1 | 24103779120594 | Noya Para, Eitakula, Jiten Sorkar | 2019-10-01 | NQ1007 | 3.1 | 15 | 3.1 | 16 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6168 | 2591.9997 | 32.6631
HBG-3.RR.167.1 | 24104249121197 | NoyaPara, EitaKhola, Solim Mia | 2019-10-02 | NQ1007 | 11.5 | 51 | 11.5 | 52 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6072 | 2687.9997 | 121.1695
HBG-3.RR.168.1 | 24104199121155 | NoyaPara, EitaKhola, Subir | 2019-10-02 | NQ1007 | 9.9 | 53 | 9.9 | 54 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6072 | 2687.9997 | 104.3112
HBG-3.RR.169.1 | 24104259121125 | NoyaPara, EitaKhola, Hamedur Rahman | 2019-10-02 | NQ1007 | 14 | 55 | 14 | 56 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6072 | 2687.9997 | 147.5107
HBG-3.RR.170.1 | 24104089121092 | NoyaPara, EitaKhola, Onil Dav Nath | 2019-10-02 | NQ1007 | 6.7 | 57 | 6.7 | 58 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6072 | 2687.9997 | 70.5944
HBG-3.RR.171.1 | 24104089121092 | NoyaPara, EitaKhola, Monoj Kumar Dav Nath | 2019-10-02 | NQ1007 | 11.8 | 59 | 11.8 | 60 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6072 | 2687.9997 | 124.3305
HBG-3.RR.172.1 | 24103979121096 | NoyaPara, EitaKhola, Mohori | 2019-10-02 | NQ1007 | 9 | 61 | 9 | 62 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6072 | 2687.9997 | 94.8283
HBG-3.RR.173.1 | 24103899121076 | NoyaPara, EitaKhola, Himanso Dav Nath | 2019-10-02 | NQ1007 | 8.6 | 63 | 8.2 | 64 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6072 | 2687.9997 | 86.3991
HBG-3.RR.174.1 | 24103989121107 | NoyaPara, EitaKhola, Dilip | 2019-10-02 | NQ1007 | 11.3 | 65 | 11.3 | 66 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6072 | 2687.9997 | 119.0622
HBG-3.RR.175.1 | 24103989121107 | NoyaPara, EitaKhola, Nogas | 2019-10-02 | NQ1007 | 12 | 67 | 12 | 68 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6072 | 2687.9997 | 126.4378
HBG-3.RR.176.1 | 24092279121075 | NoyaPara, Jogodispur, Nilmor Rai | 2019-10-02 | NQ1007 | 11.1 | 69 | 11.1 | 70 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6144 | 2615.9997 | 116.9549
HBG-3.RR.177.1 | 24092189121111 | NoyaPara, Jogodispur, Sotis Rai | 2019-10-02 | NQ1007 | 13.5 | 71 | 13.5 | 72 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6144 | 2615.9997 | 142.2425
HBG-3.RR.178.1 | 24060759117557 | Madhobpur, Khan Bari, Ward # 1, Kala Mia Khan | 2019-10-03 | MN1032 | 20.1 | 86 | 20.1 | 87 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 20.1 | 20.1 | 1.206 | 1.206 | 0.0007168 | 100% | 0% | 1.206 | 1.206 | 0.0011869 | 28 | 0.024176 | 0.024176 |  | 0 | 0 | 6216 | 2543.9997 | 211.7833
HBG-3.RR.179.1 | 24060739117553 | Madhobpur, Khan Bari, Ward # 1, Amir Khan | 2019-10-03 | MN1032 | 9.4 | 88 | 8.8 | 89 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6216 | 2543.9997 | 92.721
HBG-3.RR.180.1 | 24060869117544 | Madhobpur, Khan Bari, Ward # 1, Ali Mohammad | 2019-10-03 | MN1032 | 15 | 90 | 15 | 91 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6216 | 2543.9997 | 158.0472
HBG-3.RR.181.1 | 24060599117593 | East Madhobpur, Ward # 1, Moborak | 2019-10-03 | MN1032 | 5.8 | 92 | 5.8 | 93 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6216 | 2543.9997 | 61.1116
HBG-3.RR.182.1 | 24060599117593 | East Madhobpur, Ward # 1, Abdul Rahim | 2019-10-03 | MN1032 | 18.7 | 94 | 18.7 | 95 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6216 | 2543.9997 | 197.0322
HBG-3.RR.183.1 | 24054219117440 | Madhobpur, Gonga Nogor Rishi Para, Promod Rishi | 2019-10-05 | NQ1007 | 11.4 | 91 | 11.4 | 92 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6168 | 2591.9997 | 120.1159
HBG-3.RR.184.1 | 24054219117440 | Madhobpur, Gonga Nogor Rishi Para, Razzar Sor | 2019-10-05 | NQ1007 | 21.3 | 93 | 21.3 | 94 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 6168 | 2591.9997 | 224.4271
HBG-3.RR.185.1 | 24054229117451 | Madhobpur, Gonga Nogor Rishi Para, Swokomol | 2019-10-05 | NQ1007 | 5.3 | 95 | 5.3 | 96 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6168 | 2591.9997 | 55.8434
HBG-3.RR.186.1 | 24054229117451 | Madhobpur, Gonga Nogor Rishi Para, Asu Ram Rishi | 2019-10-05 | NQ1007 | 7.6 | 98 | 7.6 | 99 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6168 | 2591.9997 | 80.0773
HBG-3.RR.187.1 | 24054149117451 | Madhobpur, Gonga Nogor Rishi Para, Nidu Rishi | 2019-10-05 | NQ1007 | 11.8 | 100 | 11.8 | 101 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6168 | 2591.9997 | 124.3305
HBG-3.RR.187.2 | 24054149117451 | Madhobpur, Gonga Nogor Rishi Para, Nidu Rishi | 2021-01-21 | LU1001 | 3.6 | 70 | 3.6 | 71 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6168 | 2591.9997 | 37.9313
HBG-3.RR.188.1 | 24054129117451 | Madhobpur, Gonga Nogor Rishi Para, Rasmon | 2019-10-05 | NQ1007 | 13.7 | 102 | 13.7 | 103 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6168 | 2591.9997 | 144.3498
HBG-3.RR.189.1 | 24054119117451 | Madhobpur, Gonga Nogor Rishi Para, Kachon Rishi | 2019-10-05 | NQ1007 | 13.2 | 104 | 13.2 | 105 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6168 | 2591.9997 | 139.0816
HBG-3.RR.190.1 | 24054209117452 | Madhobpur, Gonga Nogor Rishi Para, Citto Ronjon Rishi | 2019-10-05 | NQ1007 | 10.8 | 106 | 10.7 | 107 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6168 | 2591.9997 | 112.7403
HBG-3.RR.191.1 | 24054319117471 | Madhobpur, Gonga Nogor Rishi Para, Didendo Rishi | 2019-10-05 | NQ1007 | 9.2 | 108 | 9.2 | 109 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6168 | 2591.9997 | 96.9356
HBG-3.RR.192.1 | 24054059117474 | Madhobpur, Gonga Nogor Rishi Para, Komol Rishi | 2019-10-05 | NQ1007 | 11 | 110 | 10.7 | 111 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6168 | 2591.9997 | 112.7403
HBG-3.RR.193.1 | 24054589117294 | Madhobpur, Santi Para, Sayed Masum Billa | 2019-10-05 | NQ1007 | 9.5 | 112 | 9.5 | 113 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6168 | 2591.9997 | 100.0966
HBG-3.RR.194.1 | 24054589117294 | Madhobpur, Santi Para, Kazi Akter | 2019-10-05 | NQ1007 | 6.7 | 114 | 6.7 | 115 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6168 | 2591.9997 | 70.5944
HBG-3.RR.194.2 | 24054589117294 | Madhobpur, Santi Para, Kazi Akter | 2020-10-14 | NQ1009 | 7 | 588 | 7 | 589 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6168 | 2591.9997 | 73.7554
HBG-3.RR.195.1 | 24054719117312 | Madhobpur, Samoli R/A, Sha Mohammod Salim | 2019-10-05 | NQ1007 | 29.1 | 116 | 29.2 | 117 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 29.2 | 29.2 | 1.752 | 1.752 | 0.0007168 | 100% | 0% | 1.752 | 1.752 | 0.0011869 | 28 | 0.035122 | 0.035122 |  | 0 | 0 | 6168 | 2591.9997 | 307.6653
HBG-3.RR.196.1 | 24060799117453 | West Madhobpur, Ward # 3, Habibur Rahaman | 2019-10-06 | NQ1007 | 5.5 | 118 | 5.5 | 119 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6216 | 2543.9997 | 57.9506
HBG-3.RR.197.1 | 24060669117439 | West Madhobpur, Ward # 3, Md Ansor Ali | 2019-10-06 | NQ1007 | 14.9 | 120 | 14.9 | 121 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6216 | 2543.9997 | 156.9936
HBG-3.RR.198.1 | 24061009117450 | West Madhobpur, Ward # 3, Alom Mia | 2019-10-06 | NQ1007 | 7.3 | 122 | 7.3 | 123 | 2022-01-01 | [9 empty] | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0
HBG-3.RR.199.1 | 24061179117457 | West Madhobpur, Ward # 3, Solaman | 2019-10-06 | NQ1007 | 5.7 | 124 | 5.7 | 125 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6216 | 2543.9997 | 60.0579
HBG-3.RR.200.1 | 24061169117441 | West Madhobpur, Ward # 3, Yunus | 2019-10-06 | NQ1007 | 12.5 | 126 | 12.5 | 127 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6216 | 2543.9997 | 131.706
HBG-3.RR.200.2 | 24061169117441 | West Madhobpur, Ward # 3, Yunus | 2021-01-21 | NQ1003 | 9.3 | 112 | 9.4 | 113 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6216 | 2543.9997 | 99.0429
HBG-3.RR.201.1 | 24113629121191 | Madhabpur, Ratanpur Bazar, Madargora, Dhakay Bari | 2019-09-30 | LX1011 | 3.9 | 109 | 3.9 | 110 | 2022-01-01 | [9 empty] | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0
HBG-3.RR.202.1 | 24113609121178 | Madhabpur, Ratanpur Bazar, Madargora, Roshid Mia | 2019-09-30 | LX1011 | 14 | 111 | 14 | 112 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6072 | 2687.9997 | 147.5107
HBG-3.RR.203.1 | 24113879121144 | Madhabpur, Ratanpur Bazar, Madargora, Rofiqul Islam | 2019-09-30 | LX1011 | 12.7 | 116 | 12.7 | 117 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6072 | 2687.9997 | 133.8133
HBG-3.RR.204.1 | 24113879121144 | Madhabpur, Ratanpur Bazar, Madargora, Korimul | 2019-09-30 | LX1011 | 10.6 | 118 | 10.6 | 119 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6072 | 2687.9997 | 111.6867
HBG-3.RR.205.1 | 24114039121134 | Madhabpur, Ratanpur Bazar, Madargora, Mohibul | 2019-09-30 | LX1011 | 11.6 | 120 | 11.6 | 121 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6072 | 2687.9997 | 122.2232
HBG-3.RR.206.1 | 24114209121137 | Madhabpur, Ratanpur Bazar, Madargora, Bodrul Islam | 2019-09-30 | LX1011 | 9.6 | 122 | 9.6 | 123 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6072 | 2687.9997 | 101.1502
HBG-3.RR.207.1 | 24114209121137 | Madhabpur, Ratanpur Bazar, Madargora, Bodrul Hassan | 2019-09-30 | LX1011 | 11.7 | 124 | 11.7 | 125 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6072 | 2687.9997 | 123.2768
HBG-3.RR.208.1 | 24114299121137 | Madhabpur, Ratanpur Bazar, Madargora, Rohoman | 2019-09-30 | LX1011 | 19 | 126 | 19 | 127 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 6072 | 2687.9997 | 200.1931
HBG-3.RR.209.1 | 24114399121128 | Madhabpur, Ratanpur Bazar, Madargora, Ayub Ali | 2019-09-30 | LX1011 | 12.8 | 130 | 12.8 | 131 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6072 | 2687.9997 | 134.867
HBG-3.RR.210.1 | 24114399121128 | Madhabpur, Ratanpur Bazar, Madargora, Mitul | 2019-09-30 | LX1011 | 10.6 | 132 | 10.7 | 133 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6072 | 2687.9997 | 112.7403
HBG-3.RR.211.1 | 24114399121128 | Madhabpur, Ratanpur Bazar, Madargora, Khurshed Ali | 2019-09-30 | LX1011 | 12.2 | 134 | 12.2 | 135 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6072 | 2687.9997 | 128.5451
HBG-3.RR.212.1 | 24114239121171 | Madhabpur, Ratanpur Bazar, Madargora, Asob Ali | 2019-09-30 | LX1011 | 15.8 | 136 | 15.8 | 137 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6072 | 2687.9997 | 166.4764
HBG-3.RR.213.1 | 24114239121171 | Madhabpur, Ratanpur Bazar, Madargora, Khurshed Ali | 2019-09-30 | LX1011 | 11.8 | 138 | 11.8 | 139 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6072 | 2687.9997 | 124.3305
HBG-3.RR.214.1 | 24102289121227 | Madhabpur, Nowapara, Etakhula Bazar, Bayzid Mia | 2019-10-02 | NQ1008 | 14.8 | 43 | 14.6 | 44 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6144 | 2615.9997 | 153.8326
HBG-3.RR.215.1 | 24102129121250 | Madhabpur, Nowapara, Etakhula Bazar, Alima Khhatun | 2019-10-02 | NQ1008 | 8.3 | 45 | 8.3 | 46 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6144 | 2615.9997 | 87.4528
HBG-3.RR.216.1 | 24102309121184 | Madhabpur, Nowapara, Etakhula Bazar, Bacchu | 2019-10-02 | NQ1008 | 18.2 | 47 | 17.5 | 48 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6144 | 2615.9997 | 184.3884
HBG-3.RR.217.1 | 24103189121164 | Madhabpur, Nowapara, Etakhula Bazar, Jewel | 2019-10-02 | NQ1008 | 14.3 | 49 | 14.1 | 50 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6096 | 2663.9997 | 148.5644
HBG-3.RR.218.1 | 24103159121159 | Madhabpur, Nowapara, Etakhula Bazar, Moynuddin | 2019-10-02 | NQ1008 | 12.3 | 51 | 12.2 | 52 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6096 | 2663.9997 | 128.5451
HBG-3.RR.219.1 | 24103739121085 | Madhabpur, Nowapara, Etakhula Bazar, Rinku Deb | 2019-10-02 | NQ1008 | 13.1 | 53 | 13.1 | 54 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6096 | 2663.9997 | 138.0279
HBG-3.RR.220.1 | 24091499121226 | Madhabpur, Jogodispur, Sontospur, Ayub Ali | 2019-10-03 | NQ1008 | 12.6 | 71 | 12.6 | 72 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6144 | 2615.9997 | 132.7597
HBG-3.RR.221.1 | 24091359121258 | Madhabpur, Jogodispur, Sontospur, Hossen Ahmmed | 2019-10-03 | NQ1008 | 11.8 | 73 | 11.6 | 74 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6144 | 2615.9997 | 122.2232
HBG-3.RR.222.1 | 24091359121258 | Madhabpur, Jogodispur, Sontospur, Hossen Ahmmed | 2019-10-03 | NQ1008 | 13.6 | 75 | 13.6 | 76 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6144 | 2615.9997 | 143.2961
HBG-3.RR.223.1 | 24091729121275 | Madhabpur, Jogodispur, Sontospur, Shohid Ali | 2019-10-03 | NQ1008 | 7.3 | 77 | 7.3 | 78 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6144 | 2615.9997 | 76.9163
HBG-3.RR.224.1 | 24091779121285 | Madhabpur, Jogodispur, Sontospur, Zallaluddin | 2019-10-03 | NQ1008 | 7.5 | 79 | 7.5 | 80 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6144 | 2615.9997 | 79.0236
HBG-3.RR.225.1 | 24091459121302 | Madhabpur, Jogodispur, Sontospur, Siddik | 2019-10-03 | NQ1008 | 12.6 | 81 | 12.2 | 82 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6144 | 2615.9997 | 128.5451
HBG-3.RR.226.1 | 24090979121251 | Madhabpur, Jogodispur, Sontospur, Derendro Pal | 2019-10-03 | NQ1008 | 16.5 | 83 | 16 | 84 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6144 | 2615.9997 | 168.5837
HBG-3.RR.227.1 | 24090979121251 | Madhabpur, Jogodispur, Sontospur, Sonkor Chondro Pal | 2019-10-03 | NQ1008 | 11.8 | 85 | 11.1 | 86 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6144 | 2615.9997 | 116.9549
HBG-3.RR.228.1 | 24090819121169 | Madhabpur, Jogodispur, Sontospur, Mokendor | 2019-10-03 | NQ1008 | 10.3 | 87 | 10.3 | 88 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6144 | 2615.9997 | 108.5258
HBG-3.RR.229.1 | 24055279117325 | Madhabpur, Samoli R/A, Polas | 2019-10-05 | NQ1008 | 28.6 | 113 | 28.2 | 114 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 28.2 | 28.2 | 1.692 | 1.692 | 0.0007168 | 100% | 0% | 1.692 | 1.692 | 0.0011869 | 28 | 0.033919 | 0.033919 |  | 0 | 0 | 6168 | 2591.9997 | 297.1288
HBG-3.RR.229.2 | 24055279117325 | Madhabpur, Samoli R/A, Polas | 2020-10-14 | NQ1009 | 14.1 | 607 | 14.1 | 608 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6168 | 2591.9997 | 148.5644
HBG-3.RR.230.1 | 24054799117342 | Madhabpur, Samoli R/A, Taher Ali | 2019-10-05 | NQ1008 | 12.9 | 115 | 12.8 | 116 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6168 | 2591.9997 | 134.867
HBG-3.RR.231.1 | 24054799117342 | Madhabpur, Samoli R/A, Jahanara Khatun | 2019-10-05 | NQ1008 | 12.1 | 117 | 11.5 | 118 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6168 | 2591.9997 | 121.1695
HBG-3.RR.232.1 | 24054979117353 | Madhabpur, Samoli R/A, Ronjit Ascharjo | 2019-10-05 | NQ1008 | 12.8 | 119 | 12.5 | 120 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6168 | 2591.9997 | 131.706
HBG-3.RR.232.2 | 24054979117353 | Madhabpur, Samoli R/A, Ronjit Ascharjo | 2021-01-21 | LU1001 | 4 | 65 | 4 | 66 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6168 | 2591.9997 | 42.1459
HBG-3.RR.233.1 | 24054979117353 | Madhabpur, Samoli R/A, Forid Ahmmed | 2019-10-05 | NQ1008 | 15.4 | 121 | 15.4 | 122 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6168 | 2591.9997 | 162.2618
HBG-3.RR.234.1 | 24055039117337 | Madhabpur, Samoli R/A, Forid Ahmmed | 2019-10-05 | NQ1008 | 12.7 | 123 | 12.7 | 124 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6168 | 2591.9997 | 133.8133
HBG-3.RR.235.1 | 24055039117337 | Madhabpur, Samoli R/A, Zodu Mia Kedar | 2019-10-05 | NQ1008 | 7.2 | 125 | 7.1 | 126 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6168 | 2591.9997 | 74.809
HBG-3.RR.236.1 | 24060089117305 | Madhabpur, Krishnonogor, Ward # 04, Dulot Khan Molllah | 2019-10-06 | NQ1008 | 20.4 | 131 | 20.4 | 132 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 20.4 | 20.4 | 1.224 | 1.224 | 0.0007168 | 100% | 0% | 1.224 | 1.224 | 0.0011869 | 28 | 0.024537 | 0.024537 |  | 0 | 0 | 6216 | 2543.9997 | 214.9442
HBG-3.RR.236.2 | 24060089117305 | Madhabpur, Krishnonogor, Ward # 04, Dulot Khan Molllah | 2022-03-06 | LU1001 | 10.9 | 20 | 10.9 | 21 | 2022-03-06 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 4680 | 2543.9997 | 94.71
HBG-3.RR.237.1 | 24060089117305 | Madhabpur, Krishnonogor, Ward # 04, Mudod Mia | 2019-10-06 | NQ1008 | 10.9 | 133 | 10.9 | 134 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6216 | 2543.9997 | 114.8476
HBG-3.RR.238.1 | 24060129117263 | Madhabpur, Krishnonogor, Ward # 04, Munsur Ali | 2019-10-06 | NQ1008 | 11.6 | 135 | 11.2 | 136 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6216 | 2543.9997 | 118.0086
HBG-3.RR.238.2 | 24060129117263 | Madhabpur, Krishnonogor, Ward # 04, Munsur Ali | 2022-03-06 | LU1001 | 9.5 | 18 | 9.5 | 19 | 2022-03-06 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 4680 | 2543.9997 | 82.5454
HBG-3.RR.239.1 | 24060209117262 | Madhabpur, Krishnonogor, Ward # 04, Abdul Ali | 2019-10-06 | NQ1008 | 11.6 | 137 | 11.6 | 138 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6216 | 2543.9997 | 122.2232
HBG-3.RR.239.2 | 24060209117262 | Madhabpur, Krishnonogor, Ward # 04, Abdul Ali | 2021-01-21 | LU1001 | 2 | 59 | 2 | 60 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6216 | 2543.9997 | 21.073
HBG-3.RR.240.1 | 24060289117268 | Madhabpur, Krishnonogor, Ward # 04, Chomok Pathan | 2019-10-06 | NQ1008 | 11.4 | 139 | 11.4 | 140 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6216 | 2543.9997 | 120.1159
HBG-3.RR.240.2 | 24060289117268 | Madhabpur, Krishnonogor, Ward # 04, Chomok Pathan | 2020-10-15 | NQ1009 | 14.4 | 693 | 14.4 | 694 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6216 | 2543.9997 | 151.7253
HBG-3.RR.241.1 | 24060289117268 | Madhabpur, Krishnonogor, Ward # 04, Faruk Pathan | 2019-10-06 | NQ1008 | 12.9 | 141 | 12.5 | 142 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6216 | 2543.9997 | 131.706
HBG-3.RR.242.1 | 24060329117338 | Madhabpur, Krishnonogor, Ward # 04, Aysha Siddika Mohila Madrasha | 2019-10-06 | NQ1008 | 13.2 | 143 | 12.7 | 144 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6216 | 2543.9997 | 133.8133
HBG-3.RR.243.1 | 24060709117333 | Madhabpur, Krishnonogor, Ward # 04, Alimur Raji | 2019-10-06 | NQ1008 | 2.3 | 145 | 2.3 | 146 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6216 | 2543.9997 | 24.2339
HBG-3.RR.244.1 | 24060779117339 | Madhabpur, East Madhabpur, Ward # 04, Ruhul Amin | 2019-10-06 | NQ1008 | 12.9 | 147 | 12.7 | 148 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6216 | 2543.9997 | 133.8133
HBG-3.RR.245.1 | 24055779117322 | Madhabpur, Krishnonogor, Ward # 04, Soleman Vuiya | 2019-10-06 | NQ1008 | 42.6 | 149 | 42.6 | 150 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 42.6 | 42.6 | 2.556 | 2.556 | 0.0007168 | 100% | 0% | 2.556 | 2.556 | 0.0011869 | 28 | 0.051239 | 0.051239 |  | 0 | 0 | 6168 | 2591.9997 | 448.8541
HBG-3.RR.246.1 | 24055669117320 | Madhabpur, Krishnonogor, Ward # 04, Sha - Milon | 2019-10-06 | NQ1008 | 8.1 | 151 | 8.4 | 152 | 2022-01-01 | 2022-09-15 | NQ1007 | 2.9 | 1 | 2.9 | 2 | 2022-09-15 | GS | 0 | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6168 | 2591.9997 | 67.4335
HBG-3.RR.247.1 | 24055669117320 | Madhabpur, Krishnonogor, Ward # 04, Khan Niketon | 2019-10-06 | NQ1008 | 10.6 | 153 | 10.7 | 154 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6168 | 2591.9997 | 112.7403
HBG-3.RR.248.1 | 24055639117321 | Madhabpur, Krishnonogor, Ward # 04, Kaysar Ahmed | 2019-10-06 | NQ1008 | 11.3 | 155 | 11.3 | 156 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6168 | 2591.9997 | 119.0622
HBG-3.RR.249.1 | 24055639117321 | Madhabpur, Krishnonogor, Ward # 04, Md. Zia | 2019-10-06 | NQ1008 | 10.5 | 157 | 10.5 | 158 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6168 | 2591.9997 | 110.6331
HBG-3.RR.250.1 | 24054539117321 | Madhabpur, Samoli R/A, Mostak Ahmmed Khan | 2019-10-07 | NQ1008 | 10 | 215 | 10 | 216 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6168 | 2591.9997 | 105.3648
HBG-3.RR.251.1 | 24111719121179 | Madhobpur, Korora, Saihamnagar, Akter Hossain | 2019-09-30 | NQ1008 | 18.1 | 1 | 17.7 | 2 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 6072 | 2687.9997 | 186.4957
HBG-3.RR.252.1 | 24112029121186 | Madhobpur, Korora, Saihamnagar, Md. Faruque Mia | 2019-09-30 | NQ1008 | 38.8 | 3 | 38.8 | 4 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 38.8 | 38.8 | 2.328 | 2.328 | 0.0007168 | 100% | 0% | 2.328 | 2.328 | 0.0011869 | 28 | 0.046668 | 0.046668 |  | 0 | 0 | 6072 | 2687.9997 | 408.8155
HBG-3.RR.252.2 | 24112029121186 | Madhobpur, Korora, Saihamnagar, Md. Faruque Mia | 2021-08-23 | LX1011 | 17.2 | 9 | 17.2 | 10 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 6072 | 2687.9997 | 181.2275
HBG-3.RR.253.1 | 24110739121174 | Madhobpur, Korora, Saihamnagar, Anowar Chowdhury | 2019-09-30 | NQ1008 | 12.1 | 5 | 12.1 | 6 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6072 | 2687.9997 | 127.4914
HBG-3.RR.254.1 | 24110739121174 | Madhobpur, Korora, Saihamnagar, Abu Sayed | 2019-09-30 | NQ1008 | 78.2 | 7 | 73.9 | 8 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 73.9 | 73.9 | 4.434 | 4.434 | 0.0007168 | 100% | 0% | 4.434 | 4.434 | 0.0011869 | 28 | 0.088887 | 0.088887 |  | 0 | 0 | 6072 | 2687.9997 | 778.646
HBG-3.RR.255.1 | 24111339121106 | Madhobpur, Korora, Saihamnagar, Sahabuddin | 2019-09-30 | NQ1008 | 13.4 | 9 | 13.4 | 10 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6072 | 2687.9997 | 141.1888
HBG-3.RR.256.1 | 24111349121115 | Madhobpur, Korora, Saihamnagar, Gias Uddin | 2019-09-30 | NQ1008 | 18.8 | 11 | 18.8 | 12 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 6072 | 2687.9997 | 198.0858
HBG-3.RR.257.1 | 24105569121029 | Madhobpur, Noapara, Kawsarnagar, Motin | 2019-09-30 | NQ1008 | 8.9 | 13 | 8.9 | 14 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6072 | 2687.9997 | 93.7747
HBG-3.RR.258.1 | 24105559121039 | Madhobpur, Noapara, Kawsarnagar, Shiraj | 2019-09-30 | NQ1008 | 14.6 | 15 | 14.6 | 16 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6072 | 2687.9997 | 153.8326
HBG-3.RR.259.1 | 24104389121233 | Madhobpur, Noapara, Purbo Bazar, Ajit Pal | 2019-10-01 | NQ1008 | 10.8 | 17 | 10.8 | 18 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6072 | 2687.9997 | 113.794
HBG-3.RR.260.1 | 24104309121231 | Madhobpur, Noapara, Purbo Bazar, Abdul Khalek | 2019-10-01 | NQ1008 | 15.3 | 19 | 15.3 | 20 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6072 | 2687.9997 | 161.2082
HBG-3.RR.261.1 | 24104269121230 | Madhobpur, Noapara, Purbo Bazar, Forid Mia | 2019-10-01 | NQ1008 | 9.6 | 21 | 9.6 | 22 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6072 | 2687.9997 | 101.1502
HBG-3.RR.262.1 | 24103349121225 | Madhobpur, Noapara, Dakkhin Bazar, Abdullah master | 2019-10-01 | NQ1008 | 23.3 | 23 | 23.3 | 24 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 23.3 | 23.3 | 1.398 | 1.398 | 0.0007168 | 100% | 0% | 1.398 | 1.398 | 0.0011869 | 28 | 0.028025 | 0.028025 |  | 0 | 0 | 6144 | 2615.9997 | 245.5
HBG-3.RR.263.1 | 24103349121225 | Madhobpur, Noapara, Dakkhin Bazar, Selim Chowdhury | 2019-10-01 | NQ1008 | 9.7 | 25 | 8.9 | 26 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6144 | 2615.9997 | 93.7747
HBG-3.RR.264.1 | 24103039121240 | Madhobpur, Itakhola, Murapara, Forman Ali | 2019-10-01 | NQ1008 | 13.1 | 27 | 13.2 | 28 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6144 | 2615.9997 | 139.0816
HBG-3.RR.265.1 | 24103039121240 | Madhobpur, Itakhola, Murapara, Shahjahan Mia | 2019-10-01 | NQ1008 | 12.4 | 29 | 11.6 | 30 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6144 | 2615.9997 | 122.2232
HBG-3.RR.266.1 | 24102859121237 | Madhobpur, Itakhola, Murapara, Selim | 2019-10-01 | NQ1008 | 11.6 | 31 | 11.6 | 32 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6144 | 2615.9997 | 122.2232
HBG-3.RR.267.1 | 24102859121237 | Madhobpur, Itakhola, Murapara, Forid | 2019-10-01 | NQ1008 | 16.7 | 33 | 16.7 | 34 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 6144 | 2615.9997 | 175.9592
HBG-3.RR.268.1 | 24102819121239 | Madhobpur, Itakhola, Murapara, Sattar Ali | 2019-10-01 | NQ1008 | 25.6 | 35 | 25.6 | 36 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 25.6 | 25.6 | 1.536 | 1.536 | 0.0007168 | 100% | 0% | 1.536 | 1.536 | 0.0011869 | 28 | 0.030792 | 0.030792 |  | 0 | 0 | 6144 | 2615.9997 | 269.7339
HBG-3.RR.269.1 | 24102819121239 | Madhobpur, Itakhola, Murapara, Monsur Ahmed | 2019-10-01 | NQ1008 | 14 | 37 | 14 | 38 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6144 | 2615.9997 | 147.5107
HBG-3.RR.270.1 | 24102599121225 | Madhobpur, Itakhola, Murapara, Bokul Member | 2019-10-01 | NQ1008 | 10.5 | 39 | 10.6 | 40 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6144 | 2615.9997 | 111.6867
HBG-3.RR.271.1 | 24102599121225 | Madhobpur, Itakhola, Murapara, Lokman Azad | 2019-10-01 | NQ1008 | 11.6 | 41 | 11.6 | 42 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6144 | 2615.9997 | 122.2232
HBG-3.RR.272.1 | 24103019121080 | Madhobpur, Itakhola, Shilpara, Milon Chandra | 2019-10-02 | NQ1008 | 9.9 | 55 | 9.9 | 56 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6096 | 2663.9997 | 104.3112
HBG-3.RR.273.1 | 24103169121079 | Madhobpur, Itakhola, Shilpara, Sonjit Shil | 2019-10-02 | NQ1008 | 22.5 | 57 | 22.5 | 58 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 22.5 | 22.5 | 1.35 | 1.35 | 0.0007168 | 100% | 0% | 1.35 | 1.35 | 0.0011869 | 28 | 0.027063 | 0.027063 |  | 0 | 0 | 6096 | 2663.9997 | 237.0708
HBG-3.RR.274.1 | 24103169121079 | Madhobpur, Itakhola, Shilpara, H # 546 | 2019-10-02 | NQ1008 | 11.6 | 61 | 11.6 | 62 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6096 | 2663.9997 | 122.2232
HBG-3.RR.275.1 | 24103309121065 | Madhobpur, Itakhola, Shilpara, Jhorna Shil | 2019-10-02 | NQ1008 | 13 | 63 | 13 | 64 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6096 | 2663.9997 | 136.9743
HBG-3.RR.276.1 | 24103239121056 | Madhobpur, Itakhola, Shilpara, Roton | 2019-10-02 | NQ1008 | 10.4 | 65 | 10.4 | 66 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6096 | 2663.9997 | 109.5794
HBG-3.RR.277.1 | 24103239121056 | Madhobpur, Itakhola, Shilpara, Pritish Ronjon | 2019-10-02 | NQ1008 | 11.6 | 67 | 11.6 | 68 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6096 | 2663.9997 | 122.2232
HBG-3.RR.278.1 | 24103119121055 | Madhobpur, Itakhola, Shilpara, Shuvash | 2019-10-02 | NQ1008 | 7.5 | 69 | 7.5 | 70 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6096 | 2663.9997 | 79.0236
HBG-3.RR.279.1 | 24091399121146 | Madhobpur, Jogodispur, Abdul Wahab | 2019-10-03 | NQ1008 | 25.3 | 89 | 25.3 | 90 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 25.3 | 25.3 | 1.518 | 1.518 | 0.0007168 | 100% | 0% | 1.518 | 1.518 | 0.0011869 | 28 | 0.030431 | 0.030431 |  | 0 | 0 | 6144 | 2615.9997 | 266.573
HBG-3.RR.280.1 | 24091399121146 | Madhobpur, Jogodispur, Abdul Gofur Master | 2019-10-03 | NQ1008 | 18.9 | 91 | 18.9 | 92 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6144 | 2615.9997 | 199.1395
HBG-3.RR.281.1 | 24091559121172 | Madhobpur, Jogodispur, Nurul islam | 2019-10-03 | NQ1008 | 7.2 | 93 | 7.2 | 94 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6144 | 2615.9997 | 75.8627
HBG-3.RR.282.1 | 24091559121172 | Madhobpur, Jogodispur, Boshir Chowdhury | 2019-10-03 | NQ1008 | 4.5 | 95 | 4.5 | 96 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6144 | 2615.9997 | 47.4142
HBG-3.RR.283.1 | 24091509121165 | Madhobpur, Jogodispur, Shamsu Chowdhury | 2019-10-03 | NQ1008 | 18.4 | 97 | 18.5 | 98 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6144 | 2615.9997 | 194.9249
HBG-3.RR.284.1 | 24055699117414 | Madhobpur, Fire Service R/A, Ashu Mia | 2019-10-03 | NQ1008 | 12 | 99 | 12 | 100 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6216 | 2543.9997 | 126.4378
HBG-3.RR.285.1 | 24055699117414 | Madhobpur, Fire Service R/A, Front Ayub Ali House | 2019-10-03 | NQ1008 | 18.4 | 103 | 18.4 | 104 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6216 | 2543.9997 | 193.8713
HBG-3.RR.286.1 | 24060029117417 | Madhobpur, Fire Service R/A, Ward# 4, Yakub Ali, H# 30 | 2019-10-03 | NQ1008 | 14.1 | 105 | 14.1 | 106 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6216 | 2543.9997 | 148.5644
HBG-3.RR.287.1 | 24055989117430 | Madhobpur, Fire Service R/A, Ward# 4, Abdur Rahman | 2019-10-03 | NQ1008 | 13.8 | 107 | 13.8 | 108 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6216 | 2543.9997 | 145.4034
HBG-3.RR.287.2 | 24055989117430 | Madhobpur, Fire Service R/A, Ward# 4, Abdur Rahman | 2020-10-14 | NQ1009 | 5.6 | 626 | 5.6 | 627 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6216 | 2543.9997 | 59.0043
HBG-3.RR.288.1 | 24060409117467 | Madhobpur, Fire Service R/A, Shajahan Mia | 2019-10-03 | NQ1008 | 13.9 | 109 | 13.9 | 110 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6216 | 2543.9997 | 146.4571
HBG-3.RR.289.1 | 24060409117467 | Madhobpur, Fire Service R/A, Mongol Mia | 2019-10-03 | NQ1008 | 18.7 | 111 | 18.4 | 112 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6216 | 2543.9997 | 193.8713
HBG-3.RR.290.1 | 24054179117224 | Madhobpur Bazar, Kalibari Road, Nobendro Bonik | 2019-10-05 | MN1032 | 4.9 | 137 | 4.9 | 138 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6168 | 2591.9997 | 51.6288
HBG-3.RR.291.1 | 24054179117224 | Madhobpur Bazar, Kalibari Road, Sontosh Roy | 2019-10-05 | MN1032 | 13.3 | 139 | 13.4 | 140 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6168 | 2591.9997 | 141.1888
HBG-3.RR.292.1 | 24054179117224 | Madhobpur Bazar, Kalibari Road, Kanai Pal | 2019-10-05 | MN1032 | 18.2 | 141 | 17.7 | 142 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 6168 | 2591.9997 | 186.4957
HBG-3.RR.293.1 | 24054179117224 | Madhobpur Bazar, Kalibari Road, Ojit Pal | 2019-10-05 | MN1032 | 16.1 | 143 | 16.1 | 144 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6168 | 2591.9997 | 169.6373
HBG-3.RR.294.1 | 24054219117206 | Madhobpur Bazar, Modok potti, Narayan Sen | 2019-10-05 | MN1032 | 10.8 | 145 | 10.8 | 146 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6168 | 2591.9997 | 113.794
HBG-3.RR.295.1 | 24054519117189 | Madhobpur Bazar, Kormokar Potti, Shipu Roy | 2019-10-05 | MN1032 | 10.2 | 149 | 9.9 | 150 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6168 | 2591.9997 | 104.3112
HBG-3.RR.296.1 | 24054469117229 | Madhobpur Bazar, Bonik Potti, Amrit Pal | 2019-10-05 | MN1032 | 11.7 | 151 | 11.7 | 152 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6168 | 2591.9997 | 123.2768
HBG-3.RR.297.1 | 24054469117229 | Madhobpur Bazar, Bonik Potti, Gourango Ghosh | 2019-10-05 | MN1032 | 13.2 | 153 | 13.4 | 154 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6168 | 2591.9997 | 141.1888
HBG-3.RR.298.1 | 24055329117218 | Madhobpur, Upazila Complex R/A, Chameli Vaban | 2019-10-06 | NQ1008 | 64.9 | 159 | 64.9 | 160 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 64.9 | 64.9 | 3.894 | 3.894 | 0.0007168 | 100% | 0% | 3.894 | 3.894 | 0.0011869 | 28 | 0.078061 | 0.078061 |  | 0 | 0 | 6168 | 2591.9997 | 683.8176
HBG-3.RR.299.1 | 24055329117218 | Madhobpur, Upazila Complex R/A, Hasna Hena | 2019-10-06 | NQ1008 | 16.3 | 163 | 16.3 | 164 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 6168 | 2591.9997 | 171.7446
HBG-3.RR.300.1 | 24055449117220 | Madhobpur, Upazila Complex R/A, Titon Ali Fokir | 2019-10-06 | NQ1008 | 11.6 | 165 | 11.6 | 166 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6168 | 2591.9997 | 122.2232
HBG-3.RR.351.1 | 24061559117582 | Madhabpur, Raipara, Rotish Rai | 2019-10-05 | MN1032 | 18.7 | 125 | 17.9 | 126 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 6216 | 2543.9997 | 188.603
HBG-3.RR.351.2 | 24061559117582 | Madhabpur, Raipara, Rotish Rai | 2022-03-06 | LU1001 | 7 | 26 | 7 | 27 | 2022-03-06 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 4680 | 2543.9997 | 60.8229
HBG-3.RR.352.1 | 24061519117588 | Madhabpur, Raipara, Subas Biswas | 2019-10-05 | MN1032 | 12.5 | 127 | 12.5 | 128 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6216 | 2543.9997 | 131.706
HBG-3.RR.353.1 | 24061519117588 | Madhabpur, Raipara, Sheli Biswas | 2019-10-05 | MN1032 | 11.6 | 129 | 10.8 | 130 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6216 | 2543.9997 | 113.794
HBG-3.RR.353.2 | 24061519117588 | Madhabpur, Raipara, Sheli Biswas | 2022-03-06 | LU1001 | 5.3 | 28 | 5.3 | 29 | 2022-03-06 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 4680 | 2543.9997 | 46.0516
HBG-3.RR.354.1 | 24061559117582 | Madhabpur, Raipara, Porimol Rai | 2019-10-05 | MN1032 | 11.9 | 131 | 11.9 | 132 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6216 | 2543.9997 | 125.3841
HBG-3.RR.355.1 | 24061559117582 | Madhabpur, Raipara, Porimol Rai | 2019-10-05 | MN1032 | 14.4 | 133 | 14.4 | 134 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6216 | 2543.9997 | 151.7253
HBG-3.RR.356.1 | 24061579117575 | Madhabpur, Raipara, Pranesh Rai | 2019-10-05 | MN1032 | 4.1 | 135 | 4.1 | 136 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6216 | 2543.9997 | 43.1996
HBG-3.RR.357.1 | 24054569117207 | Madhabpur, Nasir Nogor Road, Jogot Mantion | 2019-10-06 | MN1032 | 15.6 | 155 | 15.6 | 156 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6168 | 2591.9997 | 164.3691
HBG-3.RR.358.1 | 24054569117207 | Madhabpur, Nasir Nogor Road, Akota Mantion | 2019-10-06 | MN1032 | 14.4 | 157 | 14.4 | 158 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6168 | 2591.9997 | 151.7253
HBG-3.RR.359.1 | 24054569117207 | Madhabpur, Nasir Nogor Road, Jakariya Mamun | 2019-10-06 | MN1032 | 16 | 159 | 15.3 | 160 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6168 | 2591.9997 | 161.2082
HBG-3.RR.360.1 | 24054799117188 | Madhabpur, Nasir Nogor Road, Khan Plaza | 2019-10-06 | MN1032 | 8.9 | 161 | 8.4 | 162 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6168 | 2591.9997 | 88.5064
HBG-3.RR.361.1 | 24054599117174 | Madhabpur, West Bazar, Hasam Bapari | 2019-10-06 | MN1032 | 14.6 | 163 | 14.6 | 164 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6168 | 2591.9997 | 153.8326
HBG-3.RR.362.1 | 24054349117165 | Madhabpur, West Bazar, Masjid Road, Monir Hossan | 2019-10-06 | MN1032 | 18.9 | 165 | 18.9 | 166 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6168 | 2591.9997 | 199.1395
HBG-3.RR.363.1 | 24054349117165 | Madhabpur, West Bazar, Masjid Road, Abdul Hannan | 2019-10-06 | MN1032 | 11.6 | 167 | 11.7 | 168 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6168 | 2591.9997 | 123.2768
HBG-3.RR.364.1 | 24054269117077 | Madhabpur, Katiara Majhipara, Monoronjon Das | 2019-10-06 | MN1032 | 12.8 | 169 | 12.8 | 170 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6168 | 2591.9997 | 134.867
HBG-3.RR.365.1 | 24054269117077 | Madhabpur, Katiara Majhipara, Jhontu Das | 2019-10-06 | MN1032 | 3.2 | 171 | 3.2 | 172 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6168 | 2591.9997 | 33.7167
HBG-3.RR.366.1 | 24054139117077 | Madhabpur, Katiara Palpara, Madhup Pal | 2019-10-06 | MN1032 | 13.4 | 173 | 13.4 | 174 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6168 | 2591.9997 | 141.1888
HBG-3.RR.367.1 | 24054109117068 | Madhabpur, Katiara Majhipara, Ronodab | 2019-10-06 | MN1032 | 4.1 | 177 | 4.4 | 178 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6168 | 2591.9997 | 46.3605
HBG-3.RR.368.1 | 24054109117068 | Madhapur, Katiara, Majhipara, Subroto Ghosh | 2019-10-06 | MN1032 | 7.3 | 179 | 7.3 | 180 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6168 | 2591.9997 | 76.9163
HBG-3.RR.369.1 | 24054109117068 | Madhabpur, Katiara Majhipara, Berandro Dev Rai | 2019-10-06 | MN1032 | 12.8 | 181 | 12.8 | 182 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6168 | 2591.9997 | 134.867
HBG-3.RR.370.1 | 24060849117512 | Madhabpur, Tongbari, Johir Mia | 2019-10-07 | MN1032 | 6.7 | 213 | 6.2 | 214 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6216 | 2543.9997 | 65.3262
HBG-3.RR.371.1 | 24060849117512 | Madhabpur, Tongbari, Rohid Ali | 2019-10-07 | MN1032 | 7.7 | 215 | 7.7 | 216 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6216 | 2543.9997 | 81.1309
HBG-3.RR.372.1 | 24060849117512 | Madhabpur, Tongbari, Mohorom Ali | 2019-10-07 | MN1032 | 2.8 | 217 | 2.8 | 218 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6216 | 2543.9997 | 29.5021
HBG-3.RR.451.1 | 24061159117405 | West Madhobpur, Ward # 3, Saiful Alom | 2019-10-06 | NQ1007 | 6.6 | 128 | 6.6 | 129 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6216 | 2543.9997 | 69.5408
HBG-3.RR.452.1 | 24060559117415 | West Madhobpur, Ward # 3, Samsuddin | 2019-10-06 | NQ1007 | 10.7 | 130 | 10.7 | 131 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6216 | 2543.9997 | 112.7403
HBG-3.RR.453.1 | 24060699117412 | West Madhobpur, Ward # 3, Jillu Mia | 2019-10-06 | NQ1007 | 6.9 | 132 | 6.9 | 133 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6216 | 2543.9997 | 72.7017
HBG-3.RR.454.1 | 24060699117412 | West Madhobpur, Ward # 3, Sanu Mia | 2019-10-06 | NQ1007 | 12.2 | 134 | 12.2 | 135 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6216 | 2543.9997 | 128.5451
HBG-3.RR.454.2 | 24060699117412 | West Madhobpur, Ward # 3, Sanu Mia | 2021-01-21 | NQ1003 | 4.9 | 102 | 4.9 | 103 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6216 | 2543.9997 | 51.6288
HBG-3.RR.455.1 | 24060369117412 | West Madhobpur, Ward # 4, Sabu Mia | 2019-10-07 | NQ1007 | 12.2 | 156 | 12.3 | 157 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6216 | 2543.9997 | 129.5987
HBG-3.RR.456.1 | 24060369117412 | West Madhobpur, Ward # 4, Foize Mia | 2019-10-07 | NQ1007 | 11.6 | 158 | 11.6 | 159 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6216 | 2543.9997 | 122.2232
HBG-3.RR.457.1 | 24060279117385 | West Madhobpur, Ward # 4, Sala Uddin | 2019-10-07 | NQ1007 | 9.1 | 160 | 9.1 | 161 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6216 | 2543.9997 | 95.882
HBG-3.RR.457.2 | 24060279117385 | West Madhobpur, Ward # 4, Sala Uddin | 2021-01-21 | NQ1003 | 6.9 | 86 | 7 | 87 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6216 | 2543.9997 | 73.7554
HBG-3.RR.458.1 | 24060369117394 | West Madhobpur, Ward # 4, Joinal Mia | 2019-10-07 | NQ1007 | 5.2 | 162 | 5.2 | 163 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6216 | 2543.9997 | 54.7897
HBG-3.RR.459.1 | 24060369117394 | West Madhobpur, Ward # 4, Salaha Khatun | 2019-10-07 | NQ1007 | 12.4 | 164 | 12.4 | 165 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6216 | 2543.9997 | 130.6524
HBG-3.RR.460.1 | 24060369117394 | West Madhobpur, Ward # 4, Saddam | 2019-10-07 | NQ1007 | 12.1 | 166 | 12.1 | 167 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6216 | 2543.9997 | 127.4914
HBG-3.RR.461.1 | 24060409117397 | West Madhobpur, Ward # 4, Taher Sordar | 2019-10-07 | NQ1007 | 16.7 | 168 | 16.7 | 169 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 6216 | 2543.9997 | 175.9592
HBG-3.RR.462.1 | 24060479117391 | West Madhobpur, Ward # 4, Coton Mia | 2019-10-07 | NQ1007 | 14.6 | 170 | 14.4 | 171 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6216 | 2543.9997 | 151.7253
HBG-3.RR.463.1 | 24060529117388 | West Madhobpur, Ward # 4, Sahajan Mia | 2019-10-07 | NQ1007 | 3.8 | 172 | 3.8 | 173 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6216 | 2543.9997 | 40.0386
HBG-3.RR.463.2 | 24060529117388 | West Madhobpur, Ward # 4, Sahajan Mia | 2022-03-06 | LU1001 | 25.4 | 24 | 25.6 | 25 | 2022-03-06 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 25.6 | 25.6 | 1.536 | 1.536 | 0.0007168 | 100% | 0% | 1.536 | 1.536 | 0.0011869 | 28 | 0.030792 | 0.030792 |  | 0 | 0 | 4680 | 2543.9997 | 222.4381
HBG-3.RR.464.1 | 24060649117395 | West Madhobpur, Ward # 4, Pathan Bari | 2019-10-07 | NQ1007 | 15.2 | 174 | 15.2 | 175 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6216 | 2543.9997 | 160.1545
HBG-3.RR.465.1 | 24060649117395 | West Madhobpur, Ward # 4, Pathan Bari | 2019-10-07 | NQ1007 | 3.8 | 176 | 3.8 | 177 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6216 | 2543.9997 | 40.0386
HBG-3.RR.466.1 | 24061229117477 | West Madhobpur, Ward # 3, Abu Soddar Bari | 2019-10-07 | NQ1007 | 7.7 | 178 | 7.8 | 179 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6216 | 2543.9997 | 82.1846
HBG-3.RR.467.1 | 24061259117499 | West Madhobpur, Ward # 3, Noyab Mia | 2019-10-07 | NQ1007 | 12.5 | 180 | 12.5 | 181 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6216 | 2543.9997 | 131.706
HBG-3.RR.468.1 | 24061259117499 | West Madhobpur, Ward # 3, Tahar Mia | 2019-10-07 | NQ1007 | 13.1 | 182 | 13.2 | 183 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6216 | 2543.9997 | 139.0816
HBG-3.RR.469.1 | 24061489117510 | West Madhobpur, Ward # 3, Abdul Jahir | 2019-10-07 | NQ1007 | 18.2 | 184 | 18.2 | 185 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 6216 | 2543.9997 | 191.764
HBG-3.RR.501.1 | 24054519117340 | Madhabpur, Samoli R/A, Ronjit Das | 2019-10-07 | NQ1008 | 12.5 | 217 | 12.5 | 218 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6168 | 2591.9997 | 131.706
HBG-3.RR.502.1 | 24054479117319 | Madhabpur, Samoli R/A, Nozrul Islam | 2019-10-07 | NQ1008 | 13.4 | 219 | 12.8 | 220 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6168 | 2591.9997 | 134.867
HBG-3.RR.502.2 | 24054479117319 | Madhabpur, Samoli R/A, Nozrul Islam | 2020-10-14 | NQ1009 | 7.9 | 594 | 7.9 | 595 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6168 | 2591.9997 | 83.2382
HBG-3.RR.551.1 | 24055589117236 | Madhobpur, Upazila Complex R/A, Abdus Sattar | 2019-10-06 | NQ1008 | 21 | 167 | 20.6 | 168 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 20.6 | 20.6 | 1.236 | 1.236 | 0.0007168 | 100% | 0% | 1.236 | 1.236 | 0.0011869 | 28 | 0.024778 | 0.024778 |  | 0 | 0 | 6168 | 2591.9997 | 217.0515
HBG-3.RR.552.1 | 24055629117228 | Madhobpur, Upazila Complex R/A, Kuddus | 2019-10-06 | NQ1008 | 13.1 | 169 | 13.2 | 170 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6168 | 2591.9997 | 139.0816
HBG-3.RR.553.1 | 24055539117222 | Madhobpur, Upazila Complex R/A, Sayed Kutub Uddin | 2019-10-06 | NQ1008 | 12.8 | 172 | 12.8 | 173 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6168 | 2591.9997 | 134.867
HBG-3.RR.554.1 | 24055539117222 | Madhobpur, Upazila Complex R/A, Forid Uddin Chowdhury | 2019-10-06 | NQ1008 | 11.3 | 174 | 11.3 | 175 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6168 | 2591.9997 | 119.0622
HBG-3.RR.555.1 | 24055499117220 | Madhobpur, Upazila Complex R/A, Dulal Chowdhury | 2019-10-06 | NQ1008 | 9.6 | 176 | 9.6 | 177 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6168 | 2591.9997 | 101.1502
HBG-3.RR.556.1 | 24055459117182 | Madhobpur, Upazila Complex R/A, Square diagnostic Center | 2019-10-06 | NQ1008 | 12.9 | 178 | 12.9 | 179 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6168 | 2591.9997 | 135.9206
HBG-3.RR.556.2 | 24055459117182 | Madhobpur, Upazila Complex R/A, Square diagnostic Center | 2019-10-06 | NQ1008 | 6.8 | 180 | 6.8 | 181 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6168 | 2591.9997 | 71.6481
HBG-3.RR.557.1 | 24055249117187 | Madhobpur, Upazila Complex R/A, Golap Quarter | 2019-10-06 | NQ1008 | 13.8 | 182 | 13.8 | 183 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6168 | 2591.9997 | 145.4034
HBG-3.RR.558.1 | 24054889117227 | Madhobpur, Upazila Complex R/A, Upazila Complex Tin Shed Quarter | 2019-10-06 | NQ1008 | 7.3 | 184 | 7.3 | 185 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6168 | 2591.9997 | 76.9163
HBG-3.RR.559.1 | 24055199117114 | Madhobpur, Katiyara Sobujbagh, Ward # 6, Mubarak | 2019-10-07 | NQ1008 | 14.1 | 186 | 14.1 | 187 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6168 | 2591.9997 | 148.5644
HBG-3.RR.560.1 | 24055199117114 | Madhobpur, Katiyara Sobujbagh, Mutalib Mollik | 2019-10-07 | NQ1008 | 11.5 | 188 | 11.2 | 189 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6168 | 2591.9997 | 118.0086
HBG-3.RR.561.1 | 24055259117114 | Madhobpur, Katiyara Sobujbagh, Sonjit Saha | 2019-10-07 | NQ1008 | 4.3 | 190 | 4.3 | 191 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6168 | 2591.9997 | 45.3069
HBG-3.RR.562.1 | 24055459117098 | Madhobpur, Katiyara Sobujbagh, Sreedham Das | 2019-10-07 | NQ1008 | 16.4 | 192 | 16.1 | 193 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6168 | 2591.9997 | 169.6373
HBG-3.RR.563.1 | 24054869117105 | Madhobpur, Katiyara Sobujbagh, Nasir Nogar Road, Kuddus | 2019-10-07 | NQ1008 | 13.6 | 194 | 13.6 | 195 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6168 | 2591.9997 | 143.2961
HBG-3.RR.564.1 | 24054929117099 | Madhobpur, Katiyara Sobujbagh, Nasir Nogar Road, Al Amin | 2019-10-07 | NQ1008 | 11.3 | 196 | 11.3 | 197 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6168 | 2591.9997 | 119.0622
HBG-3.RR.565.1 | 24054879117096 | Madhobpur, Katiyara Sobujbagh, Nasir Nogar Road, Shamsul Islam | 2019-10-07 | NQ1008 | 19.2 | 198 | 19.2 | 199 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 19.2 | 19.2 | 1.152 | 1.152 | 0.0007168 | 100% | 0% | 1.152 | 1.152 | 0.0011869 | 28 | 0.023094 | 0.023094 |  | 0 | 0 | 6168 | 2591.9997 | 202.3004
HBG-3.RR.566.1 | 24054879117096 | Madhobpur, Katiyara Sobujbagh, Nasir Nogar Road, Dilip Ray | 2019-10-07 | NQ1008 | 12 | 200 | 12 | 201 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6168 | 2591.9997 | 126.4378
HBG-3.RR.567.1 | 24054979117087 | Madhobpur, Katiyara Sobujbagh, Nasir Nogar Road, Nur Mia | 2019-10-07 | NQ1008 | 13.5 | 202 | 13.5 | 203 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6168 | 2591.9997 | 142.2425
HBG-3.RR.568.1 | 24054919117078 | Madhobpur, Katiyara Sobujbagh, Nasir Nogar Road, Hazi Ayub Ali | 2019-10-07 | NQ1008 | 11.2 | 204 | 11.2 | 205 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6168 | 2591.9997 | 118.0086
HBG-3.RR.569.1 | 24054839117072 | Madhobpur, Katiyara uttar Para, Rakesh Ghosh | 2019-10-07 | NQ1008 | 15.9 | 206 | 15.9 | 207 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6168 | 2591.9997 | 167.5301
HBG-3.RR.570.1 | 24055519117316 | Madhobpur, Main road, Gudam para, Nur Mia | 2019-10-07 | NQ1008 | 38.3 | 209 | 38.3 | 210 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 38.3 | 38.3 | 2.298 | 2.298 | 0.0007168 | 100% | 0% | 2.298 | 2.298 | 0.0011869 | 28 | 0.046067 | 0.046067 |  | 0 | 0 | 6168 | 2591.9997 | 403.5472
HBG-4.RR.1.1 | 24335479131092 | Habiganj, Nabiganj, Shibpasa, Pintu Chandra | 2019-10-09 | MN1032 | 12.3 | 219 | 12.3 | 220 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6240 | 2519.9997 | 129.5987
HBG-4.RR.2.1 | 24335479131092 | Habiganj, Nabiganj, Shibpasa, Borando Bonik | 2019-10-09 | MN1032 | 18.1 | 221 | 18.1 | 222 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6240 | 2519.9997 | 190.7103
HBG-4.RR.3.1 | 24335429131089 | Habiganj, Nabiganj, Shibpasa, Panna Rani | 2019-10-09 | MN1032 | 15.4 | 223 | 15.4 | 224 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6240 | 2519.9997 | 162.2618
HBG-4.RR.4.1 | 24335369131095 | Habiganj, Nabiganj, Shibpasa, Horidhon | 2019-10-09 | MN1032 | 14.8 | 225 | 14.8 | 226 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6240 | 2519.9997 | 155.9399
HBG-4.RR.5.1 | 24335319131111 | Habiganj, Nabiganj, Shibpasa, Arun Pal | 2019-10-09 | MN1032 | 9.1 | 228 | 8.3 | 229 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6240 | 2519.9997 | 87.4528
HBG-4.RR.6.1 | 24335319131111 | Habiganj, Nabiganj, Shibpasa, Gyan Ronjon Das | 2019-10-09 | MN1032 | 10.8 | 230 | 10.8 | 231 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6240 | 2519.9997 | 113.794
HBG-4.RR.7.1 | 24335389131119 | Habiganj, Nabiganj, Shibpasa, Manik Pal | 2019-10-09 | MN1032 | 9.7 | 232 | 9.7 | 233 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6240 | 2519.9997 | 102.2039
HBG-4.RR.8.1 | 24335389131119 | Habiganj, Nabiganj, Shibpasa, Dhiman Pal | 2019-10-09 | MN1032 | 12.3 | 234 | 12.4 | 235 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6240 | 2519.9997 | 130.6524
HBG-4.RR.9.1 | 24335459131123 | Habiganj, Nabiganj, Shibpasa, Boson Dev | 2019-10-09 | MN1032 | 14.7 | 236 | 14.7 | 237 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6240 | 2519.9997 | 154.8863
HBG-4.RR.10.1 | 24335809131177 | Nabiganj, Shibpasa School Road, Modabbir Hossain | 2019-10-10 | MN1032 | 10.9 | 258 | 10.9 | 259 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6240 | 2519.9997 | 114.8476
HBG-4.RR.11.1 | 24335479131187 | Nabiganj, Shibpasa School Road, Sagota Chokroborty | 2019-10-10 | MN1032 | 8.5 | 260 | 7.9 | 261 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6240 | 2519.9997 | 83.2382
HBG-4.RR.12.1 | 24335169131042 | Nabiganj, Anmonu, Ward # 3, Raja Mia | 2019-10-10 | MN1032 | 15.5 | 262 | 14.4 | 263 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6264 | 2495.9997 | 151.7253
HBG-4.RR.13.1 | 24335089131023 | Nabiganj, Anmonu, Ward # 3, Jalal Mia | 2019-10-10 | MN1032 | 15 | 264 | 15 | 265 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6264 | 2495.9997 | 158.0472
HBG-4.RR.14.1 | 24334999131029 | Nabiganj, Anmonu, Ward # 3, Morom Ali | 2019-10-10 | MN1032 | 16.5 | 266 | 16.7 | 267 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 6264 | 2495.9997 | 175.9592
HBG-4.RR.15.1 | 24334999131029 | Nabiganj, Anmonu, Ward # 3, Kudrot Ali | 2019-10-10 | MN1032 | 24.5 | 268 | 24.5 | 269 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 6264 | 2495.9997 | 258.1438
HBG-4.RR.15.2 | 24334999131029 | Nabiganj, Anmonu, Ward # 3, Kudrot Ali | 2021-01-23 | NQ1007 | 3.4 | 68 | 3.4 | 69 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6264 | 2495.9997 | 35.824
HBG-4.RR.16.1 | 24334929131029 | Nabiganj, Anmonu, Ward # 3, Mairum Begom | 2019-10-10 | MN1032 | 16.1 | 270 | 15.6 | 271 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6264 | 2495.9997 | 164.3691
HBG-4.RR.17.1 | 24335159131007 | Nabiganj, Anmonu, Ward # 3, Shamim | 2019-10-10 | MN1032 | 10.2 | 274 | 10.2 | 275 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6264 | 2495.9997 | 107.4721
HBG-4.RR.18.1 | 24334999131109 | Nabiganj, Bashundhara R/A, H # 262/1 | 2019-10-12 | MN1032 | 12.3 | 305 | 12.3 | 306 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6240 | 2519.9997 | 129.5987
HBG-4.RR.19.1 | 24335009131089 | Nabiganj, Bashundhara R/A, H # 261 | 2019-10-12 | MN1032 | 6.5 | 307 | 6.5 | 308 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6240 | 2519.9997 | 68.4871
HBG-4.RR.20.1 | 24335009131089 | Nabiganj, Bashundhara R/A, H # 257 | 2019-10-12 | MN1032 | 10.5 | 309 | 10.5 | 310 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6240 | 2519.9997 | 110.6331
HBG-4.RR.21.1 | 24341009130445 | Nabiganj, Rajnagar, Jaleia | 2019-10-12 | MN1032 | 13.6 | 311 | 13.6 | 312 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6240 | 2519.9997 | 143.2961
HBG-4.RR.22.1 | 24343739130510 | Nabiganj, Osmany Road, H # 240 | 2019-10-12 | MN1032 | 9.3 | 313 | 9.3 | 314 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6240 | 2519.9997 | 97.9893
HBG-4.RR.23.1 | 24344579130444 | Nabiganj, Gonda, Md. Jubir Ahmed | 2019-10-13 | MN1032 | 12.1 | 315 | 11.1 | 316 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6240 | 2519.9997 | 116.9549
HBG-4.RR.24.1 | 24343449130428 | Nabiganj, Gonda, Kajol Mia | 2019-10-13 | MN1032 | 15.2 | 317 | 15.2 | 318 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6240 | 2519.9997 | 160.1545
HBG-4.RR.25.1 | 24343449130428 | Nabiganj, Gonda, Mofiz Mia | 2019-10-13 | MN1032 | 7.6 | 319 | 7.1 | 320 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6240 | 2519.9997 | 74.809
HBG-4.RR.26.1 | 24343689130430 | Nabiganj, Gonda, Elais Mia | 2019-10-13 | MN1032 | 13.1 | 321 | 13.1 | 322 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6240 | 2519.9997 | 138.0279
HBG-4.RR.27.1 | 24343689130430 | Nabiganj, Gonda, Belal Mia | 2019-10-13 | MN1032 | 9.8 | 323 | 9.8 | 324 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6240 | 2519.9997 | 103.2575
HBG-4.RR.28.1 | 24343689130430 | Nabiganj, Gonda, Abdul Mojid | 2019-10-13 | MN1032 | 9.6 | 325 | 9.6 | 326 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6240 | 2519.9997 | 101.1502
HBG-4.RR.28.2 | 24343689130430 | Nabiganj, Gonda, Abdul Mojid | 2021-01-23 | MN1032 | 18.5 | 47 | 18.5 | 48 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6240 | 2519.9997 | 194.9249
HBG-4.RR.29.1 | 24343889130437 | Nabiganj, Gonda, Abdul Mojid | 2019-10-13 | MN1032 | 10.4 | 327 | 10.4 | 328 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6240 | 2519.9997 | 109.5794
HBG-4.RR.30.1 | 24335389130128 | Nobiganj, Baniachong Road, Goyahori, Niten Deb | 2019-10-13 | NQ1007 | 12.8 | 301 | 12.8 | 302 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6264 | 2495.9997 | 134.867
HBG-4.RR.31.1 | 24335369130118 | Nobiganj, Baniachong Road, Goyahori, Arun Deb | 2019-10-13 | NQ1007 | 5.2 | 303 | 5.2 | 304 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6264 | 2495.9997 | 54.7897
HBG-4.RR.32.1 | 24335529130060 | Nobiganj, Baniachong Road, Goyahori, Arpita Talukder | 2019-10-13 | NQ1007 | 15.8 | 305 | 15.8 | 306 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6264 | 2495.9997 | 166.4764
HBG-4.RR.33.1 | 24335509130061 | Nobiganj, Baniachong Road, Goyahori, Aurobindo Deb | 2019-10-13 | NQ1007 | 7.7 | 307 | 7.7 | 308 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6264 | 2495.9997 | 81.1309
HBG-4.RR.51.1 | 24335509131130 | Nabiganj, Shibpasha, Rudrogram Road, Wab Mia Chowdhury | 2019-10-09 | MN1032 | 16.6 | 238 | 16 | 239 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6240 | 2519.9997 | 168.5837
HBG-4.RR.52.1 | 24335269131127 | Nabiganj, Shibpasha, Rudrogram Road, Ajit Kumer Baido | 2019-10-09 | MN1032 | 25.7 | 240 | 25.7 | 241 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 25.7 | 25.7 | 1.542 | 1.542 | 0.0007168 | 100% | 0% | 1.542 | 1.542 | 0.0011869 | 28 | 0.030912 | 0.030912 |  | 0 | 0 | 6240 | 2519.9997 | 270.7876
HBG-4.RR.53.1 | 24335269131127 | Nabiganj, Shibpasha, Rudrogram Road, Bidhu Bhuson Raut | 2019-10-09 | MN1032 | 13.9 | 242 | 13.9 | 243 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6240 | 2519.9997 | 146.4571
HBG-4.RR.54.1 | 24335269131127 | Nabiganj, Shibpasha, Rudrogram Road, Hazi Samsuddin Sahab | 2019-10-09 | MN1032 | 10.6 | 244 | 9.7 | 245 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6240 | 2519.9997 | 102.2039
HBG-4.RR.55.1 | 24335179131147 | Nabiganj, Shibpasha, Thakur Para, Fatama Begam | 2019-10-09 | MN1032 | 12.3 | 246 | 12.4 | 247 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6240 | 2519.9997 | 130.6524
HBG-4.RR.56.1 | 24335619131145 | Nabiganj, Shibpasha, Thakur Para, Omol | 2019-10-09 | MN1032 | 6.4 | 248 | 6.4 | 249 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6240 | 2519.9997 | 67.4335
HBG-4.RR.57.1 | 24335579131175 | Nabiganj, Shibpasha, Thakur Para, Foyjul Rahman (Gong) | 2019-10-09 | MN1032 | 4.8 | 256 | 4.8 | 257 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6240 | 2519.9997 | 50.5751
HBG-4.RR.58.1 | 24335319131171 | Nabiganj, Shibpasha, Thakur Para, Metu Chrokboti | 2019-10-09 | MN1032 | 10.8 | 254 | 10.8 | 255 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6240 | 2519.9997 | 113.794
HBG-4.RR.59.1 | 24334619131126 | Nabiganj, Joynogor, Ward # 9, Hazi Mohammad Fultab Ali | 2019-10-12 | MN1032 | 11.8 | 276 | 11 | 277 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6240 | 2519.9997 | 115.9013
HBG-4.RR.59.2 | 24334619131126 | Nabiganj, Joynogor, Ward # 9, Hazi Mohammad Fultab Ali | 2021-01-23 | NQ1003 | 10.8 | 120 | 10.8 | 121 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6240 | 2519.9997 | 113.794
HBG-4.RR.60.1 | 24334389131114 | Nabiganj, Joynogor, Ward # 9, Habibun Nesa Chowdhury | 2019-10-12 | MN1032 | 11.6 | 278 | 10.8 | 279 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6240 | 2519.9997 | 113.794
HBG-4.RR.61.1 | 24334299131114 | Nabiganj, Joynogor, Ward # 9, Anu Bonik | 2019-10-12 | MN1032 | 9.5 | 280 | 8.8 | 281 | 2022-01-01 | [9 empty] | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0
HBG-4.RR.62.1 | 24334139131099 | Nabiganj, Joynogor, Ward # 9, Biswojeet Bagchi | 2019-10-12 | MN1032 | 11.5 | 282 | 10.9 | 283 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6240 | 2519.9997 | 114.8476
HBG-4.RR.63.1 | 24333929131088 | Nabiganj, Joynogor, Ward # 9, Gazi Bhaban, Taz Uddin Ahmed | 2019-10-12 | MN1032 | 17.5 | 284 | 16.7 | 285 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 6240 | 2519.9997 | 175.9592
HBG-4.RR.64.1 | 24333919131079 | Nabiganj, Joynogor, Ward # 9, Nayamoul | 2019-10-12 | MN1032 | 16 | 288 | 16 | 289 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6240 | 2519.9997 | 168.5837
HBG-4.RR.64.2 | 24333919131079 | Nabiganj, Joynogor, Ward # 9, Nayamoul | 2020-10-13 | NQ1003 | 3.2 | 30 | 3.2 | 31 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6240 | 2519.9997 | 33.7167
HBG-4.RR.65.1 | 24332599131029 | Nabiganj, Joynogor, Ward # 9, Rasma Mohol | 2019-10-12 | MN1032 | 11.7 | 290 | 11.7 | 291 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6240 | 2519.9997 | 123.2768
HBG-4.RR.66.1 | 24332599131029 | Nabiganj, Joynogor, Ward # 9, Mamun Mia | 2019-10-12 | MN1032 | 50.6 | 295 | 50.6 | 296 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 50.6 | 50.6 | 3.036 | 3.036 | 0.0007168 | 100% | 0% | 3.036 | 3.036 | 0.0011869 | 28 | 0.060861 | 0.060861 |  | 0 | 0 | 6240 | 2519.9997 | 533.146
HBG-4.RR.67.1 | 24334789131152 | Nabiganj, Joynogor, Rudrogram Road, Sahin Mia | 2019-10-12 | MN1032 | 13 | 297 | 13 | 298 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6240 | 2519.9997 | 136.9743
HBG-4.RR.68.1 | 24334299131233 | Nabiganj, Borak Nogor, Shah Taz Uddin Road, Moksud Ali | 2019-10-12 | MN1032 | 15.6 | 299 | 15.8 | 300 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6240 | 2519.9997 | 166.4764
HBG-4.RR.69.1 | 24333989131294 | Nabiganj, Borak Nogor, Shah Taz Uddin Road, Abdul Salam | 2019-10-12 | MN1032 | 3.8 | 301 | 3.8 | 302 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6240 | 2519.9997 | 40.0386
HBG-4.RR.70.1 | 24333989131294 | Nabiganj, Borak Nogor, Shah Taz Uddin Road, Heron Mia | 2019-10-12 | MN1032 | 17.8 | 303 | 17.2 | 304 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 6240 | 2519.9997 | 181.2275
HBG-4.RR.71.1 | 24340449130385 | Nabiganj, Razabad, A.T.M Salam | 2019-10-13 | MN1032 | 10.4 | 329 | 9.6 | 330 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6264 | 2495.9997 | 101.1502
HBG-4.RR.71.2 | 24340449130385 | Nabiganj, Razabad, A.T.M Salam | 2022-03-09 | LU1001 | 18.4 | 34 | 18 | 35 | 2022-03-09 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 18 | 18 | 1.08 | 1.08 | 0.0007168 | 100% | 0% | 1.08 | 1.08 | 0.0011869 | 28 | 0.02165 | 0.02165 |  | 0 | 0 | 4656 | 2495.9997 | 154.843
HBG-4.RR.72.1 | 24340449130385 | Nabiganj, Razabad, Khaleda Akter | 2019-10-13 | MN1032 | 11.6 | 331 | 11.5 | 332 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6264 | 2495.9997 | 121.1695
HBG-4.RR.73.1 | 24340119130387 | Nabiganj, Razabad, Khaptan Ali | 2019-10-13 | MN1032 | 10.6 | 333 | 10.6 | 334 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6264 | 2495.9997 | 111.6867
HBG-4.RR.74.1 | 24335889130364 | Nabiganj, Razabad, Babul Mia | 2019-10-13 | MN1032 | 16.3 | 335 | 16.3 | 336 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 6264 | 2495.9997 | 171.7446
HBG-4.RR.75.1 | 24335889130364 | Nabiganj, Razabad, Akter Jahan, H # 89/1 | 2019-10-13 | MN1032 | 17 | 337 | 17 | 338 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 6264 | 2495.9997 | 179.1202
HBG-4.RR.76.1 | 24335689130364 | Nabiganj, Razabad, Sundor Ali | 2019-10-13 | MN1032 | 10 | 339 | 10 | 340 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6264 | 2495.9997 | 105.3648
HBG-4.RR.77.1 | 24335689130364 | Nabiganj, Razabad, Nilmoni Mia | 2019-10-13 | MN1032 | 9.7 | 341 | 9.7 | 342 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6264 | 2495.9997 | 102.2039
HBG-4.RR.78.1 | 24341079130364 | Nabiganj, Razabad, Abdul Mojid | 2019-10-13 | MN1032 | 8.7 | 343 | 8.8 | 344 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6264 | 2495.9997 | 92.721
HBG-4.RR.79.1 | 24323599130447 | Nabiganj, East Timirpur, Ward # 09, Nantu Shil | 2019-10-14 | MN1032 | 13.9 | 345 | 13.9 | 346 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6264 | 2495.9997 | 146.4571
HBG-4.RR.80.1 | 24323639130436 | Nabiganj, East Timirpur, Ward # 09, Gopal Rai | 2019-10-14 | MN1032 | 11.2 | 347 | 11.2 | 348 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6264 | 2495.9997 | 118.0086
HBG-4.RR.81.1 | 24323949130422 | Nabiganj, East Timirpur, Ward # 09, Brishnu Acharijo | 2019-10-14 | MN1032 | 12.5 | 349 | 12.6 | 350 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6264 | 2495.9997 | 132.7597
HBG-4.RR.82.1 | 24323379130471 | Nabiganj, East Timirpur, Ward # 09, Alimoddin | 2019-10-14 | MN1032 | 13.7 | 351 | 13.7 | 352 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6264 | 2495.9997 | 144.3498
HBG-4.RR.83.1 | 24323259130467 | Nabiganj, East Timirpur, Ward # 09, Shah Buddin | 2019-10-14 | MN1032 | 8.2 | 353 | 8.2 | 354 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6264 | 2495.9997 | 86.3991
HBG-4.RR.84.1 | 24323259130467 | Nabiganj, East Timirpur, Ward # 09, Razaul Korim | 2019-10-14 | MN1032 | 3.7 | 355 | 3.7 | 356 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6264 | 2495.9997 | 38.985
HBG-4.RR.85.1 | 24335159130022 | Nabiganj, Goyahori, Ward # 04, Susendro Chondro Das | 2019-10-14 | MN1032 | 7.1 | 357 | 7.1 | 358 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6264 | 2495.9997 | 74.809
HBG-4.RR.101.1 | 24340519131102 | Nabiganj, Shibpasha, Shamoli R/A, Onil Chandra Chowdhury | 2019-10-09 | NQ1007 | 12.1 | 215 | 12.1 | 216 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6240 | 2519.9997 | 127.4914
HBG-4.RR.102.1 | 24340649131104 | Nabiganj, Shibpasha, Shamoli R/A, Poritosh Chandra Deb | 2019-10-09 | NQ1007 | 14.7 | 217 | 14.7 | 218 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6240 | 2519.9997 | 154.8863
HBG-4.RR.103.1 | 24340649131104 | Nabiganj, Shibpasha, Shamoli R/A, Songkor Deb | 2019-10-09 | NQ1007 | 9.5 | 219 | 9.5 | 220 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6240 | 2519.9997 | 100.0966
HBG-4.RR.104.1 | 24335919131037 | Nabiganj, Nutun Bazar, Reza Complex, Akamot Mia | 2019-10-09 | NQ1007 | 6 | 221 | 6 | 222 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6240 | 2519.9997 | 63.2189
HBG-4.RR.105.1 | 24340249131017 | Nabiganj, Nutun Bazar, Osmani Road, Al-Hadi | 2019-10-09 | NQ1007 | 14 | 223 | 14 | 224 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6240 | 2519.9997 | 147.5107
HBG-4.RR.106.1 | 24340249131017 | Nabiganj, Nutun Bazar, Osmani Road, Al-Hadi | 2019-10-09 | NQ1007 | 9.5 | 225 | 9.5 | 226 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6240 | 2519.9997 | 100.0966
HBG-4.RR.107.1 | 24340449130556 | Nabiganj, Osmani Road, Chaleha Begum (Kafi House) | 2019-10-09 | NQ1007 | 4.2 | 227 | 4.2 | 228 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6240 | 2519.9997 | 44.2532
HBG-4.RR.108.1 | 24340219130577 | Nabiganj, Osmani Road, Rokeya Begum | 2019-10-09 | NQ1007 | 14.4 | 229 | 14.5 | 230 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 6240 | 2519.9997 | 152.779
HBG-4.RR.109.1 | 24340219130577 | Nabiganj, Osmani Road, Rubaya Begum | 2019-10-09 | NQ1007 | 10.4 | 231 | 9.9 | 232 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6240 | 2519.9997 | 104.3112
HBG-4.RR.110.1 | 24340219130585 | Nabiganj, Osmani Road, Belayat Hosen Bulbul | 2019-10-09 | NQ1007 | 13.7 | 233 | 13.7 | 234 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6240 | 2519.9997 | 144.3498
HBG-4.RR.111.1 | 24335909130550 | Nabiganj, Maddho Bazar, Manik Pal | 2019-10-10 | NQ1007 | 13 | 235 | 13.1 | 236 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6264 | 2495.9997 | 138.0279
HBG-4.RR.112.1 | 24340079130556 | Nabiganj, Maddho Bazar, Hazi Jilu Mia | 2019-10-10 | NQ1007 | 9.1 | 237 | 8.5 | 238 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6264 | 2495.9997 | 89.5601
HBG-4.RR.113.1 | 24340079130556 | Nabiganj, Maddho Bazar, Hazi Jilu Mia | 2019-10-10 | NQ1007 | 13.1 | 239 | 13.1 | 240 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6264 | 2495.9997 | 138.0279
HBG-4.RR.114.1 | 24340019130526 | Nabiganj, Maddho Bazar, Taposh Chandra Bonik | 2019-10-10 | NQ1007 | 3.5 | 241 | 3.5 | 242 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6264 | 2495.9997 | 36.8777
HBG-4.RR.115.1 | 24340449130526 | Nabiganj, J.K High School Road, Shah Khalad Mia | 2019-10-10 | NQ1007 | 7.7 | 243 | 7.7 | 244 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6264 | 2495.9997 | 81.1309
HBG-4.RR.151.1 | 24340219131209 | Nobigonj, SharPur Road, Foras Villa | 2019-10-09 | NQ1007 | 13.7 | 194 | 13.7 | 195 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6240 | 2519.9997 | 144.3498
HBG-4.RR.152.1 | 24340179131196 | Nobigonj, SharPur Road, Hazi Abdul Sobur | 2019-10-09 | NQ1007 | 5.9 | 196 | 5.9 | 197 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6240 | 2519.9997 | 62.1652
HBG-4.RR.153.1 | 24340419131179 | Nobigonj, Saplabag R/A, Alhaz Bachon Mia | 2019-10-09 | NQ1007 | 11.5 | 198 | 11.5 | 199 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6240 | 2519.9997 | 121.1695
HBG-4.RR.154.1 | 24340419131179 | Nobigonj, Saplabag R/A, H # 339/3, Md Saidul Islam | 2019-10-09 | NQ1007 | 6.9 | 200 | 6.9 | 201 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6240 | 2519.9997 | 72.7017
HBG-4.RR.155.1 | 24340129131164 | Nobigonj, Bangla Town, SharPur Road, Singer Plas | 2019-10-09 | NQ1007 | 10.6 | 202 | 10.6 | 203 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6240 | 2519.9997 | 111.6867
HBG-4.RR.156.1 | 24340019131113 | Nobigonj, SharPur Road, Sha Villa | 2019-10-09 | NQ1007 | 12.9 | 205 | 12.9 | 206 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6240 | 2519.9997 | 135.9206
HBG-4.RR.157.1 | 24340159131117 | Nobigonj, Samoli R/A, H # 306, Bimol Rai | 2019-10-09 | NQ1007 | 11.8 | 207 | 11.9 | 208 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6240 | 2519.9997 | 125.3841
HBG-4.RR.158.1 | 24340369131111 | Nobigonj, Samoli R/A, H # 319, Nilkontho Sutrodhor | 2019-10-09 | NQ1007 | 10.8 | 209 | 10.6 | 210 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6240 | 2519.9997 | 111.6867
HBG-4.RR.159.1 | 24340519131110 | Nobigonj, Samoli R/A, H # 316, Oboni Boidho | 2019-10-09 | NQ1007 | 5.4 | 211 | 5.4 | 212 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6240 | 2519.9997 | 56.897
HBG-4.RR.160.1 | 24340519131110 | Nobigonj, Samoli R/A, Mintu Das | 2019-10-09 | NQ1007 | 4.8 | 213 | 4.8 | 214 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6240 | 2519.9997 | 50.5751
HBG-4.RR.161.1 | 24341349130510 | Nobigonj, Osmani Road, H # 133, Hazi Md Kousar Ali Chowdary | 2019-10-10 | NQ1007 | 13.9 | 245 | 14 | 246 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6240 | 2519.9997 | 147.5107
HBG-4.RR.162.1 | 24341349130510 | Nobigonj, Osmani Road, H # 133, Hazi Md Kousar Ali Chowdary | 2019-10-10 | NQ1007 | 10.8 | 247 | 10.8 | 248 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6240 | 2519.9997 | 113.794
HBG-4.RR.163.1 | 24341569130505 | Nobigonj, Osmani Road, H # 123, Forid Mia | 2019-10-10 | NQ1007 | 5.1 | 249 | 5.1 | 250 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6240 | 2519.9997 | 53.7361
HBG-4.RR.164.1 | 24341709130505 | Nobigonj, Osmani Road, H # 118, Diraron Das | 2019-10-10 | NQ1007 | 9.7 | 253 | 9.7 | 254 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6240 | 2519.9997 | 102.2039
HBG-4.RR.165.1 | 24341959130400 | Nobigonj, Ovoi Nogor R/A, Md Abdul Rokib | 2019-10-12 | NQ1007 | 6.3 | 255 | 6.3 | 256 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6240 | 2519.9997 | 66.3798
HBG-4.RR.166.1 | 24341959130400 | Nobigonj, Ovoi Nogor R/A, Abdul Kadar | 2019-10-12 | NQ1007 | 5.7 | 257 | 5.6 | 258 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6240 | 2519.9997 | 59.0043
HBG-4.RR.167.1 | 24341959130400 | Nobigonj, Ovoi Nogor R/A, Mozahid Ahmed | 2019-10-12 | NQ1007 | 15.5 | 259 | 15.5 | 260 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 6240 | 2519.9997 | 163.3155
HBG-4.RR.168.1 | 24342159130394 | Nobigonj, Ovoi Nogor, H # 5/1, Sofiqul Haq | 2019-10-12 | NQ1007 | 6.4 | 261 | 6.4 | 262 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6240 | 2519.9997 | 67.4335
HBG-4.RR.169.1 | 24342319130422 | Nobigonj, Ovoi Nogor, Forhad Mia | 2019-10-12 | NQ1007 | 13.4 | 263 | 13.4 | 264 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6240 | 2519.9997 | 141.1888
HBG-4.RR.170.1 | 24342719130411 | Nobigonj, Ovoi Nogor, Samsuddin | 2019-10-12 | NQ1007 | 8 | 265 | 8 | 266 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6240 | 2519.9997 | 84.2919
HBG-4.RR.171.1 | 24342679130416 | Nobigonj, Ovoi Nogor, H # 10, Chowdary Nibas | 2019-10-12 | NQ1007 | 11.4 | 267 | 11.4 | 268 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6240 | 2519.9997 | 120.1159
HBG-4.RR.172.1 | 24342759130451 | Nobigonj, Upozala Porishod, Totho Candro | 2019-10-12 | NQ1007 | 9.6 | 269 | 9.6 | 270 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6240 | 2519.9997 | 101.1502
HBG-4.RR.173.1 | 24342759130451 | Nobigonj, Upozala Porishod, Totho Candro | 2019-10-12 | NQ1007 | 12.5 | 271 | 11.8 | 272 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6240 | 2519.9997 | 124.3305
HBG-4.RR.174.1 | 24342759130451 | Nobigonj, Upozala Porishod, Totho Candro | 2019-10-12 | NQ1007 | 11.9 | 273 | 12 | 274 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6240 | 2519.9997 | 126.4378
HBG-4.RR.175.1 | 24341989130503 | Nobigonj, Osmani Road, Shak Vobon | 2019-10-12 | NQ1007 | 11 | 275 | 11 | 276 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6240 | 2519.9997 | 115.9013
HBG-4.RR.176.1 | 24341989130503 | Nobigonj, Osmani Road, Md Saddur Rahman | 2019-10-12 | NQ1007 | 5.7 | 277 | 5.7 | 278 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6240 | 2519.9997 | 60.0579
HBG-4.RR.177.1 | 24342229130494 | Nobigonj, Osmani Road, H # 80, Md Abdul Ali | 2019-10-12 | NQ1007 | 10 | 279 | 10 | 280 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6240 | 2519.9997 | 105.3648
HBG-4.RR.178.1 | 24342369130497 | Nobigonj, Osmani Road, Alhaz Rohima Mansion | 2019-10-12 | NQ1007 | 7 | 281 | 7 | 282 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6240 | 2519.9997 | 73.7554
HBG-4.RR.179.1 | 24342459130495 | Nobigonj, Osmani Road, H # 70, Sofiq Mia | 2019-10-12 | NQ1007 | 11.3 | 283 | 11.3 | 284 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6240 | 2519.9997 | 119.0622
HBG-4.RR.180.1 | 24342549130501 | Nobigonj, Osmani Road, Jahangir Nibas | 2019-10-12 | NQ1007 | 15 | 285 | 15 | 286 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6240 | 2519.9997 | 158.0472
HBG-4.RR.181.1 | 24342549130501 | Nobigonj, Osmani Road, Rumana Villa | 2019-10-12 | NQ1007 | 10.3 | 287 | 10.3 | 288 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6240 | 2519.9997 | 108.5258
HBG-4.RR.182.1 | 24342779130499 | Nobigonj, Osmani Road, Foisol Afsol | 2019-10-12 | NQ1007 | 14.3 | 289 | 14.3 | 290 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6240 | 2519.9997 | 150.6717
HBG-4.RR.183.1 | 24344469130577 | Nobigonj, Salamathpur Road, Word # 1, H # 45/7, Nazmul Huda | 2019-10-13 | NQ1007 | 7.9 | 291 | 7.9 | 292 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6240 | 2519.9997 | 83.2382
HBG-4.RR.184.1 | 24344529131008 | Nobigonj, Salamathpur Road, Word # 1, Hazi Mohabbot Ali | 2019-10-13 | NQ1007 | 8.2 | 293 | 8.2 | 294 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6240 | 2519.9997 | 86.3991
HBG-4.RR.185.1 | 24344529131012 | Nobigonj, Salamathpur Road, Word # 1, H # 45/6, Md Aour Mia | 2019-10-13 | NQ1007 | 10 | 295 | 10 | 296 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6240 | 2519.9997 | 105.3648
HBG-4.RR.186.1 | 24345069130585 | Nobigonj, Collage Road, Word # 1, H # 35, Asdur Ali | 2019-10-13 | NQ1007 | 5.3 | 297 | 5.3 | 298 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6240 | 2519.9997 | 55.8434
HBG-4.RR.186.2 | 24345069130585 | Nobigonj, Collage Road, Word # 1, H # 35, Asdur Ali | 2022-03-10 | LU1001 | 9.3 | 36 | 9.3 | 37 | 2022-03-10 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 4608 | 2519.9997 | 79.7337
HBG-4.RR.187.1 | 24335739130021 | Nobigonj, Goyahori, Ward # 4, H # 20, Bala Rani Das | 2019-10-14 | NQ1007 | 13.2 | 310 | 13.2 | 311 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6264 | 2495.9997 | 139.0816
HBG-4.RR.188.1 | 24335739130021 | Nobigonj, Goyahori, Ward # 4, Ononto Das | 2019-10-14 | NQ1007 | 14.8 | 312 | 14.8 | 313 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6264 | 2495.9997 | 155.9399
HBG-4.RR.189.1 | 24335619130018 | Nobigonj, Goyahori, Ward # 4, Kripas Ronjon Rai | 2019-10-14 | NQ1007 | 18.3 | 314 | 17.6 | 315 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 6264 | 2495.9997 | 185.4421
HBG-4.RR.190.1 | 24335659130006 | Nobigonj, Goyahori, Ward # 4, H # 15, Sulakha Talukdar | 2019-10-14 | NQ1007 | 5.7 | 318 | 5.7 | 319 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6264 | 2495.9997 | 60.0579
HBG-4.RR.191.1 | 24335659130006 | Nobigonj, Goyahori, Ward # 4, H # 14/1, Aunup Kumar Rai | 2019-10-14 | NQ1007 | 10.3 | 320 | 10.3 | 321 | 2022-01-01 | [9 empty] | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0
HBG-4.RR.192.1 | 24335689129583 | Nobigonj, Goyahori, Ward # 4, Sribas Das | 2019-10-14 | NQ1007 | 12.8 | 322 | 12.9 | 323 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6264 | 2495.9997 | 135.9206
HBG-4.RR.193.1 | 24335689129583 | Nobigonj, Goyahori, Ward # 4, Suras Das | 2019-10-14 | NQ1007 | 9.5 | 324 | 8.9 | 325 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6264 | 2495.9997 | 93.7747
HBG-4.RR.194.1 | 24335709129571 | Nobigonj, Goyahori, Ward # 4, H # Pitu das | 2019-10-14 | NQ1007 | 14.8 | 326 | 14.3 | 327 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6264 | 2495.9997 | 150.6717
HBG-4.RR.195.1 | 24335249130022 | Nobigonj, Goyahori, Ward # 4, H # 62, Susan Das | 2019-10-14 | NQ1007 | 6.8 | 328 | 6.8 | 329 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6264 | 2495.9997 | 71.6481
HBG-4.RR.196.1 | 24335249130022 | Nobigonj, Goyahori, Ward # 4, H # 62, Susan Das | 2019-10-14 | NQ1007 | 12.2 | 330 | 12.2 | 331 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6264 | 2495.9997 | 128.5451
HBG-4.RR.201.1 | 24335429131278 | Nabiganj, Sibpasa R/A, Gurchad | 2019-10-09 | NQ1008 | 14.8 | 237 | 14.8 | 238 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6240 | 2519.9997 | 155.9399
HBG-4.RR.202.1 | 24335179131293 | Nabiganj, Sibpasa R/A, Somiron Chondrobonic | 2019-10-09 | NQ1008 | 11.1 | 239 | 11.1 | 240 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6240 | 2519.9997 | 116.9549
HBG-4.RR.203.1 | 24335179131293 | Nabiganj, Sibpasa R/A, Boni Poddas | 2019-10-09 | NQ1008 | 6.5 | 241 | 6.5 | 242 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6240 | 2519.9997 | 68.4871
HBG-4.RR.204.1 | 24335139131267 | Nabiganj, Sibpasa R/A, Md. Dudu Mia | 2019-10-09 | NQ1008 | 10.9 | 243 | 10.9 | 244 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6240 | 2519.9997 | 114.8476
HBG-4.RR.205.1 | 24334969131261 | Nabiganj, Sibpasa R/A, Miher Das | 2019-10-09 | NQ1008 | 10.4 | 245 | 10.4 | 246 | 2022-01-01 | [9 empty] | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0
HBG-4.RR.206.1 | 24335689130571 | Nobiganj, Hospital Road, Santipara, Robindro Chandro Pal | 2019-10-10 | NQ1008 | 6.9 | 275 | 6.9 | 276 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6264 | 2495.9997 | 72.7017
HBG-4.RR.207.1 | 24335319130572 | Nobiganj, Hospital Road, Santipara, Rones Vttacharge | 2019-10-10 | NQ1008 | 11 | 277 | 11 | 278 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6264 | 2495.9997 | 115.9013
HBG-4.RR.208.1 | 24335319130572 | Nobiganj, Hospital Road, Santipara, Rones Vttacharge | 2019-10-10 | NQ1008 | 14.7 | 279 | 13.7 | 280 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6264 | 2495.9997 | 144.3498
HBG-4.RR.209.1 | 24335319130572 | Nobiganj, Hospital Road, Santipara, Kripasindho Nath | 2019-10-10 | NQ1008 | 5.4 | 281 | 5.4 | 282 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6264 | 2495.9997 | 56.897
HBG-4.RR.210.1 | 24335319130572 | Nobiganj, Hospital Road, Santipara, Kripasindho Nath | 2019-10-10 | NQ1008 | 5.2 | 283 | 5.2 | 284 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6264 | 2495.9997 | 54.7897
HBG-4.RR.211.1 | 24335079130556 | Habiganj, Nobiganj, Habiganj Road, Shantipara, Foysal Soyeb | 2019-10-12 | NQ1008 | 13.2 | 285 | 13.2 | 286 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6264 | 2495.9997 | 139.0816
HBG-4.RR.212.1 | 24335209130564 | Habiganj, Nobiganj, Habiganj Road, Shantipara, Abdur Rahman Khan | 2019-10-12 | NQ1008 | 8.2 | 287 | 8.2 | 288 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6264 | 2495.9997 | 86.3991
HBG-4.RR.213.1 | 24335759130569 | Habiganj, Nobiganj, Habiganj Road, Shantipara, Abdul Awal Chy. | 2019-10-12 | NQ1008 | 14.1 | 289 | 14.3 | 290 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6264 | 2495.9997 | 150.6717
HBG-4.RR.214.1 | 24335709130454 | Habiganj, Nobiganj, Kajirgaon, Khalid Saifullah | 2019-10-12 | NQ1008 | 10.6 | 291 | 10.6 | 292 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6264 | 2495.9997 | 111.6867
HBG-4.RR.215.1 | 24335379130413 | Habiganj, Nobiganj, Kajirgaon, Abdul Karim Chy. | 2019-10-12 | NQ1008 | 3.2 | 293 | 3 | 294 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6264 | 2495.9997 | 31.6094
HBG-4.RR.216.1 | 24334429130294 | Habiganj, Nobiganj, Kajirgaon, Shah Nibas, Sabir Ahmed | 2019-10-12 | NQ1008 | 12.8 | 295 | 12.8 | 296 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6264 | 2495.9997 | 134.867
HBG-4.RR.217.1 | 24334089130294 | Habiganj, Nobiganj, Kajirgaon, Abdul Kadir | 2019-10-12 | NQ1008 | 5.7 | 297 | 5.7 | 298 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6264 | 2495.9997 | 60.0579
HBG-4.RR.217.2 | 24334089130294 | Habiganj, Nobiganj, Kajirgaon, Abdul Kadir | 2021-01-23 | LU1001 | 14.2 | 78 | 14.2 | 79 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6264 | 2495.9997 | 149.618
HBG-4.RR.218.1 | 24335109130460 | Habiganj, Nobiganj, Kajirgaon, Foyez Ahmed | 2019-10-12 | NQ1008 | 14.2 | 299 | 14.2 | 300 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6264 | 2495.9997 | 149.618
HBG-4.RR.219.1 | 24335359130304 | Nobiganj, Horipur, Ward # 05, Abdul Mannan | 2019-10-13 | NQ1008 | 16.6 | 355 | 16.6 | 356 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 6264 | 2495.9997 | 174.9056
HBG-4.RR.219.2 | 24335359130304 | Nobiganj, Horipur, Ward # 05, Abdul Mannan | 2021-08-21 | MN1018 | 6.2 | 1 | 6.2 | 2 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6264 | 2495.9997 | 65.3262
HBG-4.RR.220.1 | 24335359130304 | Nobiganj, Horipur, Ward # 05, Kobir Mia | 2019-10-13 | NQ1008 | 3.1 | 357 | 3.1 | 358 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6264 | 2495.9997 | 32.6631
HBG-4.RR.221.1 | 24335359130304 | Nobiganj, Horipur, Ward # 05, Abdul Malik | 2019-10-13 | NQ1008 | 8.7 | 359 | 8.7 | 360 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6264 | 2495.9997 | 91.6674
HBG-4.RR.222.1 | 24335359130304 | Nobiganj, Horipur, Ward # 05, Lilu Mia | 2019-10-13 | NQ1008 | 7 | 361 | 7 | 362 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6264 | 2495.9997 | 73.7554
HBG-4.RR.223.1 | 24335359130304 | Nobiganj, Horipur, Ward # 05, Lebu Mia | 2019-10-13 | NQ1008 | 11.8 | 363 | 11.7 | 364 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6264 | 2495.9997 | 123.2768
HBG-4.RR.224.1 | 24335859130292 | Nobiganj, Pirojpur, Ward # 05, Harun Mia | 2019-10-13 | NQ1008 | 18.7 | 365 | 19.3 | 366 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 6264 | 2495.9997 | 203.3541
HBG-4.RR.225.1 | 24340269130335 | Nobiganj, Pirojpur, Ward # 05, Aklis Mia | 2019-10-13 | NQ1008 | 11.8 | 367 | 11.8 | 368 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6264 | 2495.9997 | 124.3305
HBG-4.RR.226.1 | 24340019130462 | Nobiganj, Chorgau, Ward # 06, Sofuraj | 2019-10-13 | NQ1008 | 8.4 | 369 | 8.4 | 370 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6264 | 2495.9997 | 88.5064
HBG-4.RR.227.1 | 24340109130466 | Nobiganj, Sohid Sabas Ali Road, Ward # 02, Anower Hossen Mithu | 2019-10-13 | NQ1008 | 4 | 371 | 4 | 372 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6264 | 2495.9997 | 42.1459
HBG-4.RR.228.1 | 24335729131251 | Nobiganj, Sibpasa, Nohorpur Road, Malik Vobon | 2019-10-14 | NQ1008 | 14.9 | 375 | 14.9 | 376 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6240 | 2519.9997 | 156.9936
HBG-4.RR.229.1 | 24335249131244 | Nobiganj, Sibpasa, Nohorpur Road, Prodip | 2019-10-14 | NQ1008 | 12.5 | 377 | 12.5 | 378 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6240 | 2519.9997 | 131.706
HBG-4.RR.229.2 | 24335249131244 | Nobiganj, Sibpasa, Nohorpur Road, Prodip | 2019-10-14 | NQ1008 | 12.8 | 379 | 12.6 | 380 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6240 | 2519.9997 | 132.7597
HBG-4.RR.230.1 | 24335669131243 | Nobiganj, Sibpasa, Nohorpur Road, Ronju | 2019-10-14 | NQ1008 | 6.1 | 381 | 6.1 | 382 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6240 | 2519.9997 | 64.2725
HBG-4.RR.231.1 | 24335669131243 | Nobiganj, Sibpasa, Nohorpur Road, Aziz Mia | 2019-10-14 | NQ1008 | 5.8 | 383 | 5.8 | 384 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6240 | 2519.9997 | 61.1116
HBG-4.RR.232.1 | 24335349131204 | Nobiganj, Sibpasa, Nohorpur Road, Topondas | 2019-10-14 | NQ1008 | 5.6 | 385 | 5.6 | 386 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6240 | 2519.9997 | 59.0043
HBG-4.RR.233.1 | 24324739130523 | Nobiganj, West Timirpur, Ward # 09, Chitto Ronjon Das | 2019-10-14 | NQ1008 | 13.1 | 387 | 13.1 | 388 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6264 | 2495.9997 | 138.0279
HBG-4.RR.234.1 | 24324739130523 | Nobiganj, West Timirpur, Ward # 09, Onukul Roy | 2019-10-14 | NQ1008 | 6.6 | 389 | 6.6 | 390 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6264 | 2495.9997 | 69.5408
HBG-4.RR.251.1 | 24340469131413 | Nobiganj, Sherpur Road, Salamatpur, Abdul Mukit | 2019-10-09 | NQ1008 | 26.2 | 221 | 26.2 | 222 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 26.2 | 26.2 | 1.572 | 1.572 | 0.0007168 | 100% | 0% | 1.572 | 1.572 | 0.0011869 | 28 | 0.031513 | 0.031513 |  | 0 | 0 | 6240 | 2519.9997 | 276.0558
HBG-4.RR.251.2 | 24340469131413 | Nobiganj, Sherpur Road, Salamatpur, Abdul Mukit | 2021-01-23 | NQ1003 | 17.2 | 116 | 17.2 | 117 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 6240 | 2519.9997 | 181.2275
HBG-4.RR.252.1 | 24340439131367 | Nobiganj, Sherpur Road, Salamatpur, Samsun Nahar Cottage | 2019-10-09 | NQ1008 | 8.3 | 223 | 8.3 | 224 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6240 | 2519.9997 | 87.4528
HBG-4.RR.253.1 | 24340439131367 | Nobiganj, Sherpur Road, Salamatpur, Jamal Uddin | 2019-10-09 | NQ1008 | 9 | 225 | 9 | 226 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 5832 | 0 | 408 | 2519.9997 | 31.696
HBG-4.RR.254.1 | 24340419131353 | Nobiganj, Sherpur Road, Salamatpur, Md. Foyzul Haque | 2019-10-09 | NQ1008 | 17.5 | 227 | 17.5 | 228 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6240 | 2519.9997 | 184.3884
HBG-4.RR.255.1 | 24340359131344 | Nobiganj, Sherpur Road, Salamatpur, Harun Mia | 2019-10-09 | NQ1008 | 11.3 | 229 | 11.3 | 230 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6240 | 2519.9997 | 119.0622
HBG-4.RR.256.1 | 24340389131336 | Nobiganj, Sherpur Road, Salamatpur, Asha Apartment | 2019-10-09 | NQ1008 | 19.6 | 231 | 18.9 | 232 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6240 | 2519.9997 | 199.1395
HBG-4.RR.257.1 | 24340289131322 | Nobiganj, Sherpur Road, Salamatpur, Abdur Rob | 2019-10-09 | NQ1008 | 8.2 | 233 | 8.2 | 234 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6240 | 2519.9997 | 86.3991
HBG-4.RR.258.1 | 24335639131307 | Nobiganj, Sherpur Road, Nohorpur, Shibpasha Road, Forida Yasmin | 2019-10-09 | NQ1008 | 11.4 | 235 | 11.4 | 236 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6240 | 2519.9997 | 120.1159
HBG-4.RR.259.1 | 24340259131254 | Nobiganj, Sherpur Road, Saleha Khatun | 2019-10-10 | NQ1008 | 16.6 | 249 | 16.6 | 250 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 6240 | 2519.9997 | 174.9056
HBG-4.RR.260.1 | 24340259131254 | Nobiganj, Sherpur Road, Abdal Mia | 2019-10-10 | NQ1008 | 12.8 | 251 | 12.8 | 252 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6240 | 2519.9997 | 134.867
HBG-4.RR.261.1 | 24340259131254 | Nobiganj, Sherpur Road, Abdul Mohit Chowdhury | 2019-10-10 | NQ1008 | 11.1 | 253 | 11.2 | 254 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6240 | 2519.9997 | 118.0086
HBG-4.RR.262.1 | 24340209131244 | Nobiganj, Sherpur Road, Taj Villa, Kamal Mia | 2019-10-10 | NQ1008 | 10.3 | 255 | 10.3 | 256 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6240 | 2519.9997 | 108.5258
HBG-4.RR.263.1 | 24340209131244 | Nobiganj, Sherpur Road, Abdul Guljar | 2019-10-10 | NQ1008 | 13.3 | 259 | 13.3 | 260 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6240 | 2519.9997 | 140.1352
HBG-4.RR.264.1 | 24340119131168 | Nobiganj, Sherpur Road, Islami Bank Ltd., Abdul Hekim | 2019-10-10 | NQ1008 | 21.5 | 261 | 21.5 | 262 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 21.5 | 21.5 | 1.29 | 1.29 | 0.0007168 | 100% | 0% | 1.29 | 1.29 | 0.0011869 | 28 | 0.02586 | 0.02586 |  | 0 | 0 | 6240 | 2519.9997 | 226.5343
HBG-4.RR.265.1 | 24335699131038 | Nobiganj, Notun Bazar, Anmonu Road, Rita Mansion, Al-Helal | 2019-10-10 | NQ1008 | 11.7 | 263 | 11.7 | 264 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6264 | 2495.9997 | 123.2768
HBG-4.RR.266.1 | 24335539131035 | Nobiganj, Notun Bazar, Anmonu Road, Anowarul Haque | 2019-10-10 | NQ1008 | 12.6 | 265 | 12.6 | 266 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6264 | 2495.9997 | 132.7597
HBG-4.RR.267.1 | 24335539131035 | Nobiganj, Notun Bazar, Anmonu Road, Kadir Mia | 2019-10-10 | NQ1008 | 10.6 | 267 | 10.6 | 268 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6264 | 2495.9997 | 111.6867
HBG-4.RR.268.1 | 24335909131026 | Nobiganj, Notun Bazar, Sherpur Road, Chompok Kishor Kor | 2019-10-10 | NQ1008 | 11.1 | 271 | 11.1 | 272 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6264 | 2495.9997 | 116.9549
HBG-4.RR.269.1 | 24335919131018 | Nobiganj, Notun Bazar, Sherpur Road, Traffic point, Nikhil Acharjo | 2019-10-10 | NQ1008 | 18.8 | 273 | 18.8 | 274 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 6264 | 2495.9997 | 198.0858
HBG-4.RR.270.1 | 24334679130542 | Nobiganj, Shantipara, Hospital Road, Mamun Mia | 2019-10-12 | NQ1008 | 11.8 | 301 | 11.8 | 302 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6264 | 2495.9997 | 124.3305
HBG-4.RR.271.1 | 24334349130545 | Nobiganj, Hospital Road, Akkrompur R/A, Parvej Villa | 2019-10-12 | NQ1008 | 12.1 | 303 | 11.7 | 304 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6264 | 2495.9997 | 123.2768
HBG-4.RR.272.1 | 24333619130555 | Nobiganj, Hospital Road, Akkrompur R/A, Altab Ali | 2019-10-12 | NQ1008 | 7.5 | 305 | 7.5 | 306 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6264 | 2495.9997 | 79.0236
HBG-4.RR.273.1 | 24333619130555 | Nobiganj, Hospital Road, Akkrompur R/A, Zahid Commissioner | 2019-10-12 | NQ1008 | 12.6 | 307 | 12.6 | 308 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6264 | 2495.9997 | 132.7597
HBG-4.RR.274.1 | 24333599130505 | Nobiganj, Hospital Road, Sobujbagh R/A, Ronjit Pal | 2019-10-12 | NQ1008 | 14.5 | 309 | 14.5 | 310 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 6264 | 2495.9997 | 152.779
HBG-4.RR.275.1 | 24333249130541 | Nobiganj, Hospital Road, Akkrompur R/A, Nibaron Ray | 2019-10-12 | NQ1008 | 9.5 | 311 | 9.4 | 312 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6264 | 2495.9997 | 99.0429
HBG-4.RR.276.1 | 24333179130541 | Nobiganj, Hospital Road, Akkrompur R/A, Asma Chowdhury | 2019-10-12 | NQ1008 | 12.3 | 313 | 12.3 | 314 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6264 | 2495.9997 | 129.5987
HBG-4.RR.277.1 | 24334159130473 | Nobiganj, V.I.P Road, Chorgaon, Ahmed Thakur | 2019-10-12 | NQ1008 | 69.9 | 315 | 69.9 | 316 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 69.9 | 69.9 | 4.194 | 4.194 | 0.0007168 | 100% | 0% | 4.194 | 4.194 | 0.0011869 | 28 | 0.084075 | 0.084075 |  | 0 | 0 | 6264 | 2495.9997 | 736.5
HBG-4.RR.277.2 | 24334159130473 | Nobiganj, V.I.P Road, Chorgaon, Ahmed Thakur | 2019-10-12 | NQ1008 | 18.4 | 317 | 18.4 | 318 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6264 | 2495.9997 | 193.8713
HBG-4.RR.278.1 | 24334259130475 | Nobiganj, V.I.P Road, Chorgaon, Shamim Ahmed Chowdhury | 2019-10-12 | NQ1008 | 14.3 | 319 | 14.3 | 320 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6264 | 2495.9997 | 150.6717
HBG-4.RR.279.1 | 24334389130478 | Nobiganj, V.I.P Road, Chorgaon, Zahid Commissioner | 2019-10-12 | NQ1008 | 13 | 321 | 12.7 | 322 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6264 | 2495.9997 | 133.8133
HBG-4.RR.280.1 | 24333839130092 | Nobiganj, Kanaipur, Baniyachong Road, Shopon | 2019-10-13 | NQ1008 | 33.3 | 323 | 33.3 | 324 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 33.3 | 33.3 | 1.998 | 1.998 | 0.0007168 | 100% | 0% | 1.998 | 1.998 | 0.0011869 | 28 | 0.040053 | 0.040053 |  | 0 | 0 | 6264 | 2495.9997 | 350.8648
HBG-4.RR.281.1 | 24333969130103 | Nobiganj, Kanaipur, Baniyachong Road, Narayan Pal | 2019-10-13 | NQ1008 | 14.3 | 325 | 13.7 | 326 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6264 | 2495.9997 | 144.3498
HBG-4.RR.282.1 | 24334289130145 | Nobiganj, Kanaipur, Baniyachong Road, Dhirendro Gope | 2019-10-13 | NQ1008 | 8.5 | 327 | 8.5 | 328 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6264 | 2495.9997 | 89.5601
HBG-4.RR.283.1 | 24334169130178 | Nobiganj, KeliKanaipur, Baniyachong Road, Gopal Kuri | 2019-10-13 | NQ1008 | 10.4 | 329 | 10.6 | 330 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6264 | 2495.9997 | 111.6867
HBG-4.RR.284.1 | 24334169130178 | Nobiganj, KeliKanaipur, Baniyachong Road, Rakhesh Kuri | 2019-10-13 | NQ1008 | 12.1 | 331 | 12.1 | 332 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6264 | 2495.9997 | 127.4914
HBG-4.RR.285.1 | 24334219130185 | Nobiganj, KeliKanaipur, Baniyachong Road, Josheda Gope | 2019-10-13 | NQ1008 | 12.4 | 333 | 12.4 | 334 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6264 | 2495.9997 | 130.6524
HBG-4.RR.286.1 | 24334219130185 | Nobiganj, KeliKanaipur, Baniyachong Road, Roti Lal Gope | 2019-10-13 | NQ1008 | 5.7 | 335 | 5.7 | 336 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6264 | 2495.9997 | 60.0579
HBG-4.RR.287.1 | 24334219130185 | Nobiganj, KeliKanaipur, Baniyachong Road, Juboraj Gope | 2019-10-13 | NQ1008 | 5.9 | 337 | 5.9 | 338 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6264 | 2495.9997 | 62.1652
HBG-4.RR.288.1 | 24334219130185 | Nobiganj, KeliKanaipur, Baniyachong Road, Sochindro Gope | 2019-10-13 | NQ1008 | 7.1 | 339 | 7.1 | 340 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6264 | 2495.9997 | 74.809
HBG-4.RR.289.1 | 24334339130193 | Nobiganj, KeliKanaipur, Baniyachong Road, Haradhon Gong | 2019-10-13 | NQ1008 | 11.8 | 341 | 11.8 | 342 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6264 | 2495.9997 | 124.3305
HBG-4.RR.290.1 | 24334359130198 | Nobiganj, KeliKanaipur, Baniyachong Road, Bosonto Gope | 2019-10-13 | NQ1008 | 14 | 343 | 14 | 344 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6264 | 2495.9997 | 147.5107
HBG-4.RR.291.1 | 24334359130198 | Nobiganj, KeliKanaipur, Baniyachong Road, Mohonlal Gope | 2019-10-13 | NQ1008 | 13.2 | 345 | 13.2 | 346 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6264 | 2495.9997 | 139.0816
HBG-4.RR.292.1 | 24334529130210 | Nobiganj, KeliKanaipur, Baniyachong Road, Ronjit Gope | 2019-10-13 | NQ1008 | 11.9 | 347 | 11.9 | 348 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6264 | 2495.9997 | 125.3841
HBG-4.RR.293.1 | 24333979130162 | Nobiganj, KeliKanaipur, Baniyachong Road, Pobindro Gope | 2019-10-13 | NQ1008 | 13.7 | 349 | 14.4 | 350 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6264 | 2495.9997 | 151.7253
HBG-4.RR.294.1 | 24333979130162 | Nobiganj, KeliKanaipur, Baniyachong Road, Narayan Gope | 2019-10-13 | NQ1008 | 11.4 | 351 | 11.4 | 352 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6264 | 2495.9997 | 120.1159
HBG-4.RR.295.1 | 24334059130167 | Nobiganj, KeliKanaipur, Baniyachong Road, Bidhu Bhuson Gope | 2019-10-13 | NQ1008 | 15 | 353 | 15 | 354 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6264 | 2495.9997 | 158.0472
MBZ-1.CR.1.1 | 24281779145562 | Moulovi Bazar, Srimongol Road, Wapda Mor, Habib Hotel | 2019-07-10 | NQ1005 | 9.1 | 424 | 9.1 | 425 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6960 | 1799.9997 | 95.882
MBZ-1.CR.3.1 | 24292289145506 | Moulovibazar, West Bazar, M Saifur Rohman Sorok, Ahammed Hotel | 2019-07-16 | MP1032 | 10.9 | 727 | 10.9 | 728 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6912 | 1847.9997 | 114.8476
MBZ-1.RR.1.1 | 24291999146016 | Moulobibazar, Gulbag, Sunaullah Road, Julekha Khatun | 2019-01-21 | NQ1002 | 3.2 | 47 | 3.2 | 48 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6912 | 1847.9997 | 33.7167
MBZ-1.RR.2.1 | 24291899146039 | Moulobibazar, Gulbag, Sunaullah Road, Moin Mia | 2019-01-21 | NQ1002 | 9 | 49 | 9 | 50 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6912 | 1847.9997 | 94.8283
MBZ-1.RR.3.1 | 24291729146055 | Moulobibazar, Gulbag, Sunaullah Road, Berir Char, Abdur Rahim | 2019-01-21 | NQ1002 | 2.2 | 52 | 2.2 | 53 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6912 | 1847.9997 | 23.1803
MBZ-1.RR.4.1 | 24291619146018 | Moulobibazar, Gulbag, Berir Char, Delowar Mia | 2019-01-21 | NQ1002 | 2.1 | 54 | 2.1 | 55 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6912 | 1847.9997 | 22.1266
MBZ-1.RR.5.1 | 24292459146379 | Moulobibazar, Chowmohoni, Somsernagar, West Girzapara, Alhaz Moina Mia | 2019-01-21 | NQ1002 | 10.6 | 56 | 10.6 | 57 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6840 | 1919.9997 | 111.6867
MBZ-1.RR.6.1 | 24292379146379 | Moulobibazar, Chowmohoni, Somsernagar, West Girzapara, Hazi Intaz Mia | 2019-01-21 | NQ1002 | 11.4 | 58 | 11.4 | 59 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6840 | 1919.9997 | 120.1159
MBZ-1.RR.7.1 | 24291079146379 | Moulobibazar, Chowmohoni, East Girzapara, Court Road, Morshedur Rahman | 2019-01-21 | NQ1002 | 8.7 | 60 | 8.7 | 61 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 1584 | 0 | 5304 | 1871.9997 | 75.0919
MBZ-1.RR.8.1 | 24283809146481 | Moulovibazar, Sonapur Area, Sonapur Road, Milad Mia | 2019-07-07 | MP1032 | 3 | 477 | 3 | 478 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6720 | 2039.9997 | 31.6094
MBZ-1.RR.9.1 | 24283779146479 | Moulovibazar, Sonapur Area, Sonapur Road, Eklasur Rohman | 2019-07-07 | MP1032 | 10.4 | 479 | 10.4 | 480 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6720 | 2039.9997 | 109.5794
MBZ-1.RR.10.1 | 24283709146499 | Moulovibazar, Sonapur Area, Sonapur Road, Abu Reza Siddique | 2019-07-07 | MP1032 | 2.4 | 484 | 2.4 | 485 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6720 | 2039.9997 | 25.2876
MBZ-1.RR.10.2 | 24283709146499 | Moulovibazar, Sonapur Area, Sonapur Road, Abu Reza Siddique | 2021-01-25 | LU1001 | 2.8 | 90 | 2.8 | 91 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6720 | 2039.9997 | 29.5021
MBZ-1.RR.11.1 | 24283739146513 | Moulovibazar, Sonapur Area, Borobari, Sonapur Road, Tajmul Hosen Chowdhury | 2019-07-07 | MP1032 | 18.3 | 486 | 18.3 | 487 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 18.3 | 18.3 | 1.098 | 1.098 | 0.0007168 | 100% | 0% | 1.098 | 1.098 | 0.0011869 | 28 | 0.022011 | 0.022011 |  | 0 | 0 | 6720 | 2039.9997 | 192.8176
MBZ-1.RR.12.1 | 24283739146513 | Moulovibazar, Sonapur Area, Borobari, Sonapur Road, Bodrul Islam | 2019-07-07 | MP1032 | 8.5 | 488 | 7.9 | 489 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6720 | 2039.9997 | 83.2382
MBZ-1.RR.12.2 | 24283739146513 | Moulovibazar, Sonapur Area, Borobari, Sonapur Road, Bodrul Islam | 2021-01-25 | LU1001 | 5.3 | 92 | 5.3 | 93 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6720 | 2039.9997 | 55.8434
MBZ-1.RR.13.1 | 24283689146480 | Moulovibazar, Sonapur, Sonapur Road, Abdul Motin | 2019-07-08 | MP1032 | 9.6 | 490 | 9.2 | 491 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6720 | 2039.9997 | 96.9356
MBZ-1.RR.14.1 | 24283589146490 | Moulovibazar, Sonapur, Borobari, Arsadabad Sorok, Humayun Kobir Joglu | 2019-07-08 | MP1032 | 4.9 | 492 | 4.9 | 493 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 6 | 6720 | 2033.9997 | 51.5934
MBZ-1.RR.15.1 | 24283559146513 | Moulovibazar, Sonapur, Borobari, Arsadabad Sorok, Alal Mia | 2019-07-08 | MP1032 | 4.9 | 494 | 4.9 | 495 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6720 | 2039.9997 | 51.6288
MBZ-1.RR.16.1 | 24283739146575 | Moulovibazar, Sonapur, Borobari, Arsadabad Sorok, Foizur Rahman | 2019-07-08 | MP1032 | 3.8 | 496 | 3.8 | 497 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6720 | 2039.9997 | 40.0386
MBZ-1.RR.17.1 | 24283679146591 | Moulovibazar, Sonapur, Borobari, Arsadabad Sorok, Moinul Haque | 2019-07-08 | MP1032 | 1.5 | 498 | 1.5 | 499 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6720 | 2039.9997 | 15.8047
MBZ-1.RR.18.1 | 24283369146473 | Moulovibazar, Sonapur, Sonapur Road, Kazi Mohammad Shamim | 2019-07-10 | MP1032 | 1.6 | 547 | 1.6 | 548 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6720 | 2039.9997 | 16.8584
MBZ-1.RR.19.1 | 24283329146470 | Moulovibazar, Sonapur, Sonapur Road, Soiod Selim Ahmed | 2019-07-10 | MP1032 | 3.8 | 549 | 3.8 | 550 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6720 | 2039.9997 | 40.0386
MBZ-1.RR.19.2 | 24283329146470 | Moulovibazar, Sonapur, Sonapur Road, Soiod Selim Ahmed | 2021-01-25 | LU1001 | 6.9 | 88 | 6.9 | 89 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6720 | 2039.9997 | 72.7017
MBZ-1.RR.20.1 | 24283289146497 | Moulovibazar, Sonapur, Kamal Uddin Sorok, Hanif Villa | 2019-07-10 | MP1032 | 4.1 | 551 | 4.1 | 552 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6720 | 2039.9997 | 43.1996
MBZ-1.RR.21.1 | 24291879145551 | Moulvibazar, Poshchimbazar, Babychor Road, Jalil Mia | 2019-01-21 | NQ1009 | 6.2 | 1 | 6.7 | 2 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6912 | 1847.9997 | 70.5944
MBZ-1.RR.21.2 | 24291879145551 | Moulvibazar, Poshchimbazar, Babychor Road, Jalil Mia | 2021-02-08 | NQ1007 | 4 | 162 | 4 | 163 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6912 | 1847.9997 | 42.1459
MBZ-1.RR.22.1 | 24291789145536 | Moulvibazar, Poshchimbazar, Babychor Road, Md. Shamim Mia | 2019-01-21 | NQ1009 | 3.3 | 3 | 3.3 | 4 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6912 | 1847.9997 | 34.7704
MBZ-1.RR.23.1 | 24291799145556 | Moulvibazar, Poshchimbazar, Babychor Road, H # 683, Aftab Mia | 2019-01-21 | NQ1009 | 2.7 | 5 | 2.7 | 6 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6912 | 1847.9997 | 28.4485
MBZ-1.RR.24.1 | 24293109146319 | Moulvibazar, Kashinathpur ,Hazi Eshak Monjil | 2019-01-21 | NQ1009 | 10.1 | 7 | 10.1 | 8 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6792 | 1967.9997 | 106.4185
MBZ-1.RR.25.1 | 24293159146334 | Moulvibazar, Kashinathpur Road ,Abdur Rouf, Inforont of Hazi Eshak Monjil | 2019-01-21 | NQ1009 | 1.9 | 9 | 1.9 | 10 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6792 | 1967.9997 | 20.0193
MBZ-1.RR.26.1 | 24293199146317 | Moulvibazar,Shabag, Kashinath Road ,Shanti Nibas, Beside Shohid Kadet Acadamy | 2019-01-21 | NQ1009 | 1.1 | 11 | 1.1 | 12 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6792 | 1967.9997 | 11.5901
MBZ-1.RR.27.1 | 24293369146359 | Moulvibazar,Shabag, Kashinathpur Road ,Hafiza Monjil | 2019-01-21 | NQ1009 | 3.1 | 13 | 3.1 | 14 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6792 | 1967.9997 | 32.6631
MBZ-1.RR.28.1 | 24291009146389 | Moulvibazar, Girjapara, Ronodhir Dash | 2019-01-21 | NQ1009 | 6 | 15 | 6 | 16 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6888 | 1871.9997 | 63.2189
MBZ-1.RR.29.1 | 24261599145580 | Moulvibazar, Niteshwar, Hazrat Shaha Gaji Road, Ma Manjil, Aftab Mia | 2019-07-06 | MP1032 | 3.7 | 425 | 3.7 | 426 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7056 | 1703.9997 | 38.985
MBZ-1.RR.30.1 | 24264009145399 | Moulvibazar, Gomra, Jubo Prasikhon Kendro, Prosasonik Come Akademik Vobon | 2019-07-06 | MP1032 | 3.3 | 427 | 3.3 | 428 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7056 | 1703.9997 | 34.7704
MBZ-1.RR.31.1 | 24281259146241 | Moulvibazar, North Jogonnathpur, Word - 5, Mostofa | 2019-07-07 | MP1032 | 10.9 | 429 | 10.8 | 430 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7056 | 1703.9997 | 113.794
MBZ-1.RR.32.1 | 24281259146241 | Moulvibazar, North Jogonnathpur, Word - 5, Mostofa | 2019-07-07 | MP1032 | 7 | 431 | 7 | 432 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7056 | 1703.9997 | 73.7554
MBZ-1.RR.32.2 | 24281259146241 | Moulvibazar, North Jogonnathpur, Word - 5, Mostofa | 2019-07-07 | MP1032 | 1.8 | 433 | 1.8 | 434 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7056 | 1703.9997 | 18.9657
MBZ-1.RR.33.1 | 24281329146235 | Moulvibazar, North Jogonnathpur, Word - 5, Khoyessor Ahammod | 2019-07-07 | MP1032 | 10.1 | 435 | 10.1 | 436 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7056 | 1703.9997 | 106.4185
MBZ-1.RR.34.1 | 24281289146239 | Moulvibazar, North Jogonnathpur, Word - 5, Abdul Munnaf | 2019-07-07 | MP1032 | 12.9 | 437 | 12.9 | 438 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7056 | 1703.9997 | 135.9206
MBZ-1.RR.34.2 | 24281289146239 | Moulvibazar, North Jogonnathpur, Word - 5, Abdul Munnaf | 2021-01-24 | NQ1007 | 4.1 | 74 | 4.1 | 75 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7056 | 1703.9997 | 43.1996
MBZ-1.RR.35.1 | 24281119146226 | Moulvibazar, North Jogonnathpur, Word - 5, Surfan | 2019-07-07 | MP1032 | 5.1 | 439 | 5.1 | 440 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7056 | 1703.9997 | 53.7361
MBZ-1.RR.36.1 | 24281169146188 | Moulvibazar, North Jogonnathpur, Word - 5, Foysal Ahammed Helali | 2019-07-07 | MP1032 | 11.4 | 441 | 11.4 | 442 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7176 | 1583.9997 | 120.1159
MBZ-1.RR.36.2 | 24281169146188 | Moulvibazar, North Jogonnathpur, Word - 5, Foysal Ahammed Helali | 2022-10-27 | MN1018 | 7.3 | 100 | 7.3 | 101 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 0 | 1583.9997 | 13.9082
MBZ-1.RR.37.1 | 24281319146186 | Moulvibazar, North Jogonnathpur, Word - 5, H #n 9, Rezaul Karim | 2019-07-07 | MP1032 | 5.8 | 443 | 5.8 | 444 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7056 | 1703.9997 | 61.1116
MBZ-1.RR.38.1 | 24281439146192 | Moulvibazar, North Jogonnathpur, Word - 5, Nobigong House, Rezuan Uddin | 2019-07-07 | MP1032 | 3 | 447 | 3 | 448 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7056 | 1703.9997 | 31.6094
MBZ-1.RR.39.1 | 24281439146192 | Moulvibazar, North Jogonnathpur, Word - 5, Nobigong House, Rezuan Uddin | 2019-07-07 | MP1032 | 10.4 | 449 | 10.4 | 450 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7056 | 1703.9997 | 109.5794
MBZ-1.RR.40.1 | 24281489146186 | Moulvibazar, North Jogonnathpur, Word - 5, Opada Alaka, Laila Kotez | 2019-07-07 | MP1032 | 10.1 | 451 | 10.1 | 452 | 2022-01-01 | [9 empty] | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0
MBZ-1.RR.41.1 | 24291689146112 | Moulvibazar, Lake Road, Muslim quarter, Word # 4, H # 652, Najir Uddin Chowdhory | 2019-01-21 | NQ1000 | 1.1 | 123 | 1 | 124 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 6912 | 1847.9997 | 10.5365
MBZ-1.RR.42.1 | 24291749146113 | Moulvibazar, Lake Road, Muslim quarter, Word # 4, H # 474, Raisa Rahman ( Maslu Ahmed) | 2019-01-21 | NQ1000 | 1.6 | 125 | 1.6 | 126 | 2022-01-01 | [9 empty] | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0
MBZ-1.RR.43.1 | 24291959146168 | Moulvibazar, Lake Road, Muslim quarter, Word # 4, H # 498, Montor Ahmed | 2019-01-21 | NQ1000 | 11.5 | 129 | 11.1 | 130 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6840 | 1919.9997 | 116.9549
MBZ-1.RR.43.2 | 24291959146168 | Moulvibazar, Lake Road, Muslim quarter, Word # 4, H # 498, Montor Ahmed | 2019-01-21 | NQ1000 | 2.1 | 131 | 2.1 | 132 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6840 | 1919.9997 | 22.1266
MBZ-1.RR.44.1 | 24291959146168 | Moulvibazar, Lake Road, Muslim quarter, Word # 4, old H # 118, Kashem monjil | 2019-01-21 | NQ1000 | 19.3 | 133 | 19.3 | 134 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 6840 | 1919.9997 | 203.3541
MBZ-1.RR.44.2 | 24291959146168 | Moulvibazar, Lake Road, Muslim quarter, Word # 4, old H # 118, Kashem monjil | 2020-10-06 | NQ1002 | 5.3 | 85 | 5.3 | 86 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6840 | 1919.9997 | 55.8434
MBZ-1.RR.45.1 | 24291249146216 | Moulvibazar, K.B.Alaudin Road, Muslim quarter, Moinul hossain Chowdhary | 2019-01-21 | NQ1000 | 4.6 | 135 | 4.6 | 136 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6888 | 1871.9997 | 48.4678
MBZ-1.RR.46.1 | 24291559146295 | Moulvibazar, Ramkrisno mission Road, Poresh chandra dev | 2019-01-21 | NQ1000 | 3.1 | 141 | 3.2 | 142 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6888 | 1871.9997 | 33.7167
MBZ-1.RR.47.1 | 24291559146295 | Moulvibazar, Ramkrisno mission Road, Chowdhary Vabon | 2019-01-21 | NQ1000 | 1.7 | 143 | 1.7 | 144 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6888 | 1871.9997 | 17.912
MBZ-1.RR.48.1 | 24283099146074 | Moulvibazar Pourashava, Rogunondonpur, Khobirullah | 2019-07-07 | LX1011 | 11.5 | 779 | 11.5 | 780 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7056 | 1703.9997 | 121.1695
MBZ-1.RR.49.1 | 24282979146145 | Moulvibazar Pourashava, Rogunondonpur, Nearest Meher Jan Bibi Rahmania Dakhil Madrasha, Md. Jamal | 2019-07-07 | LX1011 | 6.1 | 781 | 6.1 | 782 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7056 | 1703.9997 | 64.2725
MBZ-1.RR.50.1 | 24282939146156 | Moulvibazar Pourashava, Rogunondonpur, Nearest Meher Jan Bibi Rahmania Dakhil Madrasha, kashem | 2019-07-07 | LX1011 | 3.3 | 783 | 3.3 | 784 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7056 | 1703.9997 | 34.7704
MBZ-1.RR.51.1 | 24283129146141 | Moulvibazar Pourashava, Rogunondonpur, Md. Sultan | 2019-07-07 | LX1011 | 12.1 | 787 | 12.1 | 788 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7056 | 1703.9997 | 127.4914
MBZ-1.RR.52.1 | 24283259146099 | Moulvibazar Pourashava, Rogunondonpur, Md. Masud Khan | 2019-07-07 | LX1011 | 12.9 | 789 | 12.9 | 790 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7056 | 1703.9997 | 135.9206
MBZ-1.RR.53.1 | 24283289146088 | Moulvibazar Pourashava, Rogunondonpur, Mutassir Ali | 2019-07-07 | LX1011 | 6.7 | 791 | 6.7 | 792 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7056 | 1703.9997 | 70.5944
MBZ-1.RR.54.1 | 24283359146075 | Moulvibazar Pourashava, Rogunondonpur, Abdur Sohid | 2019-07-07 | LX1011 | 11.3 | 793 | 11.3 | 794 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7056 | 1703.9997 | 119.0622
MBZ-1.RR.55.1 | 24283309146235 | Moulvibazar Pourashava, Wapda Road, Stadium Gate, Md. Abdul Haque | 2019-07-07 | LX1011 | 9.7 | 795 | 9.7 | 796 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7056 | 1703.9997 | 102.2039
MBZ-1.RR.56.1 | 24283629146376 | Moulvibazar Pourashava, Court Road, Sorok Circle Bas Bhabon | 2019-07-07 | LX1011 | 21.1 | 797 | 21.3 | 798 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 6720 | 2039.9997 | 224.4271
MBZ-1.RR.57.1 | 24283849146395 | Moulvibazar Pourashava, Court Road, Sorok Circle Bas Bhabon | 2019-07-07 | LX1011 | 4.8 | 799 | 4.8 | 800 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6720 | 2039.9997 | 50.5751
MBZ-1.RR.58.1 | 24282549146246 | Rogunondonpur, Liakot Ali Road, Stadium Gate, Md. Joglul Rahman | 2019-07-08 | LX1011 | 1.7 | 801 | 1.7 | 802 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7056 | 1703.9997 | 17.912
MBZ-1.RR.59.1 | 24282639146213 | Rogunondonpur, Liakot Ali Road, Stadium Gate, Md. Liakot Ali | 2019-07-08 | LX1011 | 3.5 | 803 | 3.5 | 804 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7056 | 1703.9997 | 36.8777
MBZ-1.RR.60.1 | 24282639146213 | Rogunondonpur, Liakot Ali Road, Stadium Gate, Md. Liakot Ali | 2019-07-08 | LX1011 | 1 | 807 | 1 | 808 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7056 | 1703.9997 | 10.5365
MBZ-1.RR.60.2 | 24282639146213 | Rogunondonpur, Liakot Ali Road, Stadium Gate, Md. Liakot Ali | 2022-03-22 | NQ1007 | 11.5 | 58 | 11.5 | 59 | 2022-03-22 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 5136 | 1703.9997 | 94.6118
MBZ-1.RR.61.1 | 24291769146112 | Moulvibazar, Lake Road, Opposite of Jakaria Monjil, Oly Ahmed | 2019-01-21 | NQ1005 | 9.8 | 17 | 9.9 | 18 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6912 | 1847.9997 | 104.3112
MBZ-1.RR.62.1 | 24291919146112 | Moulvibazar, Lake Road, Abdul Mukit Khan | 2019-01-21 | NQ1005 | 9.9 | 19 | 9.9 | 20 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6912 | 1847.9997 | 104.3112
MBZ-1.RR.63.1 | 24291879146118 | Moulvibazar, Lake Road, Word # 4, Mustak Hayder Khan, H # 661 | 2019-01-21 | NQ1005 | 3.1 | 21 | 3.1 | 22 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6912 | 1847.9997 | 32.6631
MBZ-1.RR.64.1 | 24292149146124 | Moulvibazar, Syed Mujtoba Ali Road, Hazi Ishaq Villa, H # 114 | 2019-01-21 | NQ1005 | 1.9 | 23 | 1.9 | 24 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6912 | 1847.9997 | 20.0193
MBZ-1.RR.65.1 | 24292089146169 | Moulvibazar, Muslim Quarter Road, Akil Mia, H # 490 | 2019-01-21 | NQ1005 | 10.8 | 25 | 10.5 | 26 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6840 | 1919.9997 | 110.6331
MBZ-1.RR.66.1 | 24292139146189 | Moulvibazar, Muslim Quarter Road, Opposite Of Ma And Sishu Kallyan Kendro, Dr. Muktadir Hossain, H # 8 | 2019-01-21 | NQ1005 | 11.4 | 27 | 11.4 | 28 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6840 | 1919.9997 | 120.1159
MBZ-1.RR.67.1 | 24292319146200 | Moulvibazar, Moddhopara Road. Anwar Mia, H # 387 | 2019-01-21 | NQ1005 | 5.2 | 29 | 5.2 | 30 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6840 | 1919.9997 | 54.7897
MBZ-1.RR.68.1 | 24292309146191 | Moulvibazar, Moddhopara Road. Milkar House, Ataur Rahman | 2019-01-21 | NQ1005 | 10.1 | 31 | 10.1 | 32 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6840 | 1919.9997 | 106.4185
MBZ-1.RR.69.1 | 24292499146176 | Moulvibazar, Moddhopara Road. Dipok Kumar Das, H # 282 | 2019-01-21 | NQ1005 | 1.6 | 33 | 1.6 | 34 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6840 | 1919.9997 | 16.8584
MBZ-1.RR.69.2 | 24292499146176 | Moulvibazar, Moddhopara Road. Dipok Kumar Das, H # 282 | 2021-02-08 | NQ1003 | 10 | 199 | 10 | 200 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6840 | 1919.9997 | 105.3648
MBZ-1.RR.70.1 | 24292499146180 | Moulvibazar, Moddhopara Road. Abdus Salam, H # 284 | 2019-01-21 | NQ1005 | 8.4 | 35 | 8.1 | 36 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6840 | 1919.9997 | 85.3455
MBZ-1.RR.71.1 | 24270789145493 | Moulavi Bazar, Jogonnathpur, Mohaldar Bari, Delowar Hosen | 2019-07-07 | LX1011 | 13.4 | 752 | 13.1 | 753 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7056 | 1703.9997 | 138.0279
MBZ-1.RR.71.2 | 24270789145493 | Moulavi Bazar, Jogonnathpur, Mohaldar Bari, Delowar Hosen | 2021-01-24 | NQ1003 | 8 | 134 | 8 | 135 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7056 | 1703.9997 | 84.2919
MBZ-1.RR.72.1 | 24274889146001 | Moulavi Bazar, Jogonnathpur, Goal Bari Road, Tajul Islam | 2019-07-07 | LX1011 | 10.3 | 754 | 9.6 | 755 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7056 | 1703.9997 | 101.1502
MBZ-1.RR.73.1 | 24274819145588 | Moulavi Bazar, Jogonnathpur, Goal Bari Road, Babul Mia | 2019-07-07 | LX1011 | 6.4 | 756 | 6.4 | 757 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7056 | 1703.9997 | 67.4335
MBZ-1.RR.74.1 | 24280179146000 | Moulavi Bazar, Jogonnathpur, Ward # 6, Faruk | 2019-07-07 | LX1011 | 11.2 | 758 | 11.2 | 759 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7056 | 1703.9997 | 118.0086
MBZ-1.RR.75.1 | 24280179146000 | Moulavi Bazar, Jogonnathpur, Ward # 6, Akiz Mia | 2019-07-07 | LX1011 | 10.8 | 760 | 10.8 | 761 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7056 | 1703.9997 | 113.794
MBZ-1.RR.76.1 | 24280059145595 | Moulavi Bazar, Jogonnathpur, Ward # 6, Mojibur Rahman | 2019-07-07 | LX1011 | 8 | 762 | 8 | 763 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7176 | 1583.9997 | 84.2919
MBZ-1.RR.76.2 | 24280059145595 | Moulavi Bazar, Jogonnathpur, Ward # 6, Mojibur Rahman | 2022-10-27 | MN1018 | 3.2 | 98 | 3.2 | 99 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 0 | 1583.9997 | 6.0967
MBZ-1.RR.77.1 | 24280059145595 | Moulavi Bazar, Jogonnathpur, Ward # 6, Abdul Kayom | 2019-07-07 | LX1011 | 14.5 | 764 | 14.6 | 765 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7056 | 1703.9997 | 153.8326
MBZ-1.RR.78.1 | 24275979145594 | Moulavi Bazar, Jogonnathpur, Ward # 6, Liakot Mia | 2019-07-07 | LX1011 | 9.1 | 771 | 9.1 | 772 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7056 | 1703.9997 | 95.882
MBZ-1.RR.79.1 | 24282379146115 | Moulavi Bazar, Rogunnondonpur, Wapda Gate, Nowgao School Rd, Md. Dula Miah | 2019-07-07 | LX1011 | 12.4 | 773 | 12.1 | 774 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7056 | 1703.9997 | 127.4914
MBZ-1.RR.80.1 | 24282439146116 | Moulavi Bazar, Rogunnondonpur, Wapda Gate, Nowgao School Rd, Islam Vila | 2019-07-07 | LX1011 | 6.8 | 775 | 6.3 | 776 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7056 | 1703.9997 | 66.3798
MBZ-1.RR.81.1 | 24282689146069 | Moulavi Bazar, Rogunnondonpur, Wapda Road, Ruhul Amin | 2019-07-07 | LX1011 | 9.4 | 777 | 9.4 | 778 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7056 | 1703.9997 | 99.0429
MBZ-1.RR.82.1 | 24285089146327 | Moulavi Bazar, North Kolimabad, S.R Villa, Zillu Miah. Sunu | 2019-07-08 | LX1011 | 10.8 | 822 | 10.8 | 823 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6720 | 2039.9997 | 113.794
MBZ-1.RR.83.1 | 24285129146322 | Moulavi Bazar, North Kolimabad, Late; Mohiuddin Ahamed | 2019-07-08 | LX1011 | 11 | 824 | 11 | 825 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6720 | 2039.9997 | 115.9013
MBZ-1.RR.84.1 | 24285329146311 | Moulavi Bazar, North Kolimabad, Chomru, H # 119 | 2019-07-08 | LX1011 | 10.6 | 826 | 10.6 | 827 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6720 | 2039.9997 | 111.6867
MBZ-1.RR.85.1 | 24285699146309 | Moulavi Bazar, North Kolimabad, H # 81 | 2019-07-08 | LX1011 | 11.8 | 828 | 11.8 | 829 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6888 | 1871.9997 | 124.3305
MBZ-1.RR.86.1 | 24285759146270 | Moulavi Bazar, North Kolimabad, Didar Mia | 2019-07-08 | LX1011 | 9.5 | 830 | 8.8 | 831 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6888 | 1871.9997 | 92.721
MBZ-1.RR.87.1 | 24285759146270 | Moulavi Bazar, North Kolimabad, Ahamed Villa H # 165 | 2019-07-08 | LX1011 | 3.3 | 832 | 3.3 | 833 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6888 | 1871.9997 | 34.7704
MBZ-1.RR.88.1 | 24285989146336 | Moulavi Bazar, North Kolimabad, Arambag Road, Bokshi Sulaiman | 2019-07-08 | LX1011 | 13.5 | 834 | 13.5 | 835 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6888 | 1871.9997 | 142.2425
MBZ-1.RR.89.1 | 24285969146272 | Moulavi Bazar, North Kolimabad, Soya Mia | 2019-07-08 | LX1011 | 13.4 | 836 | 13.4 | 837 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 6 | 0 | 6882 | 1871.9997 | 141.0921
MBZ-1.RR.89.2 | 24285969146272 | Moulavi Bazar, North Kolimabad, Soya Mia | 2019-07-08 | LX1011 | 5.6 | 838 | 5.3 | 839 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 4 | 0 | 6884 | 1871.9997 | 55.8179
MBZ-1.RR.90.1 | 24285959146312 | Moulavi Bazar, North Kalimabad, Fahim Store, H # 65 | 2019-07-09 | LX1011 | 10.1 | 840 | 10.1 | 841 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6888 | 1871.9997 | 106.4185
MBZ-1.RR.91.1 | 24290139146294 | Moulavi Bazar, North Kalimabad, Eleas | 2019-07-09 | LX1011 | 12.9 | 842 | 12.5 | 843 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6888 | 1871.9997 | 131.706
MBZ-1.RR.92.1 | 24285879146204 | Moulavi Bazar, Kazirgaon, Kazir Gaon Masjid Road, Khoirul Islam | 2019-07-09 | LX1011 | 11.3 | 844 | 11.3 | 845 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6888 | 1871.9997 | 119.0622
MBZ-1.RR.93.1 | 24285879146204 | Moulavi Bazar, Kazirgaon, Kazir Gaon Masjid Road, Khoirul Islam | 2019-07-09 | LX1011 | 4.5 | 846 | 4.5 | 847 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6888 | 1871.9997 | 47.4142
MBZ-1.RR.94.1 | 24285919146208 | Moulavi Bazar, Kazirgaon, Kazir Gaon Masjid Road, Beside of H # 618 | 2019-07-09 | LX1011 | 7.5 | 850 | 6.9 | 851 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6888 | 1871.9997 | 72.7017
MBZ-1.RR.95.1 | 24285919146208 | Moulavi Bazar, Kazirgaon, Kazir Gaon Masjid Road, Beside of H # 618 | 2019-07-09 | LX1011 | 11.7 | 852 | 11.7 | 853 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6888 | 1871.9997 | 123.2768
MBZ-1.RR.96.1 | 24285799146225 | Moulavi Bazar, Kazirgaon, Kazir Gaon Masjid Road, Ajmol Mia | 2019-07-09 | LX1011 | 10.9 | 854 | 10.9 | 855 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6888 | 1871.9997 | 114.8476
MBZ-1.RR.97.1 | 24290269146241 | Moulavi Bazar, Purbo Sultanpur, Purbo Sultanpur Road, Hannan Vila | 2019-07-09 | LX1011 | 12.3 | 856 | 11.9 | 857 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6888 | 1871.9997 | 125.3841
MBZ-1.RR.98.1 | 24290269146241 | Moulavi Bazar, Purbo Sultanpur, Purbo Sultanpur Road, Zillur Hazi | 2019-07-09 | LX1011 | 6.4 | 858 | 5.9 | 859 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6888 | 1871.9997 | 62.1652
MBZ-1.RR.99.1 | 24290089146189 | Moulavi Bazar, West Kazirgaon, Kazirgaon Road, H # 583/2 | 2019-07-10 | LX1011 | 11.6 | 895 | 11.6 | 896 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6888 | 1871.9997 | 122.2232
MBZ-1.RR.100.1 | 24290049146152 | Moulavi Bazar, West Kazirgaon, Kazirgaon Road, Alom Villa | 2019-07-10 | LX1011 | 10.4 | 897 | 10.4 | 898 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6888 | 1871.9997 | 109.5794
MBZ-1.RR.101.1 | 24283179146512 | Moulovibazar, Sonapur, Kamal Uddin Sorok, Sabaz Ahmed | 2019-07-10 | MP1032 | 5.5 | 553 | 5.5 | 554 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6720 | 2039.9997 | 57.9506
MBZ-1.RR.101.2 | 24283179146512 | Moulovibazar, Sonapur, Kamal Uddin Sorok, Sabaz Ahmed | 2019-07-10 | MP1032 | 4.3 | 555 | 4.3 | 556 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6720 | 2039.9997 | 45.3069
MBZ-1.RR.102.1 | 24283419146522 | Moulovibazar, Sonapur, Kamal Uddin Sorok, Moniruzzaman | 2019-07-10 | MP1032 | 6.7 | 559 | 6.7 | 560 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6720 | 2039.9997 | 70.5944
MBZ-1.RR.102.2 | 24283419146522 | Moulovibazar, Sonapur, Kamal Uddin Sorok, Moniruzzaman | 2019-07-10 | MP1032 | 5.3 | 561 | 5.3 | 562 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6720 | 2039.9997 | 55.8434
MBZ-1.RR.103.1 | 24283389146546 | Moulovibazar, Sonapur, Kamal Uddin Sorok, Fazlur Rahman | 2019-07-10 | MP1032 | 9.4 | 563 | 8.9 | 564 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6720 | 2039.9997 | 93.7747
MBZ-1.RR.103.2 | 24283389146546 | Moulovibazar, Sonapur, Kamal Uddin Sorok, Fazlur Rahman | 2019-07-10 | MP1032 | 11.4 | 565 | 11.4 | 566 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6720 | 2039.9997 | 120.1159
MBZ-1.RR.104.1 | 24283099146505 | Moulovibazar, Sonapur, Borobari, Eco Park Road, Dipu Monjil | 2019-07-10 | MP1032 | 4.3 | 567 | 4.3 | 568 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6720 | 2039.9997 | 45.3069
MBZ-1.RR.104.2 | 24283099146505 | Moulovibazar, Sonapur, Borobari, Eco Park Road, Dipu Monjil | 2019-07-10 | MP1032 | 6.8 | 569 | 6.8 | 570 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6720 | 2039.9997 | 71.6481
MBZ-1.RR.105.1 | 24283099146505 | Moulovibazar, Sonapur, Borobari, Eco Park Road, Opposite Dipu Monjil | 2019-07-10 | MP1032 | 6.9 | 571 | 6.9 | 572 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6720 | 2039.9997 | 72.7017
MBZ-1.RR.106.1 | 24282129146143 | Moulovibazar, Roghunathpur, Wapda Road, Beside Abdur Razzak | 2019-07-10 | MP1032 | 4.2 | 575 | 4.2 | 576 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7056 | 1703.9997 | 44.2532
MBZ-1.RR.107.1 | 24282139146139 | Moulovibazar, Roghunathpur, Wapda Road, Abdur Razzak | 2019-07-10 | MP1032 | 5.8 | 577 | 5.8 | 578 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7056 | 1703.9997 | 61.1116
MBZ-1.RR.107.2 | 24282139146139 | Moulovibazar, Roghunathpur, Wapda Road, Abdur Razzak | 2019-07-10 | MP1032 | 5.7 | 581 | 5.7 | 582 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7056 | 1703.9997 | 60.0579
MBZ-1.RR.108.1 | 24282079146133 | Moulovibazar, Roghunathpur, Wapda Road, Jamal Uddin | 2019-07-10 | MP1032 | 2.1 | 583 | 2.1 | 584 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7056 | 1703.9997 | 22.1266
MBZ-1.RR.109.1 | 24281869146112 | Moulovibazar, Roghunathpur, Wapda Road, Monsur Ali | 2019-07-10 | MP1032 | 2.9 | 585 | 2.9 | 586 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7056 | 1703.9997 | 30.5558
MBZ-1.RR.110.1 | 24281809146132 | Moulovibazar, Roghunathpur, Wapda Road, Hazi Danej Mia | 2019-07-10 | MP1032 | 1.6 | 587 | 1.6 | 588 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7056 | 1703.9997 | 16.8584
MBZ-1.RR.111.1 | 24281839146076 | Moulovibazar, Roghunathpur, Wapda Road, Abdul Kalam | 2019-07-10 | MP1032 | 7.6 | 589 | 7.6 | 590 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7056 | 1703.9997 | 80.0773
MBZ-1.RR.112.1 | 24284199147195 | Moulovibazar, Borshijora, Uluail, T.B Hospital Road, Hazi Rokibulla | 2019-07-11 | MP1032 | 11.9 | 615 | 11.9 | 616 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6624 | 2135.9997 | 125.3841
MBZ-1.RR.113.1 | 24284299147227 | Moulovibazar, Borshijora, T.B Hospital Road, Mohaldar Bari | 2019-07-11 | MP1032 | 6 | 617 | 6 | 618 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6624 | 2135.9997 | 63.2189
MBZ-1.RR.114.1 | 24283779147290 | Moulovibazar, Borshijora, T.B Hospital Road, Mohammad Goni | 2019-07-11 | MP1032 | 7.3 | 619 | 7.3 | 620 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 24 | 0 | 6600 | 2135.9997 | 76.7056
MBZ-1.RR.115.1 | 24283459147308 | Moulovibazar, Borshijora, New Bazar, T.B Hospital Road, Sheikh Mohammad Akil Mia | 2019-07-11 | MP1032 | 3.4 | 621 | 3.4 | 622 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6624 | 2135.9997 | 35.824
MBZ-1.RR.116.1 | 24290659146396 | Moulovibazar, Court Road, Majistrate Quarter | 2019-07-13 | MP1032 | 2.8 | 643 | 2.8 | 644 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6888 | 1871.9997 | 29.5021
MBZ-1.RR.117.1 | 24290489146392 | Moulovibazar, Court Road, Majistrate Quarter | 2019-07-13 | MP1032 | 4.6 | 645 | 4.6 | 646 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6888 | 1871.9997 | 48.4678
MBZ-1.RR.117.2 | 24290489146392 | Moulovibazar, Court Road, Majistrate Quarter | 2021-01-25 | NQ1003 | 12.9 | 143 | 12.9 | 144 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6888 | 1871.9997 | 135.9206
MBZ-1.RR.118.1 | 24290489146392 | Moulovibazar, Court Road, Majistrate Quarter | 2019-07-13 | MP1032 | 7.5 | 647 | 7.5 | 648 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6888 | 1871.9997 | 79.0236
MBZ-1.RR.119.1 | 24290579146365 | Moulovibazar, Court Road, Shakib Villa | 2019-07-13 | MP1032 | 11.6 | 649 | 11.6 | 650 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7176 | 1583.9997 | 122.2232
MBZ-1.RR.119.2 | 24290579146365 | Moulovibazar, Court Road, Shakib Villa | 2020-10-11 | NQ1002 | 11.4 | 136 | 11.4 | 137 | 2022-01-01 | 2022-10-27 | MN1018 | 1.9 | 104 | 1.8 | 105 | 2022-10-27 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7176 | 1583.9997
MBZ-1.RR.120.1 | 24292309146320 | Moulovibazar, Girjapara Road, Eleyasur Rahman | 2019-07-13 | MP1032 | 10.2 | 651 | 10.3 | 652 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6840 | 1919.9997 | 108.5258
MBZ-1.RR.121.1 | 24292299146324 | Moulovibazar, Girjapara Road, Jalalabad Vobon | 2019-07-13 | MP1032 | 9.6 | 653 | 9.6 | 654 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6840 | 1919.9997 | 101.1502
MBZ-1.RR.121.2 | 24292299146324 | Moulovibazar, Girjapara Road, Jalalabad Vobon | 2019-07-13 | MP1032 | 12.6 | 655 | 12.6 | 656 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6840 | 1919.9997 | 132.7597
MBZ-1.RR.122.1 | 24292339146337 | Moulovibazar, Girjapara Road, Sumsunnahar | 2019-07-13 | MP1032 | 1.6 | 657 | 1.6 | 658 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6840 | 1919.9997 | 16.8584
MBZ-1.RR.123.1 | 24292289146357 | Moulovibazar, Girjapara Road, Mojibur Rohman Chowdhury | 2019-07-13 | MP1032 | 2.7 | 659 | 2.7 | 660 | 2022-01-01 | [9 empty] | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0
MBZ-1.RR.123.2 | 24292289146357 | Moulovibazar, Girjapara Road, Mojibur Rohman Chowdhury | 2021-01-26 | NQ1003 | 4.8 | 150 | 4.8 | 151 | 2022-01-01 | [9 empty] | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0
MBZ-1.RR.124.1 | 24292479146295 | Moulovibazar, Chowmuhana, Court Road, Oposite Mamabari Resturant | 2019-07-13 | MP1032 | 5.3 | 661 | 5.3 | 662 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6840 | 1919.9997 | 55.8434
MBZ-1.RR.125.1 | 24292559146298 | Moulovibazar, Chowmuhana, Court Road, Habibur Rohman Lal Mia | 2019-07-13 | MP1032 | 10.8 | 663 | 10.8 | 664 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6840 | 1919.9997 | 113.794
MBZ-1.RR.126.1 | 24292559146298 | Moulovibazar, Chowmuhana, Court Road, Habibur Rohman Lal Mia | 2019-07-13 | MP1032 | 10.8 | 665 | 10.8 | 666 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6840 | 1919.9997 | 113.794
MBZ-1.RR.126.2 | 24292559146298 | Moulovibazar, Chowmuhana, Court Road, Habibur Rohman Lal Mia | 2019-07-13 | MP1032 | 12.7 | 667 | 12.7 | 668 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6840 | 1919.9997 | 133.8133
MBZ-1.RR.127.1 | 24292469146233 | Moulovibazar, Moddhopara, Central Road, Mohobbot Villa | 2019-07-13 | MP1032 | 9 | 671 | 9 | 672 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6840 | 1919.9997 | 94.8283
MBZ-1.RR.128.1 | 24292649146218 | Moulovibazar, Moddhopara, M Saifur Rohman Road, Rohman Lodge | 2019-07-13 | MP1032 | 4.1 | 673 | 4.1 | 674 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6840 | 1919.9997 | 43.1996
MBZ-1.RR.129.1 | 24292539146218 | Moulovibazar, Moddhopara, M Saifur Rohman Road, Abdul Kuddus | 2019-07-13 | MP1032 | 10.3 | 675 | 10.1 | 676 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6840 | 1919.9997 | 106.4185
MBZ-1.RR.131.1 | 24281719146172 | Moulvibazar, North Jogonnathpur, Word - 5, Mofiz | 2019-07-07 | MP1032 | 12.6 | 453 | 12.2 | 454 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7056 | 1703.9997 | 128.5451
MBZ-1.RR.132.1 | 24281679146167 | Moulvibazar, North Jogonnathpur, Word - 5, Modhu | 2019-07-07 | MP1032 | 10.7 | 455 | 10.7 | 456 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7176 | 1583.9997 | 112.7403
MBZ-1.RR.132.2 | 24281679146167 | Moulvibazar, North Jogonnathpur, Word - 5, Modhu | 2022-10-27 | MN1018 | 4.2 | 102 | 4.2 | 103 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 0 | 1583.9997 | 8.002
MBZ-1.RR.133.1 | 24281919146169 | Moulvibazar, North Jogonnathpur, Word - 5, Banesa Kotez, Moklis BA | 2019-07-07 | MP1032 | 13.7 | 457 | 13.7 | 458 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7056 | 1703.9997 | 144.3498
MBZ-1.RR.134.1 | 24282029146186 | Moulvibazar, North Jogonnathpur, Word - 5, Habibur Rahaman | 2019-07-07 | MP1032 | 2.6 | 461 | 2.6 | 462 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7056 | 1703.9997 | 27.3949
MBZ-1.RR.135.1 | 24284249146538 | Moulvibazar Sadar, Boro Bari, DIT Road, Abdul Rokib | 2019-07-08 | MP1032 | 6.6 | 500 | 6.6 | 501 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6624 | 2135.9997 | 69.5408
MBZ-1.RR.136.1 | 24284449146558 | Moulvibazar Sadar, Boro Bari, Vocational Road, Bodrul Ismail | 2019-07-08 | MP1032 | 7.2 | 505 | 7.2 | 506 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6624 | 2135.9997 | 75.8627
MBZ-1.RR.137.1 | 24283639147032 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Mirza manjil | 2019-07-08 | MP1032 | 4.6 | 507 | 4.6 | 508 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6720 | 2039.9997 | 48.4678
MBZ-1.RR.138.1 | 24283599147032 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Soyad Hafez Mukhlesur Rahaman Villa | 2019-07-08 | MP1032 | 2.1 | 513 | 2.1 | 514 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6720 | 2039.9997 | 22.1266
MBZ-1.RR.139.1 | 24283429147019 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Abdur Rouf | 2019-07-08 | MP1032 | 7.1 | 515 | 7.1 | 516 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6720 | 2039.9997 | 74.809
MBZ-1.RR.140.1 | 24283449147013 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Khusru Mia | 2019-07-08 | MP1032 | 3.4 | 517 | 3.4 | 518 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6720 | 2039.9997 | 35.824
MBZ-1.RR.140.2 | 24283449147013 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Khusru Mia | 2019-07-08 | MP1032 | 6.1 | 519 | 6.1 | 520 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6720 | 2039.9997 | 64.2725
MBZ-1.RR.141.1 | 24283299147005 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Salim Mia | 2019-07-08 | MP1032 | 8.6 | 521 | 8.6 | 522 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6720 | 2039.9997 | 90.6137
MBZ-1.RR.142.1 | 24283349146594 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Fozlul Haque | 2019-07-08 | MP1032 | 7.7 | 525 | 7.2 | 526 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6720 | 2039.9997 | 75.8627
MBZ-1.RR.143.1 | 24283369147051 | Moulvibazar Sadar, Boro Bari, Tecnical Road, Chuyeb Ahammed | 2019-07-08 | MP1032 | 4.8 | 527 | 4.8 | 528 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6720 | 2039.9997 | 50.5751
MBZ-1.RR.144.1 | 24283609147081 | Moulvibazar Sadar, Boro Bari, Sonapur, Vokeshonal Road, Sanjob | 2019-07-09 | MP1032 | 4.9 | 529 | 4.9 | 530 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6720 | 2039.9997 | 51.6288
MBZ-1.RR.145.1 | 24283779147130 | Moulvibazar Sadar, Boro Bari, Sonapur, Vokeshonal Road, Md. Somir Ahammod | 2019-07-09 | MP1032 | 9.9 | 531 | 9.9 | 532 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6720 | 2039.9997 | 104.3112
MBZ-1.RR.146.1 | 24283749147130 | Moulvibazar Sadar, Boro Bari, Sonapur, Vokeshonal Road, Bablu Mia | 2019-07-09 | MP1032 | 3.3 | 537 | 3.3 | 538 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6720 | 2039.9997 | 34.7704
MBZ-1.RR.146.2 | 24283749147130 | Moulvibazar Sadar, Boro Bari, Sonapur, Vokeshonal Road, Bablu Mia | 2019-07-09 | MP1032 | 11.8 | 533 | 11.8 | 534 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6720 | 2039.9997 | 124.3305
MBZ-1.RR.147.1 | 24283619147186 | Moulvibazar Sadar, Boro Bari, Sonapur, Vokeshonal Road, Asraf Uddin | 2019-07-09 | MP1032 | 8.1 | 539 | 7.6 | 540 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 5 | 0 | 6715 | 2039.9997 | 80.0316
MBZ-1.RR.148.1 | 24283689147186 | Moulvibazar Sadar, Boro Bari, Sonapur, Vokeshonal Road, Hurmot Ali | 2019-07-09 | MP1032 | 2.8 | 541 | 2.8 | 542 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6720 | 2039.9997 | 29.5021
MBZ-1.RR.149.1 | 24283369147060 | Moulvibazar Sadar, Boro Bari, Sonapur, Technical Road, Kamal | 2019-07-09 | MP1032 | 4.5 | 543 | 4.5 | 544 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6720 | 2039.9997 | 47.4142
MBZ-1.RR.150.1 | 24283189147097 | Moulvibazar Sadar, Boro Bari, Sonapur, Technical Road, Sundor Mia | 2019-07-09 | MP1032 | 2 | 545 | 2 | 546 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6720 | 2039.9997 | 21.073
MBZ-1.RR.151.1 | 24285179147097 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Akhlay Mia Chairmen | 2019-07-10 | MP1032 | 2.7 | 591 | 2.7 | 592 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6624 | 2135.9997 | 28.4485
MBZ-1.RR.152.1 | 24285119147099 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Abdul Monim | 2019-07-10 | MP1032 | 11.7 | 595 | 11.7 | 596 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6624 | 2135.9997 | 123.2768
MBZ-1.RR.153.1 | 24284879147125 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Asik Manjil | 2019-07-10 | MP1032 | 11.5 | 597 | 11.7 | 598 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6624 | 2135.9997 | 123.2768
MBZ-1.RR.154.1 | 24284829147133 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Haji Robban Uddin | 2019-07-10 | MP1032 | 6.1 | 599 | 6.1 | 600 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6624 | 2135.9997 | 64.2725
MBZ-1.RR.155.1 | 24284799147144 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Selina | 2019-07-10 | MP1032 | 11 | 601 | 10.5 | 602 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6624 | 2135.9997 | 110.6331
MBZ-1.RR.156.1 | 24284819147149 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Mukhlesur Rahaman | 2019-07-10 | MP1032 | 1.6 | 603 | 1.6 | 604 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6624 | 2135.9997 | 16.8584
MBZ-1.RR.157.1 | 24284819147149 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, kamrul Hasan Sirazi | 2019-07-10 | MP1032 | 5.9 | 605 | 5.9 | 606 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6624 | 2135.9997 | 62.1652
MBZ-1.RR.158.1 | 24284879147164 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Nazrul Islam | 2019-07-10 | MP1032 | 5.9 | 607 | 5.9 | 608 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6624 | 2135.9997 | 62.1652
MBZ-1.RR.159.1 | 24284879147164 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, Romzan Ali | 2019-07-10 | MP1032 | 13.7 | 609 | 13.9 | 610 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6624 | 2135.9997 | 146.4571
MBZ-1.RR.160.1 | 24284709147198 | Moulvibazar Sadar, West Borshijora, TB Hospital Road, J.B. Villa, Jolol Mia | 2019-07-10 | MP1032 | 3.6 | 613 | 3.6 | 614 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6624 | 2135.9997 | 37.9313
MBZ-1.RR.161.1 | 24284349146407 | South Kolimabad, Mission Road, H # 91/01, Kelun Mia | 2019-07-08 | LX1011 | 31.7 | 809 | 31.7 | 810 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 31.7 | 31.7 | 1.902 | 1.902 | 0.0007168 | 100% | 0% | 1.902 | 1.902 | 0.0011869 | 28 | 0.038129 | 0.038129 |  | 0 | 0 | 6720 | 2039.9997 | 334.0065
MBZ-1.RR.162.1 | 24284439146405 | South Kolimabad, Mission Road, H # 56, Abdur Rob | 2019-07-08 | LX1011 | 13.7 | 811 | 13.7 | 812 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6720 | 2039.9997 | 144.3498
MBZ-1.RR.163.1 | 24284809146359 | South Kolimabad, Kolimabad Road, Motabbir Hossen | 2019-07-08 | LX1011 | 8.3 | 814 | 8.3 | 815 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6720 | 2039.9997 | 87.4528
MBZ-1.RR.164.1 | 24284759146298 | South Kolimabad, Kolimabad Road, Abdul Khalek Khan | 2019-07-08 | LX1011 | 14.9 | 816 | 14.9 | 817 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6720 | 2039.9997 | 156.9936
MBZ-1.RR.165.1 | 24284759146298 | South Kolimabad, Kolimabad Road, Abul Basar | 2019-07-08 | LX1011 | 11 | 820 | 11 | 821 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6720 | 2039.9997 | 115.9013
MBZ-1.RR.166.1 | 24290249146263 | East Sultanpur, East Sultanpur Road, H # 640, Nazmul Baksh | 2019-07-10 | LX1011 | 13 | 860 | 13 | 861 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6888 | 1871.9997 | 136.9743
MBZ-1.RR.166.2 | 24290249146263 | East Sultanpur, East Sultanpur Road, H # 640, Nazmul Baksh | 2022-10-15 | MN1018 | 26.3 | 42 | 26.3 | 43 | 2022-10-15 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 26.3 | 26.3 | 1.578 | 1.578 | 0.0007168 | 100% | 0% | 1.578 | 1.578 | 0.0011869 | 28 | 0.031634 | 0.031634 |  | 0 | 0 | 0 | 1871.9997 | 59.2179
MBZ-1.RR.167.1 | 24290249146263 | East Sultanpur, East Sultanpur Road, H # 640, Samim | 2019-07-10 | LX1011 | 18.4 | 864 | 18.4 | 865 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 6888 | 1871.9997 | 193.8713
MBZ-1.RR.168.1 | 24290259146273 | East Sultanpur, East Sultanpur Road, H # 640/03, Mostofa | 2019-07-10 | LX1011 | 9.5 | 868 | 9.5 | 869 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6888 | 1871.9997 | 100.0966
MBZ-1.RR.169.1 | 24290269146281 | East Sultanpur, East Sultanpur Road, Kodban Villa | 2019-07-10 | LX1011 | 3.5 | 870 | 3.5 | 871 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6888 | 1871.9997 | 36.8777
MBZ-1.RR.170.1 | 24290469146293 | East Sultanpur, East Sultanpur Road, Abdul Jolil | 2019-07-10 | LX1011 | 8.8 | 876 | 8.8 | 877 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6888 | 1871.9997 | 92.721
MBZ-1.RR.170.2 | 24290469146293 | East Sultanpur, East Sultanpur Road, Abdul Jolil | 2019-07-10 | LX1011 | 2.9 | 878 | 2.9 | 879 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6888 | 1871.9997 | 30.5558
MBZ-1.RR.171.1 | 24290499146278 | East Sultanpur, East Sultanpur Road, H # 649, Momota Parvin | 2019-07-10 | LX1011 | 3.2 | 880 | 3.2 | 881 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6888 | 1871.9997 | 33.7167
MBZ-1.RR.172.1 | 24290649146227 | West Sultanpur, Kazir Gaon Road, Moklesur Rahman | 2019-07-10 | LX1011 | 10.1 | 882 | 10.1 | 883 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6888 | 1871.9997 | 106.4185
MBZ-1.RR.173.1 | 24290649146227 | West Sultanpur, Kazir Gaon Road, Md. Kayes Khan | 2019-07-10 | LX1011 | 16.8 | 884 | 16.8 | 885 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6888 | 1871.9997 | 177.0129
MBZ-1.RR.174.1 | 24290759146207 | East Sultanpur, Shah Mostofa Road, H # 680, Hazi Mozammel | 2019-07-10 | LX1011 | 10 | 886 | 9.2 | 887 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6888 | 1871.9997 | 96.9356
MBZ-1.RR.175.1 | 24290709146181 | East Sultanpur, Shah Mostofa Road, H # 689, Chowdhury Kutir | 2019-07-10 | LX1011 | 12.7 | 888 | 12.7 | 889 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6888 | 1871.9997 | 133.8133
MBZ-1.RR.176.1 | 24290709146181 | East Sultanpur, Shah Mostofa Road, Abdur Rouf Chowdhury | 2019-07-10 | LX1011 | 5.5 | 890 | 5.5 | 891 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6888 | 1871.9997 | 57.9506
MBZ-1.RR.177.1 | 24290849146178 | East Sultanpur, Goverment Staff Quarter, H # Building-5 | 2019-07-10 | LX1011 | 2.9 | 893 | 2.9 | 894 | 2022-01-01 | [9 empty] | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0
MBZ-1.RR.178.1 | 24290239146118 | West Sultanpur, Sultanpur Jame Mosjid Road, Dorga moholla, Aklu Mia Chowdhury | 2019-07-11 | LX1011 | 18.7 | 1 | 18.7 | 2 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6936 | 1823.9997 | 197.0322
MBZ-1.RR.178.2 | 24290239146118 | West Sultanpur, Sultanpur Jame Mosjid Road, Dorga moholla, Aklu Mia Chowdhury | 2019-07-11 | LX1011 | 10.9 | 5 | 10.9 | 6 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6936 | 1823.9997 | 114.8476
MBZ-1.RR.179.1 | 24290329146158 | West Sultanpur, Sultanpur Jame Mosjid Road, Dorga moholla, Kazi Asad | 2019-07-11 | LX1011 | 4.2 | 7 | 4 | 8 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6936 | 1823.9997 | 42.1459
MBZ-1.RR.179.2 | 24290329146158 | West Sultanpur, Sultanpur Jame Mosjid Road, Dorga moholla, Kazi Asad | 2022-04-11 | NQ1007 | 8.5 | 145 | 8.5 | 146 | 2022-04-11 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 4536 | 1823.9997 | 65.0231
MBZ-1.RR.180.1 | 24290919146075 | Dorga Moholla, Eidgah Road, H # 282, Md.Rafiq | 2019-07-13 | LX1011 | 9.6 | 32 | 8.9 | 33 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6936 | 1823.9997 | 93.7747
MBZ-1.RR.181.1 | 24290919146075 | Dorga Moholla, Eidgah Road, H # 282, Md.Motiur Rahman | 2019-07-13 | LX1011 | 8.7 | 34 | 8.7 | 35 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6936 | 1823.9997 | 91.6674
MBZ-1.RR.182.1 | 24290819146076 | Dorga Moholla, Eidgah Road, H # 591/1, Helen Monjil | 2019-07-13 | LX1011 | 14.2 | 36 | 14.2 | 37 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6936 | 1823.9997 | 149.618
MBZ-1.RR.183.1 | 24290819146076 | Dorga Moholla, Eidgah Road, H # 288, Syed Abdus Sobhan | 2019-07-13 | LX1011 | 12.3 | 40 | 12.3 | 41 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6936 | 1823.9997 | 129.5987
MBZ-1.RR.184.1 | 24290549146077 | Dorga Moholla, Eidgah Road, H #415, Syed Bodrul Haque | 2019-07-13 | LX1011 | 10.5 | 42 | 10.5 | 43 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6936 | 1823.9997 | 110.6331
MBZ-1.RR.185.1 | 24290549146077 | Dorga Moholla, Eidgah Road, H #415, Syed Bodrul Haque | 2019-07-13 | LX1011 | 7.1 | 44 | 7.1 | 45 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6936 | 1823.9997 | 74.809
MBZ-1.RR.186.1 | 24290939146267 | West Sultanpur, Shah Mostofa Road, Md.Samsul Islam | 2019-07-13 | LX1011 | 6.2 | 46 | 6.2 | 47 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6888 | 1871.9997 | 65.3262
MBZ-1.RR.186.2 | 24290939146267 | West Sultanpur, Shah Mostofa Road, Md.Samsul Islam | 2019-07-13 | LX1011 | 13.4 | 48 | 13.4 | 49 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6888 | 1871.9997 | 141.1888
MBZ-1.RR.187.1 | 24290939146267 | West Sultanpur, Shah Mostofa Road, Md.Razu | 2019-07-13 | LX1011 | 24.4 | 51 | 23.2 | 52 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 23.2 | 23.2 | 1.392 | 1.392 | 0.0007168 | 100% | 0% | 1.392 | 1.392 | 0.0011869 | 28 | 0.027905 | 0.027905 |  | 0 | 0 | 6888 | 1871.9997 | 244.4464
MBZ-1.RR.188.1 | 24290939146288 | Moulvibazar, Shah Mostofa Road, H # 50, Sazzadur Rahman | 2019-07-13 | LX1011 | 12 | 53 | 11.6 | 54 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6888 | 1871.9997 | 122.2232
MBZ-1.RR.189.1 | 24291089146277 | Moulvibazar, Shah Mostofa Road, Muslim Quarter, H # 617, Abul Hasim | 2019-07-13 | LX1011 | 11.1 | 55 | 11.1 | 56 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6888 | 1871.9997 | 116.9549
MBZ-1.RR.190.1 | 24294139146347 | West Soyerpur, Forest Office Road, Forest Office Fari | 2019-07-16 | LX1011 | 13.1 | 80 | 12.7 | 81 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6792 | 1967.9997 | 133.8133
MBZ-1.RR.191.1 | 24290059146146 | Moulavi Bazar, Dorgah Moholla, Sultanpur Road, H # 587 | 2019-07-10 | LX1011 | 13.2 | 899 | 13.2 | 900 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6888 | 1871.9997 | 139.0816
MBZ-1.RR.192.1 | 24285959146140 | Moulavi Bazar, Dorgah Moholla, Sultanpur Road, H # 586 | 2019-07-10 | LX1011 | 12.2 | 901 | 12.3 | 902 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6888 | 1871.9997 | 129.5987
MBZ-1.RR.193.1 | 24285759146140 | Moulavi Bazar,Kazirgaon, Kazirgaon Road, Mahmud Chowdhury, H # 875 | 2019-07-10 | LX1011 | 8.3 | 903 | 8.4 | 904 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6888 | 1871.9997 | 88.5064
MBZ-1.RR.194.1 | 24290629146105 | Moulavi Bazar, West Sultanpur, Sultanpur Masjid Road, Aziz Mia | 2019-07-11 | LX1011 | 10.6 | 11 | 10.6 | 12 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6912 | 1847.9997 | 111.6867
MBZ-1.RR.194.2 | 24290629146105 | Moulavi Bazar, West Sultanpur, Sultanpur Masjid Road, Aziz Mia | 2022-04-07 | NQ1007 | 2.9 | 132 | 2.9 | 133 | 2022-04-07 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 4608 | 1847.9997 | 22.5192
MBZ-1.RR.195.1 | 24290789146099 | Moulavi Bazar, West Sultanpur, Sultanpur Masjid Road, Mamunur Roshid | 2019-07-11 | LX1011 | 4.1 | 13 | 4.1 | 14 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6912 | 1847.9997 | 43.1996
MBZ-1.RR.196.1 | 24290789146099 | Moulavi Bazar, West Sultanpur, Sultanpur Masjid Road, Abdur Sattar | 2019-07-11 | LX1011 | 9.6 | 15 | 9.6 | 16 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6912 | 1847.9997 | 101.1502
MBZ-1.RR.196.2 | 24290789146099 | Moulavi Bazar, West Sultanpur, Sultanpur Masjid Road, Abdur Sattar | 2021-02-08 | LU1001 | 8.7 | 167 | 8.7 | 168 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6912 | 1847.9997 | 91.6674
MBZ-1.RR.197.1 | 24290949146108 | Moulavi Bazar, West Sultanpur, Sultanpur Masjid Road, Mahmud Ali | 2019-07-11 | LX1011 | 8.8 | 17 | 8.2 | 18 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6912 | 1847.9997 | 86.3991
MBZ-1.RR.197.2 | 24290949146108 | Moulavi Bazar, West Sultanpur, Sultanpur Masjid Road, Mahmud Ali | 2022-10-16 | MN1018 | 5.7 | 50 | 5.7 | 51 | 2022-10-16 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 0 | 1847.9997 | 12.6698
MBZ-1.RR.198.1 | 24290939146126 | Moulavi Bazar, West Sultanpur, Shah Mostofa Road, Dinmoni, H # 458 | 2019-07-11 | LX1011 | 12.3 | 19 | 12.3 | 20 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6912 | 1847.9997 | 129.5987
MBZ-1.RR.199.1 | 24291029146124 | Moulavi Bazar, West Sultanpur, Shah Mostofa Road, Alhaj Abdur Rohim | 2019-07-11 | LX1011 | 11 | 23 | 11 | 24 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6912 | 1847.9997 | 115.9013
MBZ-1.RR.200.1 | 24291029146124 | Moulavi Bazar, West Sultanpur, Shah Mostofa Road, Shofi | 2019-07-11 | LX1011 | 6.8 | 25 | 6.3 | 26 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6912 | 1847.9997 | 66.3798
MBZ-1.RR.201.1 | 24291089146098 | Moulavi Bazar, West Sultanpur, Shah Mostofa Rd, Md Shihab | 2019-07-11 | LX1011 | 5.8 | 27 | 5.8 | 28 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6912 | 1847.9997 | 61.1116
MBZ-1.RR.202.1 | 24291089146098 | Moulavi Bazar, West Sultanpur, Shah Mostofa Rd, Md Shihab | 2019-07-11 | LX1011 | 4.3 | 29 | 4.3 | 30 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6912 | 1847.9997 | 45.3069
MBZ-1.RR.203.1 | 24293269146413 | Moulavi Bazar, Soiyarpur School Road, Abdus Shahid | 2019-07-16 | LX1011 | 5.1 | 58 | 5.1 | 59 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6816 | 1943.9997 | 53.7361
MBZ-1.RR.204.1 | 24293369146414 | Moulavi Bazar, Soiyarpur School Road, Abdus Shahid | 2019-07-16 | LX1011 | 12.8 | 60 | 12.8 | 61 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6816 | 1943.9997 | 134.867
MBZ-1.RR.205.1 | 24293719146398 | Moulavi Bazar, Soiyarpur, Laxmibala School Road, Partho Sarothi | 2019-07-16 | LX1011 | 14 | 62 | 14 | 63 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6816 | 1943.9997 | 147.5107
MBZ-1.RR.206.1 | 24293819146398 | Moulavi Bazar, Soiyarpur, Laxmibala School Road, H # 423 | 2019-07-16 | LX1011 | 5.7 | 64 | 5.7 | 65 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6816 | 1943.9997 | 60.0579
MBZ-1.RR.207.1 | 24293959146387 | Moulavi Bazar, Forest Office Road, Bashonti Bhaban, H # 553/1 | 2019-07-16 | LX1011 | 13.1 | 66 | 13.1 | 67 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6816 | 1943.9997 | 138.0279
MBZ-1.RR.208.1 | 24293789146377 | Moulavi Bazar, Forest Office Road, Iqbal Hasan | 2019-07-16 | LX1011 | 12.9 | 70 | 12.9 | 71 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6816 | 1943.9997 | 135.9206
MBZ-1.RR.209.1 | 24294049146375 | Moulavi Bazar, Forest Office Road, Selina Khatun | 2019-07-16 | LX1011 | 7.3 | 72 | 7.3 | 73 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6792 | 1967.9997 | 76.9163
MBZ-1.RR.210.1 | 24294149146355 | Moulavi Bazar, Forest Office Road, Khairunesa Khanom | 2019-07-16 | LX1011 | 11.7 | 74 | 11.7 | 75 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6792 | 1967.9997 | 123.2768
MBZ-1.RR.211.1 | 24274969145521 | Moulovi Bazar, Jagonnathpur, Srimogol Road, Abdul mannan | 2019-07-07 | NQ1005 | 10.3 | 307 | 10.3 | 308 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7056 | 1703.9997 | 108.5258
MBZ-1.RR.212.1 | 24275159145540 | Moulovi Bazar, Jagonnathpur, Srimogol Road, Amina Villa | 2019-07-07 | NQ1005 | 2.2 | 309 | 2.2 | 310 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7056 | 1703.9997 | 23.1803
MBZ-1.RR.213.1 | 24275289145538 | Moulovi Bazar, Jagonnathpur, Srimogol Road, Kutub Miah | 2019-07-07 | NQ1005 | 6.3 | 311 | 6.3 | 312 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7056 | 1703.9997 | 66.3798
MBZ-1.RR.214.1 | 24275469145532 | Moulovi Bazar, Jagonnathpur, Srimogol Road, Hazi Mohasin | 2019-07-07 | NQ1005 | 7.3 | 314 | 7.3 | 315 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7056 | 1703.9997 | 76.9163
MBZ-1.RR.215.1 | 24283349146249 | Moulovi Bazar, Wapda Road, Chobra, Shibo khan | 2019-07-07 | NQ1005 | 10.4 | 316 | 10.4 | 317 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7056 | 1703.9997 | 109.5794
MBZ-1.RR.216.1 | 24283499146241 | Moulovi Bazar, Wapda Road, Chobra, Sayed Badorujjaman | 2019-07-07 | NQ1005 | 6.3 | 318 | 6.3 | 319 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7056 | 1703.9997 | 66.3798
MBZ-1.RR.217.1 | 24283589146235 | Moulovi Bazar, Wapda Road, Chobra, Abu Bakkor Helal | 2019-07-07 | NQ1005 | 7.1 | 320 | 7.1 | 321 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7056 | 1703.9997 | 74.809
MBZ-1.RR.217.2 | 24283589146235 | Moulovi Bazar, Wapda Road, Chobra, Abu Bakkor Helal | 2022-03-22 | NQ1007 | 12.1 | 62 | 12.1 | 63 | 2022-03-22 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 5136 | 1703.9997 | 99.5481
MBZ-1.RR.218.1 | 24283979146241 | Moulovi Bazar, Wapda Road, Chobra, Ruma Monjil | 2019-07-07 | NQ1005 | 12.2 | 322 | 12.2 | 323 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7056 | 1703.9997 | 128.5451
MBZ-1.RR.219.1 | 24284539146149 | Moulovi Bazar, Kazirgao, Habibullah | 2019-07-08 | NQ1005 | 7.1 | 362 | 7.1 | 363 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7056 | 1703.9997 | 74.809
MBZ-1.RR.220.1 | 24284589146153 | Moulovi Bazar, Kazirgao, Haris Miah | 2019-07-08 | NQ1005 | 7.5 | 364 | 7.5 | 365 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7176 | 1583.9997 | 79.0236
MBZ-1.RR.220.2 | 24284589146153 | Moulovi Bazar, Kazirgao, Haris Miah | 2022-10-27 | MN1018 | 5.3 | 82 | 5.3 | 83 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 0 | 1583.9997 | 10.0977
MBZ-1.RR.221.1 | 24284589146153 | Moulovi Bazar, Kazirgao, Mosha Miah | 2019-07-08 | NQ1005 | 5.7 | 366 | 5.7 | 367 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 5 | 0 | 7171 | 1583.9997 | 60.0237
MBZ-1.RR.221.2 | 24284589146153 | Moulovi Bazar, Kazirgao, Mosha Miah | 2022-10-27 | MN1018 | 6.4 | 84 | 6.4 | 85 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 0 | 1583.9997 | 12.1934
MBZ-1.RR.222.1 | 24284709146175 | Moulovi Bazar, Kazirgao, Baten Miah | 2019-07-08 | NQ1005 | 11.4 | 368 | 11.4 | 369 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7056 | 1703.9997 | 120.1159
MBZ-1.RR.223.1 | 24284799146178 | Moulovi Bazar, Kazirgao, Sajid Ali | 2019-07-08 | NQ1005 | 8.5 | 371 | 8.5 | 372 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7176 | 1583.9997 | 89.5601
MBZ-1.RR.223.2 | 24284799146178 | Moulovi Bazar, Kazirgao, Sajid Ali | 2022-10-27 | MN1018 | 3.6 | 86 | 3.6 | 87 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 0 | 1583.9997 | 6.8588
MBZ-1.RR.224.1 | 24284839146181 | Moulovi Bazar, Kazirgao, Samoj Ali | 2019-07-08 | NQ1005 | 9 | 373 | 9.1 | 374 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7056 | 1703.9997 | 95.882
MBZ-1.RR.225.1 | 24283999146078 | Moulovi Bazar, Chubra, Jobair Ahamed | 2019-07-09 | NQ1005 | 12.3 | 375 | 12.1 | 376 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7176 | 1583.9997 | 127.4914
MBZ-1.RR.225.2 | 24283999146078 | Moulovi Bazar, Chubra, Jobair Ahamed | 2022-10-27 | MN1018 | 5.3 | 80 | 5.3 | 81 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 0 | 1583.9997 | 10.0977
MBZ-1.RR.226.1 | 24283969146085 | Moulovi Bazar, Chubra, H # 396 | 2019-07-09 | NQ1005 | 8.7 | 377 | 8.8 | 378 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7056 | 1703.9997 | 92.721
MBZ-1.RR.227.1 | 24283969146101 | Moulovi Bazar, Chubra, Shafi | 2019-07-09 | NQ1005 | 7.2 | 380 | 7.2 | 381 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7056 | 1703.9997 | 75.8627
MBZ-1.RR.228.1 | 24283799146079 | Moulovi Bazar, Chubra, Nazid Beg | 2019-07-09 | NQ1005 | 8 | 382 | 8 | 383 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7056 | 1703.9997 | 84.2919
MBZ-1.RR.229.1 | 24284159146026 | Moulovi Bazar, Chubra, Sayed Abdul Malik | 2019-07-09 | NQ1005 | 9.9 | 384 | 9.9 | 385 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6960 | 1799.9997 | 104.3112
MBZ-1.RR.230.1 | 24284259145586 | Moulovi Bazar, Chubra, Ayas Miah | 2019-07-09 | NQ1005 | 9.9 | 386 | 9.9 | 387 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6960 | 1799.9997 | 104.3112
MBZ-1.RR.231.1 | 24284259145586 | Moulovi Bazar, Chubra, Hope Privet Hospital | 2019-07-09 | NQ1005 | 10.6 | 388 | 10.6 | 389 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6960 | 1799.9997 | 111.6867
MBZ-1.RR.232.1 | 24285099146088 | Moulovi Bazar, North Hospital Road, Dorga Moholla, Abdul Ali | 2019-07-09 | NQ1005 | 7.9 | 390 | 7.9 | 391 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6888 | 1871.9997 | 83.2382
MBZ-1.RR.233.1 | 24285199146064 | Moulovi Bazar, Kazirgao Road, Dorga Moholla, Rahman Villa | 2019-07-09 | NQ1005 | 4.8 | 392 | 4.8 | 393 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6888 | 1871.9997 | 50.5751
MBZ-1.RR.234.1 | 24285099146061 | Moulovi Bazar, Kazirgao Road, Dorga Moholla, Raihan Villa | 2019-07-09 | NQ1005 | 5.1 | 394 | 5.1 | 395 | 2022-01-01 | 2022-10-15 | MN1018 | 0.5 | 44 | 0.5 | 45 | 2022-10-15 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6888 | 1871.9997
MBZ-1.RR.235.1 | 24282139145561 | Moulovi Bazar, Srimongol Road, Kudalipul, Nurul Haque | 2019-07-10 | NQ1005 | 11.8 | 426 | 11.8 | 427 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6960 | 1799.9997 | 124.3305
MBZ-1.RR.236.1 | 24283149145568 | Moulovi Bazar, Srimongol Road, Kudalipul, Hazi Tarif Villa | 2019-07-10 | NQ1005 | 8.1 | 428 | 8.1 | 429 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6960 | 1799.9997 | 85.3455
MBZ-1.RR.237.1 | 24283499146001 | Moulovi Bazar, Srimongol Road, Raghunondonpur, Nuroj Miah | 2019-07-10 | NQ1005 | 12.8 | 430 | 12.8 | 431 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6960 | 1799.9997 | 134.867
MBZ-1.RR.238.1 | 24283299146033 | Moulovi Bazar, Srimongol Road, Raghunondonpur, Tanzil Malik | 2019-07-10 | NQ1005 | 8.1 | 432 | 8.1 | 433 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6960 | 1799.9997 | 85.3455
MBZ-1.RR.239.1 | 24284639146019 | Moulovi Bazar, Dorga Moholla, H # 241 | 2019-07-11 | NQ1005 | 9.6 | 442 | 9.6 | 443 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6960 | 1799.9997 | 101.1502
MBZ-1.RR.240.1 | 24284569146022 | Moulovi Bazar, Dorga Moholla, Shawkot Khan | 2019-07-11 | NQ1005 | 2.7 | 444 | 2.7 | 445 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6960 | 1799.9997 | 28.4485
MBZ-1.RR.241.1 | 24284569146022 | Moulovi Bazar, Dorga Moholla, Fazlo Miah | 2019-07-11 | NQ1005 | 7.8 | 446 | 7.8 | 447 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6960 | 1799.9997 | 82.1846
MBZ-1.RR.242.1 | 24284719146029 | Moulovi Bazar, Dorga Moholla, Kaptan Miah | 2019-07-11 | NQ1005 | 9.9 | 448 | 9.9 | 449 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6960 | 1799.9997 | 104.3112
MBZ-1.RR.243.1 | 24284739146026 | Moulovi Bazar, Dorga Moholla, Khalilur Rahman | 2019-07-11 | NQ1005 | 8.2 | 450 | 8.2 | 451 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6960 | 1799.9997 | 86.3991
MBZ-1.RR.244.1 | 24284729146024 | Moulovi Bazar, Dorga Moholla, Abdur Rahim | 2019-07-11 | NQ1005 | 6.3 | 452 | 6.3 | 453 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6960 | 1799.9997 | 66.3798
MBZ-1.RR.245.1 | 24285279145597 | Moulovi Bazar, Srimongol Road, 250 Bed Sadar Hospital | 2019-07-11 | NQ1005 | 3.4 | 454 | 3.4 | 455 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6936 | 1823.9997 | 35.824
MBZ-1.RR.246.1 | 24285149145598 | Moulovi Bazar, Srimongol Road, 250 Bed Sadar Hospital | 2019-07-11 | NQ1005 | 5.4 | 456 | 5.4 | 457 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6936 | 1823.9997 | 56.897
MBZ-1.RR.247.1 | 24285409145595 | Moulovi Bazar, Srimongol Road, Dorga Moholla, H # 274 | 2019-07-11 | NQ1005 | 2.8 | 458 | 2.8 | 459 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6936 | 1823.9997 | 29.5021
MBZ-1.RR.248.1 | 24285359146024 | Moulovi Bazar, Dorga Moholla, N. R. Monzil | 2019-07-11 | NQ1005 | 9.6 | 460 | 9.6 | 461 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6936 | 1823.9997 | 101.1502
MBZ-1.RR.249.1 | 24285359146024 | Moulovi Bazar, Dorga Moholla, N. R. Monzil | 2019-07-11 | NQ1005 | 7.8 | 462 | 7.8 | 463 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6936 | 1823.9997 | 82.1846
MBZ-1.RR.250.1 | 24285369146045 | Moulovi Bazar, Dorga Moholla, Amirunnesa | 2019-07-11 | NQ1005 | 8.7 | 464 | 8.7 | 465 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6936 | 1823.9997 | 91.6674
MBZ-1.RR.251.1 | 24284099146233 | South Kalimabad, Ward# 3, Ferdous Ara Crori | 2019-07-07 | NQ1005 | 9 | 324 | 9 | 325 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7056 | 1703.9997 | 94.8283
MBZ-1.RR.251.2 | 24284099146233 | South Kalimabad, Ward# 3, Ferdous Ara Crori | 2021-01-25 | MN1032 | 4.1 | 59 | 4.1 | 60 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7056 | 1703.9997 | 43.1996
MBZ-1.RR.252.1 | 24284169146220 | South Kalimabad, Ward# 3, Md. Matin | 2019-07-07 | NQ1005 | 6.3 | 326 | 6.3 | 327 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7056 | 1703.9997 | 66.3798
MBZ-1.RR.253.1 | 24284169146206 | South Kalimabad, Ward# 3, Md. Sattar | 2019-07-07 | NQ1005 | 7.8 | 328 | 7.8 | 329 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7056 | 1703.9997 | 82.1846
MBZ-1.RR.254.1 | 24284149146259 | South Kalimabad, Ward# 3, Sujina khan Villa | 2019-07-07 | NQ1005 | 6.6 | 330 | 6.7 | 331 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7056 | 1703.9997 | 70.5944
MBZ-1.RR.255.1 | 24284389146266 | South Kalimabad, Ward# 3, Batirullah | 2019-07-07 | NQ1005 | 6.6 | 332 | 6.6 | 333 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7056 | 1703.9997 | 69.5408
MBZ-1.RR.256.1 | 24284229146292 | South Kalimabad, Ward# 3, Montaj Uddin | 2019-07-07 | NQ1005 | 5.5 | 334 | 5.5 | 335 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6720 | 2039.9997 | 57.9506
MBZ-1.RR.257.1 | 24284319146292 | South Kalimabad, Ward# 3, Selim Chairman | 2019-07-07 | NQ1005 | 6.1 | 336 | 6.1 | 337 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6720 | 2039.9997 | 64.2725
MBZ-1.RR.258.1 | 24284229146314 | South Kalimabad, Ward# 3, Ataur Rahman | 2019-07-07 | NQ1005 | 9.5 | 338 | 9.5 | 339 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6720 | 2039.9997 | 100.0966
MBZ-1.RR.259.1 | 24284329146329 | South Kalimabad, Ward# 3, Ansar Hosen | 2019-07-07 | NQ1005 | 11.7 | 340 | 11.7 | 341 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6720 | 2039.9997 | 123.2768
MBZ-1.RR.260.1 | 24284369146318 | South Kalimabad, Ward# 3, Abdul Jabbar | 2019-07-07 | NQ1005 | 4.2 | 342 | 4.2 | 343 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6720 | 2039.9997 | 44.2532
MBZ-1.RR.261.1 | 24284349146305 | South Kalimabad, Ward# 3, Fajilatunnessa Chy | 2019-07-07 | NQ1005 | 2.3 | 344 | 2.3 | 345 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6720 | 2039.9997 | 24.2339
MBZ-1.RR.262.1 | 24284339146343 | South Kalimabad, Ward# 3, Majid Manjil, H# 41/6 | 2019-07-07 | NQ1005 | 12.3 | 346 | 12.3 | 347 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6720 | 2039.9997 | 129.5987
MBZ-1.RR.263.1 | 24284169146344 | South Kalimabad, Ward# 3, Kalam Villa | 2019-07-08 | NQ1005 | 7.8 | 348 | 7.8 | 349 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6720 | 2039.9997 | 82.1846
MBZ-1.RR.264.1 | 24284169146344 | South Kalimabad, Ward# 3, Maa Vaban | 2019-07-08 | NQ1005 | 2.9 | 350 | 2.9 | 351 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6720 | 2039.9997 | 30.5558
MBZ-1.RR.265.1 | 24284169146344 | South Kalimabad, Ward# 3, Md. Mofiz Mia | 2019-07-08 | NQ1005 | 4.6 | 352 | 4.6 | 353 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6720 | 2039.9997 | 48.4678
MBZ-1.RR.265.2 | 24284169146344 | South Kalimabad, Ward# 3, Md. Mofiz Mia | 2019-07-08 | NQ1005 | 4.8 | 354 | 4.8 | 355 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6720 | 2039.9997 | 50.5751
MBZ-1.RR.266.1 | 24284449146344 | South Kalimabad, Ward# 3, Abdul Malik Talukder | 2019-07-08 | NQ1005 | 5.5 | 356 | 5.7 | 357 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6720 | 2039.9997 | 60.0579
MBZ-1.RR.267.1 | 24283599146221 | Banabithi, Chubra Road, Nurul Islam | 2019-07-08 | NQ1005 | 4.8 | 358 | 4.8 | 359 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7056 | 1703.9997 | 50.5751
MBZ-1.RR.268.1 | 24283669146200 | Banabithi, Chubra Road, Abdul Ahad | 2019-07-08 | NQ1005 | 5.1 | 360 | 5.1 | 361 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7056 | 1703.9997 | 53.7361
MBZ-1.RR.268.2 | 24283669146200 | Banabithi, Chubra Road, Abdul Ahad | 2022-03-22 | NQ1007 | 10.9 | 64 | 10.9 | 65 | 2022-03-22 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 5136 | 1703.9997 | 89.6756
MBZ-1.RR.269.1 | 24283829146179 | Banabithi, Chubra Road, Vadgao villa | 2019-07-10 | NQ1005 | 13.6 | 396 | 13.6 | 397 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7056 | 1703.9997 | 143.2961
MBZ-1.RR.270.1 | 24283829146179 | Banabithi, Chubra Road, Sohel & Shakil villa | 2019-07-10 | NQ1005 | 6.9 | 398 | 7 | 399 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7056 | 1703.9997 | 73.7554
MBZ-1.RR.270.2 | 24283829146179 | Banabithi, Chubra Road, Sohel & Shakil villa | 2019-07-10 | NQ1005 | 12 | 400 | 12 | 401 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7056 | 1703.9997 | 126.4378
MBZ-1.RR.270.3 | 24283829146179 | Banabithi, Chubra Road, Sohel & Shakil villa | 2021-01-24 | NQ1003 | 4.1 | 128 | 4.1 | 129 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7056 | 1703.9997 | 43.1996
MBZ-1.RR.271.1 | 24283879146169 | Banabithi, Chubra Road, Shefa Manjil | 2019-07-10 | NQ1005 | 11.7 | 402 | 11.7 | 403 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7056 | 1703.9997 | 123.2768
MBZ-1.RR.272.1 | 24283859146151 | Banabithi, Chubra Road, Ibrahim | 2019-07-10 | NQ1005 | 3.7 | 404 | 3.7 | 405 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7056 | 1703.9997 | 38.985
MBZ-1.RR.273.1 | 24283859146151 | Banabithi, Chubra Road, Abdur Rouf | 2019-07-10 | NQ1005 | 5.8 | 406 | 5.8 | 407 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7056 | 1703.9997 | 61.1116
MBZ-1.RR.274.1 | 24283859146151 | Banabithi, Chubra Road, Front of Azid Ullah | 2019-07-10 | NQ1005 | 6.7 | 408 | 6.7 | 409 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 6.5 | 0 | 7049.5 | 1703.9997 | 70.542
MBZ-1.RR.274.2 | 24283859146151 | Banabithi, Chubra Road, Front of Azid Ullah | 2022-03-22 | NQ1007 | 6.2 | 66 | 6.2 | 67 | 2022-03-22 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 5136 | 1703.9997 | 51.0081
MBZ-1.RR.275.1 | 24283709146145 | Banabithi, Chubra Road, Kamal | 2019-07-10 | NQ1005 | 6.5 | 410 | 6.5 | 411 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7056 | 1703.9997 | 68.4871
MBZ-1.RR.276.1 | 24285199146114 | Kajirgaon, Sadar Hospital Road, Dargamoholla, Ataur Rahman | 2019-07-10 | NQ1005 | 14.7 | 412 | 14.7 | 413 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6888 | 1871.9997 | 154.8863
MBZ-1.RR.277.1 | 24285279146116 | Kajirgaon, Abu Tahir Road, Dargamoholla, Taklif Mia | 2019-07-10 | NQ1005 | 8.2 | 414 | 8.2 | 415 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6888 | 1871.9997 | 86.3991
MBZ-1.RR.278.1 | 24285629146099 | Dargamoholla, Abdul Latif Road, Adil | 2019-07-10 | NQ1005 | 12.4 | 416 | 12.4 | 417 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6936 | 1823.9997 | 130.6524
MBZ-1.RR.279.1 | 24285729146116 | Dargamoholla, Abdul Latif Road, Abdul Khalik Talukder | 2019-07-10 | NQ1005 | 10.3 | 418 | 10.3 | 419 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6936 | 1823.9997 | 108.5258
MBZ-1.RR.280.1 | 24285779146099 | Dargamoholla, Abdul Latif Road, Abdul Hannan | 2019-07-10 | NQ1005 | 22.3 | 420 | 22.3 | 421 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 6936 | 1823.9997 | 234.9635
MBZ-1.RR.281.1 | 24285239146144 | Kajirgaon, Tablik Masjid Road, Ward # 7, Asmat Ullah | 2019-07-11 | NQ1005 | 6.5 | 434 | 6.5 | 435 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6888 | 1871.9997 | 68.4871
MBZ-1.RR.282.1 | 24285279146152 | Kajirgaon, Tablik Masjid Road, Ward # 7, H # 566 | 2019-07-11 | NQ1005 | 3.5 | 436 | 3.5 | 437 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6888 | 1871.9997 | 36.8777
MBZ-1.RR.283.1 | 24285259146166 | Kajirgaon, Tablik Masjid Road, Ward # 7, Md. Mahbub Mia | 2019-07-11 | NQ1005 | 10.7 | 438 | 10.1 | 439 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6888 | 1871.9997 | 106.4185
MBZ-1.RR.284.1 | 24285379146164 | Kajirgaon, Tablik Masjid Road, Ward # 7, Rakib Villa | 2019-07-11 | NQ1005 | 6.9 | 440 | 6.9 | 441 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6888 | 1871.9997 | 72.7017
MBZ-1.RR.285.1 | 24290109146093 | Dorgamoholla, Sheikh Kazim Road, Taslim Ali | 2019-07-13 | NQ1005 | 3.4 | 476 | 3.4 | 477 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6936 | 1823.9997 | 35.824
MBZ-1.RR.285.2 | 24290109146093 | Dorgamoholla, Sheikh Kazim Road, Taslim Ali | 2019-07-13 | NQ1005 | 3.3 | 478 | 3.3 | 479 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6936 | 1823.9997 | 34.7704
MBZ-1.RR.286.1 | 24290229146078 | Dorgamoholla, Sheikh Kazim Road, Mizanur Rahman | 2019-07-13 | NQ1005 | 4.5 | 480 | 4.5 | 481 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6936 | 1823.9997 | 47.4142
MBZ-1.RR.287.1 | 24290229146078 | Dorgamoholla, Sheikh Kazim Road, Tamim Mahmud | 2019-07-13 | NQ1005 | 6.6 | 482 | 6.6 | 483 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6936 | 1823.9997 | 69.5408
MBZ-1.RR.288.1 | 24290289146064 | Dorgamoholla, Sheikh Kazim Road, Shablu | 2019-07-13 | NQ1005 | 10.6 | 484 | 10.6 | 485 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6936 | 1823.9997 | 111.6867
MBZ-1.RR.289.1 | 24290289146064 | Dorgamoholla, Sheikh Kazim Road, Bablu | 2019-07-13 | NQ1005 | 10.2 | 486 | 10.3 | 487 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6936 | 1823.9997 | 108.5258
MBZ-1.RR.289.2 | 24290289146064 | Dorgamoholla, Sheikh Kazim Road, Bablu | 2019-07-13 | NQ1005 | 6.2 | 488 | 6.2 | 489 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6936 | 1823.9997 | 65.3262
MBZ-1.RR.290.1 | 24285859146045 | Dorgamoholla, Sheikh Kazim Road, Late. Jomir Mia | 2019-07-13 | NQ1005 | 10.6 | 490 | 10.6 | 491 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6936 | 1823.9997 | 111.6867
MBZ-1.RR.291.1 | 24283639146314 | Wapda Road, Bonbithi R/A, Syed Md. Mostofa Sharak, Md. Abdul Jobbar | 2019-07-07 | NQ1007 | 4.2 | 500 | 4.2 | 501 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6720 | 2039.9997 | 44.2532
MBZ-1.RR.292.1 | 24283709146323 | Wapda Road, Bonbithi R/A, Syed Md. Mostofa Sharak, Syed Enayet Ullah | 2019-07-07 | NQ1007 | 6.2 | 502 | 6.3 | 503 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6720 | 2039.9997 | 66.3798
MBZ-1.RR.292.2 | 24283709146323 | Wapda Road, Bonbithi R/A, Syed Md. Mostofa Sharak, Syed Enayet Ullah | 2019-07-07 | NQ1007 | 5.8 | 504 | 5.8 | 505 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6720 | 2039.9997 | 61.1116
MBZ-1.RR.293.1 | 24283949146304 | Wapda Road, Bonbithi R/A, Syed Md. Mostofa Sharak, H # 241/1, Komol Gonj House | 2019-07-07 | NQ1007 | 5 | 506 | 5 | 507 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6720 | 2039.9997 | 52.6824
MBZ-1.RR.294.1 | 24283469146385 | Court Road, Banassree R/A, H # 127/2, Azij Nir | 2019-07-07 | NQ1007 | 3.1 | 508 | 3.1 | 509 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6768 | 1991.9997 | 32.6631
MBZ-1.RR.294.2 | 24283469146385 | Court Road, Banassree R/A, H # 127/2, Azij Nir | 2022-04-09 | NQ1007 | 6.5 | 136 | 6.5 | 137 | 2022-04-09 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 4416 | 1991.9997 | 50.0988
MBZ-1.RR.294.3 | 24283469146385 | Court Road, Banassree R/A, H # 127/2, Azij Nir | 2022-10-10 | MN1018 | 3.3 | 32 | 3.4 | 33 | 2022-10-10 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 0 | 1991.9997 | 8.1463
MBZ-1.RR.295.1 | 24283629146404 | P.T.I Road, Banassree R/A, H # 233, White House | 2019-07-07 | NQ1007 | 11.7 | 510 | 11.7 | 511 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6720 | 2039.9997 | 123.2768
MBZ-1.RR.296.1 | 24283609146403 | P.T.I Road, Bonbithi R/A, H # 28-02, Dream Loz | 2019-07-07 | NQ1007 | 6.7 | 512 | 6.7 | 513 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6720 | 2039.9997 | 70.5944
MBZ-1.RR.297.1 | 24283449146428 | P.T.I Road, Banassree R/A, H # 236, Motahir Villa | 2019-07-07 | NQ1007 | 9.2 | 514 | 9.2 | 515 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6720 | 2039.9997 | 96.9356
MBZ-1.RR.298.1 | 24283129146408 | P.T.I Road, Banassree R/A, H # 792, S.S.L.N | 2019-07-07 | NQ1007 | 12.1 | 516 | 12.1 | 517 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6720 | 2039.9997 | 127.4914
MBZ-1.RR.299.1 | 24283099146426 | P.T.I Road, Banassree R/A, Md. Abdus Salam | 2019-07-07 | NQ1007 | 7.3 | 518 | 7.3 | 519 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6720 | 2039.9997 | 76.9163
MBZ-1.RR.300.1 | 24282999146445 | P.T.I Road, Banassree R/A, H # 119/1, Md. Shanoor Villa | 2019-07-07 | NQ1007 | 3.4 | 520 | 3.4 | 521 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6720 | 2039.9997 | 35.824
MBZ-1.RR.301.1 | 24282259146562 | Sunapur Road, Hazi Sonaullah Sharak, Faruk Ahmed | 2019-07-08 | NQ1007 | 8.5 | 522 | 8.5 | 523 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6720 | 2039.9997 | 89.5601
MBZ-1.RR.302.1 | 24282629146587 | Sunapur Road, Hazi Sonaullah Sharak, H # 217, Md. Hossen | 2019-07-08 | NQ1007 | 4.3 | 524 | 4.3 | 525 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6720 | 2039.9997 | 45.3069
MBZ-1.RR.303.1 | 24282469147013 | Sunapur Road, Hazi Sonaullah Sharak, Mojammel Hoque | 2019-07-08 | NQ1007 | 8.7 | 526 | 8.7 | 527 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 648 | 6720 | 1391.9997 | 84.8865
MBZ-1.RR.304.1 | 24282589147076 | Sunapur Road, Hazi Sonaullah Sharak, H # 306, Abdul Motin | 2019-07-08 | NQ1007 | 4 | 528 | 4 | 529 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6720 | 2039.9997 | 42.1459
MBZ-1.RR.305.1 | 24281839147003 | Sunapur, Kalenga Road, Babul Mia | 2019-07-08 | NQ1007 | 12.8 | 530 | 12.8 | 531 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6720 | 2039.9997 | 134.867
MBZ-1.RR.306.1 | 24281709147008 | Sunapur, Kalenga Road, H # 229, Lutfa Begum | 2019-07-08 | NQ1007 | 2.5 | 532 | 2.5 | 533 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6720 | 2039.9997 | 26.3412
MBZ-1.RR.307.1 | 24281539147018 | Sunapur, Kalenga Road, Babul Mia | 2019-07-08 | NQ1007 | 7.4 | 534 | 7.4 | 535 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6720 | 2039.9997 | 77.97
MBZ-1.RR.308.1 | 24280989147082 | Sunapur, Kalenga Road, F.F Rihana Villa | 2019-07-08 | NQ1007 | 8.5 | 536 | 8 | 537 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6720 | 2039.9997 | 84.2919
MBZ-1.RR.309.1 | 24281099147102 | Sunapur, Kalenga Road, H # 245, Ibrahim Ali | 2019-07-08 | NQ1007 | 4.1 | 538 | 4.1 | 539 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6720 | 2039.9997 | 43.1996
MBZ-1.RR.310.1 | 24285669147072 | Banani, Chairman Bari, Akhlai Mia | 2019-07-10 | NQ1007 | 11.9 | 583 | 11.9 | 584 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6672 | 2087.9997 | 125.3841
MBZ-1.RR.311.1 | 24290299147079 | Banani, Borshijura, Alam Mohal | 2019-07-10 | NQ1007 | 3.8 | 585 | 3.8 | 586 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6672 | 2087.9997 | 40.0386
MBZ-1.RR.312.1 | 24290359147087 | Banani, Borshijura, H # 254, Ashikur Rahman | 2019-07-10 | NQ1007 | 11.4 | 587 | 11.4 | 588 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6672 | 2087.9997 | 120.1159
MBZ-1.RR.313.1 | 24290339147110 | Banani, Borshijura, H # 165, Shakir Manzil | 2019-07-10 | NQ1007 | 3.2 | 589 | 3.2 | 590 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6672 | 2087.9997 | 33.7167
MBZ-1.RR.314.1 | 24290459147083 | Banani, Borshijura, Atikullah | 2019-07-10 | NQ1007 | 5.1 | 591 | 5.1 | 592 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6672 | 2087.9997 | 53.7361
MBZ-1.RR.315.1 | 24290499147083 | Banani, Borshijura, Md. Abul Hossen | 2019-07-10 | NQ1007 | 5.2 | 593 | 5.2 | 594 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6672 | 2087.9997 | 54.7897
MBZ-1.RR.316.1 | 24290089147184 | Banani, Borshijura, Shat Bari Road, Bahar Monjil | 2019-07-10 | NQ1007 | 12 | 595 | 12 | 596 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6624 | 2135.9997 | 126.4378
MBZ-1.RR.317.1 | 24290589147220 | Banani, Borshijura, Mokhlesur Rahman | 2019-07-10 | NQ1007 | 5.7 | 597 | 5.7 | 598 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6624 | 2135.9997 | 60.0579
MBZ-1.RR.317.2 | 24290589147220 | Banani, Borshijura, Mokhlesur Rahman | 2019-07-10 | NQ1007 | 11.3 | 599 | 11.8 | 600 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6624 | 2135.9997 | 124.3305
MBZ-1.RR.318.1 | 24290149147218 | Banani, Borshijura, H # 223, Chulu Mia | 2019-07-10 | NQ1007 | 8.1 | 601 | 8.1 | 602 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6624 | 2135.9997 | 85.3455
MBZ-1.RR.319.1 | 24291079147260 | Banani, Borshijura, H # 159, Nazir Ahmed | 2019-07-10 | NQ1007 | 9 | 603 | 9 | 604 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6624 | 2135.9997 | 94.8283
MBZ-1.RR.320.1 | 24291079147260 | Banani, Borshijura, H # 159, Nazir Ahmed | 2019-07-10 | NQ1007 | 11.9 | 605 | 11.9 | 606 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6624 | 2135.9997 | 125.3841
MBZ-1.RR.321.1 | 24291069147278 | Banani, Borshijura, H # 159, Mokbul Mia | 2019-07-10 | NQ1007 | 3.7 | 607 | 3.7 | 608 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6624 | 2135.9997 | 38.985
MBZ-1.RR.322.1 | 24290639147083 | West Borshijura, T.B Hospital Road, Abdus Salik | 2019-07-11 | NQ1007 | 15.8 | 627 | 15.8 | 628 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6672 | 2087.9997 | 166.4764
MBZ-1.RR.323.1 | 24290769147095 | West Borshijura, T.B Hospital Road, H # 596 | 2019-07-11 | NQ1007 | 3.6 | 629 | 3.6 | 630 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6672 | 2087.9997 | 37.9313
MBZ-1.RR.324.1 | 24290939147098 | West Borshijura, Shamoli R/A, Sazzadur Rahman | 2019-07-11 | NQ1007 | 4.5 | 631 | 4.5 | 632 | 2022-01-01 | [9 empty] | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0
MBZ-1.RR.325.1 | 24291469147079 | West Borshijura, Shamoli R/A, Shohid Abdus Shahid Road, Saleha Villa | 2019-07-11 | NQ1007 | 7.6 | 633 | 7.6 | 634 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6672 | 2087.9997 | 80.0773
MBZ-1.RR.326.1 | 24291699147056 | North-West Borshijura, Shamoli R/A, Shohid Abdus Shahid Road, H # 43 | 2019-07-11 | NQ1007 | 5.7 | 635 | 5.7 | 636 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6672 | 2087.9997 | 60.0579
MBZ-1.RR.327.1 | 24291989147051 | Shamoli R/A, Shohid Abdus Shahid Road, Alaish Monjil | 2019-07-11 | NQ1007 | 32.3 | 637 | 32.3 | 638 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 32.3 | 32.3 | 1.938 | 1.938 | 0.0007168 | 100% | 0% | 1.938 | 1.938 | 0.0011869 | 28 | 0.03885 | 0.03885 |  | 0 | 0 | 6672 | 2087.9997 | 340.3283
MBZ-1.RR.327.2 | 24291989147051 | Shamoli R/A, Shohid Abdus Shahid Road, Alaish Monjil | 2022-03-23 | NQ1007 | 9.6 | 77 | 9.2 | 78 | 2022-03-23 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 4728 | 2087.9997 | 75.4239
MBZ-1.RR.328.1 | 24292279147027 | Shamoli R/A, Shohid Abdus Shahid Road, Ward No-1, H # 34, Gaziur Rahman | 2019-07-11 | NQ1007 | 6.9 | 639 | 6.9 | 640 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6672 | 2087.9997 | 72.7017
MBZ-1.RR.329.1 | 24292609146579 | Shamoli, Shomsher Nagar Road, Ward No- 01, Bolvi House | 2019-07-13 | NQ1007 | 10.4 | 659 | 10.4 | 660 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6672 | 2087.9997 | 109.5794
MBZ-1.RR.330.1 | 24292609146579 | Shamoli, Shomsher Nagar Road, Ward No- 01, Joytun Nahar | 2019-07-13 | NQ1007 | 12.6 | 661 | 12.6 | 662 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6672 | 2087.9997 | 132.7597
MBZ-1.RR.331.1 | 24260879145488 | Moulovibazar, Mokam Bazar, Prem Nagar Cha Bagan Road, Arfin Mia | 2019-07-06 | NQ1007 | 12.2 | 469 | 12.2 | 470 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7176 | 1583.9997 | 128.5451
MBZ-1.RR.331.2 | 24260879145488 | Moulovibazar, Mokam Bazar, Prem Nagar Cha Bagan Road, Arfin Mia | 2022-10-27 | MN1018 | 3.8 | 96 | 3.8 | 97 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 0 | 1583.9997 | 7.2399
MBZ-1.RR.332.1 | 24260749145491 | Moulovibazar, Mokam Bazar, Prem Nagar Cha Bagan Road, H # 22, Monwar Ali Salim Monjil | 2019-07-06 | NQ1007 | 4.8 | 471 | 4.9 | 472 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7056 | 1703.9997 | 51.6288
MBZ-1.RR.333.1 | 24260899145499 | Moulovibazar, Mokambazar, Prem Nagar, Cha Bagan Road, Shahin | 2019-07-06 | NQ1007 | 2.8 | 473 | 2.8 | 474 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7056 | 1703.9997 | 29.5021
MBZ-1.RR.334.1 | 24275699145546 | Moulovibazar Sadar, Jogonnatpur, Boro Bari Lane, Abdul Mannan | 2019-07-07 | NQ1007 | 10.2 | 475 | 10.2 | 476 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7056 | 1703.9997 | 107.4721
MBZ-1.RR.335.1 | 24280209145542 | Moulovibazar Sadar, Jogonnatpur, Beside M/S Jahin Hardware and Sanitary, Abdul Malek | 2019-07-07 | NQ1007 | 3 | 477 | 3 | 478 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7056 | 1703.9997 | 31.6094
MBZ-1.RR.336.1 | 24280389146009 | Moulovibazar Sadar, Jogonnatpur, Tilagaon, H # 23, Azkor Mia | 2019-07-07 | NQ1007 | 10.8 | 479 | 10.8 | 480 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7056 | 1703.9997 | 113.794
MBZ-1.RR.337.1 | 24280199146013 | Moulovibazar Sadar, Jogonnatpur, Tilagaon, H # 40, Haidar Mia | 2019-07-07 | NQ1007 | 4.1 | 481 | 4.1 | 482 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7056 | 1703.9997 | 43.1996
MBZ-1.RR.338.1 | 24280149146033 | Moulovibazar Sadar, Jogonnatpur, Tilagaon, H # 20, Aysha Akter | 2019-07-07 | NQ1007 | 6.6 | 483 | 6.6 | 484 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7056 | 1703.9997 | 69.5408
MBZ-1.RR.339.1 | 24280129146044 | Moulovibazar, Jogonnatpur, Tilagaon, Chhatak House, Monowara Begum | 2019-07-07 | NQ1007 | 3.8 | 485 | 3.8 | 486 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7056 | 1703.9997 | 40.0386
MBZ-1.RR.340.1 | 24280129146044 | Moulovibazar, Jogonnatpur, Tilagaon, Tilabari, Arina Cottage | 2019-07-07 | NQ1007 | 11.2 | 487 | 11.2 | 488 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7056 | 1703.9997 | 118.0086
MBZ-1.RR.341.1 | 24280319146078 | Moulovibazar, Jogonnatpur, Tilagaon, H # 09, Syed Afsor Ali | 2019-07-07 | NQ1007 | 1.6 | 489 | 1.6 | 490 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7056 | 1703.9997 | 16.8584
MBZ-1.RR.342.1 | 24280539146055 | Moulovibazar, Jogonnatpur, Tilagaon, H # 05, Abdul Hadi Khan | 2019-07-07 | NQ1007 | 4.6 | 491 | 4.6 | 492 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7056 | 1703.9997 | 48.4678
MBZ-1.RR.344.1 | 24275569146056 | Moulovibazar, Jogonnatpur, Tilagaon, Md. Eliyas | 2019-07-07 | NQ1007 | 5.5 | 495 | 5.5 | 496 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7056 | 1703.9997 | 57.9506
MBZ-1.RR.345.1 | 24275569146056 | Moulovibazar, Jogonnatpur, Tilagaon, Samsuddin Ahmed | 2019-07-07 | NQ1007 | 3.2 | 497 | 3.2 | 498 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 5 | 0 | 7051 | 1703.9997 | 33.6975
MBZ-1.RR.346.1 | 24284659146513 | Moulovibazar, Orangetila, Vocational Road, Moulana Mofojjol Hossen | 2019-07-08 | NQ1007 | 2.6 | 540 | 2.6 | 541 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6624 | 2135.9997 | 27.3949
MBZ-1.RR.347.1 | 24284499146531 | Moulovibazar, Orangetila, Vocational Road, Bodrujjaman | 2019-07-08 | NQ1007 | 4.6 | 542 | 4.6 | 543 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6624 | 2135.9997 | 48.4678
MBZ-1.RR.348.1 | 24284589146538 | Moulovibazar, Orangetila, Vocational Road, Fahimur Rahman Hajari | 2019-07-08 | NQ1007 | 8 | 544 | 8 | 545 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6624 | 2135.9997 | 84.2919
MBZ-1.RR.349.1 | 24284679146548 | Moulovibazar, Borshijura, Orangetila, Vocational Road, H # 176/2, Samrat Empire | 2019-07-08 | NQ1007 | 4 | 546 | 4.3 | 547 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6624 | 2135.9997 | 45.3069
MBZ-1.RR.350.1 | 24285069146578 | Moulovibazar, Orangetila, Vocational Road, H # 174/2, Haji Farid Villa | 2019-07-08 | NQ1007 | 8.7 | 548 | 8.7 | 549 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6624 | 2135.9997 | 91.6674
MBZ-1.RR.351.1 | 24285069146576 | Moulovibazar, Orangetila, Vocational Road, Roshid Mia | 2019-07-08 | NQ1007 | 8.9 | 550 | 8.9 | 551 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6624 | 2135.9997 | 93.7747
MBZ-1.RR.351.2 | 24285069146576 | Moulovibazar, Orangetila, Vocational Road, Roshid Mia | 2021-01-25 | NQ1007 | 3.4 | 80 | 3.4 | 81 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6624 | 2135.9997 | 35.824
MBZ-1.RR.352.1 | 24284889147059 | Moulovibazar, Orangetila, Vocational Road, Zaman | 2019-07-08 | NQ1007 | 9.3 | 552 | 9.3 | 553 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6624 | 2135.9997 | 97.9893
MBZ-1.RR.353.1 | 24284889147059 | Moulovibazar, Orangetila, Vocational Road, Md. Eklas | 2019-07-08 | NQ1007 | 39.6 | 554 | 39.6 | 555 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 39.6 | 39.6 | 2.376 | 2.376 | 0.0007168 | 100% | 0% | 2.376 | 2.376 | 0.0011869 | 28 | 0.047631 | 0.047631 |  | 0 | 0 | 6624 | 2135.9997 | 417.2447
MBZ-1.RR.354.1 | 24285069147065 | Moulovibazar, Orangetila, Vocational Road, Mashfakul Islam | 2019-07-08 | NQ1007 | 10.9 | 556 | 10.9 | 557 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6624 | 2135.9997 | 114.8476
MBZ-1.RR.355.1 | 24285419147015 | Moulovibazar, West Borshijura, T.B. Hospital Road, Md. Suruj Mia | 2019-07-09 | NQ1007 | 6.5 | 558 | 6.5 | 559 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6624 | 2135.9997 | 68.4871
MBZ-1.RR.356.1 | 24285419147015 | Moulovibazar, West Borshijura, T.B. Hospital Road, Md. Imanod Mia | 2019-07-09 | NQ1007 | 3.9 | 561 | 3.9 | 562 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6624 | 2135.9997 | 41.0923
MBZ-1.RR.356.2 | 24285419147015 | Moulovibazar, West Borshijura, T.B. Hospital Road, Md. Imanod Mia | 2022-04-06 | NQ1007 | 3.9 | 127 | 3.9 | 128 | 2022-04-06 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 4344 | 2135.9997 | 30.397
MBZ-1.RR.357.1 | 24285279147003 | Moulovibazar, West Borshijura, T.B. Hospital Road, Nazim Mia | 2019-07-09 | NQ1007 | 3.1 | 563 | 3.1 | 564 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6624 | 2135.9997 | 32.6631
MBZ-1.RR.357.2 | 24285279147003 | Moulovibazar, West Borshijura, T.B. Hospital Road, Nazim Mia | 2022-04-06 | NQ1007 | 5.3 | 129 | 5.3 | 130 | 2022-04-06 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 4344 | 2135.9997 | 41.3088
MBZ-1.RR.358.1 | 24285469147012 | Moulovibazar, West Borshijura, T.B. Hospital Road, Md. Shajahan | 2019-07-09 | NQ1007 | 8.3 | 565 | 8.3 | 566 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6624 | 2135.9997 | 87.4528
MBZ-1.RR.359.1 | 24285619147012 | Moulovibazar, West Borshijura, T.B. Hospital Road, Md. Shomidullah | 2019-07-09 | NQ1007 | 12.6 | 567 | 12.7 | 568 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6624 | 2135.9997 | 133.8133
MBZ-1.RR.360.1 | 24285619147012 | Moulovibazar, West Borshijura, T.B. Hospital Road, Md. Lokman | 2019-07-09 | NQ1007 | 3.2 | 569 | 3.2 | 570 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6624 | 2135.9997 | 33.7167
MBZ-1.RR.361.1 | 24285719147010 | Moulovibazar, West Borshijura, T.B. Hospital Road, H # 75, Arif Villa | 2019-07-09 | NQ1007 | 5.5 | 571 | 5.5 | 572 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6624 | 2135.9997 | 57.9506
MBZ-1.RR.361.2 | 24285719147010 | Moulovibazar, West Borshijura, T.B. Hospital Road, H # 75, Arif Villa | 2021-01-25 | NQ1007 | 21.1 | 82 | 21.1 | 83 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 21.1 | 21.1 | 1.266 | 1.266 | 0.0007168 | 100% | 0% | 1.266 | 1.266 | 0.0011869 | 28 | 0.025379 | 0.025379 |  | 0 | 0 | 6624 | 2135.9997 | 222.3198
MBZ-1.RR.362.1 | 24285859147009 | Moulovibazar, West Borshijura, T.B. Hospital Road, Banani, Kendrio Khanka Shorif | 2019-07-09 | NQ1007 | 6.8 | 573 | 6.8 | 574 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6624 | 2135.9997 | 71.6481
MBZ-1.RR.363.1 | 24285829146598 | Moulovibazar, West Borshijura, T.B. Hospital Road, Shakil | 2019-07-09 | NQ1007 | 12.9 | 575 | 12.9 | 576 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6624 | 2135.9997 | 135.9206
MBZ-1.RR.364.1 | 24290059146577 | Moulovibazar, West Borshijura, T.B. Hospital Road, Banani, H # 28, Munir Villa | 2019-07-09 | NQ1007 | 2.3 | 579 | 2.3 | 580 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6888 | 1871.9997 | 24.2339
MBZ-1.RR.365.1 | 24290239146586 | Moulovibazar, West Borshijura, T.B. Hospital Road, Banani, Md. Koisur Rahman | 2019-07-09 | NQ1007 | 4.4 | 581 | 4.5 | 582 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6888 | 1871.9997 | 47.4142
MBZ-1.RR.366.1 | 24290469146564 | Moulovibazar, West Borshijura, Banani, T.B. Hospital Road, Sumon Box | 2019-07-10 | NQ1007 | 11.1 | 609 | 11.1 | 610 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6888 | 1871.9997 | 116.9549
MBZ-1.RR.367.1 | 24290549146574 | Moulovibazar, West Borshijura, Banani, T.B. Hospital Road, Back Side of Mokbul Hossen | 2019-07-10 | NQ1007 | 3.9 | 611 | 3.9 | 612 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6888 | 1871.9997 | 41.0923
MBZ-1.RR.368.1 | 24290469146564 | Moulovibazar, West Borshijura, Banani, T.B. Hospital Road, Romendro Lal Bhumik | 2019-07-10 | NQ1007 | 30.8 | 614 | 30.8 | 615 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 30.8 | 30.8 | 1.848 | 1.848 | 0.0007168 | 100% | 0% | 1.848 | 1.848 | 0.0011869 | 28 | 0.037046 | 0.037046 |  | 0 | 0 | 6888 | 1871.9997 | 324.5236
MBZ-1.RR.369.1 | 24285809146578 | Moulovibazar, West Borshijura, Banani, T.B. Hospital Road, Abdul Wahid | 2019-07-10 | NQ1007 | 3.3 | 616 | 3.3 | 617 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6888 | 1871.9997 | 34.7704
MBZ-1.RR.370.1 | 24285849146568 | Moulovibazar, West Borshijura, T.B. Hospital Road, Ward # 2, H # 175, Fajlur Rahman | 2019-07-10 | NQ1007 | 9.1 | 619 | 9.1 | 620 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 1752 | 0 | 5136 | 1871.9997 | 76.7056
MBZ-1.RR.371.1 | 24291819145524 | Moulovibazar, West Bazar, Old Hospital Sorok, Rokib | 2019-07-16 | MP1032 | 3.3 | 721 | 3.3 | 722 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6912 | 1847.9997 | 34.7704
MBZ-1.RR.372.1 | 24291829145524 | Moulovibazar, West Bazar, Old Hospital Sorok, Fajlu Talukdar | 2019-07-16 | MP1032 | 11.9 | 723 | 11.9 | 724 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6912 | 1847.9997 | 125.3841
MBZ-1.RR.372.2 | 24291829145524 | Moulovibazar, West Bazar, Old Hospital Sorok, Fajlu Talukdar | 2019-07-16 | MP1032 | 3.5 | 725 | 3.5 | 726 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6912 | 1847.9997 | 36.8777
MBZ-1.RR.373.1 | 24292269145514 | Moulovibazar, M Saifur Rohman Road, Nur Brothers Cloth Store | 2019-07-16 | MP1032 | 11.6 | 729 | 11.6 | 730 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6912 | 1847.9997 | 122.2232
MBZ-1.RR.374.1 | 24292299145529 | Moulovibazar, M Saifur Rohman Road, A K Collection | 2019-07-16 | MP1032 | 6 | 731 | 6.1 | 732 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6912 | 1847.9997 | 64.2725
MBZ-1.RR.375.1 | 24292309145555 | Moulovibazar, M Saifur Rohman Road, Ali Shan | 2019-07-16 | MP1032 | 3.1 | 733 | 3.1 | 734 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6912 | 1847.9997 | 32.6631
MBZ-1.RR.376.1 | 24292369145572 | Moulovibazar, M Saifur Rohman Road, NRB Bank | 2019-07-16 | MP1032 | 11.5 | 735 | 11.5 | 736 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6912 | 1847.9997 | 121.1695
MBZ-1.RR.377.1 | 24292419145597 | Moulovibazar, M Saifur Rohman Road, Raihan Uddin | 2019-07-16 | MP1032 | 10.9 | 737 | 10.9 | 738 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6912 | 1847.9997 | 114.8476
MBZ-1.RR.377.2 | 24292419145597 | Moulovibazar, M Saifur Rohman Road, Raihan Uddin | 2019-07-16 | MP1032 | 13.6 | 739 | 13.6 | 740 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6912 | 1847.9997 | 143.2961
MBZ-1.RR.378.1 | 24292509145590 | Moulovibazar, M Saifur Rohman Road, Gaucia Fashion | 2019-07-16 | MP1032 | 4.4 | 741 | 4.4 | 742 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6912 | 1847.9997 | 46.3605
MBZ-1.RR.379.1 | 24292569146032 | Moulovibazar, M Saifur Rohman Road, Munnaf Mia | 2019-07-16 | MP1032 | 9.1 | 743 | 9.1 | 744 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6912 | 1847.9997 | 95.882
MBZ-1.RR.380.1 | 24293389146220 | Moulovibazar, Shantibagh, Shabtibagh Road, SR Vobon | 2019-07-17 | MP1032 | 6 | 17 | 6 | 18 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6840 | 1919.9997 | 63.2189
MBZ-1.RR.381.1 | 24293559146244 | Moulovibazar, Shantibagh, Shabtibagh Road, Roton Kanti Chakladar | 2019-07-17 | MP1032 | 6.5 | 19 | 6.5 | 20 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6840 | 1919.9997 | 68.4871
MBZ-1.RR.382.1 | 24292959146235 | Moulovibazar, Shantibagh, Ali Amjad Girl School Road, Partho Sarothi Vhoumik | 2019-07-17 | MP1032 | 7.2 | 21 | 7.2 | 22 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6840 | 1919.9997 | 75.8627
MBZ-1.RR.382.2 | 24292959146235 | Moulovibazar, Shantibagh, Ali Amjad Girl School Road, Partho Sarothi Vhoumik | 2022-10-13 | MN1018 | 3.6 | 40 | 3.6 | 41 | 2022-10-13 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 0 | 1919.9997 | 8.3137
MBZ-1.RR.383.1 | 24292869146244 | Moulovibazar, Shantibagh, Ali Amjad Girl School Road, Kali Mondir | 2019-07-17 | MP1032 | 9.8 | 23 | 9.8 | 24 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6840 | 1919.9997 | 103.2575
MBZ-1.RR.383.2 | 24292869146244 | Moulovibazar, Shantibagh, Ali Amjad Girl School Road, Kali Mondir | 2022-10-13 | MN1018 | 4.5 | 38 | 4.5 | 39 | 2022-10-13 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 0 | 1919.9997 | 10.3921
MBZ-1.RR.384.1 | 24292659145369 | Moulovibazar, East Borohat, Kheyaghat Road, Abdul Awal | 2019-07-17 | MP1032 | 11.7 | 25 | 11.7 | 26 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6936 | 1823.9997 | 123.2768
MBZ-1.RR.385.1 | 24292709145341 | Moulovibazar, East Borohat, Mofol Miar Basa | 2019-07-17 | MP1032 | 12 | 27 | 12 | 28 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6936 | 1823.9997 | 126.4378
MBZ-1.RR.386.1 | 24292709145341 | Moulovibazar, East Borohat, Mofol Miar Basa, Mokbul Mia | 2019-07-17 | MP1032 | 10.4 | 29 | 10.4 | 30 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6936 | 1823.9997 | 109.5794
MBZ-1.RR.387.1 | 24292709145341 | Moulovibazar, East Borohat, Mofol Miar Basa, Mokbul Mia | 2019-07-17 | MP1032 | 5.8 | 31 | 5.8 | 32 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6936 | 1823.9997 | 61.1116
MBZ-1.RR.388.1 | 24292709145341 | Moulovibazar, East Borohat, Mofol Miar Basa, Mokbul Mia | 2019-07-17 | MP1032 | 12 | 35 | 12 | 36 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6936 | 1823.9997 | 126.4378
MBZ-1.RR.388.2 | 24292709145341 | Moulovibazar, East Borohat, Mofol Miar Basa, Mokbul Mia | 2019-07-17 | MP1032 | 8.7 | 37 | 8.7 | 38 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6936 | 1823.9997 | 91.6674
MBZ-1.RR.389.1 | 24292679145386 | Moulovibazar, East Borohat, Nodirpar, Amjad Ali | 2019-07-17 | MP1032 | 12.4 | 39 | 12.4 | 40 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6936 | 1823.9997 | 130.6524
MBZ-1.RR.390.1 | 24293219145301 | Moulovibazar, East Borohat, Mojammel Haque Road, Azad | 2019-07-17 | MP1032 | 12 | 41 | 12 | 42 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6936 | 1823.9997 | 126.4378
MBZ-1.RR.391.1 | 24293159145304 | Moulovibazar, East Borohat, Mojammel Haque Road, Abu sayed | 2019-07-17 | MP1032 | 3.6 | 43 | 3.6 | 44 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6936 | 1823.9997 | 37.9313
MBZ-1.RR.392.1 | 24294719146120 | Moulovibazar, Gujarai, Bodrul Mia | 2019-07-18 | MP1032 | 11.2 | 70 | 11.2 | 71 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6840 | 1919.9997 | 118.0086
MBZ-1.RR.393.1 | 24294499146110 | Moulovibazar, Gujarai, Raina Begum | 2019-07-18 | MP1032 | 10 | 72 | 9.7 | 73 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 528 | 0 | 6312 | 1919.9997 | 96.0436
MBZ-1.RR.393.2 | 24294499146110 | Moulovibazar, Gujarai, Raina Begum | 2021-01-28 | NQ1007 | 1.6 | 113 | 1.6 | 114 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 528 | 0 | 6312 | 1919.9997 | 15.8422
MBZ-1.RR.394.1 | 24294499146110 | Moulovibazar, Gujarai, Hason Mia | 2019-07-18 | MP1032 | 20.4 | 74 | 20.4 | 75 | 2022-01-01 | [9 empty] | 20.4 | 20.4 | 1.224 | 1.224 | 0.0007168 | 100% | 0% | 1.224 | 1.224 | 0.0011869 | 28 | 0.024537 | 0.024537 |  | 0 | 0
MBZ-1.RR.395.1 | 24294519146074 | Moulovibazar, Gujarai, Abdul Gofur | 2019-07-18 | MP1032 | 6.4 | 76 | 6.4 | 77 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6840 | 1919.9997 | 67.4335
MBZ-1.RR.396.1 | 24294779146104 | Moulovibazar, Gujarai, Gujarai Moddhopara Jame Mosjid | 2019-07-18 | MP1032 | 4.8 | 78 | 4.8 | 79 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6840 | 1919.9997 | 50.5751
MBZ-1.RR.397.1 | 24295109146092 | Moulovibazar, Gujarai, Rasel | 2019-07-18 | MP1032 | 4.7 | 82 | 4.7 | 83 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6840 | 1919.9997 | 49.5215
MBZ-1.RR.398.1 | 24294449146214 | Moulovibazar, Gujarai, Chadnighat, RD # 1, Goutom Ranjan Das | 2019-07-18 | MP1032 | 2.9 | 84 | 2.9 | 85 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6792 | 1967.9997 | 30.5558
MBZ-1.RR.398.2 | 24294449146214 | Moulovibazar, Gujarai, Chadnighat, RD # 1, Goutom Ranjan Das | 2022-04-04 | NQ1007 | 4.7 | 125 | 4.7 | 126 | 2022-04-04 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 4560 | 1967.9997 | 36.9037
MBZ-1.RR.399.1 | 24294519146199 | Moulovibazar, Gujarai, Chadnighat, Abdur Rouf | 2019-07-18 | MP1032 | 13 | 86 | 12.5 | 87 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6792 | 1967.9997 | 131.706
MBZ-1.RR.400.1 | 24294589146201 | Moulovibazar, Gujarai, Chadnighat, Probad Laldhor | 2019-07-18 | MP1032 | 21.7 | 88 | 21.7 | 89 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 6792 | 1967.9997 | 228.6416
MBZ-1.RR.401.1 | 24290379146429 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House Road, Chan Mia | 2019-07-11 | MP1032 | 10.6 | 623 | 10.6 | 624 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6888 | 1871.9997 | 111.6867
MBZ-1.RR.402.1 | 24290379146429 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House Road, Chondrima | 2019-07-11 | MP1032 | 6 | 625 | 6 | 626 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6888 | 1871.9997 | 63.2189
MBZ-1.RR.403.1 | 24290609146416 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House Road, Khan Villa | 2019-07-11 | MP1032 | 8.4 | 627 | 8.4 | 628 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6888 | 1871.9997 | 88.5064
MBZ-1.RR.404.1 | 24290719146409 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House Road, Abdul Khalek Chowdhury | 2019-07-11 | MP1032 | 5.8 | 629 | 5.8 | 630 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6888 | 1871.9997 | 61.1116
MBZ-1.RR.405.1 | 24290719146409 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House Road, Shamsunnahar Khanom | 2019-07-11 | MP1032 | 7.3 | 633 | 7.3 | 634 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6888 | 1871.9997 | 76.9163
MBZ-1.RR.406.1 | 24290299146454 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House by Lane Road, Abdus Subhan | 2019-07-11 | MP1032 | 11.3 | 635 | 11.3 | 636 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6888 | 1871.9997 | 119.0622
MBZ-1.RR.407.1 | 24290299146454 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House by Lane Road, Nabib Villa | 2019-07-11 | MP1032 | 4 | 639 | 4 | 640 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6888 | 1871.9997 | 42.1459
MBZ-1.RR.408.1 | 24290439146468 | Moulvibazar Sadar, Sarkit House Alaka, Sarkit House by Lane Road, Dr. Propullo Suttradhor | 2019-07-11 | MP1032 | 13 | 641 | 13 | 642 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6888 | 1871.9997 | 136.9743
MBZ-1.RR.409.1 | 24292169146099 | Moulvibazar Sadar, Puratun Haspatal Road, Jahanara Emam | 2019-07-13 | MP1032 | 10.4 | 679 | 10.4 | 680 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6912 | 1847.9997 | 109.5794
MBZ-1.RR.409.2 | 24292169146099 | Moulvibazar Sadar, Puratun Haspatal Road, Jahanara Emam | 2019-07-13 | MP1032 | 3.5 | 683 | 3.5 | 684 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6912 | 1847.9997 | 36.8777
MBZ-1.RR.410.1 | 24292169146099 | Moulvibazar Sadar, Puratun Haspatal Road, Jahanara Emam | 2019-07-13 | MP1032 | 11.9 | 685 | 11.9 | 686 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6912 | 1847.9997 | 125.3841
MBZ-1.RR.411.1 | 24292089146093 | Moulvibazar Sadar, Puratun Haspatal Road, Bojlur Rahaman Chowdhury | 2019-07-13 | MP1032 | 17.1 | 687 | 17.1 | 688 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 6912 | 1847.9997 | 180.1738
MBZ-1.RR.411.2 | 24292089146093 | Moulvibazar Sadar, Puratun Haspatal Road, Bojlur Rahaman Chowdhury | 2019-07-13 | MP1032 | 11.5 | 689 | 11.1 | 690 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6912 | 1847.9997 | 116.9549
MBZ-1.RR.412.1 | 24292169146087 | Moulvibazar Sadar, Puratun Haspatal Road, Somru Kuthir | 2019-07-16 | MP1032 | 9.6 | 691 | 9.6 | 692 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6912 | 1847.9997 | 101.1502
MBZ-1.RR.413.1 | 24292169146087 | Moulvibazar Sadar, Puratun Haspatal Road, Abir Villa | 2019-07-16 | MP1032 | 5.7 | 693 | 5.7 | 694 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6912 | 1847.9997 | 60.0579
MBZ-1.RR.413.2 | 24292169146087 | Moulvibazar Sadar, Puratun Haspatal Road, Abir Villa | 2019-07-16 | MP1032 | 9 | 695 | 9 | 696 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6912 | 1847.9997 | 94.8283
MBZ-1.RR.414.1 | 24292189146084 | Moulvibazar Sadar, Puratun Haspatal Road, Kobir Mia | 2019-07-16 | MP1032 | 11 | 697 | 11 | 698 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6912 | 1847.9997 | 115.9013
MBZ-1.RR.415.1 | 24292119146079 | Moulvibazar Sadar, Puratun Haspatal Road, Hannan Mia | 2019-07-16 | MP1032 | 12.4 | 699 | 12.4 | 700 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6912 | 1847.9997 | 130.6524
MBZ-1.RR.416.1 | 24292119146079 | Moulvibazar Sadar, Puratun Haspatal Road, Mannan Mia | 2019-07-16 | MP1032 | 4.7 | 701 | 4.7 | 702 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6912 | 1847.9997 | 49.5215
MBZ-1.RR.417.1 | 24292169146071 | Moulvibazar Sadar, Puratun Haspatal Road, Sobirunnesa | 2019-07-16 | MP1032 | 12.8 | 703 | 12.8 | 704 | 2022-01-01 | 2022-10-16 | MN1018 | 0.2 | 54 | 0.2 | 55 | 2022-10-16 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 5 | 0 | 6907 | 1847.9997
MBZ-1.RR.418.1 | 24292059146064 | Moulvibazar Sadar, Puratun Haspatal Road, Bojlur Roshid | 2019-07-16 | MP1032 | 4.9 | 705 | 4.9 | 706 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6912 | 1847.9997 | 51.6288
MBZ-1.RR.419.1 | 24292249146010 | Moulvibazar Sadar, Moztofa Ali Road, Joshim Ahammod | 2019-07-16 | MP1032 | 8.2 | 707 | 8.2 | 708 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6912 | 1847.9997 | 86.3991
MBZ-1.RR.420.1 | 24292209145588 | Moulvibazar Sadar, Moztofa Ali Road, Ripon Mohit | 2019-07-16 | MP1032 | 7.1 | 709 | 7.1 | 710 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6912 | 1847.9997 | 74.809
MBZ-1.RR.421.1 | 24292009145517 | Moulvibazar Sadar, West Bazar, Puratun Haspatal Road, Azman | 2019-07-16 | MP1032 | 11.7 | 713 | 11.7 | 714 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6912 | 1847.9997 | 123.2768
MBZ-1.RR.421.2 | 24292009145517 | Moulvibazar Sadar, West Bazar, Puratun Haspatal Road, Azman | 2019-07-16 | MP1032 | 4.7 | 715 | 4.7 | 716 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6912 | 1847.9997 | 49.5215
MBZ-1.RR.422.1 | 24292009145517 | Moulvibazar Sadar, West Bazar, Puratun Haspatal Road, Jillur Rahaman | 2019-07-16 | MP1032 | 9.3 | 717 | 9.3 | 718 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6912 | 1847.9997 | 97.9893
MBZ-1.RR.423.1 | 24292599146118 | Moulvibazar Sadar, Santibag, M. Sayfur Rahaman Road, Kobir Mia | 2019-07-17 | MP1032 | 2.5 | 1 | 2.5 | 2 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6912 | 1847.9997 | 26.3412
MBZ-1.RR.423.2 | 24292599146118 | Moulvibazar Sadar, Santibag, M. Sayfur Rahaman Road, Kobir Mia | 2020-10-06 | NQ1002 | 6.4 | 81 | 6.4 | 82 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6912 | 1847.9997 | 67.4335
MBZ-1.RR.424.1 | 24292849146194 | Moulvibazar Sadar, Santibag, Co- Operative Road, H # 53, Jogodish Dhor | 2019-07-17 | MP1032 | 5.6 | 3 | 5.6 | 4 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6840 | 1919.9997 | 59.0043
MBZ-1.RR.425.1 | 24292899146191 | Moulvibazar Sadar, Santibag, Co- Operative Road, Shotodol | 2019-07-17 | MP1032 | 4.3 | 5 | 4.3 | 6 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6840 | 1919.9997 | 45.3069
MBZ-1.RR.426.1 | 24292919146190 | Moulvibazar Sadar, Santibag, Santibag Road, Adbytasen Adhikari | 2019-07-17 | MP1032 | 10.3 | 9 | 10.3 | 10 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6840 | 1919.9997 | 108.5258
MBZ-1.RR.427.1 | 24293179146204 | Moulvibazar Sadar, Santibag, Santibag Road, Mofazzol Ali | 2019-07-17 | MP1032 | 11.8 | 11 | 11.9 | 12 | 2022-01-01 | [9 empty] | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 | 2022-09-19 12:00 | 0 | 0
MBZ-1.RR.428.1 | 24293249146213 | Moulvibazar Sadar, Santibag, Santibag Road, H. M. Mostak Ahammed | 2019-07-17 | MP1032 | 9.5 | 13 | 9.5 | 14 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6840 | 1919.9997 | 100.0966
MBZ-1.RR.429.1 | 24292949145298 | Moulvibazar Sadar, East Borhat, Word - 6, Rd # 2, Mujammil Mia Road, Khan Manjil | 2019-07-18 | MP1032 | 12.5 | 45 | 12 | 46 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6936 | 1823.9997 | 126.4378
MBZ-1.RR.430.1 | 24292509145256 | Moulvibazar Sadar, East Borhat, Word - 6, Rd # 2, Mujammil Mia Road, Ahad Villa | 2019-07-18 | MP1032 | 9.4 | 47 | 9.4 | 48 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6936 | 1823.9997 | 99.0429
MBZ-1.RR.431.1 | 24292309145287 | Moulvibazar Sadar, East Borhat, Word - 6, Sylhet Road, Abdul Hashib | 2019-07-18 | MP1032 | 3 | 49 | 3 | 50 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6936 | 1823.9997 | 31.6094
MBZ-1.RR.432.1 | 24292349145321 | Moulvibazar Sadar, East Borhat, Word - 6, Sylhet Road, Sumon Homio Hall | 2019-07-18 | MP1032 | 17.3 | 51 | 17.3 | 52 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 6936 | 1823.9997 | 182.2811
MBZ-1.RR.433.1 | 24292389145229 | Moulvibazar Sadar, Borhat, Sylhet Road, Rabbi Ato Enterprize | 2019-07-18 | MP1032 | 10.5 | 53 | 10.5 | 54 | 2022-01-01 | [9 empty] | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0
MBZ-1.RR.434.1 | 24292559145186 | Moulvibazar Sadar, Borhat, Mokambari Road, Abdul Hannan | 2019-07-18 | MP1032 | 11.4 | 55 | 11.4 | 56 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6936 | 1823.9997 | 120.1159
MBZ-1.RR.435.1 | 24292639145185 | Moulvibazar Sadar, Borhat, Mokambari Road, Dhewpasha Villa, Haji Mojmil Mia | 2019-07-18 | MP1032 | 6.9 | 57 | 6.9 | 58 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6936 | 1823.9997 | 72.7017
MBZ-1.RR.436.1 | 24293529145194 | Moulvibazar Sadar, Borhat, Mokambari Road, Uru Mia | 2019-07-18 | MP1032 | 5.7 | 59 | 5.7 | 60 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6936 | 1823.9997 | 60.0579
MBZ-1.RR.437.1 | 24293529145194 | Moulvibazar Sadar, Borhat, Mokambari Road, Muhit Mia | 2019-07-18 | MP1032 | 4.1 | 61 | 4.1 | 62 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6936 | 1823.9997 | 43.1996
MBZ-1.RR.438.1 | 24293669145242 | Moulvibazar Sadar, Borhat, Mokambari Road, Shiblu Mia | 2019-07-18 | MP1032 | 11.7 | 63 | 11.8 | 64 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6936 | 1823.9997 | 124.3305
MBZ-1.RR.439.1 | 24293579145261 | Moulvibazar Sadar, Borhat, Mokambari Road, Chowdhury Villa | 2019-07-18 | MP1032 | 3.2 | 65 | 3.1 | 66 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6936 | 1823.9997 | 32.6631
MBZ-1.RR.440.1 | 24293549145282 | Moulvibazar Sadar, East Borhat, Khaya Ghat, Rabeya | 2019-07-18 | MP1032 | 5.9 | 68 | 5.9 | 69 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6936 | 1823.9997 | 62.1652
MBZ-1.RR.441.1 | 24294019145584 | Moulvibazar, Shabia, Word - 3, Rd # 2, Daresh Dotto | 2019-07-20 | MP1032 | 2.8 | 90 | 2.8 | 91 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6840 | 1919.9997 | 29.5021
MBZ-1.RR.442.1 | 24293719145580 | Moulvibazar, Shabia, Word - 3, Rd # 2, Ismail | 2019-07-20 | MP1032 | 11.8 | 92 | 11.8 | 93 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6840 | 1919.9997 | 124.3305
MBZ-1.RR.442.2 | 24293719145580 | Moulvibazar, Shabia, Word - 3, Rd # 2, Ismail | 2019-07-20 | MP1032 | 2.9 | 96 | 2.9 | 97 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6840 | 1919.9997 | 30.5558
MBZ-1.RR.443.1 | 24293659145590 | Moulvibazar, Shabia, Word - 3, Rd # 2, Benaronjon Dotto | 2019-07-20 | MP1032 | 8 | 98 | 8 | 99 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6840 | 1919.9997 | 84.2919
MBZ-1.RR.444.1 | 24293539145566 | Moulvibazar, Shabia, Word - 3, Rd # 2, Mostofa | 2019-07-20 | MP1032 | 9.3 | 100 | 9.3 | 101 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6840 | 1919.9997 | 97.9893
MBZ-1.RR.444.2 | 24293539145566 | Moulvibazar, Shabia, Word - 3, Rd # 2, Mostofa | 2022-04-04 | NQ1007 | 5.7 | 123 | 5.7 | 124 | 2022-04-04 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 4608 | 1919.9997 | 44.7555
MBZ-1.RR.445.1 | 24293539145566 | Moulvibazar, Shabia, Word - 3, Rd # 2, Mostofa | 2019-07-20 | MP1032 | 7.1 | 104 | 7.1 | 105 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6840 | 1919.9997 | 74.809
MBZ-1.RR.445.2 | 24293539145566 | Moulvibazar, Shabia, Word - 3, Rd # 2, Mostofa | 2019-07-20 | MP1032 | 8.1 | 106 | 8.1 | 107 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6840 | 1919.9997 | 85.3455
MBZ-1.RR.446.1 | 24293229145541 | Moulvibazar, Shabia, Word - 3, Kamal Shaha Road, Monoara | 2019-07-20 | MP1032 | 10.7 | 108 | 10.7 | 109 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6840 | 1919.9997 | 112.7403
MBZ-1.RR.447.1 | 24293229145541 | Moulvibazar, Shabia, Word - 3, Kamal Shaha Road, Shofiqur | 2019-07-20 | MP1032 | 18.6 | 110 | 17.9 | 111 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 6840 | 1919.9997 | 188.603
MBZ-1.RR.448.1 | 24293179145502 | Moulvibazar, Shabia, Shaha Moulali Road, Sobibullah | 2019-07-20 | MP1032 | 4.4 | 112 | 4.4 | 113 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6840 | 1919.9997 | 46.3605
MBZ-1.RR.449.1 | 24293689145511 | Moulvibazar, Shabia, Shaha Moulali Road, Sudhir Chondro Pal | 2019-07-20 | MP1032 | 11.3 | 114 | 11.3 | 115 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6840 | 1919.9997 | 119.0622
MBZ-1.RR.450.1 | 24293939145467 | Moulvibazar, Shabia, Word - 3, Shaha Moulali Road, Ripon | 2019-07-20 | MP1032 | 11.1 | 116 | 11.1 | 117 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6840 | 1919.9997 | 116.9549
MBZ-1.RR.451.1 | 24294069146336 | West Soyerpur, Forest Office Road, Joynal Haque Chowdhury | 2019-07-16 | LX1011 | 12.7 | 82 | 12 | 83 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6792 | 1967.9997 | 126.4378
MBZ-1.RR.452.1 | 24293719146313 | Shahbag, Kashinath Road, H # 156, Gofur Villa | 2019-07-16 | LX1011 | 14.1 | 84 | 13.4 | 85 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6792 | 1967.9997 | 141.1888
MBZ-1.RR.453.1 | 24293719146313 | Shahbag, Kashinath Road, H # 157, Zaman | 2019-07-16 | LX1011 | 8 | 87 | 8 | 88 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6792 | 1967.9997 | 84.2919
MBZ-1.RR.454.1 | 24293719146313 | Shahbag, Kashinath Road, H # 159, Rafiqul Hossen Chowdhury | 2019-07-16 | LX1011 | 5 | 89 | 5 | 90 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6792 | 1967.9997 | 52.6824
MBZ-1.RR.455.1 | 24293489146317 | Shahbag, Kashinath Road, Sirazul Islam (Manik) | 2019-07-16 | LX1011 | 13.2 | 91 | 13.2 | 92 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6792 | 1967.9997 | 139.0816
MBZ-1.RR.456.1 | 24293489146317 | Shahbag, Kashinath Road, H # 163, Zohir Ahmed | 2019-07-16 | LX1011 | 13.4 | 95 | 13.4 | 96 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6792 | 1967.9997 | 141.1888
MBZ-1.RR.457.1 | 24293489146317 | Shahbag, Kashinath Road, H # 163, Zohir Ahmed | 2019-07-16 | LX1011 | 9.3 | 97 | 9.3 | 98 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6792 | 1967.9997 | 97.9893
MBZ-1.RR.458.1 | 24293369146315 | Shahbag, Kashinath Road, H # 562/2, Abdul High | 2019-07-16 | LX1011 | 2.9 | 101 | 2.9 | 102 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6792 | 1967.9997 | 30.5558
MBZ-1.RR.459.1 | 24293599146339 | Shahbag, Kashinath Road, H # 53, Abdul Hamid | 2019-07-16 | LX1011 | 11.5 | 103 | 11.6 | 104 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6792 | 1967.9997 | 122.2232
MBZ-1.RR.460.1 | 24293759146339 | Shahbag, Kashinath Road, Nahar Lodge | 2019-07-16 | LX1011 | 12.6 | 105 | 12.1 | 106 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6792 | 1967.9997 | 127.4914
MBZ-1.RR.461.1 | 24294429146410 | Soyerpur, Forest Office Road, H # 203, Asadujjaman | 2019-07-17 | LX1011 | 11.9 | 31 | 11.4 | 32 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6816 | 1943.9997 | 120.1159
MBZ-1.RR.462.1 | 24294369146397 | Soyerpur, Forest Office Road, H # 27, Syed Tozommel Ali | 2019-07-17 | LX1011 | 2.6 | 33 | 2.6 | 34 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6816 | 1943.9997 | 27.3949
MBZ-1.RR.463.1 | 24294309146387 | Soyerpur, Forest Office Road, H # 104, Dhorani Chondro Dey | 2019-07-17 | LX1011 | 7.3 | 35 | 7.3 | 36 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6816 | 1943.9997 | 76.9163
MBZ-1.RR.464.1 | 24294719146400 | Soyerpur, Forest Office Road, H # 446/1, Md. Shafiqur Rahman | 2019-07-17 | LX1011 | 7.9 | 37 | 7.9 | 38 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6816 | 1943.9997 | 83.2382
MBZ-1.RR.465.1 | 24294429146455 | Soyerpur, Forest Office Road, Md. Harun Mia | 2019-07-17 | LX1011 | 12.3 | 39 | 12.3 | 40 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6816 | 1943.9997 | 129.5987
MBZ-1.RR.466.1 | 24294429146455 | Soyerpur, Forest Office Road, Syed Mohsin Ali | 2019-07-17 | LX1011 | 9.2 | 41 | 9.2 | 42 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6816 | 1943.9997 | 96.9356
MBZ-1.RR.467.1 | 24294559146495 | Soyerpur, Forest Office Road, Minto Das | 2019-07-17 | LX1011 | 5.4 | 43 | 5.4 | 44 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6816 | 1943.9997 | 56.897
MBZ-1.RR.468.1 | 24294429146497 | Soyerpur, Forest Office Road, Nani Gopal Chokkroborty | 2019-07-17 | LX1011 | 11.8 | 49 | 11.5 | 50 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6816 | 1943.9997 | 121.1695
MBZ-1.RR.469.1 | 24294359146535 | Soyerpur, Majerhati Road, Nipesh Chondro Das | 2019-07-17 | LX1011 | 13.1 | 51 | 13.1 | 52 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6672 | 2087.9997 | 138.0279
MBZ-1.RR.470.1 | 24294359146535 | Soyerpur, Majerhati Road, Nipesh Chondro Das | 2019-07-17 | LX1011 | 8.5 | 53 | 8.5 | 54 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6672 | 2087.9997 | 89.5601
MBZ-1.RR.470.2 | 24294359146535 | Soyerpur, Majerhati Road, Nipesh Chondro Das | 2022-03-23 | NQ1007 | 2.1 | 68 | 2 | 69 | 2022-03-23 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 4728 | 2087.9997 | 16.3965
MBZ-1.RR.471.1 | 24293099147157 | East Soyerpur, Kheyagat Road , Md. Sadikur Rahman | 2019-07-17 | LX1011 | 11.5 | 55 | 11.5 | 56 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6672 | 2087.9997 | 121.1695
MBZ-1.RR.472.1 | 24293099147157 | East Soyerpur, Kheyagat Road, Beside Giasuddin Ahmaed | 2019-07-17 | LX1011 | 13.4 | 57 | 13.4 | 58 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6672 | 2087.9997 | 141.1888
MBZ-1.RR.473.1 | 24293139147144 | East Soyerpur, Kheyagat Road, H # 207, Firoza Begum | 2019-07-17 | LX1011 | 11.7 | 59 | 11.7 | 60 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6672 | 2087.9997 | 123.2768
MBZ-1.RR.473.2 | 24293139147144 | East Soyerpur, Kheyagat Road, H # 207, Firoza Begum | 2019-07-17 | LX1011 | 2.5 | 63 | 2.5 | 64 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6672 | 2087.9997 | 26.3412
MBZ-1.RR.474.1 | 24293139147144 | East Soyerpur, Kheyagat Road, Abdul Basir | 2019-07-17 | LX1011 | 4.9 | 67 | 4.9 | 68 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6768 | 1991.9997 | 51.6288
MBZ-1.RR.475.1 | 24292169148124 | Matar Kapon, Shimultola Bazar Road, Hazi Mofiz | 2019-07-18 | LX1011 | 10 | 89 | 10 | 90 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6624 | 2135.9997 | 105.3648
MBZ-1.RR.476.1 | 24292169148124 | Matar Kapon, Shimultola Bazar Road, Hazi Mofiz | 2019-07-18 | LX1011 | 4.1 | 91 | 4.1 | 92 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6624 | 2135.9997 | 43.1996
MBZ-1.RR.477.1 | 24291799148128 | Matar Kapon, Shimultola Bazar Road, Kanu Ram Suklo Boddho | 2019-07-18 | LX1011 | 3.3 | 93 | 3.3 | 94 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6624 | 2135.9997 | 34.7704
MBZ-1.RR.478.1 | 24291689148118 | Matar Kapon, Shimultola Bazar Road, Krishno Dev | 2019-07-18 | LX1011 | 10.8 | 95 | 10.8 | 96 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6624 | 2135.9997 | 113.794
MBZ-1.RR.479.1 | 24291689148118 | Matar Kapon, Shimultola Bazar Road, Sonjite Dev | 2019-07-18 | LX1011 | 7.1 | 97 | 7.1 | 98 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 4 | 0 | 6620 | 2135.9997 | 74.7749
MBZ-1.RR.480.1 | 24291099148113 | Matar Kapon, Shimultola Bazar , Rehena Shafi | 2019-07-18 | LX1011 | 4.9 | 99 | 4.9 | 100 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6624 | 2135.9997 | 51.6288
MBZ-1.RR.481.1 | 24290939148115 | Matar Kapon, Shimultola Bazar , Roich Mia | 2019-07-18 | LX1011 | 5.9 | 101 | 5.9 | 102 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 48 | 0 | 6576 | 2135.9997 | 61.8246
MBZ-1.RR.482.1 | 24291189148154 | Matar Kapon, Beside Chiarman Bari Road, Fazlur Rahman | 2019-07-18 | LX1011 | 16.8 | 103 | 16.8 | 104 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6624 | 2135.9997 | 177.0129
MBZ-1.RR.482.2 | 24291189148154 | Matar Kapon, Beside Chiarman Bari Road, Fazlur Rahman | 2021-01-26 | NQ1007 | 4.7 | 92 | 4.7 | 93 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6624 | 2135.9997 | 49.5215
MBZ-1.RR.483.1 | 24291189148154 | Matar Kapon, Beside Chiarman Bari Road, Jitendro Dev | 2019-07-18 | LX1011 | 12.4 | 105 | 13.2 | 106 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6624 | 2135.9997 | 139.0816
MBZ-1.RR.483.2 | 24291189148154 | Matar Kapon, Beside Chiarman Bari Road, Jitendro Dev | 2021-01-26 | NQ1007 | 14 | 94 | 14 | 95 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6624 | 2135.9997 | 147.5107
MBZ-1.RR.484.1 | 24291419148159 | Matar Kapon, Beside Chiarman Bari Road, Sotish Dev | 2019-07-18 | LX1011 | 10.5 | 107 | 10.5 | 108 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6624 | 2135.9997 | 110.6331
MBZ-1.RR.484.2 | 24291419148159 | Matar Kapon, Beside Chiarman Bari Road, Sotish Dev | 2022-10-04 | MN1018 | 24.7 | 24 | 24.7 | 25 | 2022-10-04 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 24.7 | 24.7 | 1.482 | 1.482 | 0.0007168 | 100% | 0% | 1.482 | 1.482 | 0.0011869 | 28 | 0.029709 | 0.029709 |  | 0 | 0 | 0 | 2135.9997 | 63.4585
MBZ-1.RR.485.1 | 24291419148159 | Matar Kapon, Beside Chiarman Bari Road, Anil Dev | 2019-07-18 | LX1011 | 5.6 | 109 | 5.6 | 110 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6624 | 2135.9997 | 59.0043
MBZ-1.RR.486.1 | 24294689146302 | Chandnighat, South Mulaim, Tofazzel | 2019-07-20 | LX1011 | 11.6 | 111 | 11.6 | 112 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6792 | 1967.9997 | 122.2232
MBZ-1.RR.487.1 | 24294689146302 | Chandnighat, South Mulaim, Azizul Mia | 2019-07-20 | LX1011 | 8.6 | 113 | 8.6 | 114 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6792 | 1967.9997 | 90.6137
MBZ-1.RR.488.1 | 24294839146303 | Chandnighat, South Mulaim, Fazlu Mia | 2019-07-20 | LX1011 | 13.6 | 116 | 13.6 | 117 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6792 | 1967.9997 | 143.2961
MBZ-1.RR.489.1 | 24294839146303 | Chandnighat, South Mulaim, Tofazzel | 2019-07-20 | LX1011 | 11.4 | 118 | 11.1 | 119 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6792 | 1967.9997 | 116.9549
MBZ-1.RR.490.1 | 24295099146296 | Chandnighat, South Mulaim, Hazi.A.Rahman | 2019-07-20 | LX1011 | 10.5 | 120 | 10.5 | 121 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6792 | 1967.9997 | 110.6331
MBZ-1.RR.501.1 | 24293819146308 | Moulavi Bazar, Forest Office Road, Abdul Gagur | 2019-07-16 | LX1011 | 12.7 | 76 | 12.7 | 77 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6792 | 1967.9997 | 133.8133
MBZ-1.RR.502.1 | 24293819146308 | Moulavi Bazar, Forest Office Road, Ramendro | 2019-07-16 | LX1011 | 8.9 | 78 | 8.9 | 79 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6792 | 1967.9997 | 93.7747
MBZ-1.RR.502.2 | 24293819146308 | Moulavi Bazar, Forest Office Road, Ramendro | 2021-01-28 | NQ1003 | 8 | 157 | 8 | 158 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6792 | 1967.9997 | 84.2919
MBZ-1.RR.503.1 | 24292899146415 | Moulavi Bazar, Soiyarpur School Road, Opposite of Baitul Aman Jame Masjid, Khokon | 2019-07-17 | LX1011 | 8.2 | 1 | 7.6 | 2 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6816 | 1943.9997 | 80.0773
MBZ-1.RR.504.1 | 24293019146416 | Moulavi Bazar, Soiyarpur School Road, Mubarok Vila | 2019-07-17 | LX1011 | 11.4 | 3 | 11.4 | 4 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6816 | 1943.9997 | 120.1159
MBZ-1.RR.504.2 | 24293019146416 | Moulavi Bazar, Soiyarpur School Road, Mubarok Vila | 2019-07-17 | LX1011 | 13.2 | 5 | 13.3 | 6 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6816 | 1943.9997 | 140.1352
MBZ-1.RR.505.1 | 24293679146451 | Moulavi Bazar, Soiyarpur School Road, Sojit Bhattacharjo, H # 42 | 2019-07-17 | LX1011 | 8.7 | 7 | 8.7 | 8 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6816 | 1943.9997 | 91.6674
MBZ-1.RR.506.1 | 24293889146433 | Moulavi Bazar, Soiyarpur School Road, Basudeb Rai | 2019-07-17 | LX1011 | 7.4 | 9 | 7.4 | 10 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6816 | 1943.9997 | 77.97
MBZ-1.RR.507.1 | 24293939146435 | Moulavi Bazar, Soiyarpur School Road, Mukhit Vila | 2019-07-17 | LX1011 | 6 | 11 | 6 | 12 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6816 | 1943.9997 | 63.2189
MBZ-1.RR.508.1 | 24293979146432 | Moulavi Bazar, Soiyarpur School Road, Kiron, H # 55 | 2019-07-17 | LX1011 | 5.9 | 13 | 5.9 | 14 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6816 | 1943.9997 | 62.1652
MBZ-1.RR.509.1 | 24294089146424 | Moulavi Bazar, Soiyarpur School Road, Girindro Pal Own Rd, Shyamol Kumar | 2019-07-17 | LX1011 | 13.5 | 15 | 13.5 | 16 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6816 | 1943.9997 | 142.2425
MBZ-1.RR.510.1 | 24294189146431 | Moulavi Bazar, Soiyarpur School Road, Nikhil | 2019-07-17 | LX1011 | 10 | 19 | 10 | 20 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6816 | 1943.9997 | 105.3648
MBZ-1.RR.511.1 | 24294189146431 | Moulavi Bazar, Soiyarpur School Road, Binoy Kormokar | 2019-07-17 | LX1011 | 11.1 | 21 | 11.1 | 22 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6816 | 1943.9997 | 116.9549
MBZ-1.RR.512.1 | 24294189146431 | Moulavi Bazar, Soiyarpur School Road, Upesh Pal | 2019-07-17 | LX1011 | 11.2 | 23 | 11.2 | 24 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6816 | 1943.9997 | 118.0086
MBZ-1.RR.513.1 | 24294189146431 | Moulavi Bazar, Soiyarpur School Road, Putul Pal | 2019-07-17 | LX1011 | 8.9 | 25 | 8.9 | 26 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6816 | 1943.9997 | 93.7747
MBZ-1.RR.514.1 | 24294339146435 | Moulavi Bazar, Soiyarpur School Road, Somiron Pal | 2019-07-17 | LX1011 | 7.4 | 27 | 7.4 | 28 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6816 | 1943.9997 | 77.97
MBZ-1.RR.515.1 | 24294409146431 | Moulavi Bazar, Soiyarpur School Road, Ronjon Pal Ronju | 2019-07-17 | LX1011 | 10.3 | 29 | 10.3 | 30 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6816 | 1943.9997 | 108.5258
MBZ-1.RR.516.1 | 24292029147413 | Moulavi Bazar, Mathar Kapon, Road # 1, Sabbir Ahamed, H # 20 | 2019-07-18 | LX1011 | 11.6 | 69 | 11.6 | 70 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6624 | 2135.9997 | 122.2232
MBZ-1.RR.517.1 | 24292169147417 | Moulavi Bazar, Mathar Kapon, Road # 1, Word # 7, Abdul Goni | 2019-07-18 | LX1011 | 5.5 | 71 | 5.5 | 72 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6624 | 2135.9997 | 57.9506
MBZ-1.RR.518.1 | 24292209147418 | Moulavi Bazar, Mathar Kapon, Road # 1, Word # 7, Dewan Mokoddas | 2019-07-18 | LX1011 | 9.1 | 73 | 9.1 | 74 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6624 | 2135.9997 | 95.882
MBZ-1.RR.519.1 | 24292309147419 | Moulavi Bazar, Mathar Kapon, Road # 1, Word # 7, Md Mokbul Vila | 2019-07-18 | LX1011 | 11.7 | 75 | 11.1 | 76 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6624 | 2135.9997 | 116.9549
MBZ-1.RR.520.1 | 24292569147420 | Moulavi Bazar, Mathar Kapon, Road # 1, Word # 7, Rahman, H # 36 | 2019-07-18 | LX1011 | 13.4 | 77 | 12.8 | 78 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6624 | 2135.9997 | 134.867
MBZ-1.RR.521.1 | 24291919147549 | Moulavi Bazar, Mathar Kapon, Monu Barrage Road, Soiyod Monjil | 2019-07-18 | LX1011 | 11.4 | 81 | 11.1 | 82 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6624 | 2135.9997 | 116.9549
MBZ-1.RR.522.1 | 24291919147549 | Moulavi Bazar, Mathar Kapon, Monu Barrage Road, Soiyod Monjil | 2019-07-18 | LX1011 | 11.7 | 83 | 11.7 | 84 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6624 | 2135.9997 | 123.2768
MBZ-1.RR.523.1 | 24292479147566 | Moulavi Bazar, Mathar Kapon, Monu Barrage Road, Akikun Nahar | 2019-07-18 | LX1011 | 9.8 | 85 | 9.8 | 86 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6624 | 2135.9997 | 103.2575
MBZ-1.RR.524.1 | 24292609147594 | Moulavi Bazar, Mathar Kapon, Monu Barrage Road, Fahim Vila | 2019-07-18 | LX1011 | 9.3 | 87 | 8.6 | 88 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6624 | 2135.9997 | 90.6137
MBZ-1.RR.525.1 | 24303459146246 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Abdul Karim | 2019-07-20 | LX1011 | 10.8 | 137 | 10.8 | 138 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6768 | 1991.9997 | 113.794
MBZ-1.RR.526.1 | 24303459146246 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Shah Jahan Khan | 2019-07-20 | LX1011 | 8.7 | 141 | 8.7 | 142 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6768 | 1991.9997 | 91.6674
MBZ-1.RR.527.1 | 24304099146084 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Joshim | 2019-07-20 | LX1011 | 14.4 | 143 | 14.4 | 144 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6768 | 1991.9997 | 151.7253
MBZ-1.RR.528.1 | 24304099146084 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Shofique Mia | 2019-07-20 | LX1011 | 11.2 | 145 | 11.3 | 146 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6768 | 1991.9997 | 119.0622
MBZ-1.RR.529.1 | 24304099146084 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Salek Mia | 2019-07-20 | LX1011 | 11.5 | 147 | 11.5 | 148 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6768 | 1991.9997 | 121.1695
MBZ-1.RR.530.1 | 24304099146084 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Mosael | 2019-07-20 | LX1011 | 13.9 | 149 | 13.9 | 150 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6768 | 1991.9997 | 146.4571
MBZ-1.RR.530.2 | 24304099146084 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Mosael | 2019-07-20 | LX1011 | 9.6 | 151 | 9.6 | 152 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6768 | 1991.9997 | 101.1502
MBZ-1.RR.531.1 | 24304169146084 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Jahangir | 2019-07-20 | LX1011 | 12.7 | 153 | 12.7 | 154 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6768 | 1991.9997 | 133.8133
MBZ-1.RR.532.1 | 24303929146058 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Musaeed Hosen | 2019-07-20 | LX1011 | 3.5 | 157 | 3.5 | 158 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6768 | 1991.9997 | 36.8777
MBZ-1.RR.533.1 | 24303929146058 | Moulavi Bazar, Mollik Sarai, Akatuna Road, Musaeed Hosen | 2019-07-20 | LX1011 | 10.1 | 159 | 10.1 | 160 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6768 | 1991.9997 | 106.4185
MBZ-1.RR.534.1 | 24305499146290 | Moulavi Bazar, Ekatuna, Ouail Road, Ismail | 2019-07-21 | LX1011 | 7.3 | 161 | 7.3 | 162 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6816 | 1943.9997 | 76.9163
MBZ-1.RR.535.1 | 24305499146290 | Moulavi Bazar, Ekatuna, Ouail Road,Jorif Mia | 2019-07-21 | LX1011 | 7.1 | 163 | 7.1 | 164 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6816 | 1943.9997 | 74.809
MBZ-1.RR.536.1 | 24305769146259 | Moulavi Bazar, Ekatuna, Ouail Road,Roshik | 2019-07-21 | LX1011 | 12.5 | 165 | 12.3 | 166 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6816 | 1943.9997 | 129.5987
MBZ-1.RR.537.1 | 24305939146213 | Moulavi Bazar, Ekatuna, Ouail Road, Asrofa | 2019-07-21 | LX1011 | 4.8 | 167 | 5 | 168 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6816 | 1943.9997 | 52.6824
MBZ-1.RR.538.1 | 24310709145560 | Moulavi Bazar, Kochua, Uluail Road, Md Jomir Vila | 2019-07-21 | LX1011 | 13.4 | 169 | 13.4 | 170 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6816 | 1943.9997 | 141.1888
MBZ-1.RR.539.1 | 24310459145459 | Moulavi Bazar, Uluail, Sheikh Bari Road, Sheikh Abdul Rohim | 2019-07-21 | LX1011 | 12.2 | 171 | 12.2 | 172 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6816 | 1943.9997 | 128.5451
MBZ-1.RR.540.1 | 24310829145406 | Moulavi Bazar, Uluail, Uluail Road, Beside Old Jame Masjid, Ahmadur Rahman Chowdhury | 2019-07-21 | LX1011 | 5.9 | 173 | 5.9 | 174 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6816 | 1943.9997 | 62.1652
MBZ-1.RR.541.1 | 24311439146075 | Moulavi Bazar, Kochua, Ukil Uddin | 2019-07-21 | LX1011 | 9.6 | 175 | 9.6 | 176 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6816 | 1943.9997 | 101.1502
MBZ-1.RR.542.1 | 24312269145186 | Moulavi Bazar, Uluail, Ward # 4, Abdul Bari | 2019-07-22 | LX1011 | 13.4 | 220 | 13 | 221 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6816 | 1943.9997 | 136.9743
MBZ-1.RR.542.2 | 24312269145186 | Moulavi Bazar, Uluail, Ward # 4, Abdul Bari | 2022-03-27 | NQ1007 | 6.7 | 97 | 6.7 | 98 | 2022-03-27 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 4776 | 1943.9997 | 54.1546
MBZ-1.RR.542.3 | 24312269145186 | Moulavi Bazar, Uluail, Ward # 4, Abdul Bari | 2022-10-12 | MN1018 | 5.6 | 36 | 5.7 | 37 | 2022-10-12 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 0 | 1943.9997 | 13.3279
MBZ-1.RR.543.1 | 24311769145253 | Moulavi Bazar, Uluail, Ward # 4, Altafur Rahman | 2019-07-22 | LX1011 | 17.9 | 222 | 17.9 | 223 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 6816 | 1943.9997 | 188.603
MBZ-1.RR.544.1 | 24311769145253 | Moulavi Bazar, Uluail, Ward # 4, Abdul Bari | 2019-07-22 | LX1011 | 12.9 | 224 | 12.9 | 225 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6816 | 1943.9997 | 135.9206
MBZ-1.RR.545.1 | 24311609145251 | Moulavi Bazar, Uluail, Ward # 4, Kaowsar Rosid | 2019-07-22 | LX1011 | 8.7 | 226 | 8.1 | 227 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6816 | 1943.9997 | 85.3455
MBZ-1.RR.546.1 | 24302439143558 | Moulavi Bazar, Durlovpur, Ward # 8, Badsha Mia | 2019-07-22 | LX1011 | 11.6 | 228 | 11.6 | 229 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6984 | 1775.9997 | 122.2232
MBZ-1.RR.546.2 | 24302439143558 | Moulavi Bazar, Durlovpur, Ward # 8, Badsha Mia | 2021-01-27 | MN1032 | 7.3 | 73 | 7.3 | 74 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6984 | 1775.9997 | 76.9163
MBZ-1.RR.547.1 | 24302489143503 | Moulavi Bazar, Durlovpur, Ward # 8, Md Ashik | 2019-07-22 | LX1011 | 11.5 | 230 | 11.5 | 231 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 24 | 0 | 6960 | 1775.9997 | 120.8376
MBZ-1.RR.547.2 | 24302489143503 | Moulavi Bazar, Durlovpur, Ward # 8, Md Ashik | 2021-10-02 | LU1001 | 5.5 | 25 | 5.5 | 26 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 24 | 0 | 6960 | 1775.9997 | 57.7919
MBZ-1.RR.548.1 | 24302289143464 | Moulavi Bazar, Durlovpur, Ward # 8, Soiyod Boshir | 2019-07-22 | LX1011 | 7.4 | 232 | 7.4 | 233 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6984 | 1775.9997 | 77.97
MBZ-1.RR.548.2 | 24302289143464 | Moulavi Bazar, Durlovpur, Ward # 8, Soiyod Boshir | 2022-03-24 | NQ1007 | 4.8 | 89 | 4.8 | 90 | 2022-03-24 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 5016 | 1775.9997 | 39.213
MBZ-1.RR.549.1 | 24294769144164 | Moulavi Bazar, Purbo Poton Masjid Rd, Aktar | 2019-07-23 | NQ1007 | 11.1 | 203 | 11.1 | 204 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7008 | 1751.9997 | 116.9549
MBZ-1.RR.550.1 | 24294769144164 | Moulavi Bazar, Purbo Poton Masjid Rd, Liton | 2019-07-23 | NQ1007 | 11.3 | 205 | 10.4 | 206 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7008 | 1751.9997 | 109.5794
MBZ-1.RR.551.1 | 24285529146012 | Moulovi Bazar, Dorga Moholla, Selim | 2019-07-11 | NQ1005 | 4.6 | 466 | 4.6 | 467 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6936 | 1823.9997 | 48.4678
MBZ-1.RR.552.1 | 24285569146024 | Moulovi Bazar, Dorga Moholla, Dorga Villa | 2019-07-11 | NQ1005 | 4.8 | 470 | 4.8 | 471 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6936 | 1823.9997 | 50.5751
MBZ-1.RR.553.1 | 24285569146024 | Moulovi Bazar, Dorga Moholla, Mojahid Bokth | 2019-07-11 | NQ1005 | 9.7 | 472 | 9.7 | 473 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6936 | 1823.9997 | 102.2039
MBZ-1.RR.554.1 | 24285509146043 | Moulovi Bazar, Dorga Moholla, Mosku | 2019-07-11 | NQ1005 | 6.2 | 474 | 6.2 | 475 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6936 | 1823.9997 | 65.3262
MBZ-1.RR.555.1 | 24290479146021 | Dorga Moholla, Shah Mostofa Road, Bokthiyar | 2019-07-13 | NQ1005 | 7.4 | 510 | 7.4 | 511 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6936 | 1823.9997 | 77.97
MBZ-1.RR.556.1 | 24290539146027 | Dorga Moholla, Shah Mostofa Road, Okil Miah | 2019-07-13 | NQ1005 | 11.7 | 512 | 11.7 | 513 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6936 | 1823.9997 | 123.2768
MBZ-1.RR.557.1 | 24290649146025 | Dorga Moholla, Shah Mostofa Road, H # 333 | 2019-07-13 | NQ1005 | 12.6 | 514 | 12.6 | 515 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6936 | 1823.9997 | 132.7597
MBZ-1.RR.558.1 | 24290529146001 | Dorga Moholla, Shah Mostofa Road, Sayed Foruk Ali | 2019-07-13 | NQ1005 | 1.2 | 516 | 1.2 | 517 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6936 | 1823.9997 | 12.6438
MBZ-1.RR.559.1 | 24290749145598 | Dorga Moholla, Shah Mostofa Road, Hazi Abdur Rashid Monzil | 2019-07-13 | NQ1005 | 18.7 | 518 | 18.7 | 519 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6936 | 1823.9997 | 197.0322
MBZ-1.RR.560.1 | 24290159145572 | Moulovi Bazar, Srimongol Road, Ahmod Ali | 2019-07-16 | NQ1005 | 14.1 | 520 | 14.1 | 521 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6936 | 1823.9997 | 148.5644
MBZ-1.RR.561.1 | 24290159145572 | Moulovi Bazar, Srimongol Road, Sayed Youse Ali | 2019-07-16 | NQ1005 | 3.8 | 522 | 3.8 | 523 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6936 | 1823.9997 | 40.0386
MBZ-1.RR.562.1 | 24290159145572 | Moulovi Bazar, Srimongol Road, Faruk Ahamed | 2019-07-16 | NQ1005 | 6.1 | 524 | 6.1 | 525 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6936 | 1823.9997 | 64.2725
MBZ-1.RR.563.1 | 24290299145594 | Moulovi Bazar, Srimongol Road, Maa Amena Villa | 2019-07-16 | NQ1005 | 16.2 | 526 | 16.4 | 527 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6936 | 1823.9997 | 172.7983
MBZ-1.RR.564.1 | 24290489145558 | Moulovi Bazar, Srimongol Road, Berirpar, Alauddin Ahmed | 2019-07-16 | NQ1005 | 22.2 | 528 | 23 | 529 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 23 | 23 | 1.38 | 1.38 | 0.0007168 | 100% | 0% | 1.38 | 1.38 | 0.0011869 | 28 | 0.027664 | 0.027664 |  | 0 | 0 | 6936 | 1823.9997 | 242.3391
MBZ-1.RR.565.1 | 24290549145557 | Moulovi Bazar, Srimongol Road, Berirpar, Fajlur Rahman | 2019-07-16 | NQ1005 | 11.3 | 532 | 11.5 | 533 | 2022-01-01 | [9 empty] | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0
MBZ-1.RR.566.1 | 24290619145559 | Moulovi Bazar, Srimongol Road, Berirpar, Amdadul Haque | 2019-07-16 | NQ1005 | 13 | 534 | 12.7 | 535 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6936 | 1823.9997 | 133.8133
MBZ-1.RR.567.1 | 24293359146560 | Moulovi Bazar, East Sayearpur, Riasoth Ullah Road, Bodrul Villa | 2019-07-17 | NQ1005 | 11.7 | 1 | 11.7 | 2 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6672 | 2087.9997 | 123.2768
MBZ-1.RR.568.1 | 24293289146558 | Moulovi Bazar, East Sayearpur, Riasoth Ullah Road, Khela Bibi | 2019-07-17 | NQ1005 | 13.2 | 3 | 13.2 | 4 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6672 | 2087.9997 | 139.0816
MBZ-1.RR.569.1 | 24293229146558 | Moulovi Bazar, East Sayearpur, Riasoth Ullah Road, Abul Kalam | 2019-07-17 | NQ1005 | 26.1 | 5 | 26.1 | 6 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 26.1 | 26.1 | 1.566 | 1.566 | 0.0007168 | 100% | 0% | 1.566 | 1.566 | 0.0011869 | 28 | 0.031393 | 0.031393 |  | 0 | 0 | 6672 | 2087.9997 | 275.0022
MBZ-1.RR.570.1 | 24293229146558 | Moulovi Bazar, East Sayearpur, Riasoth Ullah Road, Ahmod Villa | 2019-07-17 | NQ1005 | 14.3 | 9 | 14.3 | 10 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6672 | 2087.9997 | 150.6717
MBZ-1.RR.571.1 | 24293009146555 | Moulovi Bazar, East Sayearpur, Riasoth Ullah Road, Robina Monzil | 2019-07-17 | NQ1005 | 12.1 | 11 | 12.1 | 12 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6672 | 2087.9997 | 127.4914
MBZ-1.RR.572.1 | 24293249146520 | Moulovi Bazar, Sayearpur, 1 No Sonaban Bibi Road, Joy Monzil | 2019-07-17 | NQ1005 | 6.4 | 13 | 6.4 | 14 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6672 | 2087.9997 | 67.4335
MBZ-1.RR.573.1 | 24293249146520 | Moulovi Bazar, Sayearpur, 1 No Sonaban Bibi Road, Joy Monzil | 2019-07-17 | NQ1005 | 2.7 | 15 | 2.7 | 16 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6672 | 2087.9997 | 28.4485
MBZ-1.RR.574.1 | 24293599146522 | Moulovi Bazar, Sayearpur, 1 No Sonaban Bibi Road, Emon | 2019-07-17 | NQ1005 | 2 | 17 | 2 | 18 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6672 | 2087.9997 | 21.073
MBZ-1.RR.575.1 | 24293869146526 | Moulovi Bazar, Sayearpur, 1 No Sonaban Bibi Road, Bashid Miah | 2019-07-17 | NQ1005 | 11.4 | 19 | 11.4 | 20 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6672 | 2087.9997 | 120.1159
MBZ-1.RR.576.1 | 24293899146531 | Moulovi Bazar, Sayearpur, 1 No Sonaban Bibi Road, Azad Miah | 2019-07-17 | NQ1005 | 5.9 | 21 | 5.9 | 22 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6672 | 2087.9997 | 62.1652
MBZ-1.RR.577.1 | 24294229146523 | Moulovi Bazar, East Sayearpur, Majer Hati Sarak, Jagodish | 2019-07-17 | NQ1005 | 6.2 | 23 | 6.2 | 24 | 2022-01-01 | 2022-10-10 | MN1018 | 0.2 | 30 | 0.2 | 31 | 2022-10-10 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 6768 | 1991.9997
MBZ-1.RR.578.1 | 24294299146548 | Moulovi Bazar, East Sayearpur, Majer Hati Sarak, Amir box | 2019-07-17 | NQ1005 | 10.8 | 25 | 10.8 | 26 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6672 | 2087.9997 | 113.794
MBZ-1.RR.578.2 | 24294299146548 | Moulovi Bazar, East Sayearpur, Majer Hati Sarak, Amir box | 2022-02-23 | NQ1007 | 1.5 | 72 | 1.5 | 73 | 2022-02-23 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 5400 | 2087.9997 | 13.5098
MBZ-1.RR.579.1 | 24293779147017 | Moulovi Bazar, East Sayearpur, Kartik Chandro Road, Chitto Ronjon | 2019-07-18 | NQ1005 | 10.5 | 47 | 10.6 | 48 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6672 | 2087.9997 | 111.6867
MBZ-1.RR.580.1 | 24293779147017 | Moulovi Bazar, East Sayearpur, Kartik Chandro Road, Bimol Chandro | 2019-07-18 | NQ1005 | 12.4 | 49 | 12.1 | 50 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6672 | 2087.9997 | 127.4914
MBZ-1.RR.581.1 | 24293779147017 | Moulovi Bazar, East Sayearpur, Kartik Chandro Road, Ranto Pal | 2019-07-18 | NQ1005 | 13.8 | 52 | 13.8 | 53 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6672 | 2087.9997 | 145.4034
MBZ-1.RR.582.1 | 24293769147029 | Moulovi Bazar, East Sayearpur, Kartik Chandro Road, Motindro Kumar | 2019-07-18 | NQ1005 | 8.4 | 54 | 8.5 | 55 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6672 | 2087.9997 | 89.5601
MBZ-1.RR.583.1 | 24293799147029 | Moulovi Bazar, East Sayearpur, Kartik Chandro Road, Konath Pal | 2019-07-18 | NQ1005 | 12.9 | 56 | 12.9 | 57 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6672 | 2087.9997 | 135.9206
MBZ-1.RR.584.1 | 24293519147086 | Moulovi Bazar, East Sayearpur, Kartik Chandro Road, Sontosh Das | 2019-07-18 | NQ1005 | 12.3 | 58 | 11.8 | 59 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6672 | 2087.9997 | 124.3305
MBZ-1.RR.585.1 | 24292639145088 | Moulovi Bazar, West Borhat, Ashique Villa | 2019-07-18 | NQ1005 | 7.7 | 60 | 8.1 | 61 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7008 | 1751.9997 | 85.3455
MBZ-1.RR.586.1 | 24292719145097 | Moulovi Bazar, West Borhat, Ali Monzil | 2019-07-18 | NQ1005 | 11.4 | 63 | 11.4 | 64 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7008 | 1751.9997 | 120.1159
MBZ-1.RR.587.1 | 24292949145146 | Moulovi Bazar, West Borhat, Sirajul Islam | 2019-07-18 | NQ1005 | 11.2 | 65 | 11.2 | 66 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7008 | 1751.9997 | 118.0086
MBZ-1.RR.588.1 | 24292949145146 | Moulovi Bazar, West Borhat, Baccho Miah | 2019-07-18 | NQ1005 | 12.1 | 67 | 12.1 | 68 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7008 | 1751.9997 | 127.4914
MBZ-1.RR.589.1 | 24293399145103 | Moulovi Bazar, West Borhat, Rabea | 2019-07-20 | NQ1005 | 10.2 | 89 | 10.2 | 90 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 24 | 0 | 6984 | 1751.9997 | 107.1777
MBZ-1.RR.589.2 | 24293399145103 | Moulovi Bazar, West Borhat, Rabea | 2021-10-03 | LU1001 | 6.4 | 33 | 6.4 | 34 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 24 | 0 | 6984 | 1751.9997 | 67.2487
MBZ-1.RR.590.1 | 24293399145103 | Moulovi Bazar, West Borhat, Eakbal Hossen | 2019-07-20 | NQ1005 | 12.1 | 91 | 12.1 | 92 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7008 | 1751.9997 | 127.4914
MBZ-1.RR.591.1 | 24293589145097 | Moulovi Bazar, West Borhat, Mokbul Ali | 2019-07-20 | NQ1005 | 12.9 | 93 | 12.9 | 94 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7008 | 1751.9997 | 135.9206
MBZ-1.RR.592.1 | 24293589145097 | Moulovi Bazar, West Borhat, Mokbul Ali | 2019-07-20 | NQ1005 | 14.5 | 97 | 14.5 | 98 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7008 | 1751.9997 | 152.779
MBZ-1.RR.593.1 | 24293609145118 | Moulovi Bazar, West Borhat, Hafiz Tajul Islam | 2019-07-20 | NQ1005 | 7 | 99 | 7 | 100 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7008 | 1751.9997 | 73.7554
MBZ-1.RR.594.1 | 24293609145118 | Moulovi Bazar, West Borhat, Asrof Miah | 2019-07-20 | NQ1005 | 8.5 | 101 | 8.5 | 102 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7008 | 1751.9997 | 89.5601
MBZ-1.RR.594.2 | 24293609145118 | Moulovi Bazar, West Borhat, Asrof Miah | 2021-01-28 | LU1001 | 7.8 | 115 | 7.8 | 116 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7008 | 1751.9997 | 82.1846
MBZ-1.RR.595.1 | 24293609145118 | Moulovi Bazar, West Borhat, Asrof Miah | 2019-07-20 | NQ1005 | 4.2 | 103 | 4.2 | 104 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7008 | 1751.9997 | 44.2532
MBZ-1.RR.596.1 | 24293689145119 | Moulovi Bazar, West Borhat, Shajahan Miah | 2019-07-20 | NQ1005 | 14.3 | 105 | 14.3 | 106 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7008 | 1751.9997 | 150.6717
MBZ-1.RR.597.1 | 24293619145072 | Moulovi Bazar, West Borhat, Rokea | 2019-07-20 | NQ1005 | 15.7 | 108 | 15.7 | 109 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 7008 | 1751.9997 | 165.4228
MBZ-1.RR.598.1 | 24293729145122 | Moulovi Bazar, West Borhat, Shahin | 2019-07-20 | NQ1005 | 12.3 | 110 | 12.2 | 111 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7008 | 1751.9997 | 128.5451
MBZ-1.RR.599.1 | 24293789145125 | Moulovi Bazar, West Borhat, Mortoza Miah | 2019-07-20 | NQ1005 | 12.2 | 112 | 12.2 | 113 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7008 | 1751.9997 | 128.5451
MBZ-1.RR.600.1 | 24310549146316 | Moulovi Bazar, Akatuna Village, Nurul Islam Torofdar | 2019-07-21 | NQ1005 | 25.4 | 134 | 25.4 | 135 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 25.4 | 25.4 | 1.524 | 1.524 | 0.0007168 | 100% | 0% | 1.524 | 1.524 | 0.0011869 | 28 | 0.030551 | 0.030551 |  | 0 | 0 | 6816 | 1943.9997 | 267.6266
MBZ-1.RR.601.1 | 24285859146045 | Dorgamoholla, Sheikh Kazim Road, Nur Manjil | 2019-07-13 | NQ1005 | 8.9 | 492 | 8.9 | 493 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6936 | 1823.9997 | 93.7747
MBZ-1.RR.602.1 | 24285989146051 | Dorgamoholla, Sheikh Kazim Road, Monirul Islam | 2019-07-13 | NQ1005 | 4.2 | 494 | 4.4 | 495 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6936 | 1823.9997 | 46.3605
MBZ-1.RR.603.1 | 24290109146048 | Dorgamoholla, Sheikh Kazim Road, Solaiman | 2019-07-13 | NQ1005 | 16.6 | 496 | 17.2 | 497 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 6936 | 1823.9997 | 181.2275
MBZ-1.RR.604.1 | 24290109146048 | Dorgamoholla, Sheikh Kazim Road, Solaiman | 2019-07-13 | NQ1005 | 8.7 | 500 | 8.8 | 501 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6936 | 1823.9997 | 92.721
MBZ-1.RR.605.1 | 24290169146030 | Dorgamoholla, Sheikh Kazim Road, Elias | 2019-07-13 | NQ1005 | 10.7 | 502 | 10.6 | 503 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6936 | 1823.9997 | 111.6867
MBZ-1.RR.606.1 | 24290169146030 | Dorgamoholla, Sheikh Kazim Road, Md. Koysor | 2019-07-13 | NQ1005 | 6.2 | 504 | 6.2 | 505 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6936 | 1823.9997 | 65.3262
MBZ-1.RR.607.1 | 24290329146049 | Dorgamoholla, Sayed Shah Ismail Road, Liakot | 2019-07-13 | NQ1005 | 10.4 | 506 | 10.3 | 507 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 24 | 0 | 6912 | 1823.9997 | 108.2284
MBZ-1.RR.608.1 | 24290329146049 | Dorgamoholla, Sayed Shah Ismail Road, Toufiq Mia | 2019-07-13 | NQ1005 | 11.4 | 508 | 11.4 | 509 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6936 | 1823.9997 | 120.1159
MBZ-1.RR.609.1 | 24294179146570 | Sayedpur, Riasatullah Road, Md. Jamshed Mia | 2019-07-16 | NQ1005 | 9.2 | 536 | 9.3 | 537 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 5.5 | 0 | 6666.5 | 2087.9997 | 97.9278
MBZ-1.RR.610.1 | 24294179146570 | Sayedpur, Riasatullah Road, Md. Aftab Udddin | 2019-07-16 | NQ1005 | 7.9 | 538 | 7.9 | 539 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6672 | 2087.9997 | 83.2382
MBZ-1.RR.611.1 | 24294179146570 | Sayedpur, Riasatullah Road, Badsha Mia | 2019-07-16 | NQ1005 | 11.6 | 540 | 11.6 | 541 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6672 | 2087.9997 | 122.2232
MBZ-1.RR.612.1 | 24294069146568 | Sayedpur, Riasatullah Road, Md. Jobbar Ullah | 2019-07-16 | NQ1005 | 14.1 | 542 | 14.1 | 543 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6672 | 2087.9997 | 148.5644
MBZ-1.RR.612.2 | 24294069146568 | Sayedpur, Riasatullah Road, Md. Jobbar Ullah | 2021-01-26 | LU1001 | 1.5 | 98 | 1.5 | 99 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6672 | 2087.9997 | 15.8047
MBZ-1.RR.613.1 | 24294069146568 | Sayedpur, Riasatullah Road, Beside Jobbar Ullah | 2019-07-16 | NQ1005 | 9 | 544 | 8.4 | 545 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6672 | 2087.9997 | 88.5064
MBZ-1.RR.614.1 | 24294069146568 | Sayedpur, Riasatullah Road, Maleha Villa | 2019-07-16 | NQ1005 | 7.2 | 546 | 7.3 | 547 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6672 | 2087.9997 | 76.9163
MBZ-1.RR.615.1 | 24293959146579 | Sayedpur, Riasatullah Road, Jesmin, Hazi Monafer Bari | 2019-07-16 | NQ1005 | 9.6 | 548 | 9.6 | 549 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6672 | 2087.9997 | 101.1502
MBZ-1.RR.616.1 | 24293959146579 | Sayedpur, Riasatullah Road, Nurjahan, Hazi Monafer Bari | 2019-07-16 | NQ1005 | 8 | 550 | 8 | 551 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6672 | 2087.9997 | 84.2919
MBZ-1.RR.617.1 | 24293739146554 | Sayedpur, Riasatullah Road, Jahangir | 2019-07-16 | NQ1005 | 14.2 | 552 | 14.2 | 553 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6672 | 2087.9997 | 149.618
MBZ-1.RR.618.1 | 24293569146564 | Sayedpur, Riasatullah Road, Front of Baitul Anwar Jame Mosjid, Ansar Vaban | 2019-07-16 | NQ1005 | 15.6 | 554 | 15.6 | 555 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6672 | 2087.9997 | 164.3691
MBZ-1.RR.619.1 | 24293849146486 | Sayerpur, Majher Hati Road, Nokul Chandra Pal | 2019-07-17 | NQ1005 | 5.5 | 27 | 5.5 | 28 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6816 | 1943.9997 | 57.9506
MBZ-1.RR.620.1 | 24293489146479 | Sayerpur, Majher Hati Road, Babar Ahmed | 2019-07-17 | NQ1005 | 11.7 | 29 | 11.7 | 30 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6816 | 1943.9997 | 123.2768
MBZ-1.RR.621.1 | 24293069146477 | Sayerpur, Majher Hati Road, Alauddin | 2019-07-17 | NQ1005 | 10.1 | 31 | 10.1 | 32 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6816 | 1943.9997 | 106.4185
MBZ-1.RR.622.1 | 24292889146472 | Sayerpur, Majher Hati Road, Mostofa Vaban | 2019-07-17 | NQ1005 | 11 | 33 | 11 | 34 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6816 | 1943.9997 | 115.9013
MBZ-1.RR.623.1 | 24292369147343 | Borshijura, Shamshernagar Road, Maijpara, Kawsar Parveen | 2019-07-17 | NQ1005 | 12.7 | 35 | 12.7 | 36 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6672 | 2087.9997 | 133.8133
MBZ-1.RR.624.1 | 24292369147343 | Borshijura, Shamshernagar Road, Maijpara, Pranjol | 2019-07-17 | NQ1005 | 11.3 | 37 | 11.3 | 38 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6672 | 2087.9997 | 119.0622
MBZ-1.RR.624.2 | 24292369147343 | Borshijura, Shamshernagar Road, Maijpara, Pranjol | 2019-07-17 | NQ1005 | 9.3 | 39 | 8.7 | 40 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6672 | 2087.9997 | 91.6674
MBZ-1.RR.625.1 | 24285889146018 | Dorgamoholla, Sayed Shah Ismail Road, Mother Misses Khodeja | 2019-07-17 | NQ1005 | 12.6 | 41 | 12.6 | 42 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6936 | 1823.9997 | 132.7597
MBZ-1.RR.626.1 | 24285989146081 | Dorgamoholla, Sheikh Kazim Uddin Road, Sheikh Mohammad Dudh Mia | 2019-07-17 | NQ1005 | 9.6 | 43 | 9.6 | 44 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6936 | 1823.9997 | 101.1502
MBZ-1.RR.627.1 | 24290279146086 | Dorgamoholla, Sheikh Kazim Uddin Road, Jumman Ahmed | 2019-07-17 | NQ1005 | 12.1 | 45 | 12.1 | 46 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6936 | 1823.9997 | 127.4914
MBZ-1.RR.628.1 | 24292299145096 | West Borhat, Sylhet Road, Monjur Hosen | 2019-07-18 | NQ1005 | 11.1 | 69 | 11.1 | 70 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7008 | 1751.9997 | 116.9549
MBZ-1.RR.629.1 | 24292299145122 | West Borhat, Sylhet Road, Tuta Londoni | 2019-07-18 | NQ1005 | 12.5 | 71 | 12.5 | 72 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7008 | 1751.9997 | 131.706
MBZ-1.RR.630.1 | 24292919145084 | West Borhat, Jahid Mia Road, Faruque Mia | 2019-07-18 | NQ1005 | 9.2 | 73 | 9.2 | 74 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7008 | 1751.9997 | 96.9356
MBZ-1.RR.631.1 | 24292759145031 | West Borhat, Boroikona Road, Roymona Monjil | 2019-07-18 | NQ1005 | 4.9 | 75 | 4.6 | 76 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7008 | 1751.9997 | 48.4678
MBZ-1.RR.632.1 | 24292949145023 | West Borhat, Boroikona Road, Aftab Mia | 2019-07-18 | NQ1005 | 13 | 77 | 13 | 78 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7008 | 1751.9997 | 136.9743
MBZ-1.RR.633.1 | 24293399145007 | West Borhat, Boroikona Road, Lebu Mia | 2019-07-18 | NQ1005 | 10.5 | 79 | 10.5 | 80 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7008 | 1751.9997 | 110.6331
MBZ-1.RR.634.1 | 24293609145004 | West Borhat, Boroikona Road, Okil Babu | 2019-07-18 | NQ1005 | 12.5 | 81 | 12.5 | 82 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7008 | 1751.9997 | 131.706
MBZ-1.RR.634.2 | 24293609145004 | West Borhat, Boroikona Road, Okil Babu | 2019-07-18 | NQ1005 | 7 | 85 | 7 | 86 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7008 | 1751.9997 | 73.7554
MBZ-1.RR.634.3 | 24293609145004 | West Borhat, Boroikona Road, Okil Babu | 2019-07-18 | NQ1005 | 12.9 | 87 | 12.2 | 88 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7008 | 1751.9997 | 128.5451
MBZ-1.RR.635.1 | 24304009146435 | Moulvibazar Sadar, Uttor Mulaim, Mahmud Mia | 2019-07-20 | NQ1005 | 1.8 | 114 | 1.8 | 115 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6768 | 1991.9997 | 18.9657
MBZ-1.RR.636.1 | 24304009146435 | Moulvibazar Sadar, Uttor Mulaim, Ahmad Mia | 2019-07-20 | NQ1005 | 4.5 | 116 | 4.5 | 117 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6768 | 1991.9997 | 47.4142
MBZ-1.RR.637.1 | 24304009146435 | Moulvibazar Sadar, Uttor Mulaim, Md. Mosaid | 2019-07-20 | NQ1005 | 9.4 | 118 | 9.4 | 119 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6768 | 1991.9997 | 99.0429
MBZ-1.RR.638.1 | 24303729146427 | Moulvibazar Sadar, Uttor Mulaim, Khalil Mia | 2019-07-20 | NQ1005 | 4.9 | 120 | 4.9 | 121 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6768 | 1991.9997 | 51.6288
MBZ-1.RR.639.1 | 24303579146428 | Moulvibazar Sadar, Uttor Mulaim, Ansar Mia | 2019-07-20 | NQ1005 | 10.5 | 122 | 11.3 | 123 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6768 | 1991.9997 | 119.0622
MBZ-1.RR.640.1 | 24303489146415 | Moulvibazar Sadar, Uttor Mulaim, Moyon Uddin Ahmed | 2019-07-20 | NQ1005 | 13.7 | 124 | 13.4 | 125 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6768 | 1991.9997 | 141.1888
MBZ-1.RR.641.1 | 24303869146406 | Moulvibazar Sadar, Uttor Mulaim, Sayed Mia | 2019-07-20 | NQ1005 | 2.4 | 126 | 2.4 | 127 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6768 | 1991.9997 | 25.2876
MBZ-1.RR.642.1 | 24303589146380 | Moulvibazar Sadar, Uttor Mulaim, Mia Dhan | 2019-07-20 | NQ1005 | 12.7 | 128 | 12.7 | 129 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6768 | 1991.9997 | 133.8133
MBZ-1.RR.643.1 | 24303439146348 | Moulvibazar Sadar, Uttor Mulaim, Aminul Islam | 2019-07-20 | NQ1005 | 12.7 | 130 | 12.7 | 131 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6768 | 1991.9997 | 133.8133
MBZ-1.RR.644.1 | 24304039146258 | Moulvibazar Sadar, Ekatuna Road, Mallik Sarai, Nuru Mia | 2019-07-20 | NQ1005 | 18.7 | 132 | 18.7 | 133 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6768 | 1991.9997 | 197.0322
MBZ-1.RR.645.1 | 24303799146533 | Moulvibazar Sadar, Uttar Mulaim, Mohammad Jakaria | 2019-07-21 | NQ1005 | 10.3 | 144 | 10.8 | 145 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6768 | 1991.9997 | 113.794
MBZ-1.RR.646.1 | 24314109146411 | Moulvibazar, Ekatuna Road, Borkapor, Masuk Mia | 2019-07-21 | NQ1005 | 8.5 | 146 | 8.4 | 147 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6792 | 1967.9997 | 88.5064
MBZ-1.RR.646.2 | 24314109146411 | Moulvibazar, Ekatuna Road, Borkapor, Masuk Mia | 2019-07-21 | NQ1005 | 12.4 | 148 | 12.4 | 149 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6792 | 1967.9997 | 130.6524
MBZ-1.RR.647.1 | 24315609146411 | Moulvibazar, Ekatuna Road, Borkapor, Sona Mia | 2019-07-21 | NQ1005 | 10.2 | 150 | 10.3 | 151 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6792 | 1967.9997 | 108.5258
MBZ-1.RR.647.2 | 24315609146411 | Moulvibazar, Ekatuna Road, Borkapor, Sona Mia | 2021-09-26 | LU1001 | 7.2 | 13 | 7.2 | 14 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6792 | 1967.9997 | 75.8627
MBZ-1.RR.648.1 | 24304359147067 | Moulvibazar, Borman, Doshal, Haris Mia | 2019-07-22 | NQ1005 | 11.8 | 152 | 11.8 | 153 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6816 | 1943.9997 | 124.3305
MBZ-1.RR.649.1 | 24304279147072 | Moulvibazar, Borman, Doshal, Mahmudur Rahman | 2019-07-22 | NQ1005 | 14.4 | 154 | 14.4 | 155 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6816 | 1943.9997 | 151.7253
MBZ-1.RR.650.1 | 24303339147075 | Moulvibazar, Borman, Doshal, Front of Abdul Rouf Villa | 2019-07-22 | NQ1005 | 11.3 | 157 | 11.4 | 158 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6816 | 1943.9997 | 120.1159
MBZ-1.RR.651.1 | 24292399146576 | Shamoli, Shomsher Nagar Road, Ward No- 01, Sayed Amina Manjil | 2019-07-13 | NQ1007 | 4.8 | 663 | 4.8 | 664 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6672 | 2087.9997 | 50.5751
MBZ-1.RR.652.1 | 24292319146599 | Shamoli, Shomsher Nagar Road, Ward No- 01, Md. Hosenuzzaman Sohel | 2019-07-13 | NQ1007 | 3.2 | 665 | 3.2 | 666 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6672 | 2087.9997 | 33.7167
MBZ-1.RR.653.1 | 24292839146579 | Shamoli, Shomsher Nagar Road, A.M.A.B Complex | 2019-07-13 | NQ1007 | 4.2 | 667 | 4.2 | 668 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6672 | 2087.9997 | 44.2532
MBZ-1.RR.654.1 | 24292279146513 | East Girjapara, Mostofa Kamal College Road, Wahiduzzaman | 2019-07-13 | NQ1007 | 8.5 | 669 | 8.5 | 670 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6672 | 2087.9997 | 89.5601
MBZ-1.RR.655.1 | 24292149146519 | East Girjapara, Mostofa Kamal College Road, Onimesh Chando | 2019-07-13 | NQ1007 | 10.7 | 671 | 10.7 | 672 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6672 | 2087.9997 | 112.7403
MBZ-1.RR.656.1 | 24292149146519 | East Girjapara, Mostofa Kamal College Road, Amar Das | 2019-07-13 | NQ1007 | 10.8 | 673 | 10.8 | 674 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6672 | 2087.9997 | 113.794
MBZ-1.RR.657.1 | 24292169146550 | East Girjapara, Mostofa Kamal College Road, Moni Kuthir | 2019-07-13 | NQ1007 | 4.1 | 675 | 4.1 | 676 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6672 | 2087.9997 | 43.1996
MBZ-1.RR.658.1 | 24291729146486 | East Girjapara, Mostofa Kamal College Road, H # 96/4 | 2019-07-13 | NQ1007 | 5.2 | 677 | 5.2 | 678 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6816 | 1943.9997 | 54.7897
MBZ-1.RR.659.1 | 24291699146485 | East Girjapara, Mostofa Kamal College Road, Kaptan Member | 2019-07-13 | NQ1007 | 8.8 | 679 | 8.8 | 680 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6816 | 1943.9997 | 92.721
MBZ-1.RR.660.1 | 24291669146484 | East Girjapara, Mostofa Kamal College Road, Khan Manjil-1 | 2019-07-13 | NQ1007 | 2.9 | 683 | 2.9 | 684 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6816 | 1943.9997 | 30.5558
MBZ-1.RR.661.1 | 24292419146473 | East Girjapara, Mostofa Kamal College Road, H # 100/4 | 2019-07-13 | NQ1007 | 7 | 685 | 7 | 686 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6816 | 1943.9997 | 73.7554
MBZ-1.RR.662.1 | 24292439146464 | East Girjapara, Mostofa Kamal College Road, Rokeya Parvin | 2019-07-13 | NQ1007 | 9 | 687 | 9 | 688 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6816 | 1943.9997 | 94.8283
MBZ-1.RR.663.1 | 24292359146466 | East Girjapara, Mostofa Kamal College Road, Salema | 2019-07-13 | NQ1007 | 7.3 | 689 | 7.3 | 690 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6816 | 1943.9997 | 76.9163
MBZ-1.RR.664.1 | 24292759146447 | Shomsher Nagar Road, C.N.G Bus-stand, H # 89 | 2019-07-13 | NQ1007 | 0.1 | 691 | 0.1 | 692 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 0.1 | 0.1 | 0.006 | 0.006 | 0.0007168 | 100% | 0% | 0.006 | 0.006 | 0.0011869 | 28 | 0.00012028 | 0.00012028 |  | 0 | 0 | 6816 | 1943.9997 | 1.0536
MBZ-1.RR.665.1 | 24291349146402 | East Girjapara, H # 754, Mst. Jesmin Hossen Baby | 2019-07-16 | NQ1007 | 11.7 | 737 | 11.7 | 738 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6888 | 1871.9997 | 123.2768
MBZ-1.RR.666.1 | 24291449146395 | East Girjapara, H # 20, Debobrot Shingho Chowdhury | 2019-07-16 | NQ1007 | 4.3 | 739 | 4.3 | 740 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6888 | 1871.9997 | 45.3069
MBZ-1.RR.667.1 | 24291789146403 | East Girjapara, H # 27/1, Syed Ali Raja | 2019-07-16 | NQ1007 | 13.4 | 741 | 13.4 | 742 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6840 | 1919.9997 | 141.1888
MBZ-1.RR.667.2 | 24291789146403 | East Girjapara, H # 27/1, Syed Ali Raja | 2019-07-16 | NQ1007 | 7.7 | 743 | 7.1 | 744 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6840 | 1919.9997 | 74.809
MBZ-1.RR.668.1 | 24291789146378 | East Girjapara, H # 27, Raju Ahmed | 2019-07-16 | NQ1007 | 3.2 | 745 | 3.2 | 746 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6840 | 1919.9997 | 33.7167
MBZ-1.RR.669.1 | 24292049146378 | East Girjapara, H # 84, Nouraj Mahal | 2019-07-16 | NQ1007 | 2.3 | 747 | 2.1 | 748 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6840 | 1919.9997 | 22.1266
MBZ-1.RR.670.1 | 24292179146379 | East Girjapara, H # 83, Late Mokhles Mia | 2019-07-16 | NQ1007 | 5 | 749 | 5 | 750 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6840 | 1919.9997 | 52.6824
MBZ-1.RR.671.1 | 24292759146394 | Shomsher Nagar Road, H # 93, S.A Wahid | 2019-07-16 | NQ1007 | 10.8 | 751 | 10.8 | 752 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6816 | 1943.9997 | 113.794
MBZ-1.RR.672.1 | 24292819146388 | Shomsher Nagar Road, H # 40, S.A Wahid | 2019-07-16 | NQ1007 | 6.8 | 753 | 6.8 | 754 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6816 | 1943.9997 | 71.6481
MBZ-1.RR.673.1 | 24292779146357 | Shomsher Nagar Road, H # 44, Maloncho | 2019-07-16 | NQ1007 | 14.6 | 755 | 13.6 | 756 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6816 | 1943.9997 | 143.2961
MBZ-1.RR.674.1 | 24292419147095 | Borshijura, Shajid Sharak, Gofur Manjil | 2019-07-16 | NQ1007 | 5.9 | 757 | 5.9 | 758 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6672 | 2087.9997 | 62.1652
MBZ-1.RR.675.1 | 24292409147132 | Shomsher Nagar Road, Sazid Sharak, Shofiq Manjil | 2019-07-17 | NQ1007 | 3.7 | 795 | 3.7 | 796 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6672 | 2087.9997 | 38.985
MBZ-1.RR.676.1 | 24292449147153 | Shomsher Nagar Road, Sazid Sharak, Abdul Khalek | 2019-07-17 | NQ1007 | 10.4 | 797 | 10.4 | 798 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6672 | 2087.9997 | 109.5794
MBZ-1.RR.677.1 | 24292329147148 | Shomsher Nagar Road, Sazid Sharak, Abdur Rouf | 2019-07-17 | NQ1007 | 9.8 | 799 | 9.8 | 800 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6672 | 2087.9997 | 103.2575
MBZ-1.RR.678.1 | 24292269147149 | Shomsher Nagar Road, Sazid Sharak, Abdur Razzaque | 2019-07-17 | NQ1007 | 19.3 | 801 | 18.1 | 802 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6672 | 2087.9997 | 190.7103
MBZ-1.RR.679.1 | 24293169147028 | East Soyerpur, Kartik Chandra Road, Jiaul Islam | 2019-07-17 | NQ1007 | 5.8 | 805 | 5.8 | 806 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6672 | 2087.9997 | 61.1116
MBZ-1.RR.680.1 | 24293399147030 | East Soyerpur, Kartik Chandra Road, H # 257/1, Hamida Villa | 2019-07-17 | NQ1007 | 1.8 | 809 | 1.8 | 810 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6672 | 2087.9997 | 18.9657
MBZ-1.RR.681.1 | 24293479147011 | East Soyerpur, Kartik Chandra Road, Obinash Pal | 2019-07-17 | NQ1007 | 4 | 811 | 4 | 812 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6672 | 2087.9997 | 42.1459
MBZ-1.RR.682.1 | 24293439147013 | East Soyerpur, Kartik Chandra Road, Sujit Pal | 2019-07-17 | NQ1007 | 4.5 | 815 | 4.5 | 816 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6672 | 2087.9997 | 47.4142
MBZ-1.RR.683.1 | 24293589147015 | East Soyerpur, Kartik Chandra Road, Md. Fajlue Mia | 2019-07-17 | NQ1007 | 10.8 | 817 | 10.6 | 818 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6672 | 2087.9997 | 111.6867
MBZ-1.RR.684.1 | 24293359147105 | Soyerpur, Beside Manu River, Ranjan Pal | 2019-07-17 | NQ1007 | 3.6 | 819 | 3.6 | 820 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6672 | 2087.9997 | 37.9313
MBZ-1.RR.685.1 | 24293009147134 | Shomsher Nagar Road, H # 4, Damia Villa, Abdul Kayum | 2019-07-17 | NQ1007 | 11.2 | 821 | 11.2 | 822 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6672 | 2087.9997 | 118.0086
MBZ-1.RR.685.2 | 24293009147134 | Shomsher Nagar Road, H # 4, Damia Villa, Abdul Kayum | 2019-07-17 | NQ1007 | 4.1 | 827 | 4.1 | 828 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6672 | 2087.9997 | 43.1996
MBZ-1.RR.686.1 | 24284399147341 | Noyabazar Road, Pahar Borshijura, Abdul Wahid | 2019-07-18 | NQ1007 | 6.4 | 25 | 6.5 | 26 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6624 | 2135.9997 | 68.4871
MBZ-1.RR.687.1 | 24284099147356 | Noyabazar Road, Pahar Borshijura, Abdul Barek | 2019-07-18 | NQ1007 | 10 | 27 | 10 | 28 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6624 | 2135.9997 | 105.3648
MBZ-1.RR.688.1 | 24284529148081 | Noyabazar Road, Pahar Borshijura, Abdul Malek | 2019-07-18 | NQ1007 | 15.4 | 29 | 15.4 | 30 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6624 | 2135.9997 | 162.2618
MBZ-1.RR.689.1 | 24284239148069 | Noyabazar Road, Pahar Borshijura, Md. Alauddin | 2019-07-18 | NQ1007 | 9.8 | 31 | 9.8 | 32 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6624 | 2135.9997 | 103.2575
MBZ-1.RR.690.1 | 24283389148042 | Noyabazar Road, Pahar Borshijura, Abdul Mukit | 2019-07-18 | NQ1007 | 4.8 | 33 | 4.8 | 34 | 2022-01-01 | [9 empty] | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0
MBZ-1.RR.691.1 | 24283389148042 | Noyabazar Road, Pahar Borshijura, Abdul Mukit | 2019-07-18 | NQ1007 | 3.1 | 35 | 3.1 | 36 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6624 | 2135.9997 | 32.6631
MBZ-1.RR.692.1 | 24284299147524 | Noyabazar Road, Pahar Borshijura, Sayed Manik Mia | 2019-07-18 | NQ1007 | 12.4 | 37 | 12.4 | 38 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6624 | 2135.9997 | 130.6524
MBZ-1.RR.693.1 | 24302549146369 | Chadnighat, North Mulaim, Mujibur Rahman | 2019-07-20 | NQ1007 | 5.1 | 56 | 5.1 | 57 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6768 | 1991.9997 | 53.7361
MBZ-1.RR.694.1 | 24302879146370 | Chadnighat, North Mulaim, Azam Mia | 2019-07-20 | NQ1007 | 6.8 | 58 | 6.8 | 59 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6768 | 1991.9997 | 71.6481
MBZ-1.RR.695.1 | 24302959146371 | Chadnighat, North Mulaim, Yusuf Mia | 2019-07-20 | NQ1007 | 10.1 | 60 | 10.1 | 61 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6768 | 1991.9997 | 106.4185
MBZ-1.RR.696.1 | 24303019146371 | Chadnighat, North Mulaim, Md. Mohashin | 2019-07-20 | NQ1007 | 11.3 | 62 | 11.3 | 63 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6768 | 1991.9997 | 119.0622
MBZ-1.RR.697.1 | 24303169146389 | Chadnighat, North Mulaim, Md. Abdul Mukit | 2019-07-20 | NQ1007 | 5.7 | 64 | 5.7 | 65 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6768 | 1991.9997 | 60.0579
MBZ-1.RR.698.1 | 24303289146381 | Chadnighat, North Mulaim, Soifur Mia | 2019-07-20 | NQ1007 | 5.4 | 66 | 5.4 | 67 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6768 | 1991.9997 | 56.897
MBZ-1.RR.699.1 | 24303399146364 | Chadnighat, North Mulaim, Monnan Mia | 2019-07-20 | NQ1007 | 7.1 | 68 | 7.1 | 69 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6768 | 1991.9997 | 74.809
MBZ-1.RR.700.1 | 24303279146395 | Chadnighat, North Mulaim, H # 158, Md. Nazrul Islam | 2019-07-20 | NQ1007 | 3.8 | 70 | 3.8 | 71 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6768 | 1991.9997 | 40.0386
MBZ-1.RR.701.1 | 24285909146559 | Moulovibazar, West Borshijura, T.B. Hospital Road, Ward # 2, H # 190, Fojol Mia Gong | 2019-07-10 | NQ1007 | 3.3 | 621 | 3.3 | 622 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6888 | 1871.9997 | 34.7704
MBZ-1.RR.702.1 | 24290129146560 | Moulovibazar, West Borshijura, Banani, T.B. Hospital Road, Masudur Rahman | 2019-07-10 | NQ1007 | 8.8 | 623 | 8.8 | 624 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6888 | 1871.9997 | 92.721
MBZ-1.RR.703.1 | 24290159146555 | Moulovibazar, West Borshijura, Banani, T.B. Hospital Road, Md. Mogol Chowdhury | 2019-07-10 | NQ1007 | 8 | 625 | 8 | 626 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6888 | 1871.9997 | 84.2919
MBZ-1.RR.704.1 | 24285819146474 | Moulovibazar, T.B. Hospital Road, Ward - 2, H # 147/9, Khaleda Monjil | 2019-07-11 | NQ1007 | 8.9 | 641 | 8.9 | 642 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6888 | 1871.9997 | 93.7747
MBZ-1.RR.705.1 | 24285659146475 | Moulovibazar, T.B. Hospital Road, Ward - 2, Alhaz Abdur Rob Chowdhury | 2019-07-11 | NQ1007 | 10.6 | 643 | 10.6 | 644 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6888 | 1871.9997 | 111.6867
MBZ-1.RR.706.1 | 24290019146487 | Moulovibazar, T.B. Hospital Road, West Borshijura, Burhan Monjil | 2019-07-11 | NQ1007 | 30.2 | 645 | 30.2 | 646 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 30.2 | 30.2 | 1.812 | 1.812 | 0.0007168 | 100% | 0% | 1.812 | 1.812 | 0.0011869 | 28 | 0.036324 | 0.036324 |  | 0 | 0 | 6888 | 1871.9997 | 318.2017
MBZ-1.RR.707.1 | 24290169146540 | Moulovibazar, T.B. Hospital Road, West Borshijura, H # 621, Talukder Villa | 2019-07-11 | NQ1007 | 11.7 | 647 | 11.8 | 648 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6888 | 1871.9997 | 124.3305
MBZ-1.RR.707.2 | 24290169146540 | Moulovibazar, T.B. Hospital Road, West Borshijura, H # 621, Talukder Villa | 2021-01-25 | NQ1003 | 9.1 | 139 | 9.2 | 140 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6888 | 1871.9997 | 96.9356
MBZ-1.RR.708.1 | 24290039146540 | Moulovibazar, T.B. Hospital Road, H # 1002/1, Ak. Villa | 2019-07-11 | NQ1007 | 16.1 | 649 | 16.1 | 650 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6888 | 1871.9997 | 169.6373
MBZ-1.RR.709.1 | 24292769146588 | Moulovibazar, Shomsher Nagor Road, H # 968, Md. Anowar Mia | 2019-07-11 | NQ1007 | 8 | 655 | 8 | 656 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6672 | 2087.9997 | 84.2919
MBZ-1.RR.710.1 | 24292699146581 | Moulovibazar, Shyamoli, Shomsher Nagor Road, H # 10, Abdul Weias | 2019-07-11 | NQ1007 | 6.3 | 657 | 6.3 | 658 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6672 | 2087.9997 | 66.3798
MBZ-1.RR.710.2 | 24292699146581 | Moulovibazar, Shyamoli, Shomsher Nagor Road, H # 10, Abdul Weias | 2021-01-26 | LU1001 | 10.7 | 94 | 10.7 | 95 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6672 | 2087.9997 | 112.7403
MBZ-1.RR.711.1 | 24292259146412 | Moulovibazar, East Girjapara, Kabir Mia | 2019-07-13 | NQ1007 | 7.4 | 693 | 7.4 | 694 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6816 | 1943.9997 | 77.97
MBZ-1.RR.712.1 | 24292239146431 | Moulovibazar, East Girjapara, Fakrul Ahmed | 2019-07-13 | NQ1007 | 4.8 | 697 | 4.8 | 698 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6816 | 1943.9997 | 50.5751
MBZ-1.RR.713.1 | 24292199146414 | Moulovibazar, East Girjapara, Sydur Villa | 2019-07-13 | NQ1007 | 11.1 | 699 | 11.1 | 700 | 2022-01-01 | [9 empty] | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0
MBZ-1.RR.713.2 | 24292199146414 | Moulovibazar, East Girjapara, Sydur Villa | 2019-07-13 | NQ1007 | 4.3 | 703 | 4.1 | 704 | 2022-01-01 | [9 empty] | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0
MBZ-1.RR.714.1 | 24292089146432 | Moulovibazar, East Girjapara, Ghorua Villa | 2019-07-13 | NQ1007 | 4.6 | 705 | 4.6 | 706 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6816 | 1943.9997 | 48.4678
MBZ-1.RR.715.1 | 24292079146414 | Moulovibazar, East Girjapara, H # 37, Haji Abdul Latif | 2019-07-13 | NQ1007 | 14.2 | 707 | 14.2 | 708 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6816 | 1943.9997 | 149.618
MBZ-1.RR.716.1 | 24291439146403 | Moulovibazar, East Girjapara, H # 751, Ruksana Begum | 2019-07-16 | NQ1007 | 4.6 | 713 | 4.6 | 714 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6888 | 1871.9997 | 48.4678
MBZ-1.RR.717.1 | 24291439146403 | Moulovibazar, East Girjapara, Oshid Chandra Dev Roy | 2019-07-16 | NQ1007 | 3.9 | 715 | 3.9 | 716 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6888 | 1871.9997 | 41.0923
MBZ-1.RR.717.2 | 24291439146403 | Moulovibazar, East Girjapara, Oshid Chandra Dev Roy | 2021-01-25 | NQ1003 | 10.6 | 146 | 10.6 | 147 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6888 | 1871.9997 | 111.6867
MBZ-1.RR.718.1 | 24291389146438 | Moulovibazar, East Girjapara, H # 51, Sudendu Kumar Vottacharja | 2019-07-16 | NQ1007 | 9.6 | 717 | 9.4 | 718 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6888 | 1871.9997 | 99.0429
MBZ-1.RR.719.1 | 24291589146450 | Moulovibazar, East Girjapara, H # 58, Tin Bon Villa | 2019-07-16 | NQ1007 | 23.3 | 719 | 23.3 | 720 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 23.3 | 23.3 | 1.398 | 1.398 | 0.0007168 | 100% | 0% | 1.398 | 1.398 | 0.0011869 | 28 | 0.028025 | 0.028025 |  | 0 | 0 | 6888 | 1871.9997 | 245.5
MBZ-1.RR.720.1 | 24291589146450 | Moulovibazar, East Girjapara, Laila Monjil | 2019-07-16 | NQ1007 | 11.8 | 721 | 12 | 722 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6888 | 1871.9997 | 126.4378
MBZ-1.RR.721.1 | 24291759146452 | Moulovibazar, East Girjapara, Horipodo Gosh | 2019-07-16 | NQ1007 | 12.2 | 723 | 12.2 | 724 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 6 | 0 | 6834 | 1919.9997 | 128.457
MBZ-1.RR.722.1 | 24291759146452 | Moulovibazar, East Girjapara, Monoronjon | 2019-07-16 | NQ1007 | 4.6 | 725 | 4.6 | 726 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6840 | 1919.9997 | 48.4678
MBZ-1.RR.723.1 | 24291759146452 | Moulovibazar, East Girjapara, Bissojit Vottacharja | 2019-07-16 | NQ1007 | 4.3 | 727 | 4.3 | 728 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6840 | 1919.9997 | 45.3069
MBZ-1.RR.724.1 | 24291269146445 | Moulovibazar, East Girjapara, H # 28/1, Rokib Cottage | 2019-07-16 | NQ1007 | 13 | 729 | 13 | 730 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6888 | 1871.9997 | 136.9743
MBZ-1.RR.725.1 | 24291039146447 | Moulovibazar, East Girjapara, Balisohosro Villa, Md. Bodrul Hossen | 2019-07-16 | NQ1007 | 7.6 | 731 | 7.7 | 732 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6888 | 1871.9997 | 81.1309
MBZ-1.RR.726.1 | 24291399146396 | Moulovibazar, East Girjapara, H # 21, Ojoy Kumar | 2019-07-16 | NQ1007 | 3 | 733 | 3.1 | 734 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6888 | 1871.9997 | 32.6631
MBZ-1.RR.727.1 | 24291349146402 | Moulovibazar, East Girjapara, Advocate Ronjit Kumar Gosh | 2019-07-16 | NQ1007 | 13.1 | 735 | 13.1 | 736 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6888 | 1871.9997 | 138.0279
MBZ-1.RR.728.1 | 24292829147127 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Rais Mia | 2019-07-17 | NQ1007 | 3.3 | 759 | 3.3 | 760 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6672 | 2087.9997 | 34.7704
MBZ-1.RR.729.1 | 24292829147127 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Rais Mia | 2019-07-17 | NQ1007 | 3.8 | 761 | 3.8 | 762 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6672 | 2087.9997 | 40.0386
MBZ-1.RR.729.2 | 24292829147127 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Rais Mia | 2021-01-26 | LU1001 | 2.8 | 102 | 2.8 | 103 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6672 | 2087.9997 | 29.5021
MBZ-1.RR.730.1 | 24292869147134 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Sumon Villa | 2019-07-17 | NQ1007 | 2.9 | 765 | 2.9 | 766 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6672 | 2087.9997 | 30.5558
MBZ-1.RR.731.1 | 24292729147178 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Abdul Motleb | 2019-07-17 | NQ1007 | 5.8 | 767 | 5.8 | 768 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6672 | 2087.9997 | 61.1116
MBZ-1.RR.732.1 | 24292799147194 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Kosru Membar | 2019-07-17 | NQ1007 | 7.6 | 769 | 7.7 | 770 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6672 | 2087.9997 | 81.1309
MBZ-1.RR.733.1 | 24292799147194 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Kosru Membar | 2019-07-17 | NQ1007 | 8 | 771 | 8 | 772 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6672 | 2087.9997 | 84.2919
MBZ-1.RR.734.1 | 24292539147232 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Jalal Khan | 2019-07-17 | NQ1007 | 3.4 | 773 | 3.4 | 774 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6672 | 2087.9997 | 35.824
MBZ-1.RR.735.1 | 24292329147276 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Manik Mia | 2019-07-17 | NQ1007 | 9.4 | 775 | 9.5 | 776 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6672 | 2087.9997 | 100.0966
MBZ-1.RR.735.2 | 24292329147276 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Manik Mia | 2021-09-25 | LU1001 | 18.1 | 11 | 18.1 | 12 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6672 | 2087.9997 | 190.7103
MBZ-1.RR.736.1 | 24292329147276 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Manik Mia | 2019-07-17 | NQ1007 | 8 | 777 | 8 | 778 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6672 | 2087.9997 | 84.2919
MBZ-1.RR.737.1 | 24292329147276 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Manik Mia | 2019-07-17 | NQ1007 | 36.1 | 779 | 36.1 | 780 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 36.1 | 36.1 | 2.166 | 2.166 | 0.0007168 | 100% | 0% | 2.166 | 2.166 | 0.0011869 | 28 | 0.043421 | 0.043421 |  | 0 | 0 | 6672 | 2087.9997 | 380.367
MBZ-1.RR.738.1 | 24292499147298 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Raiaan's House | 2019-07-17 | NQ1007 | 15 | 781 | 15.3 | 782 | 2022-01-01 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 6.5 | 0 | 6665.5 | 2087.9997 | 161.0885
MBZ-1.RR.738.2 | 24292499147298 | Moulovibazar, Borshijora, Maizpara, Shomshernogor Road, Raiaan's House | 2022-10-06 | MN1018 | 15.9 | 28 | 15.6 | 29 | 2022-10-06 | 2022-10-06 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 0 | 2087.9997 | 39.1784
MBZ-1.RR.739.1 | 24292049147362 | Moulovibazar, Borshijora, Sonar Bazar Road, M.G. Kibria Fattah | 2019-07-17 | NQ1007 | 9.1 | 783 | 9.1 | 784 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6624 | 2135.9997 | 95.882
MBZ-1.RR.740.1 | 24291639147348 | Moulovibazar, Borshijora, Sonar Bazar Road, Ali Villa | 2019-07-17 | NQ1007 | 11.4 | 785 | 11.4 | 786 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6624 | 2135.9997 | 120.1159
MBZ-1.RR.741.1 | 24291169147341 | Moulovibazar, Borshijora, Sonar Bazar Road, Md. Rajon | 2019-07-17 | NQ1007 | 11.4 | 787 | 11.4 | 788 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6624 | 2135.9997 | 120.1159
MBZ-1.RR.742.1 | 24291069147333 | Moulvibazar, Borshijora, Pahar, Sona Bazar Road, Parvin Villa | 2019-07-18 | NQ1007 | 9.8 | 1 | 9.8 | 2 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6624 | 2135.9997 | 103.2575
MBZ-1.RR.743.1 | 24290909147382 | Moulvibazar, Borshijora, Pahar, Sona Bazar Road, Sundor Ali | 2019-07-18 | NQ1007 | 5.9 | 3 | 5.9 | 4 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6624 | 2135.9997 | 62.1652
MBZ-1.RR.744.1 | 24290849147384 | Moulvibazar, Borshijora, Pahar, Sona Bazar Road, Alauddin Mia | 2019-07-18 | NQ1007 | 5.6 | 5 | 5.6 | 6 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6624 | 2135.9997 | 59.0043
MBZ-1.RR.745.1 | 24290599147321 | Moulvibazar, Borshijora, Pahar, Sona Bazar Road, Beka Mura Villa | 2019-07-18 | NQ1007 | 4.5 | 7 | 4.5 | 8 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6624 | 2135.9997 | 47.4142
MBZ-1.RR.746.1 | 24290559147263 | Moulvibazar, Borshijora, Pahar, Sona Bazar Road, Tajullah | 2019-07-18 | NQ1007 | 5.3 | 9 | 5.3 | 10 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6624 | 2135.9997 | 55.8434
MBZ-1.RR.747.1 | 24290189147267 | Moulvibazar, Borshijora, Pahar, Sona Bazar Road, Arjad Ullah | 2019-07-18 | NQ1007 | 9.2 | 11 | 9.2 | 12 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6624 | 2135.9997 | 96.9356
MBZ-1.RR.748.1 | 24290469147362 | Moulvibazar, Borshijora, Pahar, Notun Bazar Road, Salim Ahmed | 2019-07-18 | NQ1007 | 5.9 | 13 | 5.9 | 14 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6624 | 2135.9997 | 62.1652
MBZ-1.RR.749.1 | 24290289147316 | Moulvibazar, Borshijora, Pahar, Notun Bazar Road, Abdul Hai Ripon | 2019-07-18 | NQ1007 | 3.6 | 15 | 3.6 | 16 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6624 | 2135.9997 | 37.9313
MBZ-1.RR.750.1 | 24290159147328 | Moulvibazar, Borshijora, Pahar, Notun Bazar Road, Abdul Kalam | 2019-07-18 | NQ1007 | 11.8 | 17 | 11.9 | 18 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6624 | 2135.9997 | 125.3841
MBZ-1.RR.751.1 | 24295079145353 | Moulovibazar, Boliarbagh, 28 Bigha Road, Korpan Ulla | 2019-07-20 | MP1032 | 15.7 | 120 | 15.7 | 121 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 6840 | 1919.9997 | 165.4228
MBZ-1.RR.752.1 | 24295159145356 | Moulovibazar, Boliarbagh, 28 Bigha Road, Abdul Malek | 2019-07-20 | MP1032 | 4.6 | 122 | 4.6 | 123 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6840 | 1919.9997 | 48.4678
MBZ-1.RR.753.1 | 24295329145364 | Moulovibazar, Boliarbagh, 28 Bigha Road, Sirajul Islam | 2019-07-20 | MP1032 | 12.6 | 124 | 12.3 | 125 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6840 | 1919.9997 | 129.5987
MBZ-1.RR.754.1 | 24295399145366 | Moulovibazar, Boliarbagh, 28 Bigha Road, Beside Forman Mia | 2019-07-20 | MP1032 | 3.1 | 126 | 3.1 | 127 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6840 | 1919.9997 | 32.6631
MBZ-1.RR.755.1 | 24295499145368 | Moulovibazar, Boliarbagh, 28 Bigha Road, Koium | 2019-07-20 | MP1032 | 4.8 | 128 | 4.8 | 129 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6840 | 1919.9997 | 50.5751
MBZ-1.RR.756.1 | 24295599145367 | Moulovibazar, Boliarbagh, 28 Bigha Road, Beside Helal | 2019-07-20 | MP1032 | 9.9 | 130 | 10 | 131 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6840 | 1919.9997 | 105.3648
MBZ-1.RR.757.1 | 24295689145370 | Moulovibazar, Boliarbagh, 28 Bigha Road, Mahmud Ali | 2019-07-20 | MP1032 | 7.4 | 132 | 7.4 | 133 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6840 | 1919.9997 | 77.97
MBZ-1.RR.757.2 | 24295689145370 | Moulovibazar, Boliarbagh, 28 Bigha Road, Mahmud Ali | 2021-01-27 | NQ1007 | 15.6 | 107 | 15.6 | 108 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6840 | 1919.9997 | 164.3691
MBZ-1.RR.758.1 | 24295929145372 | Moulovibazar, Boliarbagh, 28 Bigha Road, Ambian Miah | 2019-07-20 | MP1032 | 15.4 | 134 | 15.4 | 135 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6840 | 1919.9997 | 162.2618
MBZ-1.RR.758.2 | 24295929145372 | Moulovibazar, Boliarbagh, 28 Bigha Road, Ambian Miah | 2021-01-27 | NQ1007 | 3.3 | 109 | 3.3 | 110 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6840 | 1919.9997 | 34.7704
MBZ-1.RR.759.1 | 24292899146276 | Moulovibazar, Court Road, Pulokpur Kaiosto | 2019-07-20 | MP1032 | 12 | 136 | 11.8 | 137 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6840 | 1919.9997 | 124.3305
MBZ-1.RR.760.1 | 24303429146541 | Moulovibazar, Uttor Mulaem, Bodrul Mia | 2019-07-21 | MP1032 | 12.3 | 164 | 12.3 | 165 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6768 | 1991.9997 | 129.5987
MBZ-1.RR.761.1 | 24320779146392 | Moulovibazar, Ekatona, Burikona, Beraimabad Road, Saiful Islam | 2019-07-21 | MP1032 | 12.2 | 166 | 12.2 | 167 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6792 | 1967.9997 | 128.5451
MBZ-1.RR.762.1 | 24320779146392 | Moulovibazar, Ekatona, Burikona, Beraimabad Road, Serajul Islam | 2019-07-21 | MP1032 | 9.7 | 168 | 9.7 | 169 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6792 | 1967.9997 | 102.2039
MBZ-1.RR.763.1 | 24320569146389 | Moulovibazar, Ekatona, Burikona, Beraimabad Road, Sohel | 2019-07-21 | MP1032 | 9.3 | 170 | 9.3 | 171 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6792 | 1967.9997 | 97.9893
MBZ-1.RR.763.2 | 24320569146389 | Moulovibazar, Ekatona, Burikona, Beraimabad Road, Sohel | 2020-10-05 | NQ1000 | 0.8 | 3 | 0.8 | 4 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 0.8 | 0.8 | 0.048 | 0.048 | 0.0007168 | 100% | 0% | 0.048 | 0.048 | 0.0011869 | 28 | 0.00096224 | 0.00096224 |  | 0 | 0 | 6792 | 1967.9997 | 8.4292
MBZ-1.RR.763.3 | 24320569146389 | Moulovibazar, Ekatona, Burikona, Beraimabad Road, Sohel | 2020-10-05 | NQ1000 | 10.4 | 7 | 10.4 | 8 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6792 | 1967.9997 | 109.5794
MBZ-1.RR.764.1 | 24305619147071 | Moulovibazar, Kuisar, Azadur Rohman | 2019-07-22 | MP1032 | 10.7 | 173 | 10.7 | 174 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6816 | 1943.9997 | 112.7403
MBZ-1.RR.764.2 | 24305619147071 | Moulovibazar, Kuisar, Azadur Rohman | 2019-07-22 | MP1032 | 9.7 | 175 | 9.7 | 176 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6816 | 1943.9997 | 102.2039
MBZ-1.RR.765.1 | 24305779147069 | Moulovibazar, Kuisar, Anwar Mia | 2019-07-22 | MP1032 | 2 | 177 | 2 | 178 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6816 | 1943.9997 | 21.073
MBZ-1.RR.766.1 | 24305779147069 | Moulovibazar, Kuisar, Anwar Mia | 2019-07-22 | MP1032 | 12.2 | 179 | 12.2 | 180 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6816 | 1943.9997 | 128.5451
MBZ-1.RR.767.1 | 24310169147085 | Moulovibazar, Kuisar, Soiod Ersad Ali | 2019-07-22 | MP1032 | 3.2 | 181 | 3.2 | 182 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6816 | 1943.9997 | 33.7167
MBZ-1.RR.768.1 | 24310449147071 | Moulovibazar, Kuisar, Soiod Saad Ali | 2019-07-22 | MP1032 | 13.6 | 183 | 13.6 | 184 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6816 | 1943.9997 | 143.2961
MBZ-1.RR.769.1 | 24310449147071 | Moulovibazar, Kuisar, Beside Soiod Saad Ali | 2019-07-22 | MP1032 | 15.1 | 185 | 14.8 | 186 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6816 | 1943.9997 | 155.9399
MBZ-1.RR.770.1 | 24310449147071 | Moulovibazar, Kuisar, Mohammad Ali | 2019-07-22 | MP1032 | 18.2 | 187 | 18.2 | 188 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 6816 | 1943.9997 | 191.764
MBZ-1.RR.771.1 | 24302999143451 | Moulovibazar, Konokpur, Sylhet Road, Mosabbir Khan | 2019-07-23 | MP1032 | 4.1 | 211 | 4.1 | 212 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6984 | 1775.9997 | 43.1996
MBZ-1.RR.772.1 | 24302999143451 | Moulovibazar, Konokpur, Sylhet Road, Mosabbir Khan | 2019-07-23 | MP1032 | 8.7 | 213 | 8.7 | 214 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6984 | 1775.9997 | 91.6674
MBZ-1.RR.773.1 | 24302819143460 | Moulovibazar, Konokpur, Sylhet Road, Soiad Mun Ali | 2019-07-23 | MP1032 | 11.5 | 215 | 11.2 | 216 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6984 | 1775.9997 | 118.0086
MBZ-1.RR.774.1 | 24295339144059 | Moulovibazar, shah Bondar, Majkandi Road, Sufia Nibash | 2019-07-23 | MP1032 | 10.3 | 217 | 10 | 218 | 2022-01-01 | [9 empty] | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0
MBZ-1.RR.775.1 | 24295269144058 | Moulovibazar, shah Bondar, Majkandi Road, Abdul Musabbir | 2019-07-23 | MP1032 | 3.7 | 219 | 3.7 | 220 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6984 | 1775.9997 | 38.985
MBZ-1.RR.776.1 | 24295769143586 | Moulovibazar, shah Bondar, Majkandi, Abdul Baset | 2019-07-23 | MP1032 | 11.4 | 221 | 11.4 | 222 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6984 | 1775.9997 | 120.1159
MBZ-1.RR.777.1 | 24295969143552 | Moulovibazar, shah Bondar, Maijpara, Munshi Bari, Suja Muhaimud | 2019-07-23 | MP1032 | 4.1 | 223 | 4.1 | 224 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6984 | 1775.9997 | 43.1996
MBZ-1.RR.778.1 | 24295719143561 | Moulovibazar, shah Bondar, Maijpara, Munshi Bari, Fuad Jaman | 2019-07-23 | MP1032 | 5.3 | 225 | 5.3 | 226 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6984 | 1775.9997 | 55.8434
MBZ-1.RR.779.1 | 24295719143561 | Moulovibazar, shah Bondar, Maijpara, Munshi Bari, Forhad Jaman | 2019-07-23 | MP1032 | 11.2 | 227 | 11.2 | 228 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6984 | 1775.9997 | 118.0086
MBZ-1.RR.780.1 | 24295719143561 | Moulovibazar, shah Bondar, Maijpara, Munshi Bari, Forhad Jaman | 2019-07-23 | MP1032 | 3.1 | 229 | 3.1 | 230 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6984 | 1775.9997 | 32.6631
MBZ-1.RR.781.1 | 24295389143297 | Moulovibazar, Fotepur, Subir Deb | 2019-07-23 | MP1032 | 1.6 | 231 | 1.6 | 232 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6984 | 1775.9997 | 16.8584
MBZ-1.RR.782.1 | 24295389143297 | Moulovibazar, Fotepur, Horipado | 2019-07-23 | MP1032 | 1.7 | 233 | 1.7 | 234 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7152 | 1607.9997 | 17.912
MBZ-1.RR.782.2 | 24295389143297 | Moulovibazar, Fotepur, Horipado | 2022-10-26 | MN1018 | 3.6 | 69 | 3.5 | 70 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 0 | 1607.9997 | 6.7693
MBZ-1.RR.783.1 | 24295469143279 | Moulovibazar, Fotepur, Digendro | 2019-07-23 | MP1032 | 10.6 | 235 | 10.6 | 236 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6984 | 1775.9997 | 111.6867
MBZ-1.RR.784.1 | 24283789146286 | Moulvibazar, Moddho Bonbithi Residential Area, Wapda Road, Resma Begum | 2019-07-07 | MP1032 | 13.6 | 463 | 13.2 | 464 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6720 | 2039.9997 | 139.0816
MBZ-1.RR.785.1 | 24282719146482 | Moulovibazar, Bonosree R/A, Sohid Mukit Road, Muhibur Rohman | 2019-07-07 | MP1032 | 4.7 | 465 | 4.7 | 466 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6720 | 2039.9997 | 49.5215
MBZ-1.RR.786.1 | 24282329146513 | Moulovibazar, Bonosree R/A, Sohid Mukit Road, Folsu Mia | 2019-07-07 | MP1032 | 4.5 | 467 | 4.5 | 468 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6720 | 2039.9997 | 47.4142
MBZ-1.RR.787.1 | 24284099146470 | Moulovibazar, Sonapur Area, Sonapur Road, Monir Mia, Miah Monjil | 2019-07-07 | MP1032 | 4.7 | 469 | 4.7 | 470 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6720 | 2039.9997 | 49.5215
MBZ-1.RR.788.1 | 24284099146470 | Moulovibazar, Sonapur Area, Sonapur Road, Abdul Monaem Gong | 2019-07-07 | MP1032 | 1.9 | 471 | 1.9 | 472 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 3.5 | 0 | 6716.5 | 2039.9997 | 20.0113
MBZ-1.RR.788.2 | 24284099146470 | Moulovibazar, Sonapur Area, Sonapur Road, Abdul Monaem Gong | 2022-04-09 | NQ1007 | 10.9 | 134 | 11 | 135 | 2022-04-09 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 4368 | 2039.9997 | 84.7826
MBZ-1.RR.789.1 | 24283949146462 | Moulovibazar, Sonapur Area, Sonapur Road, Habibur Rohman | 2019-07-07 | MP1032 | 6.6 | 473 | 6.6 | 474 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6720 | 2039.9997 | 69.5408
MBZ-1.RR.790.1 | 24283949146462 | Moulovibazar, Sonapur Area, Sonapur Road, Beside Habibur Rohman | 2019-07-07 | MP1032 | 8.5 | 475 | 8.5 | 476 | 2022-01-01 | 2022-10-08 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6720 | 2039.9997 | 89.5601
MBZ-1.RR.791.1 | 24291769145071 | Moulovibazar, East Helalpur, Khedur Road, Sujon Ahmed | 2019-07-25 | MP1032 | 4.1 | 264 | 4.1 | 265 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7008 | 1751.9997 | 43.1996
MBZ-1.RR.792.1 | 24291089145107 | Moulovibazar, East Helalpur, Khedur Road, Sheikh Abdur Rob | 2019-07-25 | MP1032 | 11.8 | 266 | 11.8 | 267 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7008 | 1751.9997 | 124.3305
MBZ-1.RR.792.2 | 24291089145107 | Moulovibazar, East Helalpur, Khedur Road, Sheikh Abdur Rob | 2019-07-25 | MP1032 | 10.4 | 268 | 10.4 | 269 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7008 | 1751.9997 | 109.5794
MBZ-1.RR.793.1 | 24291089145107 | Moulovibazar, East Helalpur, Khedur Road, Sheikh Abdur Rob | 2019-07-25 | MP1032 | 12.6 | 270 | 12.6 | 271 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7176 | 1583.9997 | 132.7597
MBZ-1.RR.793.2 | 24291089145107 | Moulovibazar, East Helalpur, Khedur Road, Sheikh Abdur Rob | 2022-10-27 | MN1018 | 5.6 | 73 | 5.6 | 74 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 0 | 1583.9997 | 10.6693
MBZ-1.RR.794.1 | 24285289145031 | Moulovibazar, West Mostofapur, Khedur Road, Akim Mia | 2019-07-25 | MP1032 | 3.8 | 272 | 3.8 | 273 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6960 | 1799.9997 | 40.0386
MBZ-1.RR.795.1 | 24285459145021 | Moulovibazar, West Mostofapur, Khedur Road, Abdul Khalek | 2019-07-25 | MP1032 | 4.2 | 274 | 4.2 | 275 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6960 | 1799.9997 | 44.2532
MBZ-1.RR.796.1 | 24285419144598 | Moulovibazar, West Mostofapur, Khedur Road, Tanvir Ahmed Sumon | 2019-07-25 | MP1032 | 7.6 | 276 | 7.6 | 277 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6960 | 1799.9997 | 80.0773
MBZ-1.RR.797.1 | 24285289145079 | Moulovibazar, West Mostofapur, Khedur Road, Ersad | 2019-07-25 | MP1032 | 10.1 | 278 | 10.1 | 279 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6960 | 1799.9997 | 106.4185
MBZ-1.RR.797.2 | 24285289145079 | Moulovibazar, West Mostofapur, Khedur Road, Ersad | 2020-10-06 | NQ1002 | 21.6 | 87 | 21.6 | 88 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 6960 | 1799.9997 | 227.588
MBZ-1.RR.798.1 | 24285009145168 | Moulovibazar, Mostofapur, Mostofapur Road, Altafur Rohman | 2019-07-25 | MP1032 | 9.6 | 280 | 8.9 | 281 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6960 | 1799.9997 | 93.7747
MBZ-1.RR.799.1 | 24285129145179 | Moulovibazar, Mostofapur, Mostofapur Road, Soiod Mehedi Hasan | 2019-07-25 | MP1032 | 9.3 | 282 | 9.3 | 283 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 120 | 0 | 6840 | 1799.9997 | 96.647
MBZ-1.RR.800.1 | 24284779145219 | Moulovibazar, Mostofapur, Mostofapur Road, Soiod Foysal Ahmed | 2019-07-25 | MP1032 | 9.3 | 284 | 9.3 | 285 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6960 | 1799.9997 | 97.9893
MBZ-1.RR.801.1 | 24293939145467 | Moulvibazar, Shabia, Word - 3, Shaha Moulali Road, Somaronjon | 2019-07-20 | MP1032 | 13.2 | 118 | 13.2 | 119 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6840 | 1919.9997 | 139.0816
MBZ-1.RR.802.1 | 24295399145281 | Moulvibazar, Chadni Ghat, Boliyar Bag, Ataispaika, Toffail Ahammed | 2019-07-21 | MP1032 | 12.9 | 138 | 12.9 | 139 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6840 | 1919.9997 | 135.9206
MBZ-1.RR.803.1 | 24294829145281 | Moulvibazar, Chadni Ghat, Boliyar Bag, Ataispaika, Abdus Salam | 2019-07-21 | MP1032 | 9.5 | 142 | 9.5 | 143 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6840 | 1919.9997 | 100.0966
MBZ-1.RR.804.1 | 24294579145288 | Moulvibazar, Chadni Ghat, Boliyar Bag, Ataispaika, Asraf | 2019-07-21 | MP1032 | 6.1 | 146 | 6.1 | 147 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6840 | 1919.9997 | 64.2725
MBZ-1.RR.805.1 | 24294439145268 | Moulvibazar, Chadni Ghat, Boliyar Bag, Chadni Ghat Road, Masud Ahammed | 2019-07-21 | MP1032 | 11.1 | 148 | 11.1 | 149 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6840 | 1919.9997 | 116.9549
MBZ-1.RR.805.2 | 24294439145268 | Moulvibazar, Chadni Ghat, Boliyar Bag, Chadni Ghat Road, Masud Ahammed | 2019-07-21 | MP1032 | 2.7 | 150 | 2.7 | 151 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6840 | 1919.9997 | 28.4485
MBZ-1.RR.806.1 | 24294509145262 | Moulvibazar, Chadni Ghat, Boliyar Bag, Chadni Ghat Road, Sazzad | 2019-07-21 | MP1032 | 11 | 152 | 11 | 153 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6840 | 1919.9997 | 115.9013
MBZ-1.RR.807.1 | 24294509145262 | Moulvibazar, Chadni Ghat, Boliyar Bag, Chadni Ghat Road, Bodrul | 2019-07-21 | MP1032 | 15.8 | 154 | 15.8 | 155 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 6840 | 1919.9997 | 166.4764
MBZ-1.RR.808.1 | 24295949145201 | Moulvibazar, Chadni Ghat, Boliyar Bag, Boliyar Bag Road, Khondokar Abdul Muhid | 2019-07-21 | MP1032 | 3.7 | 156 | 3.7 | 157 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6840 | 1919.9997 | 38.985
MBZ-1.RR.808.2 | 24295949145201 | Moulvibazar, Chadni Ghat, Boliyar Bag, Boliyar Bag Road, Khondokar Abdul Muhid | 2019-07-21 | MP1032 | 13.9 | 158 | 13.9 | 159 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6840 | 1919.9997 | 146.4571
MBZ-1.RR.809.1 | 24295359145117 | Moulvibazar, Chadni Ghat, Boliyar Bag, Abu Mia | 2019-07-21 | MP1032 | 13.3 | 160 | 13.3 | 161 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6840 | 1919.9997 | 140.1352
MBZ-1.RR.810.1 | 24295359145117 | Moulvibazar, Chadni Ghat, Boliyar Bag, Alaima | 2019-07-21 | MP1032 | 4.7 | 162 | 4.7 | 163 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6840 | 1919.9997 | 49.5215
MBZ-1.RR.811.1 | 24303739147378 | Moulvibazar, Akatona, Borman, Akatona Road, Sufia | 2019-07-22 | MP1032 | 12.5 | 189 | 12.5 | 190 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6816 | 1943.9997 | 131.706
MBZ-1.RR.811.2 | 24303739147378 | Moulvibazar, Akatona, Borman, Akatona Road, Sufia | 2019-07-22 | MP1032 | 8.6 | 191 | 8 | 192 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6816 | 1943.9997 | 84.2919
MBZ-1.RR.812.1 | 24304119147251 | Moulvibazar, Akatona, Borman, Bangaon, Borman Road, Akhlasur Rahaman | 2019-07-22 | MP1032 | 11.6 | 193 | 11.6 | 194 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6816 | 1943.9997 | 122.2232
MBZ-1.RR.812.2 | 24304119147251 | Moulvibazar, Akatona, Borman, Bangaon, Borman Road, Akhlasur Rahaman | 2022-03-27 | NQ1007 | 3.9 | 93 | 3.9 | 94 | 2022-03-27 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 4776 | 1943.9997 | 31.5228
MBZ-1.RR.813.1 | 24304119147251 | Moulvibazar, Akatona, Borman, Bangaon, Borman Road, Akhlasur Rahaman | 2019-07-22 | MP1032 | 4.8 | 195 | 4.8 | 196 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6816 | 1943.9997 | 50.5751
MBZ-1.RR.814.1 | 24304119147251 | Moulvibazar, Akatona, Borman, Bangaon, Borman Road, Akhlasur Rahaman | 2019-07-22 | MP1032 | 6.4 | 197 | 6.2 | 198 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6816 | 1943.9997 | 65.3262
MBZ-1.RR.815.1 | 24302589143414 | Moulvibazar, Durlovpur, Basid Mia | 2019-07-22 | MP1032 | 11.8 | 199 | 11.9 | 200 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6984 | 1775.9997 | 125.3841
MBZ-1.RR.816.1 | 24303199143391 | Moulvibazar, Durlovpur, Pachghori Bari, Abdul Kayum | 2019-07-22 | MP1032 | 10.4 | 201 | 10.4 | 202 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6984 | 1775.9997 | 109.5794
MBZ-1.RR.816.2 | 24303199143391 | Moulvibazar, Durlovpur, Pachghori Bari, Abdul Kayum | 2019-07-22 | MP1032 | 2.5 | 203 | 2.5 | 204 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6984 | 1775.9997 | 26.3412
MBZ-1.RR.817.1 | 24303019143386 | Moulvibazar, Durlovpur, Pachghori Bari, Golam Kibria | 2019-07-22 | MP1032 | 12.4 | 205 | 12.4 | 206 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6984 | 1775.9997 | 130.6524
MBZ-1.RR.818.1 | 24302819143380 | Moulvibazar, Durlovpur, Pachghori Bari, Momshad ahammod | 2019-07-22 | MP1032 | 12.3 | 207 | 12.3 | 208 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6984 | 1775.9997 | 129.5987
MBZ-1.RR.818.2 | 24302819143380 | Moulvibazar, Durlovpur, Pachghori Bari, Momshad ahammod | 2019-07-22 | MP1032 | 3.4 | 209 | 3.4 | 210 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6984 | 1775.9997 | 35.824
MBZ-1.RR.819.1 | 24295309143296 | Moulvibazar, Konokpur, Fotepur, Gupesh Dep | 2019-07-23 | MP1032 | 12.7 | 237 | 12.7 | 238 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6984 | 1775.9997 | 133.8133
MBZ-1.RR.820.1 | 24295309143296 | Moulvibazar, Konokpur, Fotepur, Gobendo Dep | 2019-07-23 | MP1032 | 3.3 | 239 | 3.2 | 240 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6984 | 1775.9997 | 33.7167
MBZ-1.RR.821.1 | 24295399143217 | Moulvibazar, Konokpur, Fotepur, Younus Siddiki | 2019-07-23 | MP1032 | 11.6 | 241 | 11.6 | 242 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 48 | 0 | 6936 | 1775.9997 | 121.5535
MBZ-1.RR.821.2 | 24295399143217 | Moulvibazar, Konokpur, Fotepur, Younus Siddiki | 2021-01-27 | LU1001 | 4.1 | 108 | 4.1 | 109 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 48 | 0 | 6936 | 1775.9997 | 42.9629
MBZ-1.RR.822.1 | 24300199143072 | Moulvibazar, Konokpur, Dulia, Asid Mia | 2019-07-23 | MP1032 | 11.2 | 243 | 11.2 | 244 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6984 | 1775.9997 | 118.0086
MBZ-1.RR.823.1 | 24300269143065 | Moulvibazar, Konokpur, Dulia, Salamia | 2019-07-23 | MP1032 | 2.9 | 245 | 2.9 | 246 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6984 | 1775.9997 | 30.5558
MBZ-1.RR.823.2 | 24300269143065 | Moulvibazar, Konokpur, Dulia, Salamia | 2019-07-23 | MP1032 | 29.6 | 250 | 28.2 | 251 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 28.2 | 28.2 | 1.692 | 1.692 | 0.0007168 | 100% | 0% | 1.692 | 1.692 | 0.0011869 | 28 | 0.033919 | 0.033919 |  | 0 | 0 | 6984 | 1775.9997 | 297.1288
MBZ-1.RR.824.1 | 24295949143083 | Moulvibazar, Konokpur, Dulia, Alomgir Mukit | 2019-07-23 | MP1032 | 12.9 | 252 | 12.5 | 253 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6984 | 1775.9997 | 131.706
MBZ-1.RR.824.2 | 24295949143083 | Moulvibazar, Konokpur, Dulia, Alomgir Mukit | 2019-07-23 | MP1032 | 5 | 254 | 5 | 255 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6984 | 1775.9997 | 52.6824
MBZ-1.RR.825.1 | 24295849143099 | Moulvibazar, Konokpur, Dulia, Anowar | 2019-07-23 | MP1032 | 3.4 | 256 | 3.4 | 257 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6984 | 1775.9997 | 35.824
MBZ-1.RR.826.1 | 24292559144507 | Moulvibazar, Kucher Mohal, Dhaka - Sylhet Road, Thai Aluminium Ind. Ltd. | 2019-07-23 | MP1032 | 12.5 | 258 | 12.4 | 259 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 5 | 0 | 7171 | 1583.9997 | 130.5778
MBZ-1.RR.826.2 | 24292559144507 | Moulvibazar, Kucher Mohal, Dhaka - Sylhet Road, Thai Aluminium Ind. Ltd. | 2022-03-29 | NQ1007 | 5.3 | 105 | 5.3 | 106 | 2022-03-29 | 2022-10-27 | MN1018 | 0.4 | 92 | 0.4 | 93 | 2022-10-27 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 5088 | 1583.9997
MBZ-1.RR.827.1 | 24292149144538 | Moulvibazar, Kucher Mohal, Dhaka - Sylhet Road, Yeahur Mia | 2019-07-23 | MP1032 | 10 | 260 | 10 | 261 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7008 | 1751.9997 | 105.3648
MBZ-1.RR.827.2 | 24292149144538 | Moulvibazar, Kucher Mohal, Dhaka - Sylhet Road, Yeahur Mia | 2019-07-23 | MP1032 | 7.9 | 262 | 7.9 | 263 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7008 | 1751.9997 | 83.2382
MBZ-1.RR.828.1 | 24284439145305 | Moulvibazar, Mostofapur R/A, Mostofapur Kuthir | 2019-07-25 | MP1032 | 12.3 | 288 | 12.3 | 289 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6960 | 1799.9997 | 129.5987
MBZ-1.RR.829.1 | 24284239145311 | Moulvibazar, Mostofapur R/A, Word - 4, Sazzadur Rahaman | 2019-07-25 | MP1032 | 5.2 | 290 | 5.2 | 291 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6960 | 1799.9997 | 54.7897
MBZ-1.RR.829.2 | 24284239145311 | Moulvibazar, Mostofapur R/A, Word - 4, Sazzadur Rahaman | 2019-07-25 | MP1032 | 9.8 | 292 | 9.8 | 293 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6960 | 1799.9997 | 103.2575
MBZ-1.RR.830.1 | 24284159145296 | Moulvibazar, Mostofapur R/A, Word - 4, Abul Hosen | 2019-07-25 | MP1032 | 20.1 | 294 | 20.1 | 295 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 20.1 | 20.1 | 1.206 | 1.206 | 0.0007168 | 100% | 0% | 1.206 | 1.206 | 0.0011869 | 28 | 0.024176 | 0.024176 |  | 1680 | 0 | 5280 | 1799.9997 | 171.1673
MBZ-1.RR.830.2 | 24284159145296 | Moulvibazar, Mostofapur R/A, Word - 4, Abul Hosen | 2020-10-05 | NQ1002 | 2.5 | 64 | 2.5 | 65 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 1680 | 0 | 5280 | 1799.9997 | 21.2895
MBZ-1.RR.831.1 | 24283889145269 | Moulvibazar, Mostofapur R/A, Word - 4, Soyud Obaydur Rahaman | 2019-07-25 | MP1032 | 11.6 | 296 | 11.6 | 297 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6960 | 1799.9997 | 122.2232
MBZ-1.RR.832.1 | 24283889145269 | Moulvibazar, Mostofapur R/A, Word - 4, Soyud Abu Bakkar | 2019-07-25 | MP1032 | 5.2 | 298 | 5.2 | 299 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6960 | 1799.9997 | 54.7897
MBZ-1.RR.833.1 | 24284289145244 | Moulvibazar, Mostofapur, Word - 4, Md. Mojibil Mia | 2019-07-25 | MP1032 | 7.4 | 300 | 7.4 | 301 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6960 | 1799.9997 | 77.97
MBZ-1.RR.834.1 | 24284289145244 | Moulvibazar, Mostofapur, Word - 4, Edon Mia | 2019-07-25 | MP1032 | 14.1 | 302 | 13.8 | 303 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6960 | 1799.9997 | 145.4034
MBZ-1.RR.835.1 | 24284289145244 | Moulvibazar, Mostofapur, Word - 4, Mosi Mia | 2019-07-25 | MP1032 | 20.8 | 304 | 20.9 | 305 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 20.9 | 20.9 | 1.254 | 1.254 | 0.0007168 | 100% | 0% | 1.254 | 1.254 | 0.0011869 | 28 | 0.025138 | 0.025138 |  | 0 | 0 | 6960 | 1799.9997 | 220.2125
MBZ-1.RR.836.1 | 24284289145244 | Moulvibazar, Mostofapur, Word - 4, Rofique Mia | 2019-07-25 | MP1032 | 10.4 | 306 | 10.5 | 307 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6960 | 1799.9997 | 110.6331
MBZ-1.RR.837.1 | 24284359145247 | Moulvibazar, Mostofapur, Word - 4, Israyel Mia | 2019-07-25 | MP1032 | 5 | 308 | 5 | 309 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6960 | 1799.9997 | 52.6824
MBZ-1.RR.838.1 | 24284049145237 | Moulvibazar, Mostofapur, Word - 4, Ankor Ali | 2019-07-25 | MP1032 | 11.9 | 310 | 11.9 | 311 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6960 | 1799.9997 | 125.3841
MBZ-1.RR.838.2 | 24284049145237 | Moulvibazar, Mostofapur, Word - 4, Ankor Ali | 2021-01-24 | MN1032 | 5.2 | 49 | 5.2 | 50 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6960 | 1799.9997 | 54.7897
MBZ-1.RR.839.1 | 24284049145237 | Moulvibazar, Mostofapur, Word - 4, Anowar Ali | 2019-07-25 | MP1032 | 11.4 | 312 | 11.4 | 313 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6960 | 1799.9997 | 120.1159
MBZ-1.RR.840.1 | 24283999145221 | Moulvibazar, Mostofapur, Word - 4, Ashrafullah | 2019-07-25 | MP1032 | 6.4 | 314 | 6.4 | 315 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6960 | 1799.9997 | 67.4335
MBZ-1.RR.841.1 | 24283919145235 | Moulvibazar, Mostofapur, Word - 4, Rokib Mia | 2019-07-25 | MP1032 | 3.6 | 316 | 3.6 | 317 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6960 | 1799.9997 | 37.9313
MBZ-1.RR.842.1 | 24290889145378 | Gobindasree, Purbo Dorkapon, Kamal mia | 2019-07-27 | MP1032 | 6.9 | 337 | 6.9 | 338 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6960 | 1799.9997 | 72.7017
MBZ-1.RR.843.1 | 24290639145378 | Gobindasree, Purbo Dorkapon, Mina Bagum | 2019-07-27 | MP1032 | 8 | 339 | 8 | 340 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6960 | 1799.9997 | 84.2919
MBZ-1.RR.844.1 | 24290599145320 | Gobindasree, West Dorkapon, Syed Moazzem Hossen | 2019-07-27 | MP1032 | 4.3 | 343 | 4.3 | 344 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6960 | 1799.9997 | 45.3069
MBZ-1.RR.845.1 | 24290439145402 | Purbo Dorkapon, Jolil Mastar | 2019-07-27 | MP1032 | 11.1 | 345 | 11.1 | 346 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6912 | 1847.9997 | 116.9549
MBZ-1.RR.846.1 | 24290769145424 | Purbo Dorkapon, Azad Mia | 2019-07-27 | MP1032 | 2.9 | 347 | 2.9 | 348 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6912 | 1847.9997 | 30.5558
MBZ-1.RR.847.1 | 24290879145427 | Purbo Dorkapon, Rafique Aysha Monjil | 2019-07-27 | MP1032 | 12.3 | 349 | 12.3 | 350 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6912 | 1847.9997 | 129.5987
MBZ-1.RR.848.1 | 24291029145477 | Gobindasree, Riazuddin | 2019-07-27 | MP1032 | 5.1 | 351 | 5.1 | 352 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6912 | 1847.9997 | 53.7361
MBZ-1.RR.849.1 | 24291029145477 | Gobindasree, Riazuddin | 2019-07-27 | MP1032 | 12.2 | 353 | 12.4 | 354 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6912 | 1847.9997 | 130.6524
MBZ-1.RR.850.1 | 24291029145477 | Gobindasree, Riazuddin | 2019-07-27 | MP1032 | 4.5 | 355 | 4.5 | 356 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6912 | 1847.9997 | 47.4142
MBZ-1.RR.851.1 | 24295369146286 | Chandnighat, South Mulaim, Abdul Bashir | 2019-07-20 | LX1011 | 10.1 | 122 | 10.1 | 123 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6792 | 1967.9997 | 106.4185
MBZ-1.RR.852.1 | 24294399146297 | Chandnighat, Royshree Road, Md.Bosir Box | 2019-07-20 | LX1011 | 9.1 | 124 | 9.1 | 125 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6792 | 1967.9997 | 95.882
MBZ-1.RR.853.1 | 24294579146238 | Chandnighat, Kulaura Road, Md.Farhan | 2019-07-20 | LX1011 | 4.5 | 127 | 4.5 | 128 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6792 | 1967.9997 | 47.4142
MBZ-1.RR.854.1 | 24301109146290 | Uttar Mulaim, Akatuna Road, Md.Mosharof | 2019-07-20 | LX1011 | 5.2 | 129 | 5.2 | 130 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6768 | 1991.9997 | 54.7897
MBZ-1.RR.855.1 | 24301379146294 | Uttar Mulaim, Akatuna Road, Md.Shofiqur Rahman | 2019-07-20 | LX1011 | 13.7 | 131 | 13.7 | 132 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6768 | 1991.9997 | 144.3498
MBZ-1.RR.856.1 | 24301559146290 | Uttar Mulaim, Akatuna Road, Rahmania Bhabon | 2019-07-20 | LX1011 | 12 | 133 | 12 | 134 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6768 | 1991.9997 | 126.4378
MBZ-1.RR.856.2 | 24301559146290 | Uttar Mulaim, Akatuna Road, Rahmania Bhabon | 2021-09-28 | LU1001 | 3.8 | 21 | 3.8 | 22 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6768 | 1991.9997 | 40.0386
MBZ-1.RR.857.1 | 24301559146290 | Uttar Mulaim, Akatuna Road, Rahmania Bhabon | 2019-07-20 | LX1011 | 19.1 | 135 | 19.1 | 136 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 6768 | 1991.9997 | 201.2468
MBZ-1.RR.858.1 | 24311079146122 | Akatuna, Kochua, Md.Rashid Mia | 2019-07-21 | LX1011 | 16.2 | 177 | 16.3 | 178 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 6816 | 1943.9997 | 171.7446
MBZ-1.RR.859.1 | 24311169146149 | Akatuna, Kochua, Siraz Mia | 2019-07-21 | LX1011 | 8.5 | 179 | 8.5 | 180 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6816 | 1943.9997 | 89.5601
MBZ-1.RR.860.1 | 24311169146149 | Akatuna, Kochua, Maruf Mia | 2019-07-21 | LX1011 | 12.2 | 181 | 12.2 | 182 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6816 | 1943.9997 | 128.5451
MBZ-1.RR.861.1 | 24311549146133 | Akatuna, Kochua, Abdul Mannan | 2019-07-21 | LX1011 | 12.4 | 183 | 11.4 | 184 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6816 | 1943.9997 | 120.1159
MBZ-1.RR.862.1 | 24311549146133 | Akatuna, Kochua, Rasel Mia | 2019-07-21 | LX1011 | 10 | 185 | 10 | 186 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6816 | 1943.9997 | 105.3648
MBZ-1.RR.863.1 | 24311549146133 | Akatuna, Kochua, Musabbir Mia | 2019-07-21 | LX1011 | 3.5 | 189 | 3.5 | 190 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6816 | 1943.9997 | 36.8777
MBZ-1.RR.864.1 | 24311529146176 | Akatuna, Kochua, Alauddin Mia | 2019-07-21 | LX1011 | 14.1 | 192 | 14.1 | 193 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6816 | 1943.9997 | 148.5644
MBZ-1.RR.865.1 | 24311529146176 | Akatuna, Kochua, Md.Lon Mia | 2019-07-21 | LX1011 | 6.5 | 196 | 6.5 | 197 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6816 | 1943.9997 | 68.4871
MBZ-1.RR.866.1 | 24311639146182 | Akatuna, Kochua, Mojib Mia | 2019-07-21 | LX1011 | 3.6 | 198 | 3.6 | 199 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6816 | 1943.9997 | 37.9313
MBZ-1.RR.866.2 | 24311639146182 | Akatuna, Kochua, Mojib Mia | 2021-09-26 | LU1001 | 6.6 | 15 | 6.6 | 16 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6816 | 1943.9997 | 69.5408
MBZ-1.RR.867.1 | 24311639146182 | Akatuna, Kochua, Mojib Mia | 2019-07-21 | LX1011 | 13.5 | 202 | 13.5 | 203 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6816 | 1943.9997 | 142.2425
MBZ-1.RR.867.2 | 24311639146182 | Akatuna, Kochua, Mojib Mia | 2021-09-26 | LU1001 | 13.3 | 17 | 13.5 | 18 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6816 | 1943.9997 | 142.2425
MBZ-1.RR.868.1 | 24311639146182 | Akatuna, Kochua, Mojib Mia | 2019-07-21 | LX1011 | 12.4 | 204 | 12.5 | 205 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6816 | 1943.9997 | 131.706
MBZ-1.RR.869.1 | 24311429146442 | Akatuna, Moulvibari, Tuku Mia Chiarman | 2019-07-22 | LX1011 | 13.5 | 206 | 13.5 | 207 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6816 | 1943.9997 | 142.2425
MBZ-1.RR.870.1 | 24311699146470 | Akatuna, Lomba bari, Abdul Bari | 2019-07-22 | LX1011 | 12.3 | 208 | 12.4 | 209 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6816 | 1943.9997 | 130.6524
MBZ-1.RR.871.1 | 24311699146470 | Akatuna, Lomba bari, Masud Mia | 2019-07-22 | LX1011 | 4.6 | 212 | 4.6 | 213 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6816 | 1943.9997 | 48.4678
MBZ-1.RR.872.1 | 24311699146470 | Akatuna, Lomba bari, Liton Mia | 2019-07-22 | LX1011 | 3.3 | 214 | 3.3 | 215 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6816 | 1943.9997 | 34.7704
MBZ-1.RR.873.1 | 24311849146474 | Akatuna, Lomba bari, Labu Mia | 2019-07-22 | LX1011 | 3.6 | 216 | 3.6 | 217 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6816 | 1943.9997 | 37.9313
MBZ-1.RR.874.1 | 24310959146440 | Akatuna, Lomba bari, Babu Mia | 2019-07-22 | LX1011 | 11.8 | 218 | 11.8 | 219 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6816 | 1943.9997 | 124.3305
MBZ-1.RR.875.1 | 24302019143591 | Konokpur, Durlovpur, Masuk Mia | 2019-07-23 | LX1011 | 11.3 | 234 | 11.3 | 235 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6984 | 1775.9997 | 119.0622
MBZ-1.RR.876.1 | 24302019143591 | Konokpur, Durlovpur, Kadir Mia | 2019-07-23 | LX1011 | 14.9 | 236 | 15 | 237 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6984 | 1775.9997 | 158.0472
MBZ-1.RR.877.1 | 24301499144067 | Konokpur, Durlovpur, Md. Amlu Mia | 2019-07-23 | LX1011 | 11.1 | 238 | 11.1 | 239 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6984 | 1775.9997 | 116.9549
MBZ-1.RR.878.1 | 24301279144066 | Konokpur, Dhopasa, Masud Mia | 2019-07-23 | LX1011 | 15.2 | 240 | 15.2 | 241 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6984 | 1775.9997 | 160.1545
MBZ-1.RR.879.1 | 24301279144066 | Konokpur, Dhopasa, Masud Mia | 2019-07-23 | LX1011 | 12.2 | 242 | 12.3 | 243 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6984 | 1775.9997 | 129.5987
MBZ-1.RR.880.1 | 24301279144066 | Konokpur, Dhopasa, Sekendar Mia | 2019-07-23 | LX1011 | 11.6 | 244 | 11.7 | 245 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6984 | 1775.9997 | 123.2768
MBZ-1.RR.881.1 | 24301269144022 | Konokpur, Dhopasa, Md. Aziz | 2019-07-23 | LX1011 | 13.5 | 247 | 13.5 | 248 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6984 | 1775.9997 | 142.2425
MBZ-1.RR.882.1 | 24301269144022 | Konokpur, Dhopasa, Azad | 2019-07-23 | LX1011 | 7 | 249 | 7 | 250 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6984 | 1775.9997 | 73.7554
MBZ-1.RR.883.1 | 24301269144022 | Konokpur, Dhopasa, Raza Mia | 2019-07-23 | LX1011 | 12.9 | 251 | 12.9 | 252 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6984 | 1775.9997 | 135.9206
MBZ-1.RR.884.1 | 24301269144022 | Konokpur, Dhopasa, Salim | 2019-07-23 | LX1011 | 13.3 | 253 | 13.3 | 254 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6984 | 1775.9997 | 140.1352
MBZ-1.RR.885.1 | 24300609144044 | Konokpur, Dhopasa, Akboruddin | 2019-07-23 | LX1011 | 8.8 | 255 | 8.8 | 256 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6984 | 1775.9997 | 92.721
MBZ-1.RR.886.1 | 24300609144044 | Konokpur, Dhopasa, Abu Ahmed | 2019-07-23 | LX1011 | 6.8 | 257 | 6.3 | 258 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6984 | 1775.9997 | 66.3798
MBZ-1.RR.887.1 | 24300439144017 | Konokpur, Dhopasa, Harun Roshid | 2019-07-23 | LX1011 | 12.1 | 259 | 12.1 | 260 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6984 | 1775.9997 | 127.4914
MBZ-1.RR.888.1 | 24291869144582 | Hilalpur, Syed Mohsin Ali Road, Mawlana Habibur rahman | 2019-07-25 | LX1011 | 20.7 | 261 | 20.7 | 262 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 20.7 | 20.7 | 1.242 | 1.242 | 0.0007168 | 100% | 0% | 1.242 | 1.242 | 0.0011869 | 28 | 0.024898 | 0.024898 |  | 0 | 0 | 7008 | 1751.9997 | 218.1052
MBZ-1.RR.889.1 | 24291869144582 | Hilalpur, Syed Mohsin Ali Road, Harun Rashid | 2019-07-25 | LX1011 | 12.8 | 263 | 12.8 | 264 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7008 | 1751.9997 | 134.867
MBZ-1.RR.890.1 | 24291729144573 | Hilalpur, Syed Mohsin Ali Road, Md. Kobir | 2019-07-25 | LX1011 | 7 | 265 | 7 | 266 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7008 | 1751.9997 | 73.7554
MBZ-1.RR.891.1 | 24291729144573 | Hilalpur, Syed Mohsin Ali Road, Ishak Mia | 2019-07-25 | LX1011 | 6.5 | 267 | 6.5 | 268 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7008 | 1751.9997 | 68.4871
MBZ-1.RR.892.1 | 24291689144581 | Hilalpur, Syed Mohsin Ali Road, Mobassir Mia | 2019-07-25 | LX1011 | 6.4 | 271 | 6.4 | 272 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7008 | 1751.9997 | 67.4335
MBZ-1.RR.893.1 | 24291639144584 | Hilalpur, Syed Mohsin Ali Road, Harun Rashid | 2019-07-25 | LX1011 | 14.9 | 273 | 14.9 | 274 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7008 | 1751.9997 | 156.9936
MBZ-1.RR.894.1 | 24291139145011 | Hilalpur, Forid Mia (Monwar Begum Mohila Member) | 2019-07-25 | LX1011 | 9.1 | 275 | 9.1 | 276 | 2022-01-01 | 2022-10-27 | MN1018 | 0.5 | 87 | 0.5 | 88 | 2022-10-27 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7176 | 1583.9997
MBZ-1.RR.895.1 | 24291879145033 | Moulvibazar Sador, Jugidohor, Pritinir | 2019-07-25 | LX1011 | 2.6 | 277 | 2.6 | 278 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7008 | 1751.9997 | 27.3949
MBZ-1.RR.896.1 | 24292019145091 | Moulvibazar Sador, Jugidohor, M/S Sri Loknath Thi Aluminium | 2019-07-25 | LX1011 | 10.7 | 279 | 10.7 | 280 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7008 | 1751.9997 | 112.7403
MBZ-1.RR.897.1 | 24292109145103 | Moulvibazar Sador, Borkapon, Md. Motiur Rahman | 2019-07-25 | LX1011 | 5.6 | 281 | 5.6 | 282 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7176 | 1583.9997 | 59.0043
MBZ-1.RR.897.2 | 24292109145103 | Moulvibazar Sador, Borkapon, Md. Motiur Rahman | 2022-10-27 | MN1018 | 4.6 | 77 | 4.6 | 78 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 0 | 1583.9997 | 8.764
MBZ-1.RR.898.1 | 24291969145106 | Boro Kapon, Sazzadur Mia Bari Rasta, Mostofa Mia | 2019-07-25 | LX1011 | 14.8 | 285 | 14.8 | 286 | 2022-01-01 | 2022-10-27 | MN1018 | 0.5 | 75 | 0.5 | 76 | 2022-10-27 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7176 | 1583.9997
MBZ-1.RR.899.1 | 24291969145104 | Boro Kapon, Sazzadur Mia Bari Rasta, Mobarok Mia | 2019-07-25 | LX1011 | 8 | 287 | 8 | 288 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7008 | 1751.9997 | 84.2919
MBZ-1.RR.900.1 | 24291969145104 | Boro Kapon, Sazzadur Mia Bari Rasta, Abdul Mannan | 2019-07-25 | LX1011 | 5 | 289 | 5 | 290 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7008 | 1751.9997 | 52.6824
MBZ-1.RR.901.1 | 24294629144172 | Moulavi Bazar, Purbo Poton Masjid Rd, Hazi Afsar | 2019-07-23 | NQ1007 | 1.9 | 207 | 1.9 | 208 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7008 | 1751.9997 | 20.0193
MBZ-1.RR.902.1 | 24294629144172 | Moulavi Bazar, Purbo Poton Masjid Rd, Aftab | 2019-07-23 | NQ1007 | 3.1 | 209 | 3.1 | 210 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7008 | 1751.9997 | 32.6631
MBZ-1.RR.903.1 | 24294319144187 | Moulavi Bazar, Purbo Poton Masjid Rd, Nur Ahmed | 2019-07-23 | NQ1007 | 10.2 | 211 | 10.3 | 212 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7008 | 1751.9997 | 108.5258
MBZ-1.RR.903.2 | 24294319144187 | Moulavi Bazar, Purbo Poton Masjid Rd, Nur Ahmed | 2022-03-29 | NQ1007 | 5 | 99 | 5 | 100 | 2022-03-29 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 4920 | 1751.9997 | 40.1252
MBZ-1.RR.904.1 | 24294859144261 | Moulavi Bazar, Sirainagar, Ali Akbor | 2019-07-23 | NQ1007 | 9.4 | 213 | 9.4 | 214 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7008 | 1751.9997 | 99.0429
MBZ-1.RR.905.1 | 24294729144259 | Moulavi Bazar, Sirainagar, Soiyod Akbor Ali | 2019-07-23 | NQ1007 | 5.7 | 215 | 5.7 | 216 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7008 | 1751.9997 | 60.0579
MBZ-1.RR.906.1 | 24294729144259 | Moulavi Bazar, Sirainagar, Soiyod Akoddos Ali | 2019-07-23 | NQ1007 | 9.8 | 217 | 10.2 | 218 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7008 | 1751.9997 | 107.4721
MBZ-1.RR.907.1 | 24294539144259 | Moulavi Bazar, Sirainagar, Akoddos Ali | 2019-07-23 | NQ1007 | 11.4 | 219 | 11.4 | 220 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7008 | 1751.9997 | 120.1159
MBZ-1.RR.908.1 | 24294889144336 | Moulavi Bazar, Sirainagar, Kadir | 2019-07-23 | NQ1007 | 6.1 | 221 | 6.1 | 222 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7008 | 1751.9997 | 64.2725
MBZ-1.RR.909.1 | 24272869144468 | Vujball, Goyghar, Mostofa | 2019-07-27 | MP1032 | 11.8 | 320 | 11.8 | 321 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6960 | 1799.9997 | 124.3305
MBZ-1.RR.910.1 | 24272869144468 | Vujball, Goyghar, Mostofa | 2019-07-27 | MP1032 | 18.1 | 322 | 18.1 | 323 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6960 | 1799.9997 | 190.7103
MBZ-1.RR.911.1 | 24272869144468 | Vujball, Goyghar, Mostofa | 2019-07-27 | MP1032 | 3.7 | 324 | 3.7 | 325 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6960 | 1799.9997 | 38.985
MBZ-1.RR.912.1 | 24272569144468 | Vujball, Goyghar, Mona Mia | 2019-07-27 | MP1032 | 4.4 | 326 | 4.4 | 327 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6960 | 1799.9997 | 46.3605
MBZ-1.RR.913.1 | 24272219144489 | Vujball, Goyghar, Norendrow Kumar Das | 2019-07-27 | MP1032 | 11.5 | 328 | 11.5 | 329 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6960 | 1799.9997 | 121.1695
MBZ-1.RR.914.1 | 24272389144435 | Vujball, Ajmaru, Shumon Pal | 2019-07-27 | MP1032 | 4 | 330 | 4 | 331 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6960 | 1799.9997 | 42.1459
MBZ-1.RR.915.1 | 24272389144435 | Vujball, Ajmaru, Shumon Pal | 2019-07-27 | MP1032 | 79.1 | 332 | 79.1 | 333 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 79.1 | 79.1 | 4.746 | 4.746 | 0.0007168 | 100% | 0% | 4.746 | 4.746 | 0.0011869 | 28 | 0.095141 | 0.095141 |  | 6 | 0 | 6954 | 1799.9997 | 832.8648
MBZ-1.RR.916.1 | 24291519145381 | Gobindosree, Dorkapon Road, Syed Masud Ali | 2019-07-27 | MP1032 | 6.6 | 335 | 7.2 | 336 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6912 | 1847.9997 | 75.8627
MBZ-1.RR.917.1 | 24291259145509 | Gobindosree, Word # 8, Fajlul Rahaman | 2019-07-28 | MP1032 | 13.4 | 363 | 13.4 | 364 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6912 | 1847.9997 | 141.1888
MBZ-1.RR.918.1 | 24291259145509 | Gobindosree, Word # 8, Mokid Islam | 2019-07-28 | MP1032 | 1.7 | 365 | 1.7 | 366 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6912 | 1847.9997 | 17.912
MBZ-1.RR.919.1 | 24291309145501 | Gobindosree, Word # 8, Oliur Rahaman | 2019-07-28 | MP1032 | 29.7 | 367 | 30.5 | 368 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 30.5 | 30.5 | 1.83 | 1.83 | 0.0007168 | 100% | 0% | 1.83 | 1.83 | 0.0011869 | 28 | 0.036685 | 0.036685 |  | 0 | 0 | 6912 | 1847.9997 | 321.3627
MBZ-1.RR.920.1 | 24291179145450 | Gobindosree, Word # 8, Tohid Mia | 2019-07-28 | MP1032 | 3.4 | 371 | 3.4 | 372 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6912 | 1847.9997 | 35.824
MBZ-1.RR.921.1 | 24291459145420 | Gobindosree, Word # 8, Hazi Mashukur Rahman | 2019-07-28 | MP1032 | 16.2 | 373 | 16.2 | 374 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 6912 | 1847.9997 | 170.691
MBZ-1.RR.922.1 | 24291459145420 | Gobindosree, Word # 8, Hazi Mashukur Rahman | 2019-07-28 | MP1032 | 8.2 | 375 | 8.3 | 376 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6912 | 1847.9997 | 87.4528
MBZ-1.RR.922.2 | 24291459145420 | Gobindosree, Word # 8, Hazi Mashukur Rahman | 2022-10-16 | MN1018 | 5.7 | 46 | 5.7 | 47 | 2022-10-16 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 0 | 1847.9997 | 12.6698
MBZ-1.RR.923.1 | 24291159145417 | Gobindosree, Word # 8, Masud Ahmed | 2019-07-28 | MP1032 | 13.3 | 377 | 13 | 378 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6912 | 1847.9997 | 136.9743
MBZ-1.RR.924.1 | 24291159145417 | Gobindosree, Word # 8, Masud Ahmed | 2019-07-28 | MP1032 | 6.8 | 379 | 6.3 | 380 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6912 | 1847.9997 | 66.3798
MBZ-1.RR.925.1 | 24291679145381 | Gobindosree, Word # 8, Durlov Vila | 2019-07-28 | MP1032 | 2.9 | 381 | 2.9 | 382 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6912 | 1847.9997 | 30.5558
MBZ-1.RR.926.1 | 24291679145388 | Gobindosree, Word # 8, Bilkis Tower | 2019-07-28 | MP1032 | 12 | 383 | 12 | 384 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6912 | 1847.9997 | 126.4378
MBZ-1.RR.927.1 | 24292059145424 | Gobindosree, Word # 8, Rakib Mia | 2019-07-28 | MP1032 | 3.3 | 385 | 3.3 | 386 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6912 | 1847.9997 | 34.7704
MBZ-1.RR.928.1 | 24292059145424 | Gobindosree, Word # 8, Mannan | 2019-07-28 | MP1032 | 12.1 | 387 | 12.1 | 388 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6912 | 1847.9997 | 127.4914
MBZ-1.RR.929.1 | 24291999145355 | Gobindosree, Darog Road, Khalek Monjil | 2019-07-28 | MP1032 | 4.2 | 389 | 4.2 | 390 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6912 | 1847.9997 | 44.2532
MBZ-1.RR.930.1 | 24291979145359 | Gobindosree, Darog Road, Khalek Monjil | 2019-07-28 | MP1032 | 3.9 | 391 | 3.9 | 392 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6912 | 1847.9997 | 41.0923
MBZ-1.RR.951.1 | 24310629146317 | Moulovi Bazar, Akatuna Village, Shamim Ahmed | 2019-07-21 | NQ1005 | 12.6 | 136 | 12.6 | 137 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6816 | 1943.9997 | 132.7597
MBZ-1.RR.951.2 | 24310629146317 | Moulovi Bazar, Akatuna Village, Shamim Ahmed | 2021-09-27 | LU1001 | 10.2 | 19 | 10.2 | 20 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6816 | 1943.9997 | 107.4721
MBZ-1.RR.952.1 | 24310759146316 | Moulovi Bazar, Akatuna Village, Dulal Complex | 2019-07-21 | NQ1005 | 13.6 | 138 | 13.6 | 139 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6816 | 1943.9997 | 143.2961
MBZ-1.RR.953.1 | 24312449146381 | Moulovi Bazar, Akatuna Village, Hazi Bari | 2019-07-21 | NQ1005 | 15.8 | 140 | 16 | 141 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6816 | 1943.9997 | 168.5837
MBZ-1.RR.954.1 | 24312449146381 | Moulovi Bazar, Akatuna Village, Hazi Bari | 2019-07-21 | NQ1005 | 21.6 | 142 | 21.6 | 143 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 6816 | 1943.9997 | 227.588
MBZ-1.RR.955.1 | 24303669147320 | Moulovi Bazar, Akatuna, Borman Village, Mobarok Miah | 2019-07-22 | NQ1005 | 13.1 | 165 | 13.1 | 166 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6816 | 1943.9997 | 138.0279
MBZ-1.RR.956.1 | 24303669147320 | Moulovi Bazar, Akatuna, Borman Village, Haris Miah | 2019-07-22 | NQ1005 | 14.4 | 167 | 14.4 | 168 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6816 | 1943.9997 | 151.7253
MBZ-1.RR.957.1 | 24302539143462 | Moulovi Bazar, Durlovpur, Touahid Miah | 2019-07-22 | NQ1005 | 11.2 | 169 | 11.2 | 170 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6984 | 1775.9997 | 118.0086
MBZ-1.RR.958.1 | 24302539143462 | Moulovi Bazar, Durlovpur, Mendi Miah | 2019-07-22 | NQ1005 | 13.1 | 171 | 13.1 | 172 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6984 | 1775.9997 | 138.0279
MBZ-1.RR.959.1 | 24302369143419 | Moulovi Bazar, Durlovpur, Anowar Parveg | 2019-07-22 | NQ1005 | 9.3 | 173 | 9.3 | 174 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6984 | 1775.9997 | 97.9893
MBZ-1.RR.960.1 | 24294559144110 | Moulovi Bazar, Konokpur, Shah Bondor, Poton, Abdul Oahid Babul | 2019-07-23 | NQ1005 | 11.6 | 193 | 11.6 | 194 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6984 | 1775.9997 | 122.2232
MBZ-1.RR.961.1 | 24294699144100 | Moulovi Bazar, Konokpur, Shah Bondor, Poton, Jakir Ahmed | 2019-07-23 | NQ1005 | 9.2 | 195 | 9.5 | 196 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6984 | 1775.9997 | 100.0966
MBZ-1.RR.962.1 | 24294659144086 | Moulovi Bazar, Konokpur, Shah Bondor, Poton, Shahid | 2019-07-23 | NQ1005 | 26.5 | 197 | 26.5 | 198 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 26.5 | 26.5 | 1.59 | 1.59 | 0.0007168 | 100% | 0% | 1.59 | 1.59 | 0.0011869 | 28 | 0.031874 | 0.031874 |  | 0 | 0 | 6984 | 1775.9997 | 279.2168
MBZ-1.RR.963.1 | 24294899144112 | Moulovi Bazar, Konokpur, Shah Bondor, Poton, Dulal Ahmed | 2019-07-23 | NQ1005 | 3.9 | 199 | 3.9 | 200 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6984 | 1775.9997 | 41.0923
MBZ-1.RR.964.1 | 24291229144480 | Moulovi Bazar, Hilalpur, Bahar, Modon Road, Somon | 2019-07-23 | NQ1005 | 8.7 | 201 | 8.7 | 202 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7008 | 1751.9997 | 91.6674
MBZ-1.RR.965.1 | 24291229144466 | Moulovi Bazar, Hilalpur, Bahar, Modon Road, Sayed Asaddor Ali | 2019-07-23 | NQ1005 | 9.3 | 203 | 9.3 | 204 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7008 | 1751.9997 | 97.9893
MBZ-1.RR.966.1 | 24283739144346 | Moulovi Bazar, Mostofapur, Bahar Mordon, Khalilur Rahman | 2019-07-25 | NQ1005 | 11.4 | 227 | 11.5 | 228 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7152 | 1607.9997 | 121.1695
MBZ-1.RR.967.1 | 24283989144292 | Moulovi Bazar, Mostofapur, Bahar Mordon, Rahi | 2019-07-25 | NQ1005 | 3.6 | 229 | 3.6 | 230 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7152 | 1607.9997 | 37.9313
MBZ-1.RR.968.1 | 24284139144224 | Moulovi Bazar, Mostofapur, Bahar Mordon, Khan Bari | 2019-07-25 | NQ1005 | 11.8 | 231 | 11.8 | 232 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7152 | 1607.9997 | 124.3305
MBZ-1.RR.969.1 | 24284139144224 | Moulovi Bazar, Mostofapur, Bahar Mordon, Khan Bari | 2019-07-25 | NQ1005 | 10.4 | 233 | 9.8 | 234 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7152 | 1607.9997 | 103.2575
MBZ-1.RR.970.1 | 24284139144224 | Moulovi Bazar, Mostofapur, Bahar Mordon, Shahabuddin | 2019-07-25 | NQ1005 | 11.9 | 235 | 11.9 | 236 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7152 | 1607.9997 | 125.3841
MBZ-1.RR.971.1 | 24284139144224 | Moulovi Bazar, Mostofapur, Bahar Mordon, Shahabuddin | 2019-07-25 | NQ1005 | 12.2 | 237 | 12.2 | 238 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7152 | 1607.9997 | 128.5451
MBZ-1.RR.971.2 | 24284139144224 | Moulovi Bazar, Mostofapur, Bahar Mordon, Shahabuddin | 2022-10-26 | MN1018 | 2.1 | 60 | 2.1 | 61 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 0 | 1607.9997 | 4.0616
MBZ-1.RR.972.1 | 24284179144222 | Moulovi Bazar, Mostofapur, Bahar Mordon, Sono Miah | 2019-07-25 | NQ1005 | 5.6 | 239 | 5.6 | 240 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7152 | 1607.9997 | 59.0043
MBZ-1.RR.972.2 | 24284179144222 | Moulovi Bazar, Mostofapur, Bahar Mordon, Sono Miah | 2022-10-26 | MN1018 | 16.8 | 66 | 16.8 | 67 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 0 | 1607.9997 | 32.4928
MBZ-1.RR.973.1 | 24290059145254 | West Dhorkapon, Ward # 9, Fokir Bari, Shah Bahuddinn | 2019-07-27 | NQ1005 | 23 | 262 | 23 | 263 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 23 | 23 | 1.38 | 1.38 | 0.0007168 | 100% | 0% | 1.38 | 1.38 | 0.0011869 | 28 | 0.027664 | 0.027664 |  | 0 | 0 | 6960 | 1799.9997 | 242.3391
MBZ-1.RR.974.1 | 24290059145254 | West Dhorkapon, Ward # 9, Fokir Bari, Shah Koies Mia | 2019-07-27 | NQ1005 | 11.4 | 264 | 11.4 | 265 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6960 | 1799.9997 | 120.1159
MBZ-1.RR.975.1 | 24290059145254 | West Dhorkapon, Ward # 9, Fokir Bari, Shah Fozlul Akhter | 2019-07-27 | NQ1005 | 13.7 | 266 | 13.4 | 267 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6960 | 1799.9997 | 141.1888
MBZ-1.RR.976.1 | 24290599145217 | Borkapon, Shekhergaon Road, Ward # 9, Makhon Mia (Beside Shahi Jame Mosque) | 2019-07-27 | NQ1005 | 10.5 | 268 | 10.5 | 269 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6936 | 1823.9997 | 110.6331
MBZ-1.RR.977.1 | 24290749145219 | Borkapon, Shekhergaon Road, Ward # 9, Baitul Hamd House | 2019-07-27 | NQ1005 | 14.4 | 271 | 14.4 | 272 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6936 | 1823.9997 | 151.7253
MBZ-1.RR.978.1 | 24290989145209 | Borkapon, Shekhergaon Road, Ward # 9, Mahmood Mia | 2019-07-27 | NQ1005 | 14.6 | 273 | 14.6 | 274 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6936 | 1823.9997 | 153.8326
MBZ-1.RR.979.1 | 24290979145190 | Borkapon, Shekhergaon Road, Ward # 9, Aankar Monjil | 2019-07-27 | NQ1005 | 7.6 | 275 | 7.6 | 276 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6936 | 1823.9997 | 80.0773
MBZ-1.RR.980.1 | 24290859145175 | Borkapon, Shekhergaon Road, Ward # 9, Motabber Hossen | 2019-07-27 | NQ1005 | 11.4 | 277 | 11.4 | 278 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6936 | 1823.9997 | 120.1159
MBZ-1.RR.981.1 | 24290789145173 | Borkapon, Shekhergaon Road, Ward # 9, Moijuddin Ahmed | 2019-07-27 | NQ1005 | 11.1 | 279 | 11.1 | 280 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6936 | 1823.9997 | 116.9549
MBZ-1.RR.982.1 | 24291069145239 | Borkapon, Shekhergaon Road, Ward # 9, Muhit Mia | 2019-07-27 | NQ1005 | 3.3 | 281 | 3.3 | 282 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6936 | 1823.9997 | 34.7704
MBZ-1.RR.983.1 | 24291349145238 | Borkapon, Shekhergaon Road, Ward # 9, Pakhi Mia (Beside Syed Bari Mosque) | 2019-07-27 | NQ1005 | 7.2 | 283 | 7.2 | 284 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6936 | 1823.9997 | 75.8627
MBZ-1.RR.984.1 | 24291699145230 | Borkapon, Shekhergaon Road, Ward # 9, Md Tayel Ahmed | 2019-07-27 | NQ1005 | 8.3 | 285 | 8.3 | 286 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6936 | 1823.9997 | 87.4528
MBZ-1.RR.984.2 | 24291699145230 | Borkapon, Shekhergaon Road, Ward # 9, Md Tayel Ahmed | 2022-04-13 | NQ1007 | 6.6 | 151 | 6.6 | 152 | 2022-04-13 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 4488 | 1823.9997 | 50.1075
MBZ-1.RR.985.1 | 24292059145238 | Borkapon, Shekhergaon Road, Ward # 9, Islam Cottege | 2019-07-27 | NQ1005 | 3.3 | 287 | 3.3 | 288 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6936 | 1823.9997 | 34.7704
MBZ-1.RR.986.1 | 24291409145500 | Poschim Bazar Market, Dhaka Sylhet Road, Gobindosree, Liakot Mia(Opposite Uttara Motors) | 2019-07-28 | NQ1005 | 10.7 | 305 | 10.7 | 306 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6912 | 1847.9997 | 112.7403
MBZ-1.RR.987.1 | 24291409145489 | Poschim Bazar , Dhaka Sylhet Road, Gobindosree, Link Road, Moynul Islam | 2019-07-28 | NQ1005 | 12.6 | 307 | 12.6 | 308 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6912 | 1847.9997 | 132.7597
MBZ-1.RR.1001.1 | 24303339147075 | Moulvibazar, Borman, Doshal, Front of Abdul Rouf Villa | 2019-07-22 | NQ1005 | 14.2 | 159 | 13.7 | 160 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6816 | 1943.9997 | 144.3498
MBZ-1.RR.1001.2 | 24303339147075 | Moulvibazar, Borman, Doshal, Front of Abdul Rouf Villa | 2019-07-22 | NQ1005 | 7.7 | 161 | 7.7 | 162 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6816 | 1943.9997 | 81.1309
MBZ-1.RR.1002.1 | 24303339147075 | Moulvibazar, Borman, Doshal, Abdul Rouf Villa | 2019-07-22 | NQ1005 | 3.6 | 163 | 3.7 | 164 | 2022-01-01 | 2022-10-12 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6816 | 1943.9997 | 38.985
MBZ-1.RR.1003.1 | 24291399146098 | Muslim Quarter, Lake Road, Ekota Villa, Jobbar Mia | 2019-07-23 | NQ1005 | 5 | 175 | 5 | 176 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6912 | 1847.9997 | 52.6824
MBZ-1.RR.1004.1 | 24295059143596 | Kanakpur, Banidhupi, Sohel Mia | 2019-07-23 | NQ1005 | 13.5 | 177 | 13.5 | 178 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 5208 | 0 | 1776 | 1775.9997 | 57.6764
MBZ-1.RR.1005.1 | 24295059143596 | Kanakpur, Banidhupi, Giashuddin | 2019-07-23 | NQ1005 | 10 | 179 | 10 | 180 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6984 | 1775.9997 | 105.3648
MBZ-1.RR.1006.1 | 24295059143596 | Kanakpur, Banidhupi, Owarisuddin | 2019-07-23 | NQ1005 | 6.7 | 181 | 6.7 | 182 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6984 | 1775.9997 | 70.5944
MBZ-1.RR.1007.1 | 24294299144029 | Kanakpur, Banidhupi, Ferdus Mia | 2019-07-23 | NQ1005 | 8.3 | 183 | 8.3 | 184 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6984 | 1775.9997 | 87.4528
MBZ-1.RR.1008.1 | 24293909144064 | Kanakpur, Banidhupi, Bajekorati, Kupesh Chandru Dap | 2019-07-23 | NQ1005 | 10.8 | 185 | 10.8 | 186 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6984 | 1775.9997 | 113.794
MBZ-1.RR.1009.1 | 24293909144064 | Kanakpur, Banidhupi, Robindru Dap | 2019-07-23 | NQ1005 | 8.9 | 187 | 8.2 | 188 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6984 | 1775.9997 | 86.3991
MBZ-1.RR.1009.2 | 24293909144064 | Kanakpur, Banidhupi, Robindru Dap | 2019-07-23 | NQ1005 | 1.4 | 189 | 1.4 | 190 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6984 | 1775.9997 | 14.7511
MBZ-1.RR.1010.1 | 24294349144127 | Shah Bandar, Poton, Soyeb Ahamed | 2019-07-23 | NQ1005 | 12 | 191 | 12 | 192 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6984 | 1775.9997 | 126.4378
MBZ-1.RR.1011.1 | 24283939144365 | Moulvibazar Sadar, Baharmordon, Shaira Mia | 2019-07-25 | NQ1005 | 12.4 | 205 | 12.4 | 206 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 48 | 0 | 7104 | 1607.9997 | 129.9365
MBZ-1.RR.1012.1 | 24283939144365 | Moulvibazar Sadar, Baharmordon, Late M. Saifur Rahman | 2019-07-25 | NQ1005 | 16.6 | 207 | 16.6 | 208 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 7152 | 1607.9997 | 174.9056
MBZ-1.RR.1013.1 | 24283669144354 | Moulvibazar Sadar, Begum Dulle Samad Road, Faruque Ahmed | 2019-07-25 | NQ1005 | 13.2 | 209 | 13.2 | 210 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7152 | 1607.9997 | 139.0816
MBZ-1.RR.1014.1 | 24283409144346 | Moulvibazar Sadar, Begum Dulle Samad Road, Baharmordon, Ataur Rahman | 2019-07-25 | NQ1005 | 35.9 | 213 | 36.8 | 214 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 36.8 | 36.8 | 2.208 | 2.208 | 0.0007168 | 100% | 0% | 2.208 | 2.208 | 0.0011869 | 28 | 0.044263 | 0.044263 |  | 0 | 0 | 7152 | 1607.9997 | 387.7425
MBZ-1.RR.1015.1 | 24283409144346 | Moulvibazar Sadar, Baharmordon, Shahi Bari | 2019-07-25 | NQ1005 | 10.7 | 215 | 10.7 | 216 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7152 | 1607.9997 | 112.7403
MBZ-1.RR.1016.1 | 24283409144346 | Moulvibazar Sadar, Baharmordon, Shahi Bari | 2019-07-25 | NQ1005 | 7 | 217 | 7 | 218 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7152 | 1607.9997 | 73.7554
MBZ-1.RR.1017.1 | 24283219144331 | Moulvibazar Sadar, Baharmordon, Morshed Ali | 2019-07-25 | NQ1005 | 6.5 | 219 | 6.5 | 220 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7152 | 1607.9997 | 68.4871
MBZ-1.RR.1018.1 | 24283219144331 | Moulvibazar Sadar, Baharmordon, Front of Morshed Ali | 2019-07-25 | NQ1005 | 5.6 | 221 | 5.6 | 222 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7152 | 1607.9997 | 59.0043
MBZ-1.RR.1019.1 | 24283369144305 | Moulvibazar Sadar, Baharmordon, Ershad Khan | 2019-07-25 | NQ1005 | 14.2 | 223 | 14.2 | 224 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7152 | 1607.9997 | 149.618
MBZ-1.RR.1020.1 | 24283289144265 | Moulvibazar Sadar, Baharmordon, Rufian | 2019-07-25 | NQ1005 | 11.1 | 225 | 11.1 | 226 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7152 | 1607.9997 | 116.9549
MBZ-1.RR.1021.1 | 24285289145231 | Uttor Mostofapur, Mostofapur Road, Sayed Bari, Abdul Kobir | 2019-07-27 | NQ1005 | 10.9 | 241 | 10.9 | 242 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6960 | 1799.9997 | 114.8476
MBZ-1.RR.1022.1 | 24285289145231 | Uttor Mostofapur, Mostofapur Road, Sayed Bari, Abdul Kobir | 2019-07-27 | NQ1005 | 12.2 | 243 | 11.9 | 244 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6960 | 1799.9997 | 125.3841
MBZ-1.RR.1023.1 | 24285669145244 | Uttor, Mostofapur, Mostofapur Road, Sayed Bari, Dilay mia | 2019-07-27 | NQ1005 | 10.8 | 248 | 10.8 | 249 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 7.5 | 0 | 6952.5 | 1799.9997 | 113.6966
MBZ-1.RR.1024.1 | 24290159145312 | West Dharkapon, Word # 8, Akbor Monjil, Lutfor Alli | 2019-07-27 | NQ1005 | 6.7 | 250 | 6.7 | 251 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6960 | 1799.9997 | 70.5944
MBZ-1.RR.1025.1 | 24290159145312 | West Dharkapon, Word # 8, Akbor Monjil, Lutfor Alli | 2019-07-27 | NQ1005 | 19.2 | 252 | 19.4 | 253 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 19.4 | 19.4 | 1.164 | 1.164 | 0.0007168 | 100% | 0% | 1.164 | 1.164 | 0.0011869 | 28 | 0.023334 | 0.023334 |  | 0 | 0 | 6960 | 1799.9997 | 204.4077
MBZ-1.RR.1026.1 | 24285909145277 | West Dharkapon, Word # 8, S.M.Umed Alli | 2019-07-27 | NQ1005 | 9 | 254 | 9 | 255 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6960 | 1799.9997 | 94.8283
MBZ-1.RR.1027.1 | 24285959145252 | West Dharkapon, word # 8, Fokir Bari, Muhit Uddin | 2019-07-27 | NQ1005 | 17.7 | 256 | 17.7 | 257 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 6960 | 1799.9997 | 186.4957
MBZ-1.RR.1028.1 | 24285959145252 | West Dharkapon, word # 8, Fokir Bari, Muhit Uddin | 2019-07-27 | NQ1005 | 6.3 | 258 | 6.3 | 259 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6960 | 1799.9997 | 66.3798
MBZ-1.RR.1029.1 | 24285959145252 | West Dharkapon, word # 8, Fokir Bari, Muhit Uddin | 2019-07-27 | NQ1005 | 15.6 | 260 | 15.6 | 261 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6960 | 1799.9997 | 164.3691
MBZ-1.RR.1030.1 | 24291329145181 | Moulvi Bazar, Borkapara, Shekherghaw Road, Word # 9, Abdul Johir Mia | 2019-07-28 | NQ1005 | 3.9 | 289 | 4 | 290 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6936 | 1823.9997 | 42.1459
MBZ-1.RR.1031.1 | 24291479145202 | Moulvi Bazar, Borkapara, Shekherghaw Road, Word # 9, Sathar Mia | 2019-07-28 | NQ1005 | 12.8 | 291 | 12.8 | 292 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6936 | 1823.9997 | 134.867
MBZ-1.RR.1032.1 | 24283719145546 | Moulvi Bazar, Mostofapur, Pashulia R/A, Eshankon Road, Word # 3, Nehar Steel | 2019-07-28 | NQ1005 | 7.3 | 293 | 7.3 | 294 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6960 | 1799.9997 | 76.9163
MBZ-1.RR.1033.1 | 24283639145541 | Moulvi Bazar, Mostofapur, Pashulia R/A, Eshankon Road, Word # 3, Akondo Villa | 2019-07-28 | NQ1005 | 6.1 | 295 | 6.1 | 296 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6960 | 1799.9997 | 64.2725
MBZ-1.RR.1034.1 | 24283569145520 | Moulvi Bazar, Mostofapur, Pashulia R/A, Eshankon Road, Word # 3, Liakot Ali | 2019-07-28 | NQ1005 | 8.6 | 297 | 8.6 | 298 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6960 | 1799.9997 | 90.6137
MBZ-1.RR.1035.1 | 24283489145512 | Moulvi Bazar, Mostofapur, Pashulia R/A, Eshankon Road, Word # 3, Salekar Rahman | 2019-07-28 | NQ1005 | 13.2 | 299 | 12.8 | 300 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6960 | 1799.9997 | 134.867
MBZ-1.RR.1036.1 | 24290419145557 | Moulvi Bazar, Srimongol Road, Dorjirmor, Syed Anisur Rahman | 2019-07-28 | NQ1005 | 2.7 | 303 | 2.7 | 304 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6936 | 1823.9997 | 28.4485
MBZ-1.RR.1051.1 | 24303839146282 | Chadnighat, North Mulaim, Mollik Shorai, Abdur Razzak | 2019-07-20 | NQ1007 | 14.7 | 72 | 14.7 | 73 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6768 | 1991.9997 | 154.8863
MBZ-1.RR.1052.1 | 24303489146553 | Chadnighat, North Mulaim, Hazi Siddik Mia | 2019-07-21 | NQ1007 | 2.6 | 101 | 2.6 | 102 | 2022-01-01 | 2022-10-10 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6768 | 1991.9997 | 27.3949
MBZ-1.RR.1053.1 | 24321059146424 | Biraimabad, Burikona, Wasir Manjil | 2019-07-21 | NQ1007 | 10.4 | 103 | 10.4 | 104 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6792 | 1967.9997 | 109.5794
MBZ-1.RR.1054.1 | 24321029146378 | Biraimabad, Burikona, Yunus Mia | 2019-07-21 | NQ1007 | 13.4 | 105 | 13.4 | 106 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6792 | 1967.9997 | 141.1888
MBZ-1.RR.1055.1 | 24321099146362 | Biraimabad, Burikona, Hazi Rabban Mia | 2019-07-21 | NQ1007 | 6.9 | 107 | 6.9 | 108 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6792 | 1967.9997 | 72.7017
MBZ-1.RR.1056.1 | 24321729146427 | Ekatuna Road, Biraimabad, Md. Ansar Mia | 2019-07-22 | NQ1007 | 12.9 | 109 | 12.9 | 110 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6792 | 1967.9997 | 135.9206
MBZ-1.RR.1057.1 | 24321729146427 | Ekatuna Road, Biraimabad, Md. Abdul Majid | 2019-07-22 | NQ1007 | 6.2 | 111 | 6.2 | 112 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6792 | 1967.9997 | 65.3262
MBZ-1.RR.1058.1 | 24321729146427 | Ekatuna Road, Biraimabad, Md. Abdul Motin | 2019-07-22 | NQ1007 | 8.9 | 113 | 8.2 | 114 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6792 | 1967.9997 | 86.3991
MBZ-1.RR.1059.1 | 24321659146387 | Ekatuna Road, Biraimabad, Sheli Begum | 2019-07-22 | NQ1007 | 3.9 | 115 | 3.9 | 116 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6792 | 1967.9997 | 41.0923
MBZ-1.RR.1060.1 | 24321659146387 | Ekatuna Road, Biraimabad, Md. Shua Mia | 2019-07-22 | NQ1007 | 5.9 | 119 | 5.9 | 120 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6792 | 1967.9997 | 62.1652
MBZ-1.RR.1061.1 | 24321869146419 | Ekatuna Road, Biraimabad, Shofiq Mia | 2019-07-22 | NQ1007 | 3.8 | 121 | 3.8 | 122 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6792 | 1967.9997 | 40.0386
MBZ-1.RR.1062.1 | 24321819146426 | Ekatuna Road, Biraimabad, Shohid Mia | 2019-07-22 | NQ1007 | 7.1 | 123 | 7.1 | 124 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6792 | 1967.9997 | 74.809
MBZ-1.RR.1063.1 | 24322229146392 | Ekatuna Road, Biraimabad, Abdul Monnan | 2019-07-22 | NQ1007 | 4.9 | 125 | 4.9 | 126 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6792 | 1967.9997 | 51.6288
MBZ-1.RR.1064.1 | 24322299146391 | Ekatuna Road, Biraimabad, Dana Mia | 2019-07-22 | NQ1007 | 13.1 | 127 | 13.1 | 128 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6792 | 1967.9997 | 138.0279
MBZ-1.RR.1065.1 | 24322849146399 | Ekatuna Road, Biraimabad, Md. Eleman Mia | 2019-07-22 | NQ1007 | 5.1 | 129 | 5.1 | 130 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6792 | 1967.9997 | 53.7361
MBZ-1.RR.1065.2 | 24322849146399 | Ekatuna Road, Biraimabad, Md. Eleman Mia | 2022-10-11 | MN1018 | 5.8 | 34 | 5.8 | 35 | 2022-10-11 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 0 | 1967.9997 | 13.7292
MBZ-1.RR.1066.1 | 24322909146398 | Ekatuna Road, Biraimabad, Md. Islam Uddin | 2019-07-22 | NQ1007 | 5.1 | 131 | 5.1 | 132 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6792 | 1967.9997 | 53.7361
MBZ-1.RR.1067.1 | 24322669146383 | Ekatuna Road, Biraimabad, Ruel Ahmod | 2019-07-22 | NQ1007 | 9.7 | 133 | 9.7 | 134 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6792 | 1967.9997 | 102.2039
MBZ-1.RR.1068.1 | 24310659142582 | Noldaria Commercial Area, Mamrakpur, Azad Mia | 2019-07-23 | NQ1007 | 13.2 | 161 | 13.2 | 162 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6984 | 1775.9997 | 139.0816
MBZ-1.RR.1069.1 | 24310879142566 | Noldaria Commercial Area, Mamrakpur, Abul Kalam | 2019-07-23 | NQ1007 | 1.4 | 163 | 1.4 | 164 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6984 | 1775.9997 | 14.7511
MBZ-1.RR.1070.1 | 24310679142576 | Noldaria Commercial Area, Mamrakpur, Badsha Mia | 2019-07-23 | NQ1007 | 13.2 | 165 | 13.2 | 166 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6984 | 1775.9997 | 139.0816
MBZ-1.RR.1071.1 | 24310979142474 | Noldaria Commercial Area, Mamrakpur, Haidar Mia | 2019-07-23 | NQ1007 | 4.5 | 167 | 4.5 | 168 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6984 | 1775.9997 | 47.4142
MBZ-1.RR.1072.1 | 24311079143035 | Noldaria Commercial Area, Mamrakpur, Fazal Mia | 2019-07-23 | NQ1007 | 1.3 | 169 | 1.3 | 170 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 6984 | 1775.9997 | 13.6974
MBZ-1.RR.1072.2 | 24311079143035 | Noldaria Commercial Area, Mamrakpur, Fazal Mia | 2021-10-07 | LU1001 | 2.9 | 39 | 2.9 | 40 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6984 | 1775.9997 | 30.5558
MBZ-1.RR.1073.1 | 24311079143035 | Noldaria Commercial Area, Mamrakpur, Forid Mia | 2019-07-23 | NQ1007 | 8.5 | 171 | 8.5 | 172 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6984 | 1775.9997 | 89.5601
MBZ-1.RR.1074.1 | 24311439143056 | Noldaria Commercial Area, Mamrakpur, Nurul Islam | 2019-07-23 | NQ1007 | 7.3 | 173 | 7.3 | 174 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6984 | 1775.9997 | 76.9163
MBZ-1.RR.1074.2 | 24311439143056 | Noldaria Commercial Area, Mamrakpur, Nurul Islam | 2021-10-07 | LU1001 | 2.2 | 44 | 2.2 | 45 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6984 | 1775.9997 | 23.1803
MBZ-1.RR.1075.1 | 24311489143056 | Noldaria Commercial Area, Mamrakpur, Md. Mendi Mia | 2019-07-23 | NQ1007 | 4.2 | 175 | 4.2 | 176 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6984 | 1775.9997 | 44.2532
MBZ-1.RR.1076.1 | 24311109143073 | Noldaria Commercial Area, Mamrakpur, Abu Sufian | 2019-07-23 | NQ1007 | 14.6 | 177 | 14.6 | 178 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6984 | 1775.9997 | 153.8326
MBZ-1.RR.1076.2 | 24311109143073 | Noldaria Commercial Area, Mamrakpur, Abu Sufian | 2021-10-07 | LU1001 | 10.8 | 42 | 10.8 | 43 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6984 | 1775.9997 | 113.794
MBZ-1.RR.1077.1 | 24291859144254 | Dighipara-Ghorua Road, Ghorua, Lomba Bari, Md. Aftab Uddin | 2019-07-25 | NQ1007 | 3.2 | 226 | 3.2 | 227 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7008 | 1751.9997 | 33.7167
MBZ-1.RR.1078.1 | 24291439144257 | Dighipara-Ghorua Road, Ghorua, Hazi Renu Mia | 2019-07-25 | NQ1007 | 1.6 | 228 | 1.6 | 229 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7008 | 1751.9997 | 16.8584
MBZ-1.RR.1079.1 | 24291149144313 | Ghorua, Ward No-1, Amor Chondro Dev | 2019-07-25 | NQ1007 | 10.7 | 230 | 10.5 | 231 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7008 | 1751.9997 | 110.6331
MBZ-1.RR.1080.1 | 24291109144398 | Ghorua, Ward No-1, Shahed Bari, Md. Shahed Ahmod | 2019-07-25 | NQ1007 | 5.2 | 233 | 5.2 | 234 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7008 | 1751.9997 | 54.7897
MBZ-1.RR.1081.1 | 24291389143524 | Halghor, Ward No-9, Md. Bodrul Hossen Chowdhury | 2019-07-25 | NQ1007 | 10.5 | 235 | 10.5 | 236 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7152 | 1607.9997 | 110.6331
MBZ-1.RR.1082.1 | 24291389143524 | Halghor, Ward No-9, Md. Kamrul Hossen Chowdhury | 2019-07-25 | NQ1007 | 7.1 | 239 | 7.1 | 240 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7152 | 1607.9997 | 74.809
MBZ-1.RR.1083.1 | 24290509143534 | Rakha, Ward No-7, Abul Kalam Khan | 2019-07-25 | NQ1007 | 8.5 | 251 | 8.8 | 252 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7152 | 1607.9997 | 92.721
MBZ-1.RR.1084.1 | 24290249143562 | Rakha, H # 61, Misbauddin Khan | 2019-07-25 | NQ1007 | 4.2 | 253 | 4.3 | 254 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7152 | 1607.9997 | 45.3069
MBZ-1.RR.1084.2 | 24290249143562 | Rakha, H # 61, Misbauddin Khan | 2021-10-03 | LU1001 | 4.2 | 31 | 4.2 | 32 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7152 | 1607.9997 | 44.2532
MBZ-1.RR.1085.1 | 24285909143560 | Rakha, Ward No-7, Shahaf Uddin Khan | 2019-07-25 | NQ1007 | 2.4 | 255 | 2.2 | 256 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7152 | 1607.9997 | 23.1803
MBZ-1.RR.1086.1 | 24290289143600 | Rakha, Ward No-7, H # 60, Md. Jomshed Khan | 2019-07-25 | NQ1007 | 31.6 | 257 | 30.5 | 258 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 30.5 | 30.5 | 1.83 | 1.83 | 0.0007168 | 100% | 0% | 1.83 | 1.83 | 0.0011869 | 28 | 0.036685 | 0.036685 |  | 0 | 0 | 7152 | 1607.9997 | 321.3627
MBZ-1.RR.1086.2 | 24290289143600 | Rakha, Ward No-7, H # 60, Md. Jomshed Khan | 2021-10-03 | LU1001 | 17 | 27 | 16.6 | 28 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 7152 | 1607.9997 | 174.9056
MBZ-1.RR.1087.1 | 24290309143537 | Rakha, Ward No-7, Md. Abdul Motin | 2019-07-25 | NQ1007 | 11.5 | 259 | 11.5 | 260 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7152 | 1607.9997 | 121.1695
MBZ-1.RR.1088.1 | 24284719145488 | Moulvibazar, Islambag, Abdullah Contractor | 2019-07-27 | LX1011 | 7 | 333 | 7 | 334 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6912 | 1847.9997 | 73.7554
MBZ-1.RR.1089.1 | 24284599145476 | Moulvibazar, Islambag, Sreemongal Road, Shoron | 2019-07-27 | LX1011 | 10.6 | 335 | 10.6 | 336 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6912 | 1847.9997 | 111.6867
MBZ-1.RR.1090.1 | 24284279145492 | Moulvibazar, Islambag, Sreemongal Road, Adv. Tarek | 2019-07-27 | LX1011 | 10.9 | 337 | 10.9 | 338 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6912 | 1847.9997 | 114.8476
MBZ-1.RR.1091.1 | 24283979145474 | Moulvibazar, Islambag, Sreemongal Road, Saiyod Amirul Islam | 2019-07-27 | LX1011 | 9.7 | 339 | 9.7 | 340 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6912 | 1847.9997 | 102.2039
MBZ-1.RR.1092.1 | 24284589145498 | Moulvibazar, Islambag, Dr. Shamsuddin | 2019-07-27 | LX1011 | 10.8 | 341 | 10.8 | 342 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6912 | 1847.9997 | 113.794
MBZ-1.RR.1093.1 | 24284439145489 | Moulvibazar, Islambag, Rokeya Monjil, Md. Abdur Rahim | 2019-07-27 | LX1011 | 9.3 | 343 | 9.3 | 344 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6912 | 1847.9997 | 97.9893
MBZ-1.RR.1094.1 | 24284369145545 | Moulvibazar, Islambag, Sreemongal Road, Soyful Alam Khan | 2019-07-27 | LX1011 | 5.9 | 345 | 5.9 | 346 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6912 | 1847.9997 | 62.1652
MBZ-1.RR.1095.1 | 24284219145452 | Moulvibazar, Islambag, Rashid Monjil, Rashid Uddin Ahmed | 2019-07-27 | LX1011 | 11.9 | 347 | 11.4 | 348 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6912 | 1847.9997 | 120.1159
MBZ-1.RR.1096.1 | 24292319145228 | Moulvibazar, Sylhet Road, Borkapon, Masud Mia ( Councillor ) | 2019-07-27 | LX1011 | 11.2 | 350 | 11.2 | 351 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6936 | 1823.9997 | 118.0086
MBZ-1.RR.1097.1 | 24292319145228 | Moulvibazar, Sylhet Road, Borkapon, Masud Mia ( Councillor ) | 2019-07-27 | LX1011 | 8 | 352 | 8 | 353 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6936 | 1823.9997 | 84.2919
MBZ-1.RR.1101.1 | 24284719147322 | Moulvibazar, Borshijora, Notun Bazar Road, Azad Mia | 2019-07-18 | NQ1007 | 2.2 | 19 | 2.2 | 20 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6624 | 2135.9997 | 23.1803
MBZ-1.RR.1101.2 | 24284719147322 | Moulvibazar, Borshijora, Notun Bazar Road, Azad Mia | 2022-10-04 | MN1018 | 14.3 | 26 | 14.3 | 27 | 2022-10-04 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 0 | 2135.9997 | 36.7391
MBZ-1.RR.1102.1 | 24284719147322 | Moulvibazar, Borshijora, Notun Bazar Road, Mussabir Mia | 2019-07-18 | NQ1007 | 40.1 | 21 | 40.1 | 22 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 40.1 | 40.1 | 2.406 | 2.406 | 0.0007168 | 100% | 0% | 2.406 | 2.406 | 0.0011869 | 28 | 0.048232 | 0.048232 |  | 0 | 0 | 6624 | 2135.9997 | 422.5129
MBZ-1.RR.1103.1 | 24284579147338 | Moulvibazar, Borshijora, Notun Bazar Road, Syed Ali | 2019-07-18 | NQ1007 | 10.5 | 23 | 10.5 | 24 | 2022-01-01 | 2022-10-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6624 | 2135.9997 | 110.6331
MBZ-1.RR.1104.1 | 24294249146252 | Moulvibazar, Chadnighat, Kulaura Road, Ahmed Member | 2019-07-20 | NQ1007 | 2.7 | 39 | 2.7 | 40 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6792 | 1967.9997 | 28.4485
MBZ-1.RR.1105.1 | 24295029146272 | Moulvibazar, Chadnighat, Kulaura Road, Romzan Ali | 2019-07-20 | NQ1007 | 6 | 41 | 6 | 42 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6792 | 1967.9997 | 63.2189
MBZ-1.RR.1106.1 | 24294979146272 | Moulvibazar, Chadnighat, Kulaura Road, Abdur Rahman | 2019-07-20 | NQ1007 | 10.3 | 43 | 10 | 44 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6792 | 1967.9997 | 105.3648
MBZ-1.RR.1107.1 | 24294559146271 | Moulvibazar, Chadnighat, Kulaura Road, Shofiqul Islam | 2019-07-20 | NQ1007 | 3.8 | 46 | 3.8 | 47 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6792 | 1967.9997 | 40.0386
MBZ-1.RR.1108.1 | 24294579146275 | Moulvibazar, Chadnighat, Bypass Road, Jahanara Monjil | 2019-07-20 | NQ1007 | 5.8 | 48 | 5.8 | 49 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6792 | 1967.9997 | 61.1116
MBZ-1.RR.1109.1 | 24294439146276 | Moulvibazar, Chadnighat, Bypass Road, Bishojit Dea Onup | 2019-07-20 | NQ1007 | 3.3 | 50 | 3.3 | 51 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6792 | 1967.9997 | 34.7704
MBZ-1.RR.1110.1 | 24294379146277 | Moulvibazar, Chadnighat, Bypass Road, Jamal Uddin Freedom Fighter | 2019-07-20 | NQ1007 | 10.5 | 52 | 10.5 | 53 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6792 | 1967.9997 | 110.6331
MBZ-1.RR.1111.1 | 24295479146282 | Moulvibazar, Chadnighat, Kulaura Road, Hossen Mia | 2019-07-20 | NQ1007 | 4 | 54 | 4 | 55 | 2022-01-01 | 2022-10-11 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6792 | 1967.9997 | 42.1459
MBZ-1.RR.1112.1 | 24294579145248 | Moulvibazar, Boliarbagh, Boliarbagh Road, Md. Junu Monjil | 2019-07-21 | NQ1007 | 5.1 | 74 | 5.3 | 75 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6840 | 1919.9997 | 55.8434
MBZ-1.RR.1113.1 | 24294849145240 | Moulvibazar, Boliarbagh, Boliarbagh Road, Ayat Ullah | 2019-07-21 | NQ1007 | 6.2 | 76 | 6.2 | 77 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6840 | 1919.9997 | 65.3262
MBZ-1.RR.1114.1 | 24295389145240 | Moulvibazar, Boliarbagh, Ataishpaika, Abbas Ali | 2019-07-21 | NQ1007 | 2.9 | 78 | 2.9 | 79 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6840 | 1919.9997 | 30.5558
MBZ-1.RR.1115.1 | 24295389145240 | Moulvibazar, Boliarbagh, Ataishpaika, Sayed Soleman Hossen | 2019-07-21 | NQ1007 | 7.6 | 80 | 7.6 | 81 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6840 | 1919.9997 | 80.0773
MBZ-1.RR.1116.1 | 24294779145218 | Moulvibazar, Boliarbagh, Boliarbagh Road, Boiddo Bari | 2019-07-21 | NQ1007 | 8.4 | 82 | 8.4 | 83 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6840 | 1919.9997 | 88.5064
MBZ-1.RR.1117.1 | 24295169145202 | Moulvibazar, Boliarbagh, Boliarbagh Road, Haji Bari | 2019-07-21 | NQ1007 | 3.1 | 84 | 3.1 | 85 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6840 | 1919.9997 | 32.6631
MBZ-1.RR.1118.1 | 24295839145199 | Moulvibazar, Boliarbagh, Boliarbagh Jame Mosjid Road, Abdul Karim | 2019-07-21 | NQ1007 | 21.4 | 86 | 21.4 | 87 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 6840 | 1919.9997 | 225.4807
MBZ-1.RR.1119.1 | 24294979145163 | Moulvibazar, West Boliarbagh, Sidique Mia | 2019-07-21 | NQ1007 | 6 | 88 | 6 | 89 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6840 | 1919.9997 | 63.2189
MBZ-1.RR.1120.1 | 24295089145166 | Moulvibazar, West Boliarbagh, Sajid Mia | 2019-07-21 | NQ1007 | 5.8 | 90 | 5.8 | 91 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6840 | 1919.9997 | 61.1116
MBZ-1.RR.1121.1 | 24294959145134 | Moulvibazar, West Boliarbagh, Sahinur Torofdar Bari | 2019-07-21 | NQ1007 | 9 | 92 | 9 | 93 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6840 | 1919.9997 | 94.8283
MBZ-1.RR.1122.1 | 24294959145134 | Moulvibazar, West Boliarbagh, Sahinur Torofdar Bari | 2019-07-21 | NQ1007 | 7.1 | 94 | 7.1 | 95 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6840 | 1919.9997 | 74.809
MBZ-1.RR.1123.1 | 24294959145134 | Moulvibazar, West Boliarbagh, Sahinur Torofdar Bari | 2019-07-21 | NQ1007 | 8.9 | 98 | 8.9 | 99 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6840 | 1919.9997 | 93.7747
MBZ-1.RR.1124.1 | 24304069143279 | Moulvibazar, Durlovpur, Konokpur, Zayed Ali Khan | 2019-07-22 | NQ1007 | 12.2 | 135 | 12.3 | 136 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6984 | 1775.9997 | 129.5987
MBZ-1.RR.1125.1 | 24304069143279 | Moulvibazar, Durlovpur, Konokpur, Zayed Ali Khan | 2019-07-22 | NQ1007 | 11.7 | 137 | 11.7 | 138 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6984 | 1775.9997 | 123.2768
MBZ-1.RR.1126.1 | 24303919143246 | Moulvibazar, Durlovpur, Konokpur, Abdul Khalik | 2019-07-22 | NQ1007 | 26.6 | 139 | 26.6 | 140 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 26.6 | 26.6 | 1.596 | 1.596 | 0.0007168 | 100% | 0% | 1.596 | 1.596 | 0.0011869 | 28 | 0.031994 | 0.031994 |  | 0 | 0 | 6984 | 1775.9997 | 280.2704
MBZ-1.RR.1126.2 | 24303919143246 | Moulvibazar, Durlovpur, Konokpur, Abdul Khalik | 2021-01-27 | MN1032 | 3.9 | 67 | 3.9 | 68 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6984 | 1775.9997 | 41.0923
MBZ-1.RR.1127.1 | 24303829143200 | Moulvibazar, Durlovpur, Konokpur, M.A. Hannan | 2019-07-22 | NQ1007 | 10.1 | 141 | 10.1 | 142 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6984 | 1775.9997 | 106.4185
MBZ-1.RR.1128.1 | 24303919143137 | Moulvibazar, Durlovpur, Konokpur, Abid Monjil | 2019-07-22 | NQ1007 | 8.3 | 143 | 8.3 | 144 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6984 | 1775.9997 | 87.4528
MBZ-1.RR.1129.1 | 24303949143140 | Moulvibazar, Durlovpur, Konokpur, Motin Mia | 2019-07-22 | NQ1007 | 18.5 | 147 | 18.5 | 148 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6984 | 1775.9997 | 194.9249
MBZ-1.RR.1130.1 | 24303389143089 | Moulvibazar, Durlovpur, Shahria, Panchghori Bari, Mokbul Mia | 2019-07-22 | NQ1007 | 7.9 | 149 | 7.8 | 150 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6984 | 1775.9997 | 82.1846
MBZ-1.RR.1130.2 | 24303389143089 | Moulvibazar, Durlovpur, Shahria, Panchghori Bari, Mokbul Mia | 2022-03-24 | NQ1007 | 6.2 | 83 | 6.2 | 84 | 2022-03-24 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 5016 | 1775.9997 | 50.6502
MBZ-1.RR.1131.1 | 24303389143089 | Moulvibazar, Durlovpur, Shahria, Panchghori Bari, Sohid Mia | 2019-07-22 | NQ1007 | 5.2 | 153 | 5.2 | 154 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6984 | 1775.9997 | 54.7897
MBZ-1.RR.1132.1 | 24303209143087 | Moulvibazar, Durlovpur, Shahria, Panchghori Bari, Mohibur Rahman | 2019-07-22 | NQ1007 | 12.8 | 155 | 12.8 | 156 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6984 | 1775.9997 | 134.867
MBZ-1.RR.1133.1 | 24303209143087 | Moulvibazar, Durlovpur, Shahria, Panchghori Bari, Lesu Mia | 2019-07-22 | NQ1007 | 9 | 157 | 9 | 158 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6984 | 1775.9997 | 94.8283
MBZ-1.RR.1134.1 | 24303209143087 | Moulvibazar, Durlovpur, Shahria, Panchghori Bari, Nurul Mia | 2019-07-22 | NQ1007 | 8.3 | 159 | 8.3 | 160 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6984 | 1775.9997 | 87.4528
MBZ-1.RR.1135.1 | 24294609144424 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, Kamal Boksh | 2019-07-23 | NQ1007 | 8.3 | 179 | 8.3 | 180 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7008 | 1751.9997 | 87.4528
MBZ-1.RR.1136.1 | 24294479144422 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, Ankhar Boksh | 2019-07-23 | NQ1007 | 8.4 | 181 | 8.4 | 182 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7008 | 1751.9997 | 88.5064
MBZ-1.RR.1137.1 | 24294379144426 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, Abdul Hamid Jahangir | 2019-07-23 | NQ1007 | 11 | 183 | 11 | 184 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7176 | 1583.9997 | 115.9013
MBZ-1.RR.1137.2 | 24294379144426 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, Abdul Hamid Jahangir | 2022-10-27 | MN1018 | 3.4 | 94 | 3.4 | 95 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 0 | 1583.9997 | 6.4778
MBZ-1.RR.1138.1 | 24293969144427 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, Mr. Abdul Mosobbir | 2019-07-23 | NQ1007 | 4.8 | 185 | 4.8 | 186 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7008 | 1751.9997 | 50.5751
MBZ-1.RR.1139.1 | 24293539144371 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, North Ghorua Lomba Bari, Nur Mia | 2019-07-23 | NQ1007 | 81 | 187 | 81.2 | 188 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 81.2 | 81.2 | 4.872 | 4.872 | 0.0007168 | 100% | 0% | 4.872 | 4.872 | 0.0011869 | 28 | 0.097667 | 0.097667 |  | 0 | 0 | 7008 | 1751.9997 | 855.5623
MBZ-1.RR.1140.1 | 24293539144371 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, North Ghorua Lomba Bari, Toskir Uddin | 2019-07-23 | NQ1007 | 2.7 | 189 | 2.7 | 190 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7008 | 1751.9997 | 28.4485
MBZ-1.RR.1141.1 | 24293539144371 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, North Ghorua Lomba Bari, Badsha Mia | 2019-07-23 | NQ1007 | 2.6 | 191 | 2.6 | 192 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7008 | 1751.9997 | 27.3949
MBZ-1.RR.1142.1 | 24293539144371 | Moulvibazar, Sreerampur, Ghorua Balikandi Road, North Ghorua Lomba Bari, Mosnu Mia | 2019-07-23 | NQ1007 | 3.1 | 193 | 3.1 | 194 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7008 | 1751.9997 | 32.6631
MBZ-1.RR.1143.1 | 24293149144477 | Moulvibazar, Kuchar Mohol, Digheer Par Road, M. Hossain & Razia Hossain Villa | 2019-07-23 | NQ1007 | 3.9 | 195 | 3.9 | 196 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7008 | 1751.9997 | 41.0923
MBZ-1.RR.1144.1 | 24292569144465 | Moulvibazar, Kuchar Mohol, Digheer Par Road, Ruyel Ahmed | 2019-07-23 | NQ1007 | 3.8 | 197 | 3.8 | 198 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7008 | 1751.9997 | 40.0386
MBZ-1.RR.1145.1 | 24292539144449 | Moulvibazar, Kuchar Mohol, Digheer Par Road, Boshon Miar Bari | 2019-07-23 | NQ1007 | 3.9 | 199 | 3.9 | 200 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7008 | 1751.9997 | 41.0923
MBZ-1.RR.1146.1 | 24292379144377 | Moulvibazar, Kuchar Mohol, Digheer Par Road, Asad Master | 2019-07-23 | NQ1007 | 10.4 | 201 | 10.6 | 202 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7008 | 1751.9997 | 111.6867
MBZ-1.RR.1147.1 | 24285539143544 | Moulvibazar, Jogotshi, Raka, Digheer Par Road, Matin Villa | 2019-07-25 | NQ1007 | 14.5 | 261 | 14.1 | 262 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7152 | 1607.9997 | 148.5644
MBZ-1.RR.1147.2 | 24285539143544 | Moulvibazar, Jogotshi, Raka, Digheer Par Road, Matin Villa | 2021-08-14 | LX1011 | 8 | 6 | 8 | 7 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7152 | 1607.9997 | 84.2919
MBZ-1.RR.1148.1 | 24285529143579 | Moulvibazar, Jogotshi, Raka, Digheer Par Road, Abdul Mojid | 2019-07-25 | NQ1007 | 2.4 | 263 | 2.4 | 264 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7152 | 1607.9997 | 25.2876
MBZ-1.RR.1149.1 | 24285099143582 | Moulvibazar, Jogotshi, Raka, Digheer Par Road, Fajlur Rahman | 2019-07-25 | NQ1007 | 6.2 | 267 | 6.2 | 268 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7152 | 1607.9997 | 65.3262
MBZ-1.RR.1150.1 | 24285029143580 | Moulvibazar, Jogotshi, Raka, Digheer Par Road, Mostofa Mia | 2019-07-25 | NQ1007 | 5.9 | 269 | 5.9 | 270 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7152 | 1607.9997 | 62.1652
MBZ-1.RR.1151.1 | 24284439145226 | Moulovibazar, Mostofapur, Mostofapur Road, Saidur Rohman | 2019-07-25 | MP1032 | 13.1 | 286 | 12.7 | 287 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6960 | 1799.9997 | 133.8133
MBZ-1.RR.1152.1 | 24291809145114 | Boro Kapon, Sazzadur Mia Bari Rasta, Md.Mosabbir Mia | 2019-07-25 | LX1011 | 10.3 | 291 | 10.3 | 292 | 2022-01-01 | 2022-10-27 | MN1018 | 0.5 | 71 | 0.5 | 72 | 2022-10-27 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7176 | 1583.9997
MBZ-1.RR.1153.1 | 24291809145114 | Boro Kapon, Sazzadur Mia Bari Rasta, Ripon Ahmed | 2019-07-25 | LX1011 | 9.7 | 293 | 9.7 | 294 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7008 | 1751.9997 | 102.2039
MBZ-1.RR.1154.1 | 24291809145114 | Boro Kapon, Sazzadur Mia Bari Rasta, Md.Alamgir | 2019-07-25 | LX1011 | 8.5 | 295 | 8.5 | 296 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7008 | 1751.9997 | 89.5601
MBZ-1.RR.1155.1 | 24292149145144 | West Boro Kapon, Hazi Abdur Rahman | 2019-07-25 | LX1011 | 10.7 | 297 | 10.7 | 298 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7008 | 1751.9997 | 112.7403
MBZ-1.RR.1156.1 | 24292149145144 | West Boro Kapon, Hazi Abdur Rahman | 2019-07-25 | LX1011 | 6.7 | 299 | 6.7 | 300 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7008 | 1751.9997 | 70.5944
MBZ-1.RR.1157.1 | 24292009145144 | West Boro Kapon, Chowdhury Villa | 2019-07-25 | LX1011 | 11.7 | 301 | 11.7 | 302 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7008 | 1751.9997 | 123.2768
MBZ-1.RR.1158.1 | 24292009145144 | West Boro Kapon, Shamim Mia | 2019-07-25 | LX1011 | 8.9 | 303 | 8.9 | 304 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7008 | 1751.9997 | 93.7747
MBZ-1.RR.1158.2 | 24292009145144 | West Boro Kapon, Shamim Mia | 2022-04-13 | NQ1007 | 5.6 | 149 | 5.6 | 150 | 2022-04-13 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 4560 | 1751.9997 | 42.5154
MBZ-1.RR.1159.1 | 24291949145170 | Boro Kapon, Boro Kapon School Road, Monir Mia | 2019-07-25 | LX1011 | 19.3 | 305 | 19.3 | 306 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 6936 | 1823.9997 | 203.3541
MBZ-1.RR.1160.1 | 24291949145170 | Boro Kapon, Boro Kapon School Road, Moju Mia | 2019-07-25 | LX1011 | 13.6 | 307 | 13.6 | 308 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6936 | 1823.9997 | 143.2961
MBZ-1.RR.1161.1 | 24284729143568 | Moulvibazar, Jogotshi, Raka, Dosbali, Abdul Goffar | 2019-07-25 | NQ1007 | 3.7 | 271 | 3.7 | 272 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7152 | 1607.9997 | 38.985
MBZ-1.RR.1161.2 | 24284729143568 | Moulvibazar, Jogotshi, Raka, Dosbali, Abdul Goffar | 2021-10-03 | LU1001 | 13 | 35 | 12.7 | 36 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7152 | 1607.9997 | 133.8133
MBZ-1.RR.1162.1 | 24284439143533 | Moulvibazar, Jogotshi, Raka, Dosbali, Advocate Kamal | 2019-07-25 | NQ1007 | 9.9 | 273 | 9.9 | 274 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7152 | 1607.9997 | 104.3112
MBZ-1.RR.1163.1 | 24284359143532 | Moulvibazar, Jogotshi, Raka, Dosbali, Abdul Qaiyum | 2019-07-25 | NQ1007 | 3.4 | 275 | 3.4 | 276 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7152 | 1607.9997 | 35.824
MBZ-1.RR.1164.1 | 24283499143493 | Moulvibazar, Jogotshi, Raka, Dosbali, Abdur Rouf | 2019-07-25 | NQ1007 | 11.5 | 277 | 11.1 | 278 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7152 | 1607.9997 | 116.9549
MBZ-1.RR.1165.1 | 24283059143453 | Moulvibazar, Jogotshi, Dojob Ali, Kobiraj Bari, Abdul Aziz | 2019-07-25 | NQ1007 | 2.1 | 279 | 2.1 | 280 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7152 | 1607.9997 | 22.1266
MBZ-1.RR.1165.2 | 24283059143453 | Moulvibazar, Jogotshi, Dojob Ali, Kobiraj Bari, Abdul Aziz | 2022-03-29 | NQ1007 | 7.1 | 101 | 7.1 | 102 | 2022-03-29 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 5064 | 1607.9997 | 56.9778
MBZ-1.RR.1166.1 | 24283059143453 | Moulvibazar, Jogotshi, Dojob Ali, Kobiraj Bari, Bacchu Mia | 2019-07-25 | NQ1007 | 7.3 | 281 | 7.3 | 282 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7152 | 1607.9997 | 76.9163
MBZ-1.RR.1167.1 | 24283059143453 | Moulvibazar, Jogotshi, Dojob Ali, Kobiraj Bari, Moshidur Rahman | 2019-07-25 | NQ1007 | 11.8 | 283 | 11.8 | 284 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7152 | 1607.9997 | 124.3305
MBZ-1.RR.1167.2 | 24283059143453 | Moulvibazar, Jogotshi, Dojob Ali, Kobiraj Bari, Moshidur Rahman | 2022-10-26 | MN1018 | 3.6 | 62 | 3.6 | 63 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 0 | 1607.9997 | 6.9627
MBZ-1.RR.1168.1 | 24283059143453 | Moulvibazar, Jogotshi, Dojob Ali, Kobiraj Bari, Mokidur Rahman | 2019-07-25 | NQ1007 | 7.6 | 285 | 7.6 | 286 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7152 | 1607.9997 | 80.0773
MBZ-1.RR.1169.1 | 24283059143453 | Moulvibazar, Jogotshi, Dojob Ali, Kobiraj Bari, Fazlu Karim | 2019-07-25 | NQ1007 | 57.9 | 287 | 57.9 | 288 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 57.9 | 57.9 | 3.474 | 3.474 | 0.0007168 | 100% | 0% | 3.474 | 3.474 | 0.0011869 | 28 | 0.069642 | 0.069642 |  | 0 | 0 | 7152 | 1607.9997 | 610.0623
MBZ-1.RR.1170.1 | 24285359145332 | Moulvibazar, Mustafapur Road, Wast Dharkapon, Al Hossen Jame Mosjid | 2019-07-27 | LX1011 | 11.5 | 309 | 11.4 | 310 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6960 | 1799.9997 | 120.1159
MBZ-1.RR.1171.1 | 24285169145452 | Moulvibazar, Mustafapur, Dharkapon, H # 857, Shah Monjil | 2019-07-27 | LX1011 | 10.5 | 311 | 10.5 | 312 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6912 | 1847.9997 | 110.6331
MBZ-1.RR.1172.1 | 24285169145462 | Moulvibazar, Mustafapur, Dharkapon, M.A Kuddus Villa, H # 289 | 2019-07-27 | LX1011 | 10.3 | 313 | 10.3 | 314 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6912 | 1847.9997 | 108.5258
MBZ-1.RR.1173.1 | 24285079145469 | Moulvibazar, Mustafapur, Dharkapon, Siraji House, H # 0856/01 | 2019-07-27 | LX1011 | 4.7 | 315 | 4.7 | 316 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6912 | 1847.9997 | 49.5215
MBZ-1.RR.1174.1 | 24285299145481 | Moulvibazar, Mustafapur, Dharkapon Road, Rina Cottage, H # 208/3 | 2019-07-27 | LX1011 | 3.1 | 317 | 3.1 | 318 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6912 | 1847.9997 | 32.6631
MBZ-1.RR.1175.1 | 24285539145476 | Moulvibazar, Mustafapur, Dharkapon Road, Meher Monjil, H # 0859-01 | 2019-07-27 | LX1011 | 3.2 | 321 | 3.2 | 322 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6912 | 1847.9997 | 33.7167
MBZ-1.RR.1176.1 | 24285649145480 | Moulvibazar, Dharkapon Road, Farazi Apartment, H # 149(2) | 2019-07-27 | LX1011 | 6.2 | 323 | 6.1 | 324 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6912 | 1847.9997 | 64.2725
MBZ-1.RR.1177.1 | 24285739145470 | Moulvibazar, East Dharkapon Dharkapon Road, Bodrol Alam | 2019-07-27 | LX1011 | 4.6 | 325 | 4.6 | 326 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6912 | 1847.9997 | 48.4678
MBZ-1.RR.1177.2 | 24285739145470 | Moulvibazar, East Dharkapon Dharkapon Road, Bodrol Alam | 2019-07-27 | LX1011 | 12.1 | 327 | 12.1 | 328 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6912 | 1847.9997 | 127.4914
MBZ-1.RR.1178.1 | 24285859145483 | Moulvibazar, East Dharkapon Road, Al Sajid Regency House | 2019-07-27 | LX1011 | 4.1 | 329 | 4.1 | 330 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6912 | 1847.9997 | 43.1996
MBZ-1.RR.1179.1 | 24285859145483 | Moulvibazar, East Dharkapon Road, Dorji Mohol, Aftab Monjil, H # 209 | 2019-07-27 | LX1011 | 10.7 | 331 | 10.9 | 332 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 4.5 | 0 | 6907.5 | 1847.9997 | 114.7886
MBZ-1.RR.1180.1 | 24290549145445 | Moulvibazar, East Dharkapon, Dharkapon Road, Sayed Anisur Rahman | 2019-07-28 | LX1011 | 26.4 | 354 | 26.4 | 355 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 26.4 | 26.4 | 1.584 | 1.584 | 0.0007168 | 100% | 0% | 1.584 | 1.584 | 0.0011869 | 28 | 0.031754 | 0.031754 |  | 0 | 0 | 6912 | 1847.9997 | 278.1631
MBZ-1.RR.1181.1 | 24290549145445 | Moulvibazar, East Dharkapon, Dharkapon Road, Masud | 2019-07-28 | LX1011 | 1.6 | 356 | 1.6 | 357 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6912 | 1847.9997 | 16.8584
MBZ-1.RR.1182.1 | 24290739145467 | Moulvibazar, East Dharkapon, Dharkapon Road, Sayed Joynal Abedin | 2019-07-28 | LX1011 | 10.3 | 358 | 10 | 359 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6912 | 1847.9997 | 105.3648
MBZ-1.RR.1182.2 | 24290739145467 | Moulvibazar, East Dharkapon, Dharkapon Road, Sayed Joynal Abedin | 2021-01-24 | MN1032 | 3.7 | 51 | 3.7 | 52 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6912 | 1847.9997 | 38.985
MBZ-1.RR.1183.1 | 24290729145492 | Moulvibazar, Dorji Mohol, Dharkapon Road, Sayed Mujibul Islam | 2019-07-28 | LX1011 | 1.8 | 360 | 1.8 | 361 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6912 | 1847.9997 | 18.9657
MBZ-1.RR.1184.1 | 24285919145481 | Moulvibazar, East Dharkapon Road, Jakia Store, Azizur Rahman | 2019-07-28 | LX1011 | 7.1 | 362 | 7.1 | 363 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6912 | 1847.9997 | 74.809
MBZ-1.RR.1185.1 | 24285979145469 | Moulvibazar, East Dharkapon, Bonbeta Area, Shefakh | 2019-07-28 | LX1011 | 3 | 364 | 3 | 365 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6912 | 1847.9997 | 31.6094
MBZ-1.RR.1186.1 | 24284639145546 | Moulvibazar, Sreemangal Road, Sabujbag, Chowdhury Villa, H # 69 | 2019-07-28 | LX1011 | 24.2 | 366 | 24.2 | 367 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 24.2 | 24.2 | 1.452 | 1.452 | 0.0007168 | 100% | 0% | 1.452 | 1.452 | 0.0011869 | 28 | 0.029108 | 0.029108 |  | 0 | 0 | 6960 | 1799.9997 | 254.9828
MBZ-1.RR.1186.2 | 24284639145546 | Moulvibazar, Sreemangal Road, Sabujbag, Chowdhury Villa, H # 69 | 2022-04-11 | NQ1007 | 11.5 | 143 | 11.5 | 144 | 2022-04-11 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 4560 | 1799.9997 | 87.9724
MBZ-1.RR.1187.1 | 24273379145495 | Moulvibazar, Sreemangal Road, Jagannatpur, Azadur Rahman (Azad) | 2019-07-28 | LX1011 | 34.6 | 368 | 34.6 | 369 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 34.6 | 34.6 | 2.076 | 2.076 | 0.0007168 | 100% | 0% | 2.076 | 2.076 | 0.0011869 | 28 | 0.041617 | 0.041617 |  | 0 | 0 | 7056 | 1703.9997 | 364.5623
MBZ-1.RR.1201.1 | 24282799145336 | Mostafapur, Paguliya, Ward # 3, Abdul Karim | 2019-07-27 | NQ1007 | 13.4 | 319 | 13.4 | 320 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6960 | 1799.9997 | 141.1888
MBZ-1.RR.1202.1 | 24282359145317 | Mostafapur, Paguliya, Ward # 3, H # 249, Nurul Huda Kuraishi | 2019-07-27 | NQ1007 | 11.6 | 321 | 11.6 | 322 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6960 | 1799.9997 | 122.2232
MBZ-1.RR.1203.1 | 24282359145317 | Mostafapur, Paguliya, Ward # 3, H # 248, Azizul Alam Kuraishi | 2019-07-27 | NQ1007 | 7.1 | 323 | 7.4 | 324 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6960 | 1799.9997 | 77.97
MBZ-1.RR.1204.1 | 24282359145317 | Mostafapur, Paguliya, Ward # 3, H # 247, Mohiuddin | 2019-07-27 | NQ1007 | 5.7 | 325 | 5.7 | 326 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6960 | 1799.9997 | 60.0579
MBZ-1.RR.1205.1 | 24282449145304 | Mostafapur, Paguliya, Ward # 3, H # 237, Md. Asraf Ahamed Kuraishi | 2019-07-27 | NQ1007 | 4.7 | 327 | 4.7 | 328 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6960 | 1799.9997 | 49.5215
MBZ-1.RR.1206.1 | 24282349145394 | Mostafapur, Paguliya, Ward # 3, H # 324, Kairul Islam Khosru | 2019-07-27 | NQ1007 | 13 | 329 | 13 | 330 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6960 | 1799.9997 | 136.9743
MBZ-1.RR.1207.1 | 24282299145392 | Mostafapur, Paguliya, Ward # 3, H # 320, Abdur Rahim | 2019-07-27 | NQ1007 | 11.3 | 331 | 11.3 | 332 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6960 | 1799.9997 | 119.0622
MBZ-1.RR.1208.1 | 24282169145391 | Mostafapur, Paguliya, Ward # 3, Moshiur Rahman | 2019-07-27 | NQ1007 | 3.3 | 333 | 3.2 | 334 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6960 | 1799.9997 | 33.7167
MBZ-1.RR.1209.1 | 24282689145388 | Mostafapur, Paguliya, Ward # 3, Md. Giyas Mia | 2019-07-27 | NQ1007 | 16.1 | 335 | 16.1 | 336 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6960 | 1799.9997 | 169.6373
MBZ-1.RR.1210.1 | 24282859145370 | Mostafapur, Paguliya, Ward # 3, Sopnil, Abdur Rouf | 2019-07-27 | NQ1007 | 2.1 | 337 | 2.1 | 338 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6960 | 1799.9997 | 22.1266
MBZ-1.RR.1211.1 | 24282859145370 | Mostafapur, Paguliya, Ward # 3, H # 265, Abdul Bashed | 2019-07-27 | NQ1007 | 10.6 | 343 | 10.6 | 344 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6960 | 1799.9997 | 111.6867
MBZ-1.RR.1212.1 | 24283999144031 | Nagra, Chondi Vandhar, Boliar Bug, Boksh Monjil, Aminul Boksh | 2019-07-28 | NQ1007 | 11.9 | 357 | 11.9 | 358 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7152 | 1607.9997 | 125.3841
MBZ-1.RR.1213.1 | 24283389144072 | Nagra, Chondi Vandhar, Boliar Bug, Rakha Khan Mohol, Alhaj Roich Khan | 2019-07-28 | NQ1007 | 9.9 | 359 | 9.9 | 360 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7152 | 1607.9997 | 104.3112
MBZ-1.RR.1213.2 | 24283389144072 | Nagra, Chondi Vandhar, Boliar Bug, Rakha Khan Mohol, Alhaj Roich Khan | 2022-10-26 | MN1018 | 2.7 | 58 | 2.7 | 59 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 0 | 1607.9997 | 5.2221
MBZ-1.RR.1231.1 | 24283959145314 | East Mostofapur, Near By Shekh Rumel Chairman Bari, Bulu Mia | 2019-07-27 | NQ1007 | 12.7 | 289 | 12.7 | 290 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6960 | 1799.9997 | 133.8133
MBZ-1.RR.1232.1 | 24283759145313 | East Mostofapur, Near By Shekh Rumel Chairman Bari, Syed Year Ali | 2019-07-27 | NQ1007 | 3.7 | 293 | 3.7 | 294 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6960 | 1799.9997 | 38.985
MBZ-1.RR.1233.1 | 24283759145313 | East Mostofapur, Near By Shekh Rumel Chairman Bari, Belal Hossen | 2019-07-27 | NQ1007 | 4.4 | 295 | 4.4 | 296 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6960 | 1799.9997 | 46.3605
MBZ-1.RR.1234.1 | 24283609145296 | East Mostofapur, Near By Shekh Rumel Chairman Bari, Joynob Bibi | 2019-07-27 | NQ1007 | 10.5 | 297 | 10.5 | 298 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6960 | 1799.9997 | 110.6331
MBZ-1.RR.1235.1 | 24283609145296 | Mostofapur, Word # 4, Babli Akhtar | 2019-07-27 | NQ1007 | 9.8 | 299 | 9.8 | 300 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6960 | 1799.9997 | 103.2575
MBZ-1.RR.1236.1 | 24283609145296 | Mostofapur, Word # 4, Nur Islam | 2019-07-27 | NQ1007 | 4.9 | 301 | 4.9 | 302 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6960 | 1799.9997 | 51.6288
MBZ-1.RR.1237.1 | 24283609145296 | Mostofapur, Word # 4, Md. Masuk Ahmed, Ahmed Cotage | 2019-07-27 | NQ1007 | 3.6 | 303 | 3.6 | 304 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6960 | 1799.9997 | 37.9313
MBZ-1.RR.1238.1 | 24283449145316 | Mostofapur, Word # 4, Hazi Abdul Khalique, H&H House | 2019-07-27 | NQ1007 | 4.1 | 305 | 4.1 | 306 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6960 | 1799.9997 | 43.1996
MBZ-1.RR.1239.1 | 24282689145195 | Gondhorvopur, Ishankor Road, Pal Bari, Nirmol Kanti Pal | 2019-07-27 | NQ1007 | 3.2 | 307 | 3.3 | 308 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6960 | 1799.9997 | 34.7704
MBZ-1.RR.1240.1 | 24282239145199 | Gondhorvopur, Word # 3, Salim Ahmed | 2019-07-27 | NQ1007 | 6.3 | 309 | 6.3 | 310 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6960 | 1799.9997 | 66.3798
MBZ-1.RR.1240.2 | 24282239145199 | Gondhorvopur, Word # 3, Salim Ahmed | 2021-01-24 | LU1001 | 13.7 | 80 | 13.7 | 81 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6960 | 1799.9997 | 144.3498
MBZ-1.RR.1241.1 | 24282239145199 | Gondhorvopur, Word # 3, Salim Ahmed | 2019-07-27 | NQ1007 | 3.9 | 311 | 3.9 | 312 | 2022-01-01 | [9 empty] | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0
MBZ-1.RR.1242.1 | 24282239145199 | Gondhorvopur, Word # 3, Rofiqullah | 2019-07-27 | NQ1007 | 3.7 | 313 | 3.7 | 314 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6960 | 1799.9997 | 38.985
MBZ-1.RR.1243.1 | 24282239145199 | Gondhorvopur, Word # 3, Bodrul Alom | 2019-07-27 | NQ1007 | 3.6 | 317 | 3.6 | 318 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6960 | 1799.9997 | 37.9313
MBZ-1.RR.1243.2 | 24282239145199 | Gondhorvopur, Word # 3, Bodrul Alom | 2021-01-24 | LU1001 | 3.3 | 84 | 3.3 | 85 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6960 | 1799.9997 | 34.7704
MBZ-1.RR.1244.1 | 24282819145408 | Pagulia R/A, Word # 7, Sobuj Ronjon Kor | 2019-07-28 | NQ1007 | 5.1 | 345 | 5.1 | 346 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6960 | 1799.9997 | 53.7361
MBZ-1.RR.1245.1 | 24283179145428 | Pagulia R/A, Word # 7, Khanom monjil, Mahmuda khanom | 2019-07-28 | NQ1007 | 2.5 | 347 | 2.5 | 348 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6960 | 1799.9997 | 26.3412
MBZ-1.RR.1246.1 | 24283179145428 | Pagulia R/A, Word # 7, Khanom monjil, Mahmuda khanom | 2019-07-28 | NQ1007 | 4 | 349 | 4 | 350 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6960 | 1799.9997 | 42.1459
MBZ-1.RR.1247.1 | 24283249145366 | Pagulia R/A, Word # 7, Syed monjil, Syed Bahauddin | 2019-07-28 | NQ1007 | 9.7 | 351 | 9.7 | 352 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6960 | 1799.9997 | 102.2039
MBZ-1.RR.1248.1 | 24283289145481 | Pagulia R/A, Islam Bagh, Nahid Villa | 2019-07-28 | NQ1007 | 3.2 | 353 | 3.2 | 354 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6960 | 1799.9997 | 33.7167
MBZ-1.RR.1249.1 | 24282919145538 | Islam Bagh, Talukder Villa, Abul Monsur | 2019-07-28 | NQ1007 | 6.1 | 355 | 6.1 | 356 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6960 | 1799.9997 | 64.2725
MBZ-1.RR.1250.1 | 24290649145425 | Purbo Dhorkapon, Dhorkapon Road, Altafur Rahman | 2019-08-26 | MN1032 | 2 | 188 | 2 | 189 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6912 | 1847.9997 | 21.073
MBZ-1.RR.1251.1 | 24290649145425 | Purbo Dhorkapon, Dhorkapon Road, Sayed Khurshed Ali | 2019-08-26 | MN1032 | 2.6 | 190 | 2.6 | 191 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 4440 | 0 | 2472 | 1847.9997 | 13.5098
MBZ-1.RR.1251.2 | 24290649145425 | Purbo Dhorkapon, Dhorkapon Road, Sayed Khurshed Ali | 2021-02-08 | NQ1003 | 15 | 204 | 15 | 205 | 2022-01-01 | 2022-10-16 | MN1018 | 0.6 | 56 | 0.6 | 57 | 2022-10-16 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 4440 | 0 | 2472 | 1847.9997
MBZ-1.RR.1261.1 | 24291029145477 | Gobindasree, Riazuddin | 2019-07-27 | MP1032 | 4.9 | 357 | 4.9 | 358 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6912 | 1847.9997 | 51.6288
MBZ-1.RR.1262.1 | 24291149145477 | Gobindasree, Ali Hossin | 2019-07-27 | MP1032 | 10.6 | 359 | 10.6 | 360 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6912 | 1847.9997 | 111.6867
MBZ-1.RR.1263.1 | 24291149145477 | Gobindasree, Ali Hossin | 2019-07-27 | MP1032 | 10.9 | 361 | 10.9 | 362 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6912 | 1847.9997 | 114.8476
MBZ-2.CR.2.1 | 24183179144001 | Sreemangal, Dak Bangla Road, Dawan Bakery | 2019-08-04 | MP1032 | 1.6 | 611 | 1.6 | 612 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6216 | 2543.9997 | 16.8584
MBZ-2.CR.3.1 | 24185339144022 | Srimangal, Moulvibazar Road, 1 No Poll, Hazi Khalimia market, Loki Hottle | 2019-07-29 | NQ1005 | 12.8 | 332 | 12.3 | 333 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6240 | 2519.9997 | 129.5987
MBZ-2.RR.1.1 | 24182879144215 | Sreemangal, Purbasha, Purbasha Road, M.A. Muktadir | 2019-01-22 | NQ1002 | 5.3 | 62 | 5.3 | 63 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6144 | 2615.9997 | 55.8434
MBZ-2.RR.2.1 | 24182399144238 | Sreemangal, West Purbasha, Dr. Abdul Kiwum Road, Zille Suebhani | 2019-01-22 | NQ1002 | 9.3 | 66 | 9.3 | 67 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6144 | 2615.9997 | 97.9893
MBZ-2.RR.3.1 | 24182919144251 | Sreemangal, West Purbasha, Purbaddri Road, Bongshi Lal Baroy | 2019-01-22 | NQ1002 | 14.1 | 68 | 14.1 | 69 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6144 | 2615.9997 | 148.5644
MBZ-2.RR.4.1 | 24182919144251 | Sreemangal, West Purbasha, Purbaddri Road, Benoy Dotto | 2019-01-22 | NQ1002 | 11.5 | 70 | 11.5 | 71 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6144 | 2615.9997 | 121.1695
MBZ-2.RR.5.1 | 24182449144278 | Sreemangal, West Purbasha, Purbaddri Road, Monoj Bikash Deb | 2019-01-22 | NQ1002 | 23.6 | 72 | 23.6 | 73 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 23.6 | 23.6 | 1.416 | 1.416 | 0.0007168 | 100% | 0% | 1.416 | 1.416 | 0.0011869 | 28 | 0.028386 | 0.028386 |  | 0 | 0 | 6144 | 2615.9997 | 248.661
MBZ-2.RR.6.1 | 24182669144340 | Sreemangal, East Purbasha, Pallabi Road, Front Of Shibaloy | 2019-01-22 | NQ1002 | 20 | 74 | 20 | 75 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 6144 | 2615.9997 | 210.7296
MBZ-2.RR.7.1 | 24182919144327 | Sreemangal, Purbasha, Pallabi Road, Bomkim Bordhon | 2019-01-22 | NQ1002 | 2.4 | 76 | 2.4 | 77 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6144 | 2615.9997 | 25.2876
MBZ-2.RR.8.1 | 24194819144247 | Uttor Baraura, Majergao, Khitish Dhar | 2019-07-29 | MP1032 | 12.5 | 393 | 12.5 | 394 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6096 | 2663.9997 | 131.706
MBZ-2.RR.9.1 | 24194579144256 | Uttor Baraura, Majergao, Probad Deb | 2019-07-29 | MP1032 | 1.9 | 395 | 1.9 | 396 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6096 | 2663.9997 | 20.0193
MBZ-2.RR.10.1 | 24194479144254 | Uttor Baraura, Majergao, Beshnopodo Aeharjo | 2019-07-29 | MP1032 | 4.3 | 397 | 4.3 | 398 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6096 | 2663.9997 | 45.3069
MBZ-2.RR.11.1 | 24194479144254 | Uttor Baraura, Majergao, Beshnopodo Aeharjo | 2019-07-29 | MP1032 | 2.3 | 401 | 2.3 | 402 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6096 | 2663.9997 | 24.2339
MBZ-2.RR.12.1 | 24194449144293 | Uttor Baraura, Majergao, Shankar Deb | 2019-07-29 | MP1032 | 5 | 403 | 5 | 404 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6096 | 2663.9997 | 52.6824
MBZ-2.RR.13.1 | 24194449144293 | Uttor Baraura, Majergao, Shankar Deb | 2019-07-29 | MP1032 | 9.1 | 405 | 9.2 | 406 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6096 | 2663.9997 | 96.9356
MBZ-2.RR.14.1 | 24194689144320 | Uttor Baraura, Majergao, Badol | 2019-07-29 | MP1032 | 2.6 | 413 | 2.6 | 414 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6096 | 2663.9997 | 27.3949
MBZ-2.RR.15.1 | 24194729144339 | Uttor Baraura, Majergao, Potab Ronjon Dhor | 2019-07-29 | MP1032 | 7.8 | 415 | 7.8 | 416 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6096 | 2663.9997 | 82.1846
MBZ-2.RR.16.1 | 24194589144392 | Uttor Baraura, Majergao, Torun Kante Torat | 2019-07-29 | MP1032 | 4.4 | 417 | 4.4 | 418 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6096 | 2663.9997 | 46.3605
MBZ-2.RR.17.1 | 24194649144383 | Uttor Baraura, Majergao, Nermol Deb | 2019-07-29 | MP1032 | 11.2 | 419 | 11.2 | 420 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6096 | 2663.9997 | 118.0086
MBZ-2.RR.18.1 | 24185939144154 | Sremongol, Surova R/A, Momtaj Rahman | 2019-07-30 | MP1032 | 5 | 439 | 5 | 440 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6096 | 2663.9997 | 52.6824
MBZ-2.RR.19.1 | 24185939144154 | Sremongol, Surova R/A, Momtaj Rahman | 2019-07-30 | MP1032 | 11.8 | 441 | 11.8 | 442 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6096 | 2663.9997 | 124.3305
MBZ-2.RR.20.1 | 24185659144174 | Sremongol, Surova R/A, Abdul Maleq | 2019-07-30 | MP1032 | 4.9 | 443 | 4.9 | 444 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6096 | 2663.9997 | 51.6288
MBZ-2.RR.21.1 | 24183289144181 | Moulvibazar, Sreemongal,Shamoli R/A, Block # B, H # 12, Md. Sohel Mia | 2019-01-22 | NQ1009 | 12.9 | 17 | 12.9 | 18 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6144 | 2615.9997 | 135.9206
MBZ-2.RR.22.1 | 24183979144222 | Moulvibazar, Sreemongal,Shamoli R/A, Block # C, H # 48, Rofi Ahamed | 2019-01-22 | NQ1009 | 1.1 | 19 | 1.1 | 20 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6144 | 2615.9997 | 11.5901
MBZ-2.RR.23.1 | 24183829144203 | Moulvibazar, Sreemongal,Shamoli R/A, Block # C, H # 41, Sayed Mozibur Rahman | 2019-01-22 | NQ1009 | 3.4 | 21 | 3.4 | 22 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6144 | 2615.9997 | 35.824
MBZ-2.RR.24.1 | 24183779144252 | Moulvibazar, Sreemongal,Shamoli R/A, Block # D, H # 76, Abdul Maksud | 2019-01-22 | NQ1009 | 6.1 | 25 | 5.8 | 26 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6144 | 2615.9997 | 61.1116
MBZ-2.RR.25.1 | 24183279144240 | Moulvibazar, Sreemongal,Shamoli R/A, Block # C,Ibrahimpur Road, Helena Beside of Depshikha School | 2019-01-22 | NQ1009 | 10 | 27 | 10 | 28 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6144 | 2615.9997 | 105.3648
MBZ-2.RR.26.1 | 24183549144292 | Moulvibazar, Sreemongal,Shamoli R/A, Ibrahimpur Road, Abdul Haque | 2019-01-22 | NQ1009 | 1.9 | 29 | 1.9 | 30 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6144 | 2615.9997 | 20.0193
MBZ-2.RR.27.1 | 24183549144292 | Moulvibazar, Sreemongal,Shamoli R/A, Ibrahimpur Road, Mokid | 2019-01-22 | NQ1009 | 13.7 | 31 | 13.7 | 32 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6144 | 2615.9997 | 144.3498
MBZ-2.RR.28.1 | 24184159144343 | Moulvibazar, Sreemongal, East Biraimpur,Ward # 3, Biraimpur Road, Altafur Rahman, Nearby Radanath Gov: School | 2019-01-22 | NQ1009 | 1.1 | 33 | 1.1 | 34 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6144 | 2615.9997 | 11.5901
MBZ-2.RR.29.1 | 24183829144328 | Moulvibazar, Sreemongal, East Biraimpur,Ward # 3, Biraimpur Road, Nasima Villa | 2019-01-22 | NQ1009 | 1.2 | 35 | 1.2 | 36 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6144 | 2615.9997 | 12.6438
MBZ-2.RR.30.1 | 24190729144098 | Sremangal,Block # B, Shorove R/A, Ashutus Roy | 2019-07-29 | MP1032 | 7.6 | 421 | 7 | 422 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6096 | 2663.9997 | 73.7554
MBZ-2.RR.31.1 | 24190729144098 | Sremangal,Block # B, Shorove R/A, Debroto Chondo Deb | 2019-07-29 | MP1032 | 29.1 | 423 | 29.1 | 424 | 2022-01-01 | [9 empty] | 29.1 | 29.1 | 1.746 | 1.746 | 0.0007168 | 100% | 0% | 1.746 | 1.746 | 0.0011869 | 28 | 0.035001 | 0.035001 |  | 0 | 0
MBZ-2.RR.32.1 | 24190589144093 | Sremangal,Block # B, Shorove R/A, Santush Kumar Kar | 2019-07-29 | MP1032 | 11.9 | 425 | 11.9 | 426 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6096 | 2663.9997 | 125.3841
MBZ-2.RR.33.1 | 24190759144108 | Sremangal,Block # B, Shorove R/A, Shufian Ali | 2019-07-29 | MP1032 | 53.1 | 427 | 53.1 | 428 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 53.1 | 53.1 | 3.186 | 3.186 | 0.0007168 | 100% | 0% | 3.186 | 3.186 | 0.0011869 | 28 | 0.063868 | 0.063868 |  | 0 | 0 | 6096 | 2663.9997 | 559.4872
MBZ-2.RR.34.1 | 24190589144107 | Sremangal,Block # B, Shorove R/A, Shebu Das | 2019-07-29 | MP1032 | 7.5 | 429 | 7.5 | 430 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6096 | 2663.9997 | 79.0236
MBZ-2.RR.35.1 | 24190629144146 | Sremangal,Block # B, Shorove R/A, Golam Mostofa | 2019-07-29 | MP1032 | 10.8 | 431 | 11.1 | 432 | 2022-01-01 | [9 empty] | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0
MBZ-2.RR.36.1 | 24190599144152 | Sremangal,Block # B, Shorove R/A, H # 24 | 2019-07-29 | MP1032 | 42.3 | 437 | 42.3 | 438 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 42.3 | 42.3 | 2.538 | 2.538 | 0.0007168 | 100% | 0% | 2.538 | 2.538 | 0.0011869 | 28 | 0.050878 | 0.050878 |  | 0 | 0 | 6096 | 2663.9997 | 445.6932
MBZ-2.RR.37.1 | 24190339144155 | Sremangal,Block # A, Shorove R/A, H # 50 (Orun) | 2019-07-29 | NQ1007 | 5.6 | 386 | 5.6 | 387 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6096 | 2663.9997 | 59.0043
MBZ-2.RR.38.1 | 24190339144155 | Sremangal,Block # A, Shorove R/A, H # 50 | 2019-07-29 | NQ1007 | 12.6 | 388 | 12.6 | 389 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6096 | 2663.9997 | 132.7597
MBZ-2.RR.39.1 | 24190339144155 | Sremangal,Block # A, Shorove R/A, Mohon Chokroboty | 2019-07-29 | NQ1007 | 25 | 390 | 25 | 391 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 25 | 25 | 1.5 | 1.5 | 0.0007168 | 100% | 0% | 1.5 | 1.5 | 0.0011869 | 28 | 0.03007 | 0.03007 |  | 0 | 0 | 6096 | 2663.9997 | 263.412
MBZ-2.RR.40.1 | 24190439144157 | Sremangal,Block # A, Shorove R/A, Ragon Vela | 2019-07-29 | NQ1007 | 10.9 | 392 | 10.9 | 393 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6096 | 2663.9997 | 114.8476
MBZ-2.RR.40.2 | 24190439144157 | Sremangal,Block # A, Shorove R/A, Ragon Vela | 2020-10-10 | NQ1002 | 10.6 | 94 | 10.6 | 95 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6096 | 2663.9997 | 111.6867
MBZ-2.RR.41.1 | 24175989143578 | Sreemangal, Muslimbag Road, Md. Jamal Khan | 2019-01-22 | NQ1000 | 3.2 | 145 | 3.2 | 146 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6144 | 2615.9997 | 33.7167
MBZ-2.RR.42.1 | 24175989143578 | Sreemangal, Muslimbag Road, Yasin | 2019-01-22 | NQ1000 | 2.4 | 147 | 2.3 | 148 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6144 | 2615.9997 | 24.2339
MBZ-2.RR.43.1 | 24180089143535 | Sreemangal, Muslimbag, Md. Khalilur Rahman | 2019-01-22 | NQ1000 | 1.1 | 149 | 1.1 | 150 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6144 | 2615.9997 | 11.5901
MBZ-2.RR.44.1 | 24180039143512 | Sreemangal, Muslimbag, A. Rahim vhuya | 2019-01-22 | NQ1000 | 17.1 | 151 | 17.1 | 152 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 6144 | 2615.9997 | 180.1738
MBZ-2.RR.45.1 | 24175929143574 | Sreemangal, Muslimbag Road,Ripon | 2019-01-22 | NQ1000 | 12.2 | 153 | 11.8 | 154 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6144 | 2615.9997 | 124.3305
MBZ-2.RR.46.1 | 24175789143572 | Sreemangal, Muslimbag Road, Sarfaraz Khan | 2019-01-22 | NQ1000 | 2.1 | 155 | 2.1 | 156 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6144 | 2615.9997 | 22.1266
MBZ-2.RR.47.1 | 24175769143554 | Sreemangal, Muslimbag, Chinumia | 2019-01-22 | NQ1000 | 1 | 157 | 1 | 158 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 6144 | 2615.9997 | 10.5365
MBZ-2.RR.48.1 | 24175849143537 | Sreemangal, Muslimbag,Humayon Khan | 2019-01-22 | NQ1000 | 18.4 | 159 | 18.5 | 160 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6144 | 2615.9997 | 194.9249
MBZ-2.RR.49.1 | 24175849143537 | Sreemangal, Muslimbag, A. Mazid | 2019-01-22 | NQ1000 | 8 | 161 | 8 | 162 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6144 | 2615.9997 | 84.2919
MBZ-2.RR.50.1 | 24175909143522 | Sreemangal, Muslimbag, Idris mia | 2019-01-22 | NQ1000 | 1.5 | 163 | 1.4 | 164 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6144 | 2615.9997 | 14.7511
MBZ-2.RR.51.1 | 24175739143538 | Sreemangal, Muslimbag, Anguri Begum | 2019-01-22 | NQ1000 | 3.1 | 165 | 3.1 | 166 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6144 | 2615.9997 | 32.6631
MBZ-2.RR.52.1 | 24175689143565 | Sreemangal, Muslimbag Road, A. Rahim molla | 2019-01-22 | NQ1000 | 17.3 | 168 | 17.5 | 169 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 6144 | 2615.9997 | 184.3884
MBZ-2.RR.53.1 | 24175329143559 | Sreemangal, Muslimbag Road, Sofor Ali | 2019-01-22 | NQ1000 | 4.7 | 170 | 4.7 | 171 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6120 | 2639.9997 | 49.5215
MBZ-2.RR.54.1 | 24175329143559 | Sreemangal, Muslimbag Road, Wadud mia | 2019-01-22 | NQ1000 | 1.7 | 172 | 1.7 | 173 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6120 | 2639.9997 | 17.912
MBZ-2.RR.55.1 | 24175079143549 | Sreemangal, Muslimbag Road, A. Sattar Shikh | 2019-01-22 | NQ1000 | 2.9 | 175 | 2.9 | 176 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6120 | 2639.9997 | 30.5558
MBZ-2.RR.56.1 | 24175079143549 | Sreemangal, Muslimbag Road, Parvin Aktar mina | 2019-01-22 | NQ1000 | 6.2 | 177 | 6.2 | 178 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6120 | 2639.9997 | 65.3262
MBZ-2.RR.57.1 | 24201669144277 | Srimangal, Echobpur, Dhaka Sylhet Highway, 3 No Union, Ward # 1, Ronojit Ded | 2019-07-28 | NQ1005 | 14.6 | 310 | 14.6 | 311 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6096 | 2663.9997 | 153.8326
MBZ-2.RR.58.1 | 24193899144217 | Srimangal, North Varaura, 3 No Union, Ward # 2, Ronodhir Deb | 2019-07-29 | NQ1005 | 3.6 | 312 | 3.6 | 313 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6096 | 2663.9997 | 37.9313
MBZ-2.RR.59.1 | 24193909144217 | Srimangal, North Varaura, 3 No Union, Ward # 2, Chitto ronjon Dutta | 2019-07-29 | NQ1005 | 14.6 | 314 | 14.6 | 315 | 2022-01-01 | [9 empty] | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0
MBZ-2.RR.60.1 | 24192389144151 | Srimangal, South Varaura, 3 No Union, Ward # 3, Aahad Mia | 2019-07-29 | NQ1005 | 11 | 316 | 11 | 317 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6096 | 2663.9997 | 115.9013
MBZ-2.RR.61.1 | 24180859144003 | Sreemangal, Muslimbag, Anowar Uddin | 2019-01-22 | NQ1005 | 4.1 | 37 | 4.1 | 38 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6144 | 2615.9997 | 43.1996
MBZ-2.RR.62.1 | 24180739143597 | Sreemangal, Muslimbag, Goni Mia | 2019-01-22 | NQ1005 | 1.5 | 39 | 1.5 | 40 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6144 | 2615.9997 | 15.8047
MBZ-2.RR.63.1 | 24180719143585 | Sreemangal, Muslimbag, Nurul Islam | 2019-01-22 | NQ1005 | 1.8 | 41 | 1.8 | 42 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6144 | 2615.9997 | 18.9657
MBZ-2.RR.64.1 | 24180739143577 | Sreemangal, Muslimbag, Chand Mia | 2019-01-22 | NQ1005 | 1.7 | 43 | 1.7 | 44 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6144 | 2615.9997 | 17.912
MBZ-2.RR.65.1 | 24180719143566 | Sreemangal, Muslimbag, Titu Mia | 2019-01-22 | NQ1005 | 9 | 45 | 9 | 46 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6144 | 2615.9997 | 94.8283
MBZ-2.RR.66.1 | 24180709143561 | Sreemangal, Muslimbag, Residential Area, Shafiq Mia | 2019-01-22 | NQ1005 | 10.8 | 47 | 10.6 | 48 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 6096 | 0 | 48 | 2615.9997 | 33.965
MBZ-2.RR.67.1 | 24180769143560 | Sreemangal, Muslimbag, Residential Area, Aziz Mia | 2019-01-22 | NQ1005 | 4.1 | 49 | 4.1 | 50 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6144 | 2615.9997 | 43.1996
MBZ-2.RR.68.1 | 24180599143594 | Sreemangal, Muslimbag, Residential Area, Sanwar Uddin | 2019-01-22 | NQ1005 | 12.8 | 51 | 12.8 | 52 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6144 | 2615.9997 | 134.867
MBZ-2.RR.69.1 | 24180899143485 | Sreemangal, Khasgao, Near By Sindur Kha Road, Sayem Hossein | 2019-01-22 | NQ1005 | 3.6 | 53 | 3.6 | 54 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6120 | 2639.9997 | 37.9313
MBZ-2.RR.70.1 | 24180459143468 | Sreemangal, Khasgao, Salik Ahmed | 2019-01-22 | NQ1005 | 1.6 | 55 | 1.6 | 56 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6120 | 2639.9997 | 16.8584
MBZ-2.RR.71.1 | 24184399144037 | Srimangal, Jaynogor R/A, Word # 9, Sri Loknath Mondhir, Rana Deab Roy | 2019-07-29 | NQ1005 | 8 | 334 | 8 | 335 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6216 | 2543.9997 | 84.2919
MBZ-2.RR.72.1 | 24184269144028 | Srimangal, Jaynagor R/A, Word # 9, Juthi Bikas Das | 2019-07-29 | NQ1005 | 11.7 | 336 | 11.7 | 337 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6216 | 2543.9997 | 123.2768
MBZ-2.RR.73.1 | 24184069144027 | Srimangal, North College Road, Word # 9, H # 66, Alom's Square | 2019-07-29 | NQ1005 | 11.9 | 338 | 11.9 | 339 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6216 | 2543.9997 | 125.3841
MBZ-2.RR.73.2 | 24184069144027 | Srimangal, North College Road, Word # 9, H # 66, Alom's Square | 2021-02-03 | LU1001 | 3.7 | 142 | 3.7 | 143 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6216 | 2543.9997 | 38.985
MBZ-2.RR.74.1 | 24184069144027 | Srimangal, North College Road, Word # 9, H # 66, Alom's Square | 2019-07-29 | NQ1005 | 5.6 | 342 | 5.7 | 343 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6216 | 2543.9997 | 60.0579
MBZ-2.RR.75.1 | 24184069144027 | Srimangal, North College Road, Word # 9, H # 66, Alom's Square | 2019-07-29 | NQ1005 | 10.5 | 344 | 10.5 | 345 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6216 | 2543.9997 | 110.6331
MBZ-2.RR.76.1 | 24184229144008 | Srimangal, Mastar Para R/A, Sree Sree Santoshi Matar Mondhir, Sapon Kumar Roy | 2019-07-29 | NQ1005 | 2.6 | 346 | 2.6 | 347 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6216 | 2543.9997 | 27.3949
MBZ-2.RR.77.1 | 24184179144005 | Srimangal, Mastar Para R/A, Sree Sree Santoshi Matar Mondhir, Gobindo Bonik | 2019-07-29 | NQ1005 | 10.1 | 348 | 10.1 | 349 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6216 | 2543.9997 | 106.4185
MBZ-2.RR.78.1 | 24184339144013 | Srimangal, Mastar Para R/A, Word # 9, Priolal Shaha | 2019-07-29 | NQ1005 | 11.1 | 350 | 11.1 | 351 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6216 | 2543.9997 | 116.9549
MBZ-2.RR.79.1 | 24184379144012 | Srimangal, Mastar Para R/A, Word # 9, Subir Kumar Das | 2019-07-29 | NQ1005 | 9.8 | 352 | 9.8 | 353 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6216 | 2543.9997 | 103.2575
MBZ-2.RR.80.1 | 24184409144017 | Srimangal, Mastar Para R/A, Word # 9, Sebabroto Das | 2019-07-29 | NQ1005 | 12.1 | 354 | 12.1 | 355 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6216 | 2543.9997 | 127.4914
MBZ-2.RR.81.1 | 24184409144017 | Srimangal, Mastar Para R/A, Word # 9, Sudhir Ranjon Das | 2019-07-29 | NQ1005 | 5.6 | 356 | 5.6 | 357 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6216 | 2543.9997 | 59.0043
MBZ-2.RR.82.1 | 24181989143551 | Sreemangal, Word # 6, Shaplabag R/A, Notun Bazar, Govt Reail Colony | 2019-07-31 | NQ1005 | 12.5 | 391 | 12.5 | 392 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6144 | 2615.9997 | 131.706
MBZ-2.RR.83.1 | 24181069143587 | Sreemangal, Shidur Khan Road, Word # 2, Champa Begom | 2019-07-31 | NQ1005 | 8.9 | 393 | 8.9 | 394 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6144 | 2615.9997 | 93.7747
MBZ-2.RR.84.1 | 24180949143577 | Sreemangal, Shidur Khan Road, Word # 2, Yeakub Ali Khan | 2019-07-31 | NQ1005 | 10.5 | 395 | 10.5 | 396 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6144 | 2615.9997 | 110.6331
MBZ-2.RR.85.1 | 24181189143497 | Sreemangal, Shindur Khan Road, Word # 3, Ajijul Haque | 2019-07-31 | NQ1005 | 14.1 | 397 | 14.1 | 398 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6120 | 2639.9997 | 148.5644
MBZ-2.RR.86.1 | 24181189143497 | Sreemangal, Shindur Khan Road, Word # 3, Ajijul Haque | 2019-07-31 | NQ1005 | 8.1 | 399 | 8.1 | 400 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6120 | 2639.9997 | 85.3455
MBZ-2.RR.87.1 | 24180559143507 | Sreemangal, Khasghaw, Nobodhara R/A, Jamal Islam | 2019-07-31 | NQ1005 | 5.8 | 401 | 5.8 | 402 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6120 | 2639.9997 | 61.1116
MBZ-2.RR.88.1 | 24175029143352 | Sreemangal, Shindurkhan Road, Notun Bazar, Md.Abdul Ajij | 2019-08-01 | NQ1005 | 52 | 427 | 52 | 428 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 52 | 52 | 3.12 | 3.12 | 0.0007168 | 100% | 0% | 3.12 | 3.12 | 0.0011869 | 28 | 0.062545 | 0.062545 |  | 0 | 0 | 6120 | 2639.9997 | 547.897
MBZ-2.RR.89.1 | 24175029143352 | Sreemangal, Shindurkhan Road, Notun Bazar, Ram Nagar, Subol Das | 2019-08-01 | NQ1005 | 4 | 431 | 4 | 432 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6120 | 2639.9997 | 42.1459
MBZ-2.RR.90.1 | 24175039143331 | Sreemangal, Shindurkhan Road, Notun Bazar, Ram Nagar, Rai Ronjon Ghos | 2019-08-01 | NQ1005 | 2.8 | 433 | 2.8 | 434 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6120 | 2639.9997 | 29.5021
MBZ-2.RR.91.1 | 24175039143331 | Sreemangal, Shindurkhan Road, Notun Bazar, Ram Nagar, Rai Ronjon Ghos | 2019-08-01 | NQ1005 | 17.5 | 435 | 17.6 | 436 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 6120 | 2639.9997 | 185.4421
MBZ-2.RR.92.1 | 24175819143380 | Sreemangal, Shindurkhan Road, Word #4, Md.Selim Chowdhury | 2019-08-01 | NQ1005 | 4.6 | 437 | 4.6 | 438 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6120 | 2639.9997 | 48.4678
MBZ-2.RR.93.1 | 24180019143359 | Sreemangal, Shindurkhan Road, Deloar Miar Bari, Word # 4, Deloar Mia | 2019-08-01 | NQ1005 | 14.5 | 439 | 14.5 | 440 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 6120 | 2639.9997 | 152.779
MBZ-2.RR.94.1 | 24180159143398 | Sreemangal, Shindurkhan Road, Word # 4, Alvi Mia | 2019-08-01 | NQ1005 | 8.8 | 441 | 8.8 | 442 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6120 | 2639.9997 | 92.721
MBZ-2.RR.95.1 | 24180509143376 | Sreemangal, Shindurkhan Road, Pochim baug R/A, Sazzad Hossen | 2019-08-01 | NQ1005 | 11.4 | 443 | 11.4 | 444 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6120 | 2639.9997 | 120.1159
MBZ-2.RR.96.1 | 24180489143373 | Sreemangal, Shindurkhan Road, Pochim baug R/A, Noni Gopal Das | 2019-08-01 | NQ1005 | 8.3 | 445 | 8.3 | 446 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6120 | 2639.9997 | 87.4528
MBZ-2.RR.97.1 | 24180509143352 | Sreemangal, Shindurkhan Road, Pochim baug R/A, Md.Rofik Mia | 2019-08-01 | NQ1005 | 12.8 | 447 | 12.8 | 448 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6120 | 2639.9997 | 134.867
MBZ-2.RR.98.1 | 24180509143352 | Sreemangal, Shindurkhan Road, Pochim baug R/A, Md.Rofik Mia | 2019-08-01 | NQ1005 | 6.2 | 449 | 6.2 | 450 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6120 | 2639.9997 | 65.3262
MBZ-2.RR.99.1 | 24180309143381 | Sreemangal, Shindurkhan Road, Pochim baug R/A, Abdul Malek | 2019-08-01 | NQ1005 | 15.1 | 451 | 15.1 | 452 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6120 | 2639.9997 | 159.1009
MBZ-2.RR.100.1 | 24173329144250 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Brojendro Narayon | 2019-08-03 | NQ1005 | 13.9 | 476 | 13.2 | 477 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6120 | 2639.9997 | 139.0816
MBZ-2.RR.101.1 | 24205849144432 | Sreemangal, Kakiabazar , Kakiabazar Road, Sofiuddin Khan | 2019-07-28 | LX1011 | 3.6 | 370 | 3.6 | 371 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6096 | 2663.9997 | 37.9313
MBZ-2.RR.102.1 | 24193929144132 | Sreemangal, Moulvibazar Road, Ward # 2, Uttar Vara Ura, Md. Shamimul Haque | 2019-07-29 | LX1011 | 12.2 | 372 | 12.2 | 373 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6096 | 2663.9997 | 128.5451
MBZ-2.RR.103.1 | 24193739144138 | Sreemangal, Moulvibazar Road, Ward # 2, Uttar Vara Ura, Porimal Chandra Mollik | 2019-07-29 | LX1011 | 14.6 | 374 | 14.7 | 375 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6096 | 2663.9997 | 154.8863
MBZ-2.RR.104.1 | 24193509144143 | Sreemangal, Moulvibazar Road, Ward # 2, Uttar Vara Ura, Ajay Dev | 2019-07-29 | LX1011 | 10.2 | 378 | 10.2 | 379 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6096 | 2663.9997 | 107.4721
MBZ-2.RR.105.1 | 24193499144058 | Sreemangal, Ward # 2, Uttar Vara Ura Jame Mashjid Road, Yaur Mia | 2019-07-29 | LX1011 | 3.3 | 380 | 3.3 | 381 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6096 | 2663.9997 | 34.7704
MBZ-2.RR.106.1 | 24191469144059 | Sreemangal, Union # 3, South Vara Ura, Jetty Road, Molin Gosh | 2019-07-29 | LX1011 | 10.4 | 382 | 10.4 | 383 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6096 | 2663.9997 | 109.5794
MBZ-2.RR.107.1 | 24191589144045 | Sreemangal, Union # 3, South Vara Ura, Jetty Road, Tomal Chakrabarti | 2019-07-29 | LX1011 | 2.3 | 384 | 2.3 | 385 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6096 | 2663.9997 | 24.2339
MBZ-2.RR.108.1 | 24191579143571 | Sreemangal, Union # 3, South Vara Ura, Jetty Road, Shireen Cottage, M.A. Kabir | 2019-07-29 | LX1011 | 12 | 386 | 12 | 387 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6096 | 2663.9997 | 126.4378
MBZ-2.RR.108.2 | 24191579143571 | Sreemangal, Union # 3, South Vara Ura, Jetty Road, Shireen Cottage, M.A. Kabir | 2021-02-03 | NQ1003 | 11.8 | 196 | 12 | 197 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6096 | 2663.9997 | 126.4378
MBZ-2.RR.109.1 | 24191669143553 | Sreemangal, Union # 3, South Vara Ura, Jetty Road, Md. Fazlur Rahman | 2019-07-29 | LX1011 | 10.5 | 388 | 10.5 | 389 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6096 | 2663.9997 | 110.6331
MBZ-2.RR.110.1 | 24190599143509 | Sreemangal, Union No. 3, Ward # 3, Shondhani R/A, Fotik Bishwash | 2019-07-30 | LX1011 | 7.5 | 408 | 7.5 | 409 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6096 | 2663.9997 | 79.0236
MBZ-2.RR.111.1 | 24190929143538 | Sreemangal, Union No. 3, Ward # 3, South Vara Ura, Shondhani R/A, Rabindra Rudro Pal | 2019-07-30 | LX1011 | 9.6 | 410 | 9.6 | 411 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6096 | 2663.9997 | 101.1502
MBZ-2.RR.112.1 | 24190819143479 | Sreemangal, Union No. 3, Ward # 3, South Vara Ura, Shondhani R/A, Abdul Awal Bhuiyan | 2019-07-30 | LX1011 | 14.3 | 412 | 14.3 | 413 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6096 | 2663.9997 | 150.6717
MBZ-2.RR.112.2 | 24190819143479 | Sreemangal, Union No. 3, Ward # 3, South Vara Ura, Shondhani R/A, Abdul Awal Bhuiyan | 2019-07-30 | LX1011 | 2.1 | 414 | 2.1 | 415 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6096 | 2663.9997 | 22.1266
MBZ-2.RR.113.1 | 24191139143391 | Sreemangal, Union No. 3, Pashchim Vara Ura, Aleya Begum | 2019-07-30 | LX1011 | 2.6 | 416 | 2.6 | 417 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6240 | 2519.9997 | 27.3949
MBZ-2.RR.114.1 | 24191359143400 | Sreemangal, Union No. 3, Ward # 2, Pashchim Vara Ura, Azman Ali | 2019-07-30 | LX1011 | 7.7 | 418 | 7.7 | 419 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6240 | 2519.9997 | 81.1309
MBZ-2.RR.115.1 | 24183949143541 | Sreemangal, Moulvibazar Road, Opposite Road of Sreemangal Police Station, Rashida Villa | 2019-07-31 | LX1011 | 8.7 | 420 | 9 | 421 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6216 | 2543.9997 | 94.8283
MBZ-2.RR.115.2 | 24183949143541 | Sreemangal, Moulvibazar Road, Opposite Road of Sreemangal Police Station, Rashida Villa | 2019-07-31 | LX1011 | 38.3 | 422 | 38.3 | 423 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 38.3 | 38.3 | 2.298 | 2.298 | 0.0007168 | 100% | 0% | 2.298 | 2.298 | 0.0011869 | 28 | 0.046067 | 0.046067 |  | 0 | 0 | 6216 | 2543.9997 | 403.5472
MBZ-2.RR.116.1 | 24183279143461 | Sreemangal, Habiganj Road, Ward # 8, Taufik Parvez Shaykat | 2019-07-31 | LX1011 | 13.6 | 424 | 13.6 | 425 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6216 | 2543.9997 | 143.2961
MBZ-2.RR.117.1 | 24183399143461 | Sreemangal, Habiganj Road, Ward # 8, Belal Ahmad | 2019-07-31 | LX1011 | 11.8 | 426 | 11.8 | 427 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6216 | 2543.9997 | 124.3305
MBZ-2.RR.117.2 | 24183399143461 | Sreemangal, Habiganj Road, Ward # 8, Belal Ahmad | 2019-07-31 | LX1011 | 13.6 | 428 | 13.6 | 429 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6216 | 2543.9997 | 143.2961
MBZ-2.RR.118.1 | 24183399143461 | Sreemangal, Habiganj Road, Ward # 8, Kamal Ahmad | 2019-07-31 | LX1011 | 14.4 | 430 | 14.4 | 431 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6216 | 2543.9997 | 151.7253
MBZ-2.RR.119.1 | 24183219143457 | Sreemangal, Habiganj Road, Hotel Mukta ( Residential ) | 2019-07-31 | LX1011 | 24.5 | 433 | 24.5 | 434 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 6216 | 2543.9997 | 258.1438
MBZ-2.RR.120.1 | 24183399143409 | Sreemangal, Habiganj Road, Arambag R/A, M. Villa, Malek Mia | 2019-07-31 | LX1011 | 10.8 | 435 | 10.8 | 436 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6216 | 2543.9997 | 113.794
MBZ-2.RR.121.1 | 24183449143412 | Sreemangal, Habiganj Road, Arambag R/A, Shamim Ahmad | 2019-07-31 | LX1011 | 4.3 | 437 | 4.3 | 438 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6216 | 2543.9997 | 45.3069
MBZ-2.RR.122.1 | 24183579143324 | Sreemangal, Habiganj Road, Ruposhpur R/A, Promod Ranjan Debnath | 2019-07-31 | LX1011 | 19.4 | 439 | 19.4 | 440 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 19.4 | 19.4 | 1.164 | 1.164 | 0.0007168 | 100% | 0% | 1.164 | 1.164 | 0.0011869 | 28 | 0.023334 | 0.023334 |  | 0 | 0 | 6216 | 2543.9997 | 204.4077
MBZ-2.RR.123.1 | 24183819143295 | Sreemangal, Habiganj Road, Ruposhpur R/A, Ronjeet Kumar Debnath | 2019-07-31 | LX1011 | 10.8 | 441 | 10.8 | 442 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6216 | 2543.9997 | 113.794
MBZ-2.RR.124.1 | 24183869143300 | Sreemangal, Habiganj Road, Ruposhpur R/A, Bhanu Acharjyo | 2019-07-31 | LX1011 | 5.7 | 443 | 5.7 | 444 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6216 | 2543.9997 | 60.0579
MBZ-2.RR.125.1 | 24183519143249 | Sreemangal, Habiganj Road, Sabujbag R/A, Ajay Babu | 2019-08-01 | LX1011 | 2 | 483 | 2 | 484 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6216 | 2543.9997 | 21.073
MBZ-2.RR.126.1 | 24183119143223 | Sreemangal, Habiganj Road, Sabujbag R/A, Shachindra Chandra Shutrodhor | 2019-08-01 | LX1011 | 9.3 | 485 | 8.5 | 486 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6168 | 2591.9997 | 89.5601
MBZ-2.RR.127.1 | 24183179143225 | Sreemangal, Habiganj Road, Sabujbag R/A, Sri Jibendra Kumer Deb | 2019-08-01 | LX1011 | 14.2 | 487 | 14.2 | 488 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6168 | 2591.9997 | 149.618
MBZ-2.RR.128.1 | 24183259143212 | Sreemangal, Habiganj Road, Sabujbag R/A, Shankar Deb | 2019-08-01 | LX1011 | 4.5 | 489 | 4.5 | 490 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6168 | 2591.9997 | 47.4142
MBZ-2.RR.129.1 | 24183319143218 | Sreemangal, Habiganj Road, Sabujbag R/A, Subodh Chandra Das | 2019-08-01 | LX1011 | 3.8 | 491 | 3.9 | 492 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6168 | 2591.9997 | 41.0923
MBZ-2.RR.130.1 | 24183099143207 | Sreemangal, Habiganj Road, Sabujbag R/A, Suvash Ray | 2019-08-03 | LX1011 | 11.3 | 493 | 11.3 | 494 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6168 | 2591.9997 | 119.0622
MBZ-2.RR.131.1 | 24182959143165 | Sreemangal, Habiganj Road, Sabujbag R/A, Babul Pal | 2019-08-03 | LX1011 | 14 | 495 | 14 | 496 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6168 | 2591.9997 | 147.5107
MBZ-2.RR.132.1 | 24182659143181 | Sreemangal, Habiganj Road, Sabujbag R/A, Jahor Lal Chowdhury | 2019-08-03 | LX1011 | 14.4 | 497 | 14.4 | 498 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6168 | 2591.9997 | 151.7253
MBZ-2.RR.133.1 | 24183529143155 | Sreemangal, Habiganj Road, Sabujbag R/A, Kishor Kor | 2019-08-03 | LX1011 | 4.4 | 499 | 4.4 | 500 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6168 | 2591.9997 | 46.3605
MBZ-2.RR.134.1 | 24183859143185 | Sreemangal, Habiganj Road, Sabujbag R/A, Bijan Pal | 2019-08-03 | LX1011 | 2.9 | 501 | 2.9 | 502 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6216 | 2543.9997 | 30.5558
MBZ-2.RR.135.1 | 24184059143178 | Sreemangal, Habiganj Road, Sabujbag R/A, Aynul Islam | 2019-08-03 | LX1011 | 3.1 | 503 | 3.1 | 504 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6216 | 2543.9997 | 32.6631
MBZ-2.RR.136.1 | 24183929143217 | Sreemangal, Habiganj Road, Sabujbag R/A, Ratan Bonik | 2019-08-03 | LX1011 | 19.8 | 505 | 19.8 | 506 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 19.8 | 19.8 | 1.188 | 1.188 | 0.0007168 | 100% | 0% | 1.188 | 1.188 | 0.0011869 | 28 | 0.023815 | 0.023815 |  | 0 | 0 | 6216 | 2543.9997 | 208.6223
MBZ-2.RR.137.1 | 24184179143175 | Sreemangal, Habiganj Road, Sabujbag R/A, Abdul Hannan | 2019-08-03 | LX1011 | 8.7 | 507 | 8.7 | 508 | 2022-01-01 | [9 empty] | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 | 2022-09-12 12:00 | 0 | 0
MBZ-2.RR.138.1 | 24183119143161 | Sreemangal, Habiganj Road, Sabujbag R/A, Jitendra Kumar Das | 2019-08-03 | LX1011 | 9.8 | 509 | 9.8 | 510 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6168 | 2591.9997 | 103.2575
MBZ-2.RR.139.1 | 24183159143142 | Sreemangal, Habiganj Road, Sabujbag R/A, Chand Bhaban, Choyan Kanti Chand | 2019-08-03 | LX1011 | 12.3 | 511 | 12.3 | 512 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6168 | 2591.9997 | 129.5987
MBZ-2.RR.140.1 | 24183659143325 | Sreemangal, Ruposhpur R/A, Jyoti Lal Dev | 2019-08-04 | LX1011 | 11.8 | 531 | 11.8 | 532 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6216 | 2543.9997 | 124.3305
MBZ-2.RR.141.1 | 24183129143088 | Sreemangal, Habiganj Road, Sabujbag R/A, Akhil Chandra Dev | 2019-08-04 | LX1011 | 11.4 | 533 | 12.4 | 534 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6168 | 2591.9997 | 130.6524
MBZ-2.RR.142.1 | 24182849143079 | Sreemangal, Habiganj Road, Sabujbag R/A, Subodh Das | 2019-08-04 | LX1011 | 13.4 | 535 | 13.4 | 536 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6168 | 2591.9997 | 141.1888
MBZ-2.RR.143.1 | 24183149143087 | Sreemangal, Habiganj Road, Sabujbag R/A, Shakti Broto Das Gupta | 2019-08-04 | LX1011 | 6.7 | 537 | 6.7 | 538 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6168 | 2591.9997 | 70.5944
MBZ-2.RR.144.1 | 24183189143065 | Sreemangal, Habiganj Road, Sabujbag R/A, Ajay Ray | 2019-08-04 | LX1011 | 6.7 | 539 | 6.7 | 540 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6168 | 2591.9997 | 70.5944
MBZ-2.RR.145.1 | 24183179143063 | Sreemangal, Habiganj Road, Sabujbag R/A, Nipendra Biswas | 2019-08-04 | LX1011 | 6.4 | 541 | 6.4 | 542 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6168 | 2591.9997 | 67.4335
MBZ-2.RR.146.1 | 24183179143063 | Sreemangal, Habiganj Road, Sabujbag R/A, Dinbondhu Dev | 2019-08-04 | LX1011 | 11.9 | 543 | 11.9 | 544 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6168 | 2591.9997 | 125.3841
MBZ-2.RR.147.1 | 24182869143048 | Sreemangal, Habiganj Road, Sabujbag R/A, Shudhir Chandra | 2019-08-04 | LX1011 | 8.2 | 545 | 8.2 | 546 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6168 | 2591.9997 | 86.3991
MBZ-2.RR.148.1 | 24183059143043 | Sreemangal, Habiganj Road, Sabujbag R/A, Apu Chakroborti | 2019-08-04 | LX1011 | 11.2 | 547 | 11.2 | 548 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6168 | 2591.9997 | 118.0086
MBZ-2.RR.149.1 | 24183119142596 | Sreemangal, Habiganj Road, Sabujbag R/A, Taposh Roy | 2019-08-04 | LX1011 | 3 | 549 | 3 | 550 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6168 | 2591.9997 | 31.6094
MBZ-2.RR.150.1 | 24183019142579 | Sreemangal, Habiganj Road, Sabujbag R/A, Sunil Shil | 2019-08-04 | LX1011 | 3.2 | 551 | 3.2 | 552 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6168 | 2591.9997 | 33.7167
MBZ-2.RR.151.1 | 24191009144048 | Sreemangal, Moulvibazar Road, South Baraura, 3No pool, Kazi Abdul Karim | 2019-07-29 | LX1011 | 4.6 | 390 | 4.6 | 391 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6096 | 2663.9997 | 48.4678
MBZ-2.RR.152.1 | 24190839144031 | Sreemangal, Moulvibazar Road, South Baraura, 3No pool, Sankar Sheel | 2019-07-29 | LX1011 | 2.8 | 392 | 2.8 | 393 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6096 | 2663.9997 | 29.5021
MBZ-2.RR.153.1 | 24190269144008 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Alpona Villa | 2019-07-29 | LX1011 | 8.8 | 394 | 8.8 | 395 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6096 | 2663.9997 | 92.721
MBZ-2.RR.154.1 | 24190309143596 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Pronoy Acharjee | 2019-07-29 | LX1011 | 14.2 | 396 | 13.1 | 397 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6096 | 2663.9997 | 138.0279
MBZ-2.RR.155.1 | 24190259143594 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Abdul Hamid | 2019-07-29 | LX1011 | 6.3 | 398 | 6.3 | 399 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6096 | 2663.9997 | 66.3798
MBZ-2.RR.156.1 | 24190699144021 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Olok Ghosh | 2019-07-29 | LX1011 | 11.5 | 400 | 11.5 | 401 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6096 | 2663.9997 | 121.1695
MBZ-2.RR.156.2 | 24190699144021 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Olok Ghosh | 2021-02-03 | NQ1007 | 12.9 | 144 | 12.9 | 145 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6096 | 2663.9997 | 135.9206
MBZ-2.RR.157.1 | 24190599143567 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Shuvroto Dev | 2019-07-29 | LX1011 | 10.9 | 402 | 10.9 | 403 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6096 | 2663.9997 | 114.8476
MBZ-2.RR.158.1 | 24190669143566 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Jogodis Bonik | 2019-07-29 | LX1011 | 4.7 | 404 | 4.7 | 405 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6096 | 2663.9997 | 49.5215
MBZ-2.RR.159.1 | 24190599143509 | Sreemangal, South Baraura, Shandhani R/A, Suna Mia Road, Ashim Kumar Shaha | 2019-07-29 | LX1011 | 11.9 | 406 | 11.9 | 407 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6096 | 2663.9997 | 125.3841
MBZ-2.RR.160.1 | 24183819143357 | Sreemangal, Rupashpur R/A, Akhra Road, Jugendra Deb Nath | 2019-07-31 | LX1011 | 10.9 | 445 | 10.9 | 446 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6216 | 2543.9997 | 114.8476
MBZ-2.RR.161.1 | 24183959143355 | Sreemangal, Rupashpur R/A, Akhra Road, Boshonto Kumar Ray | 2019-07-31 | LX1011 | 9 | 447 | 9 | 448 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6216 | 2543.9997 | 94.8283
MBZ-2.RR.162.1 | 24184209143328 | Sreemangal, Rupashpur R/A, Akhra Road, Bimol Pal | 2019-07-31 | LX1011 | 4.6 | 449 | 4.6 | 450 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6216 | 2543.9997 | 48.4678
MBZ-2.RR.163.1 | 24184329143324 | Sreemangal, Rupashpur R/A, Akhra Road, Sreekanto Pal (Manna) | 2019-07-31 | LX1011 | 7.6 | 451 | 7.6 | 452 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6216 | 2543.9997 | 80.0773
MBZ-2.RR.164.1 | 24184829143339 | Sreemangal, Rupashpur R/A, Akhra Road, Jugesh Shutro Dhar | 2019-07-31 | LX1011 | 11 | 453 | 11 | 454 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6216 | 2543.9997 | 115.9013
MBZ-2.RR.165.1 | 24184839143322 | Sreemangal, Rupashpur R/A, Beside Akhra Mondir, Benu Pal | 2019-07-31 | LX1011 | 28.7 | 455 | 28.7 | 456 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 28.7 | 28.7 | 1.722 | 1.722 | 0.0007168 | 100% | 0% | 1.722 | 1.722 | 0.0011869 | 28 | 0.03452 | 0.03452 |  | 0 | 0 | 6216 | 2543.9997 | 302.397
MBZ-2.RR.166.1 | 24184739143337 | Sreemangal, Rupashpur R/A, Beside Akhra Mondir, Bidhan Chandra Pal | 2019-07-31 | LX1011 | 14.9 | 457 | 14.8 | 458 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6216 | 2543.9997 | 155.9399
MBZ-2.RR.167.1 | 24184709143304 | Sreemangal, Rupashpur R/A, Akhra Road, Porimol Bhowmic | 2019-07-31 | LX1011 | 3.2 | 459 | 3.2 | 460 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6216 | 2543.9997 | 33.7167
MBZ-2.RR.168.1 | 24184489143292 | Sreemangal, Rupashpur R/A, Akhra Road, Shudip Kumar Sharma | 2019-07-31 | LX1011 | 5.9 | 461 | 5.9 | 462 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6216 | 2543.9997 | 62.1652
MBZ-2.RR.169.1 | 24184479143291 | Sreemangal, Rupashpur R/A, Akhra Road, Nihir Acharjo | 2019-07-31 | LX1011 | 3.6 | 463 | 3.6 | 464 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6216 | 2543.9997 | 37.9313
MBZ-2.RR.170.1 | 24184469143271 | Sreemangal, Rupashpur R/A, Akhra Road, Niblu Chandra | 2019-07-31 | LX1011 | 5.3 | 465 | 5.3 | 466 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6216 | 2543.9997 | 55.8434
MBZ-2.RR.171.1 | 24184519143257 | Sreemangal, Rupashpur R/A, Akhra Road, Sen Villa, H # 270 | 2019-07-31 | LX1011 | 11.4 | 467 | 11.5 | 468 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6216 | 2543.9997 | 121.1695
MBZ-2.RR.172.1 | 24184079143302 | Sreemangal, Rupashpur R/A, Biplob Deb | 2019-08-01 | LX1011 | 4 | 469 | 4 | 470 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6216 | 2543.9997 | 42.1459
MBZ-2.RR.173.1 | 24184099143291 | Sreemangal, Rupashpur R/A, Dulal Kanti Deb | 2019-08-01 | LX1011 | 11 | 471 | 10.9 | 472 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6216 | 2543.9997 | 114.8476
MBZ-2.RR.174.1 | 24183949143281 | Sreemangal, Rupashpur R/A, Ranjit Bowddha | 2019-08-01 | LX1011 | 3.8 | 473 | 3.8 | 474 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6216 | 2543.9997 | 40.0386
MBZ-2.RR.175.1 | 24184109143277 | Sreemangal, Rupashpur R/A, Ajit Das | 2019-08-01 | LX1011 | 12.5 | 475 | 12.5 | 476 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6216 | 2543.9997 | 131.706
MBZ-2.RR.176.1 | 24184109143277 | Sreemangal, Rupashpur R/A, Bipod Bondhu Bhottacharjo | 2019-08-01 | LX1011 | 4.9 | 477 | 4.9 | 478 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6216 | 2543.9997 | 51.6288
MBZ-2.RR.177.1 | 24184179143241 | Sreemangal, Rupashpur R/A, Mayaa Bowddha (Sochi Babu) | 2019-08-01 | LX1011 | 11.7 | 479 | 11.6 | 480 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6216 | 2543.9997 | 122.2232
MBZ-2.RR.177.2 | 24184179143241 | Sreemangal, Rupashpur R/A, Mayaa Bowddha (Sochi Babu) | 2022-03-07 | NQ1007 | 5.5 | 32 | 5.5 | 33 | 2022-03-07 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 4656 | 2543.9997 | 47.6307
MBZ-2.RR.178.1 | 24184559143247 | Sreemangal, Rupashpur R/A, Meena Bhaban, Narayon Pal | 2019-08-01 | LX1011 | 6.8 | 481 | 6.8 | 482 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6216 | 2543.9997 | 71.6481
MBZ-2.RR.179.1 | 24183309143111 | Sreemangal, Sabujbag R/A, Makhon Das | 2019-08-03 | LX1011 | 3.3 | 513 | 3.3 | 514 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6168 | 2591.9997 | 34.7704
MBZ-2.RR.180.1 | 24183579143097 | Sreemangal, Sabujbag R/A, Thakurpara, Biplob Chakrabarti | 2019-08-03 | LX1011 | 30.4 | 515 | 30.5 | 516 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 30.5 | 30.5 | 1.83 | 1.83 | 0.0007168 | 100% | 0% | 1.83 | 1.83 | 0.0011869 | 28 | 0.036685 | 0.036685 |  | 0 | 0 | 6168 | 2591.9997 | 321.3627
MBZ-2.RR.181.1 | 24184029143106 | Sreemangal, Sabujbag R/A, Thakurpara, Gokulanondo Ghosshami | 2019-08-03 | LX1011 | 2.4 | 517 | 2.4 | 518 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6216 | 2543.9997 | 25.2876
MBZ-2.RR.182.1 | 24184209143058 | Sreemangal, Sabujbag R/A, Thakur Bari, Gowrango Chakrabarti | 2019-08-03 | LX1011 | 14.6 | 519 | 14.5 | 520 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 6216 | 2543.9997 | 152.779
MBZ-2.RR.183.1 | 24184349143070 | Sreemangal, Sabujbag R/A, Indramuhon Sharani, Manoranjon Deb Nath | 2019-08-03 | LX1011 | 4.3 | 521 | 4.3 | 522 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6216 | 2543.9997 | 45.3069
MBZ-2.RR.184.1 | 24184349143070 | Sreemangal, Sabujbag R/A, Indramuhon Sharani, Kajol Kanti Das | 2019-08-03 | LX1011 | 4.4 | 523 | 4.4 | 524 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6216 | 2543.9997 | 46.3605
MBZ-2.RR.185.1 | 24184349143070 | Sreemangal, Sabujbag R/A, Indramuhon Sharani, Somiron Ray | 2019-08-03 | LX1011 | 5.9 | 525 | 5.9 | 526 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6216 | 2543.9997 | 62.1652
MBZ-2.RR.186.1 | 24184349143070 | Sreemangal, Sabujbag R/A, Indramuhon Sharani, Gonesh Das | 2019-08-03 | LX1011 | 3.6 | 527 | 3.3 | 528 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6216 | 2543.9997 | 34.7704
MBZ-2.RR.187.1 | 24183469143071 | Sreemangal, Sabujbag R/A, Arun Kumar Chandra | 2019-08-03 | LX1011 | 8 | 529 | 8 | 530 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6168 | 2591.9997 | 84.2919
MBZ-2.RR.187.2 | 24183469143071 | Sreemangal, Sabujbag R/A, Arun Kumar Chandra | 2021-02-02 | NQ1003 | 3.3 | 184 | 3.3 | 185 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6168 | 2591.9997 | 34.7704
MBZ-2.RR.187.3 | 24183469143071 | Sreemangal, Sabujbag R/A, Arun Kumar Chandra | 2021-02-02 | NQ1003 | 9.8 | 186 | 9.8 | 187 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6168 | 2591.9997 | 103.2575
MBZ-2.RR.188.1 | 24184339142504 | Sreemangal, Sabujbag R/A, Tuhin & Nabil Villa, Abdul Karim (Sawdagor) | 2019-08-04 | LX1011 | 12.4 | 553 | 12.4 | 554 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6168 | 2591.9997 | 130.6524
MBZ-2.RR.189.1 | 24184589142502 | Sreemangal, Sabujbag, R/A, Geyanendra Kumar dey | 2019-08-04 | LX1011 | 4.1 | 555 | 4.1 | 556 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6168 | 2591.9997 | 43.1996
MBZ-2.RR.190.1 | 24183569144088 | Sreemangal, Court Road(Uttar), Firoz Chowdhury | 2019-08-04 | LX1011 | 10.9 | 557 | 10.4 | 558 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6144 | 2615.9997 | 109.5794
MBZ-2.RR.191.1 | 24183629144047 | Sreemangal, Guho Road, Abu Taher | 2019-08-05 | LX1011 | 7.5 | 559 | 7.5 | 560 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6216 | 2543.9997 | 79.0236
MBZ-2.RR.192.1 | 24183629144047 | Sreemangal, Guho Road, Nasir Uddin | 2019-08-05 | LX1011 | 10.4 | 561 | 10.4 | 562 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6216 | 2543.9997 | 109.5794
MBZ-2.RR.193.1 | 24183629144047 | Sreemangal, Guho Road, Nasir Uddin | 2019-08-05 | LX1011 | 3.6 | 563 | 3.6 | 564 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6216 | 2543.9997 | 37.9313
MBZ-2.RR.194.1 | 24183629144047 | Sreemangal, Guho Road, Amirunnesa(Hazi Basir Uddin) | 2019-08-05 | LX1011 | 2.7 | 565 | 2.6 | 566 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6216 | 2543.9997 | 27.3949
MBZ-2.RR.195.1 | 24183909144035 | Sreemangal, Guho Road, Fazlur Rahman | 2019-08-05 | LX1011 | 6.3 | 567 | 6.3 | 568 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6216 | 2543.9997 | 66.3798
MBZ-2.RR.196.1 | 24184559144139 | Sreemangal, Jurpool, College Road, Aysha Akter, H # 100 | 2019-08-05 | LX1011 | 28.1 | 569 | 28.1 | 570 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 28.1 | 28.1 | 1.686 | 1.686 | 0.0007168 | 100% | 0% | 1.686 | 1.686 | 0.0011869 | 28 | 0.033799 | 0.033799 |  | 0 | 0 | 6096 | 2663.9997 | 296.0751
MBZ-2.RR.201.1 | 24193059144089 | Sreemongol, North Varaura, Maya Nibas, Bodrul Islam | 2019-07-29 | NQ1007 | 1.1 | 363 | 1.1 | 364 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6096 | 2663.9997 | 11.5901
MBZ-2.RR.202.1 | 24191779144085 | Sreemongol, South Varaura, Baitun Nur Jame Mosjid, Sirajul Kaium | 2019-07-29 | NQ1007 | 2.3 | 365 | 2.3 | 366 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6096 | 2663.9997 | 24.2339
MBZ-2.RR.203.1 | 24185739144007 | Sreemongol, Morhum Abdul Aziz Road, Baridhara R/A, H # 652, , Asini Bindu Niketon | 2019-07-29 | NQ1007 | 10.4 | 367 | 10.4 | 368 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6240 | 2519.9997 | 109.5794
MBZ-2.RR.204.1 | 24185939144000 | Sreemongol, Morhum Abdul Aziz Road, Baridhara R/A, H # 156, Hazi Mohammad Nahid | 2019-07-29 | NQ1007 | 11.8 | 369 | 11.8 | 370 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6240 | 2519.9997 | 124.3305
MBZ-2.RR.205.1 | 24185509143577 | Sreemongol, Morhum Abdul Aziz Road, Baridhara R/A, Hemendro devnath | 2019-07-29 | NQ1007 | 13.5 | 372 | 13.5 | 373 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6240 | 2519.9997 | 142.2425
MBZ-2.RR.206.1 | 24184109143528 | Sreemongol, R.K Mission Road, Saidul Hasan, Front Of Ram krisno Sebacharom | 2019-07-30 | NQ1007 | 13.6 | 396 | 13.6 | 397 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6216 | 2543.9997 | 143.2961
MBZ-2.RR.207.1 | 24184109143528 | Sreemongol, R.K Mission Road, Afsar Uddin, Front Of Ram krisno Sebacharom | 2019-07-30 | NQ1007 | 11 | 398 | 11 | 399 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6216 | 2543.9997 | 115.9013
MBZ-2.RR.208.1 | 24184169143506 | Sreemongol, R.K Mission Road, Sumon villa, Dulu Mia | 2019-07-30 | NQ1007 | 5.4 | 400 | 5.4 | 401 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6216 | 2543.9997 | 56.897
MBZ-2.RR.209.1 | 24184059143488 | Sreemongol, Sona Mia Road, Md Sanaur Rahman | 2019-07-30 | NQ1007 | 3.8 | 402 | 3.8 | 403 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6216 | 2543.9997 | 40.0386
MBZ-2.RR.210.1 | 24183879143488 | Sreemongol, Sona Mia Road, Md Shafiqul Hoque | 2019-07-30 | NQ1007 | 3 | 404 | 3 | 405 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6216 | 2543.9997 | 31.6094
MBZ-2.RR.211.1 | 24184399143483 | Sreemongol, R.K Mission Road, Khaled Mia | 2019-07-30 | NQ1007 | 1.2 | 406 | 1.2 | 407 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6216 | 2543.9997 | 12.6438
MBZ-2.RR.211.2 | 24184399143483 | Sreemongol, R.K Mission Road, Khaled Mia | 2021-02-03 | LU1001 | 7.4 | 140 | 7.4 | 141 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6216 | 2543.9997 | 77.97
MBZ-2.RR.212.1 | 24184799143494 | Sreemangal, Acoddor Ali Road, Md Lutfor Rahman Rahman | 2019-07-31 | NQ1007 | 13.6 | 408 | 13.6 | 409 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6240 | 2519.9997 | 143.2961
MBZ-2.RR.213.1 | 24185269143535 | Sreemangal, Chatholic Mission Road, Onil Pal | 2019-07-31 | NQ1007 | 6.3 | 410 | 6.3 | 411 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6240 | 2519.9997 | 66.3798
MBZ-2.RR.214.1 | 24185409143518 | Sreemangal, Chatholic Mission Road, Alhaj Mochlon monjil | 2019-07-31 | NQ1007 | 5.7 | 412 | 5.7 | 413 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6240 | 2519.9997 | 60.0579
MBZ-2.RR.215.1 | 24185479143523 | Sreemangal, Chatholic Mission Road, Orundev | 2019-07-31 | NQ1007 | 5.6 | 416 | 5.6 | 417 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6240 | 2519.9997 | 59.0043
MBZ-2.RR.216.1 | 24185499143522 | Sreemangal, Chatholic Mission Road, Romendro Narayon Pal | 2019-07-31 | NQ1007 | 3.5 | 418 | 3.5 | 419 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6240 | 2519.9997 | 36.8777
MBZ-2.RR.217.1 | 24185469143492 | Sreemangal, Chatholic Mission Road, Sree Mohendro Lal | 2019-07-31 | NQ1007 | 10 | 420 | 10 | 421 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6240 | 2519.9997 | 105.3648
MBZ-2.RR.218.1 | 24185679143495 | Sreemangal, Chatholic Mission Road, Uttam Dev Nath | 2019-07-31 | NQ1007 | 6.1 | 422 | 6.1 | 423 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6240 | 2519.9997 | 64.2725
MBZ-2.RR.219.1 | 24185749143497 | Sreemangal, Chatholic Mission Road, Nurul Islam | 2019-07-31 | NQ1007 | 6.3 | 424 | 6.3 | 425 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6240 | 2519.9997 | 66.3798
MBZ-2.RR.220.1 | 24185749143497 | Sreemangal, Chatholic Mission Road, Abdul Zabbar | 2019-07-31 | NQ1007 | 12.2 | 426 | 12.5 | 427 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6240 | 2519.9997 | 131.706
MBZ-2.RR.221.1 | 24185559143451 | Sreemangal, Chatholic Mission Road, Joyonto Pal | 2019-07-31 | NQ1007 | 12.4 | 428 | 12.4 | 429 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6240 | 2519.9997 | 130.6524
MBZ-2.RR.222.1 | 24185679143447 | Sreemangal, Chatholic Mission Road, Din Islam | 2019-07-31 | NQ1007 | 11.8 | 430 | 11.8 | 431 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6240 | 2519.9997 | 124.3305
MBZ-2.RR.223.1 | 24184939143401 | Sreemangal, Ukilbari Road, Hazi Md Abdul Jalil | 2019-08-01 | NQ1007 | 25.4 | 455 | 25.4 | 456 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 25.4 | 25.4 | 1.524 | 1.524 | 0.0007168 | 100% | 0% | 1.524 | 1.524 | 0.0011869 | 28 | 0.030551 | 0.030551 |  | 0 | 0 | 6240 | 2519.9997 | 267.6266
MBZ-2.RR.224.1 | 24185139143394 | Sreemangal, West Varaura Road, Mottalib Vaban | 2019-08-01 | NQ1007 | 12.2 | 457 | 12 | 458 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6240 | 2519.9997 | 126.4378
MBZ-2.RR.225.1 | 24185209143403 | Sreemangal, West Varaura, Amzad Ali Road, Abdul Hamid | 2019-08-01 | NQ1007 | 12.9 | 459 | 12.9 | 460 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6240 | 2519.9997 | 135.9206
MBZ-2.RR.226.1 | 24185439143406 | Sreemangal, West Varaura Road, Amzad Ali Road, Abdul Khaled | 2019-08-01 | NQ1007 | 2.7 | 461 | 2.7 | 462 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6240 | 2519.9997 | 28.4485
MBZ-2.RR.227.1 | 24185569143339 | Sreemangal, West Varaura, West Varaura Road, Kazi Nurul Huda | 2019-08-01 | NQ1007 | 14 | 463 | 14 | 464 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 6240 | 2519.9997 | 147.5107
MBZ-2.RR.228.1 | 24190629143367 | Sreemangal, West Varaura, West Varaura Road, Md Fazlur Rahman | 2019-08-01 | NQ1007 | 12.4 | 465 | 12.4 | 466 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6240 | 2519.9997 | 130.6524
MBZ-2.RR.229.1 | 24190249143431 | Sreemangal, West Varaura, Amzad Ali Road, Abdul Motin | 2019-08-01 | NQ1007 | 9.3 | 467 | 9.2 | 468 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6240 | 2519.9997 | 96.9356
MBZ-2.RR.230.1 | 24182319143102 | Sreemangal, Devbari Road, Late Nirmolendu Dev | 2019-08-03 | NQ1007 | 5.3 | 487 | 5.3 | 488 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6168 | 2591.9997 | 55.8434
MBZ-2.RR.231.1 | 24182319143102 | Sreemangal, Devbari Road, Biman Bihari Dev | 2019-08-03 | NQ1007 | 5.2 | 489 | 5.2 | 490 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6168 | 2591.9997 | 54.7897
MBZ-2.RR.232.1 | 24182009143133 | Sreemangal, Shukhnir R/A, Shukhnir R/A Road, H # 14, Sodes Kumar | 2019-08-03 | NQ1007 | 4 | 491 | 4 | 492 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6168 | 2591.9997 | 42.1459
MBZ-2.RR.233.1 | 24182009143133 | Sreemangal, Shukhnir R/A, Shukhnir R/A Road, H # 14, Prodip Kumar dash | 2019-08-03 | NQ1007 | 13 | 493 | 13 | 494 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6168 | 2591.9997 | 136.9743
MBZ-2.RR.234.1 | 24182009143133 | Sreemangal, Shukhnir R/A, Shukhnir R/A Road, H # 1185, Niranjon Pal | 2019-08-03 | NQ1007 | 10.2 | 495 | 10.2 | 496 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6168 | 2591.9997 | 107.4721
MBZ-2.RR.235.1 | 24181619143138 | Sreemangal, Shukhnir R/A, Muktijodda Road, H # 23, Late Pijus Kanti Dev | 2019-08-03 | NQ1007 | 3 | 497 | 3 | 498 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6168 | 2591.9997 | 31.6094
MBZ-2.RR.236.1 | 24181779143143 | Sreemangal, Shukhnir R/A, Muktijodda Road, H # 5, Sanatan | 2019-08-03 | NQ1007 | 5.6 | 499 | 5.6 | 500 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6168 | 2591.9997 | 59.0043
MBZ-2.RR.237.1 | 24181719143106 | Sreemangal, Lalbug R/A, Nangtar Mazar. Md. Foysal Ahamed | 2019-08-03 | NQ1007 | 12.4 | 503 | 12.4 | 504 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6168 | 2591.9997 | 130.6524
MBZ-2.RR.237.2 | 24181719143106 | Sreemangal, Lalbug R/A, Nangtar Mazar. Md. Foysal Ahamed | 2022-03-06 | NQ1007 | 5.2 | 30 | 5.2 | 31 | 2022-03-06 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 4632 | 2591.9997 | 45.1827
MBZ-2.RR.238.1 | 24182149143033 | Sreemangal, Lalbug R/A, Mahatab Uddin | 2019-08-04 | NQ1007 | 18.7 | 521 | 18.3 | 522 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 18.3 | 18.3 | 1.098 | 1.098 | 0.0007168 | 100% | 0% | 1.098 | 1.098 | 0.0011869 | 28 | 0.022011 | 0.022011 |  | 0 | 0 | 6168 | 2591.9997 | 192.8176
MBZ-2.RR.239.1 | 24182229142572 | Sreemangal, Lalbug R/A, Md. Suruk Mia | 2019-08-04 | NQ1007 | 8.5 | 523 | 8.5 | 524 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6168 | 2591.9997 | 89.5601
MBZ-2.RR.240.1 | 24182479142550 | East Sreemangal, Lalbug R/A, Late Gopendro Chondro Dev | 2019-08-04 | NQ1007 | 10.6 | 525 | 10.6 | 526 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6168 | 2591.9997 | 111.6867
MBZ-2.RR.241.1 | 24182659142553 | East Sreemangal, Lalbug R/A, Babul Roy | 2019-08-04 | NQ1007 | 6.7 | 527 | 6.7 | 528 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6168 | 2591.9997 | 70.5944
MBZ-2.RR.242.1 | 24182659142553 | East Sreemangal, Lalbug R/A, Nepal Sarkar | 2019-08-04 | NQ1007 | 10.3 | 529 | 10.3 | 530 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6168 | 2591.9997 | 108.5258
MBZ-2.RR.243.1 | 24182829142480 | Sreemangal, Lalbug R/A, Rojot Kanti Suttro dhor | 2019-08-04 | NQ1007 | 11.4 | 533 | 11.4 | 534 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6168 | 2591.9997 | 120.1159
MBZ-2.RR.244.1 | 24182449142472 | East Sreemangal, Lalbug R/A, Mohibur Rahman | 2019-08-04 | NQ1007 | 10.5 | 535 | 10.5 | 536 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6168 | 2591.9997 | 110.6331
MBZ-2.RR.245.1 | 24182999142467 | East Sreemangal, Lalbug R/A, Compok Kanti Pal | 2019-08-04 | NQ1007 | 11.5 | 539 | 11.5 | 540 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6168 | 2591.9997 | 121.1695
MBZ-2.RR.246.1 | 24183239142522 | East Sreemangal, Sobujbg R/A, Sree Mhindro Kumar Dash | 2019-08-04 | NQ1007 | 12.8 | 541 | 12.8 | 542 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6168 | 2591.9997 | 134.867
MBZ-2.RR.247.1 | 24183239142522 | East Sreemangal, Sobujbg R/A, Robindro Suttoro dhor | 2019-08-04 | NQ1007 | 3.7 | 545 | 3.7 | 546 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6168 | 2591.9997 | 38.985
MBZ-2.RR.248.1 | 24183189144124 | Sreemangal, Bhanugach Road, Shyamoli R/A, H # 09, R-B-F-L Chowdhury Villa | 2019-08-05 | LX1011 | 11.4 | 571 | 11.4 | 572 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6144 | 2615.9997 | 120.1159
MBZ-2.RR.251.1 | 24185639144036 | Sreemangal, Moulovibazar Road, Ruposhpur, Chuni Lal Bonik | 2019-07-29 | NQ1007 | 11.5 | 374 | 11.5 | 375 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6240 | 2519.9997 | 121.1695
MBZ-2.RR.252.1 | 24185479144030 | Sreemangal, Ruposhpur, Baridhara R/A, Block- Padma, H # 16 | 2019-07-29 | NQ1007 | 7 | 376 | 7 | 377 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6240 | 2519.9997 | 73.7554
MBZ-2.RR.253.1 | 24185539144002 | Sreemangal, Ruposhpur, Baridhara R/A, Block- Padma, H # 18, Boshir Monjil | 2019-07-29 | NQ1007 | 10.5 | 380 | 10.5 | 381 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6240 | 2519.9997 | 110.6331
MBZ-2.RR.254.1 | 24185539144002 | Sreemangal, Ruposhpur, Baridhara R/A, Block- Padma, M R Masud Monjil | 2019-07-29 | NQ1007 | 9.4 | 382 | 9.4 | 383 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6240 | 2519.9997 | 99.0429
MBZ-2.RR.255.1 | 24184209143531 | Sreemangal, R K Mission Road, Opposite of Sree Sree Radhanath Bhaban, Juned & Brothers House | 2019-07-29 | NQ1007 | 9.8 | 384 | 9.9 | 385 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6216 | 2543.9997 | 104.3112
MBZ-2.RR.256.1 | 24185679143471 | Sreemangal, North Ruposhpur, Cathlic Mission Road, Rajendra Kuthir | 2019-07-31 | NQ1007 | 4.9 | 432 | 4.9 | 433 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6240 | 2519.9997 | 51.6288
MBZ-2.RR.257.1 | 24185679143471 | Sreemangal, North Ruposhpur, Cathlic Mission Road, Shadhon Kumar Dash | 2019-07-31 | NQ1007 | 10.5 | 434 | 10 | 435 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6240 | 2519.9997 | 105.3648
MBZ-2.RR.258.1 | 24185959143475 | Sreemangal, North Ruposhpur, Cathlic Mission Road, Bishambor Debnath | 2019-07-31 | NQ1007 | 3 | 436 | 3 | 437 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6240 | 2519.9997 | 31.6094
MBZ-2.RR.259.1 | 24185919143440 | Sreemangal, North Ruposhpur, Cathlic Mission Road, Orwn Boiddo | 2019-07-31 | NQ1007 | 4 | 438 | 4.1 | 439 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6240 | 2519.9997 | 43.1996
MBZ-2.RR.260.1 | 24185919143440 | Sreemangal, North Ruposhpur, Cathlic Mission Road, Gourango Chandra | 2019-07-31 | NQ1007 | 3.2 | 441 | 3.2 | 442 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6240 | 2519.9997 | 33.7167
MBZ-2.RR.261.1 | 24184239143468 | Sreemangal, R K Mission Road, LP School Sarak, Iqbal Nibash | 2019-07-31 | NQ1007 | 10.4 | 443 | 10.6 | 444 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6216 | 2543.9997 | 111.6867
MBZ-2.RR.262.1 | 24184289143454 | Sreemangal, R K Mission Road, LP School Sarak, Bodrun Villa | 2019-07-31 | NQ1007 | 6.4 | 445 | 6.4 | 446 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6216 | 2543.9997 | 67.4335
MBZ-2.RR.263.1 | 24184289143454 | Sreemangal, R K Mission Road, LP School Sarak, Momota | 2019-07-31 | NQ1007 | 3 | 447 | 3 | 448 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6216 | 2543.9997 | 31.6094
MBZ-2.RR.264.1 | 24185039143437 | Sreemangal, Bangobir Road, Shah Jaman | 2019-07-31 | NQ1007 | 3.1 | 449 | 3.1 | 450 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6240 | 2519.9997 | 32.6631
MBZ-2.RR.265.1 | 24185039143437 | Sreemangal, Bangobir Road, Shah Jaman | 2019-07-31 | NQ1007 | 3.6 | 451 | 3.6 | 452 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6240 | 2519.9997 | 37.9313
MBZ-2.RR.266.1 | 24185119143442 | Sreemangal, Bangobir Road, Alhaz Mohammad Abdur Rahim | 2019-07-31 | NQ1007 | 7.3 | 453 | 7.3 | 454 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6240 | 2519.9997 | 76.9163
MBZ-2.RR.267.1 | 24184319143440 | Sreemangal, RK Mission Road, LP School Sarak, Basith & Bela | 2019-08-01 | NQ1007 | 4.2 | 469 | 4.2 | 470 | 2022-01-01 | [9 empty] | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0
MBZ-2.RR.268.1 | 24185159143466 | Sreemangal, Bangobir Road, Johura Monjil | 2019-08-01 | NQ1007 | 9.9 | 471 | 10 | 472 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6240 | 2519.9997 | 105.3648
MBZ-2.RR.269.1 | 24185159143466 | Sreemangal, Bangobir Road, Johura Monjil | 2019-08-01 | NQ1007 | 11.5 | 473 | 11.5 | 474 | 2022-01-01 | 2022-09-18 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6240 | 2519.9997 | 121.1695
MBZ-2.RR.271.1 | 24182279143224 | Sreemangal, Deb Bari Road, Prodip Deb Jhoton | 2019-08-01 | NQ1007 | 10.2 | 477 | 10.2 | 478 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6168 | 2591.9997 | 107.4721
MBZ-2.RR.272.1 | 24182259143211 | Sreemangal, Deb Bari Road, Mohammad Mokhlesur Rahman | 2019-08-01 | NQ1007 | 5.6 | 479 | 5.6 | 480 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6168 | 2591.9997 | 59.0043
MBZ-2.RR.273.1 | 24182279143174 | Sreemangal, Deb Bari Road, Saint Martha's High School | 2019-08-01 | NQ1007 | 9.5 | 481 | 9.1 | 482 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6168 | 2591.9997 | 95.882
MBZ-2.RR.274.1 | 24182349143145 | Sreemangal, Deb Bari Road, Suchetona Kuthir | 2019-08-01 | NQ1007 | 14.8 | 483 | 15.3 | 484 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6168 | 2591.9997 | 161.2082
MBZ-2.RR.275.1 | 24181929143042 | East Sreemangal, Lalbag Road, Salek Mia | 2019-08-03 | NQ1007 | 11.3 | 507 | 11.3 | 508 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6168 | 2591.9997 | 119.0622
MBZ-2.RR.276.1 | 24181809143031 | East Sreemangal, Lalbag Road, Rubel Mia | 2019-08-03 | NQ1007 | 3.4 | 509 | 3.4 | 510 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6168 | 2591.9997 | 35.824
MBZ-2.RR.277.1 | 24181989143030 | East Sreemangal, Lalbag Road, Ibrahim Mia | 2019-08-03 | NQ1007 | 12.7 | 511 | 12.7 | 512 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6168 | 2591.9997 | 133.8133
MBZ-2.RR.278.1 | 24182059143033 | East Sreemangal, Lalbag Road, Pronob Debnath | 2019-08-03 | NQ1007 | 14.3 | 513 | 14.3 | 514 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 6168 | 2591.9997 | 150.6717
MBZ-2.RR.279.1 | 24182059143033 | East Sreemangal, Lalbag Road, Khodeja Begum | 2019-08-03 | NQ1007 | 8.6 | 515 | 8.6 | 516 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 3672 | 0 | 2496 | 2591.9997 | 52.6304
MBZ-2.RR.280.1 | 24182219143055 | East Sreemangal, Beside of Upojela Chairman Bari, Onjon Kumar Deb | 2019-08-03 | NQ1007 | 4.5 | 517 | 4.5 | 518 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6168 | 2591.9997 | 47.4142
MBZ-2.RR.281.1 | 24182419143071 | East Sreemangal, Beside of Upojela Chairman Bari, Durga Dash Acharja | 2019-08-03 | NQ1007 | 4.6 | 519 | 4.6 | 520 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6168 | 2591.9997 | 48.4678
MBZ-2.RR.282.1 | 24182879142438 | Sreemangal, Lalbag R/A, Hazi Baharam House | 2019-08-04 | NQ1007 | 3.8 | 547 | 3.8 | 548 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6168 | 2591.9997 | 40.0386
MBZ-2.RR.283.1 | 24182679142404 | Sreemangal, Lalbag, Hafsa Mia | 2019-08-04 | NQ1007 | 5.4 | 549 | 5.4 | 550 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6168 | 2591.9997 | 56.897
MBZ-2.RR.284.1 | 24183649144035 | Sreemangal, Guho Road, Junayed Ahmed Chowdhury | 2019-08-04 | NQ1007 | 10.3 | 551 | 10.3 | 552 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6216 | 2543.9997 | 108.5258
MBZ-2.RR.285.1 | 24183039144248 | Sreemangal, Purbasha R/A, Badsha Mia | 2019-08-05 | NQ1007 | 13.7 | 553 | 13.7 | 554 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6144 | 2615.9997 | 144.3498
MBZ-2.RR.286.1 | 24182969144236 | Sreemangal, Purbasha R/A, Raju | 2019-08-05 | NQ1007 | 14.4 | 555 | 14.4 | 556 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6144 | 2615.9997 | 151.7253
MBZ-2.RR.287.1 | 24183149144264 | Sreemangal, Purbasha R/A, Prodip Kumar Baroi | 2019-08-05 | NQ1007 | 12.4 | 557 | 12.4 | 558 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6144 | 2615.9997 | 130.6524
MBZ-2.RR.288.1 | 24183019144263 | Sreemangal, Purbasha R/A, Manik Rikasho | 2019-08-05 | NQ1007 | 2.9 | 559 | 2.9 | 560 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6144 | 2615.9997 | 30.5558
MBZ-2.RR.289.1 | 24183269144337 | Sreemangal, Purbasha R/A, Taher Mia | 2019-08-05 | NQ1007 | 38 | 561 | 38 | 562 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 38 | 38 | 2.28 | 2.28 | 0.0007168 | 100% | 0% | 2.28 | 2.28 | 0.0011869 | 28 | 0.045706 | 0.045706 |  | 0 | 0 | 6144 | 2615.9997 | 400.3863
MBZ-2.RR.290.1 | 24183039144328 | Sreemangal, Purbasha R/A, Shebu Ghosh | 2019-08-05 | NQ1007 | 7.1 | 563 | 7.1 | 564 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6144 | 2615.9997 | 74.809
MBZ-2.RR.291.1 | 24183039144328 | Sreemangal, Purbasha R/A, Shajahan | 2019-08-05 | NQ1007 | 13.8 | 565 | 13.4 | 566 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6144 | 2615.9997 | 141.1888
MBZ-2.RR.292.1 | 24182919144354 | Sreemangal, Purbasha R/A, Professor Nirependralal Dash | 2019-08-05 | NQ1007 | 12.5 | 567 | 12.6 | 568 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6144 | 2615.9997 | 132.7597
MBZ-2.RR.301.1 | 24185839144192 | Sremongol, Surova R/A, Sattar Mia | 2019-07-30 | MP1032 | 9.2 | 445 | 9.3 | 446 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6096 | 2663.9997 | 97.9893
MBZ-2.RR.302.1 | 24185699144195 | Sremongol, Surova R/A, Rob Mia | 2019-07-30 | MP1032 | 6.1 | 447 | 6.1 | 448 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6096 | 2663.9997 | 64.2725
MBZ-2.RR.303.1 | 24185609144203 | Sremongol, Surova R/A, Delara Khatun | 2019-07-30 | MP1032 | 3.6 | 449 | 3.6 | 450 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6096 | 2663.9997 | 37.9313
MBZ-2.RR.304.1 | 24185479144197 | Sremongol, Surova R/A, Momin Mia | 2019-07-30 | MP1032 | 6.7 | 451 | 6.7 | 452 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6096 | 2663.9997 | 70.5944
MBZ-2.RR.305.1 | 24185409144177 | Sremongol, Boshundhora R/A, 10,Tarek Iekbal | 2019-07-31 | MP1032 | 3.7 | 453 | 3.7 | 454 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6096 | 2663.9997 | 38.985
MBZ-2.RR.306.1 | 24185409144177 | Sremongol, Boshundhora R/A, 10,Tarek Iekbal | 2019-07-31 | MP1032 | 1.5 | 455 | 1.5 | 456 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6096 | 2663.9997 | 15.8047
MBZ-2.RR.307.1 | 24185409144177 | Sremongol, Boshundhora R/A, 10,Tarek Iekbal | 2019-07-31 | MP1032 | 11 | 457 | 11 | 458 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6096 | 2663.9997 | 115.9013
MBZ-2.RR.308.1 | 24185929144137 | Sremongol, Surove R/A, Syed Mostakim Ali | 2019-07-31 | MP1032 | 6 | 459 | 6 | 460 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6096 | 2663.9997 | 63.2189
MBZ-2.RR.309.1 | 24185589144128 | Sremongol, Berampur, Nurul Haque | 2019-07-31 | MP1032 | 11.3 | 461 | 11.3 | 462 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6096 | 2663.9997 | 119.0622
MBZ-2.RR.310.1 | 24185439144093 | Sremongol, Purbo Ruposhpur, Md. Israfil | 2019-07-31 | MP1032 | 3.4 | 463 | 3.4 | 464 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6096 | 2663.9997 | 35.824
MBZ-2.RR.311.1 | 24185439144092 | Sremongol, Purbo Ruposhpur, Md. Israfil | 2019-07-31 | MP1032 | 5.1 | 465 | 5.1 | 466 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6096 | 2663.9997 | 53.7361
MBZ-2.RR.312.1 | 24185329144092 | Sremongol, Purbo Ruposhpur, Abdul Khaleq | 2019-07-31 | MP1032 | 11.5 | 467 | 11.5 | 468 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6096 | 2663.9997 | 121.1695
MBZ-2.RR.313.1 | 24185119144115 | Sremongol, Poschim Berampur, Hamid Member House | 2019-07-31 | MP1032 | 18.5 | 469 | 18.6 | 470 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 6096 | 2663.9997 | 195.9786
MBZ-2.RR.313.2 | 24185119144115 | Sremongol, Poschim Berampur, Hamid Member House | 2022-03-09 | NQ1007 | 1.4 | 42 | 1.4 | 43 | 2022-03-09 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 4488 | 2663.9997 | 12.0433
MBZ-2.RR.314.1 | 24185109144157 | Sremongol, Poschim Berampur, Nurane R/A, Soukot Mia | 2019-07-31 | MP1032 | 12.3 | 471 | 12.3 | 472 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6096 | 2663.9997 | 129.5987
MBZ-2.RR.315.1 | 24185109144157 | Sremongol, Poschim Berampur, Nurane R/A, Soukot Mia | 2019-07-31 | MP1032 | 4.8 | 475 | 4.8 | 476 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6096 | 2663.9997 | 50.5751
MBZ-2.RR.316.1 | 24182549143350 | Sreemangal, Sahebag R/A, Nosorullah Rood, Block - A, H # 5, Moshbbir Ali | 2019-08-01 | MP1032 | 10.8 | 498 | 11 | 499 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6216 | 2543.9997 | 115.9013
MBZ-2.RR.317.1 | 24182189143356 | Sreemangal, Sahebag R/A, Nosorullah Rood, Block - A, Md. Abul Kalam | 2019-08-01 | MP1032 | 11.6 | 500 | 11.5 | 501 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6216 | 2543.9997 | 121.1695
MBZ-2.RR.318.1 | 24182179143334 | Sreemangal, Sahebag R/A, Nosorullah Rood, Rahima Bagum | 2019-08-01 | MP1032 | 12.6 | 502 | 12.7 | 503 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6216 | 2543.9997 | 133.8133
MBZ-2.RR.319.1 | 24182229143321 | Sreemangal, Sahebag R/A, Nosorullah Rood, Abdul Barek | 2019-08-01 | MP1032 | 6 | 504 | 6 | 505 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6216 | 2543.9997 | 63.2189
MBZ-2.RR.320.1 | 24181829143294 | Sreemangal, Sahebag R/A, Md. Khorshed Alom | 2019-08-01 | MP1032 | 11.4 | 506 | 11.4 | 507 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6120 | 2639.9997 | 120.1159
MBZ-2.RR.321.1 | 24181749143292 | Sreemangal, Sahebag R/A, Abdul Hannan Mollah | 2019-08-01 | MP1032 | 10.7 | 508 | 10.7 | 509 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6120 | 2639.9997 | 112.7403
MBZ-2.RR.322.1 | 24181769143287 | Sreemangal, Sahebag R/A, Dowan Md. Monirujaman | 2019-08-01 | MP1032 | 11.1 | 510 | 10.6 | 511 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6120 | 2639.9997 | 111.6867
MBZ-2.RR.323.1 | 24181659143280 | Sreemangal, Sahebag R/A, Md. Badsha Mia | 2019-08-01 | MP1032 | 8.8 | 512 | 8.8 | 513 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6120 | 2639.9997 | 92.721
MBZ-2.RR.324.1 | 24181489143269 | Sreemangal, Sahebag R/A, A.S.M. Azadur Rahman( P.P. Moulovebazar) | 2019-08-01 | MP1032 | 10.9 | 514 | 10.9 | 515 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6120 | 2639.9997 | 114.8476
MBZ-2.RR.325.1 | 24181549143315 | Sreemangal, Sahebag R/A, Kajol | 2019-08-01 | MP1032 | 10.2 | 516 | 10.2 | 517 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6120 | 2639.9997 | 107.4721
MBZ-2.RR.326.1 | 24181509143314 | Sreemangal, Sahebag R/A, Billah | 2019-08-01 | MP1032 | 10.2 | 518 | 10.2 | 519 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6120 | 2639.9997 | 107.4721
MBZ-2.RR.327.1 | 24181519143317 | Sreemangal, Sahebag R/A, Kobir Ahmed | 2019-08-01 | MP1032 | 10.1 | 520 | 9.4 | 521 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6120 | 2639.9997 | 99.0429
MBZ-2.RR.328.1 | 24175729142514 | Sreemangal, South Uttorsur, Dokkina Ronjon Pal | 2019-08-03 | MP1032 | 5.9 | 539 | 5.9 | 540 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6168 | 2591.9997 | 62.1652
MBZ-2.RR.329.1 | 24175369142507 | Sreemangal, South Uttorsur, Nirmol Pal | 2019-08-03 | MP1032 | 3 | 541 | 3 | 542 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6168 | 2591.9997 | 31.6094
MBZ-2.RR.330.1 | 24175139142496 | Sreemangal, South Uttorsur, Obonemol Pal | 2019-08-03 | MP1032 | 5.5 | 545 | 5.1 | 546 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6168 | 2591.9997 | 53.7361
MBZ-2.RR.331.1 | 24175139142496 | Sreemangal, South Uttorsur, Onu Pal | 2019-08-03 | MP1032 | 12.6 | 549 | 12.6 | 550 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6168 | 2591.9997 | 132.7597
MBZ-2.RR.332.1 | 24175069142485 | Sreemangal, South Uttorsur, Noyon Ray | 2019-08-03 | MP1032 | 10.7 | 551 | 10.7 | 552 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6168 | 2591.9997 | 112.7403
MBZ-2.RR.333.1 | 24175479142443 | Sreemangal, South Uttorsur, Kartik Vottacharjo | 2019-08-03 | MP1032 | 11.8 | 557 | 11.8 | 558 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6168 | 2591.9997 | 124.3305
MBZ-2.RR.334.1 | 24175479142443 | Sreemangal, South Uttorsur, Kartik Vottacharjo | 2019-08-03 | MP1032 | 10.8 | 559 | 10.1 | 560 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6168 | 2591.9997 | 106.4185
MBZ-2.RR.335.1 | 24175309142406 | Sreemangal, South Uttorsur, Monindro Sukkro Dor | 2019-08-03 | MP1032 | 6 | 563 | 6 | 564 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6168 | 2591.9997 | 63.2189
MBZ-2.RR.336.1 | 24175129142400 | Sreemangal, South Uttorsur, Sudansu Ronjon Das | 2019-08-03 | MP1032 | 12 | 567 | 12 | 568 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6168 | 2591.9997 | 126.4378
MBZ-2.RR.337.1 | 24175059142403 | Sreemangal, South Uttorsur, Sudansu Roy | 2019-08-03 | MP1032 | 22.8 | 569 | 22.9 | 570 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 22.9 | 22.9 | 1.374 | 1.374 | 0.0007168 | 100% | 0% | 1.374 | 1.374 | 0.0011869 | 28 | 0.027544 | 0.027544 |  | 0 | 0 | 6168 | 2591.9997 | 241.2854
MBZ-2.RR.338.1 | 24175869142242 | Sreemangal, South Uttorsur, Shamol Das | 2019-08-04 | MP1032 | 12.1 | 589 | 12.1 | 590 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6168 | 2591.9997 | 127.4914
MBZ-2.RR.339.1 | 24175789142239 | Sreemangal, South Uttorsur, Jontu | 2019-08-04 | MP1032 | 12.2 | 591 | 12.2 | 592 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6168 | 2591.9997 | 128.5451
MBZ-2.RR.340.1 | 24175789142239 | Sreemangal, South Uttorsur, Alauddin | 2019-08-04 | MP1032 | 11.8 | 593 | 11.8 | 594 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6168 | 2591.9997 | 124.3305
MBZ-2.RR.341.1 | 24190129144144 | Sreemangal, Shorove Para R/A, Rd # A, Ner Anjon Bonik | 2019-07-31 | MP1032 | 2.2 | 477 | 2.2 | 478 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6096 | 2663.9997 | 23.1803
MBZ-2.RR.342.1 | 24185969144096 | Sreemangal, Shorove Para R/A, Rd # A, Humaion Kabir | 2019-07-31 | MP1032 | 5.8 | 479 | 5.8 | 480 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6096 | 2663.9997 | 61.1116
MBZ-2.RR.343.1 | 24185969144096 | Sreemangal, Shorove Para R/A, Rd # A, Shalem Ahmed | 2019-07-31 | MP1032 | 3.9 | 483 | 3.7 | 484 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6096 | 2663.9997 | 38.985
MBZ-2.RR.344.1 | 24185969144096 | Sreemangal, Shorove Para R/A, Rd # A, H # 25 | 2019-07-31 | MP1032 | 11 | 486 | 11 | 487 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6096 | 2663.9997 | 115.9013
MBZ-2.RR.345.1 | 24190289144100 | Sreemangal, Shorove Para R/A, H # 8 | 2019-07-31 | MP1032 | 3.5 | 488 | 3.5 | 489 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6096 | 2663.9997 | 36.8777
MBZ-2.RR.346.1 | 24190289144100 | Sreemangal, Shorove Para R/A, H # 8 | 2019-07-31 | MP1032 | 5.6 | 490 | 5.6 | 491 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6096 | 2663.9997 | 59.0043
MBZ-2.RR.347.1 | 24190289144100 | Sreemangal, Shorove Para R/A, H # 8 | 2019-07-31 | MP1032 | 23.7 | 492 | 23.7 | 493 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 23.7 | 23.7 | 1.422 | 1.422 | 0.0007168 | 100% | 0% | 1.422 | 1.422 | 0.0011869 | 28 | 0.028506 | 0.028506 |  | 0 | 0 | 6096 | 2663.9997 | 249.7146
MBZ-2.RR.348.1 | 24182919143424 | Sreemangal, Shantibag R/A, Shagordighi Road, Block # F, H # 70, Nurnobi Monzil | 2019-07-31 | MP1032 | 9.8 | 494 | 9.9 | 495 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6144 | 2615.9997 | 104.3112
MBZ-2.RR.349.1 | 24182919143424 | Sreemangal, Shantibag R/A, Shagordighi Road, Block # F, H # 70, Nurnobi Monzil | 2019-07-31 | MP1032 | 10.1 | 496 | 10.5 | 497 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6144 | 2615.9997 | 110.6331
MBZ-2.RR.350.1 | 24182059143364 | Sreemangal, Shahebug, Nosorullah Road, Meju Alom | 2019-08-01 | MP1032 | 8 | 523 | 8 | 524 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6216 | 2543.9997 | 84.2919
MBZ-2.RR.351.1 | 24181819143363 | Sreemangal, Shahebug, Nosorullah Road, Mohebul Haque | 2019-08-01 | MP1032 | 4.8 | 525 | 4.8 | 526 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6216 | 2543.9997 | 50.5751
MBZ-2.RR.352.1 | 24181969143390 | Sreemangal, Shahebug, Nosorullah Road, Hazi Md. Toslim Mia | 2019-08-01 | MP1032 | 3.6 | 527 | 3.6 | 528 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6216 | 2543.9997 | 37.9313
MBZ-2.RR.353.1 | 24182159143389 | Sreemangal, Shahebug, Nosorullah Road, Mubarokullah | 2019-08-01 | MP1032 | 11.8 | 529 | 11.8 | 530 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6216 | 2543.9997 | 124.3305
MBZ-2.RR.354.1 | 24182119143389 | Sreemangal, Shahebug, Nosorullah Road, Mashuk | 2019-08-01 | MP1032 | 29.1 | 531 | 29.1 | 532 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 29.1 | 29.1 | 1.746 | 1.746 | 0.0007168 | 100% | 0% | 1.746 | 1.746 | 0.0011869 | 28 | 0.035001 | 0.035001 |  | 0 | 0 | 6216 | 2543.9997 | 306.6116
MBZ-2.RR.355.1 | 24180669142594 | Sreemangal, Habigong Road, Boktiruddin Ahmed | 2019-08-01 | MP1032 | 6.8 | 533 | 6.8 | 534 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6168 | 2591.9997 | 71.6481
MBZ-2.RR.356.1 | 24180639142571 | Sreemangal, Habigong Road, Mokbul Hosen | 2019-08-01 | MP1032 | 10.8 | 535 | 10.8 | 536 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6168 | 2591.9997 | 113.794
MBZ-2.RR.357.1 | 24181749142511 | Sreemangal, Uttor Uttor Shor, Gorda Dheger Par, MD. Bassu Mia | 2019-08-03 | MP1032 | 34 | 571 | 34 | 572 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 34 | 34 | 2.04 | 2.04 | 0.0007168 | 100% | 0% | 2.04 | 2.04 | 0.0011869 | 28 | 0.040895 | 0.040895 |  | 0 | 0 | 6168 | 2591.9997 | 358.2404
MBZ-2.RR.358.1 | 24181749142511 | Sreemangal, Uttor Uttor Shor, Gorda Dheger Par, Hazi Sajad | 2019-08-03 | MP1032 | 4.9 | 573 | 4.9 | 574 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6168 | 2591.9997 | 51.6288
MBZ-2.RR.359.1 | 24181589142506 | Sreemangal, Uttor Uttor Shor, Gorda Dheger Par, Rony Pal | 2019-08-03 | MP1032 | 60.5 | 575 | 60.5 | 576 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 60.5 | 60.5 | 3.63 | 3.63 | 0.0007168 | 100% | 0% | 3.63 | 3.63 | 0.0011869 | 28 | 0.072769 | 0.072769 |  | 0 | 0 | 6168 | 2591.9997 | 637.4571
MBZ-2.RR.360.1 | 24181389142474 | Sreemangal, Uttor Uttor Shor, Sudansu Dhar | 2019-08-03 | MP1032 | 9.5 | 577 | 9.5 | 578 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6168 | 2591.9997 | 100.0966
MBZ-2.RR.361.1 | 24181389142474 | Sreemangal, Uttor Uttor Shor, Sudansu Dhar | 2019-08-03 | MP1032 | 11 | 579 | 10.8 | 580 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6168 | 2591.9997 | 113.794
MBZ-2.RR.362.1 | 24181389142474 | Sreemangal, Uttor Uttor Shor, Sudansu Dhar | 2019-08-03 | MP1032 | 23.2 | 581 | 23.2 | 582 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 23.2 | 23.2 | 1.392 | 1.392 | 0.0007168 | 100% | 0% | 1.392 | 1.392 | 0.0011869 | 28 | 0.027905 | 0.027905 |  | 0 | 0 | 6168 | 2591.9997 | 244.4464
MBZ-2.RR.363.1 | 24180799142349 | Sreemangal, Uttor Uttor Shor R/A, Raza Mia | 2019-08-03 | MP1032 | 18.5 | 583 | 18.5 | 584 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6168 | 2591.9997 | 194.9249
MBZ-2.RR.363.2 | 24180799142349 | Sreemangal, Uttor Uttor Shor R/A, Raza Mia | 2021-09-19 | MN1018 | 6.6 | 31 | 6.6 | 32 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6168 | 2591.9997 | 69.5408
MBZ-2.RR.364.1 | 24181389142393 | Sreemangal, Uttor Uttor Shor R/A, Gitu Mohon Baidya | 2019-08-03 | MP1032 | 8.5 | 585 | 8.6 | 586 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6168 | 2591.9997 | 90.6137
MBZ-2.RR.365.1 | 24184529144382 | Sreemangal, East Birampur, Shofikur Rahaman | 2019-08-05 | MP1032 | 12.4 | 625 | 12.3 | 626 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6144 | 2615.9997 | 129.5987
MBZ-2.RR.381.1 | 24192389144151 | Srimangal, South Varaura, 3 No Union, Ward # 3, Moin Ullah | 2019-07-29 | NQ1005 | 3.4 | 318 | 3.4 | 319 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6096 | 2663.9997 | 35.824
MBZ-2.RR.382.1 | 24192339144149 | Srimangal, South Varaura, 3 No Union, Ward # 3, Aainullah | 2019-07-29 | NQ1005 | 11.2 | 320 | 10.9 | 321 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6096 | 2663.9997 | 114.8476
MBZ-2.RR.383.1 | 24192339144149 | Srimangal, South Varaura, 3 No Union, Ward # 3, Saifullah | 2019-07-29 | NQ1005 | 11.5 | 322 | 11.5 | 323 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6096 | 2663.9997 | 121.1695
MBZ-2.RR.384.1 | 24192339144149 | Srimangal, South Varaura, 3 No Union, Ward # 3, Enayet Hossen | 2019-07-29 | NQ1005 | 10.6 | 324 | 10.2 | 325 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6096 | 2663.9997 | 107.4721
MBZ-2.RR.385.1 | 24192409144166 | Srimangal, South Varaura, 3 No Union, Ward # 3, Kawser Mia | 2019-07-29 | NQ1005 | 6.1 | 326 | 6.1 | 327 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6096 | 2663.9997 | 64.2725
MBZ-2.RR.386.1 | 24192409144166 | Srimangal, South Varaura, 3 No Union, Ward # 3, Shamshu Mia | 2019-07-29 | NQ1005 | 4.2 | 328 | 4.2 | 329 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6096 | 2663.9997 | 44.2532
MBZ-2.RR.387.1 | 24191609144096 | Srimangal, Moulovibazar Road, 4 No Pool, Kazi Villa, Kazi Abdul Karim | 2019-07-29 | NQ1005 | 1.5 | 330 | 1.5 | 331 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6096 | 2663.9997 | 15.8047
MBZ-2.RR.388.1 | 24184699143591 | Srimangal, Moulovibazar Road, Ahmed manson | 2019-07-30 | NQ1005 | 11.9 | 358 | 11.9 | 359 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6216 | 2543.9997 | 125.3841
MBZ-2.RR.388.2 | 24184699143591 | Srimangal, Moulovibazar Road, Ahmed manson | 2021-02-03 | LU1001 | 2 | 148 | 2 | 149 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6216 | 2543.9997 | 21.073
MBZ-2.RR.389.1 | 24183239143502 | Srimangal, Hobigonj Road, Puran Bazar Point, Jahangir Alom | 2019-07-30 | NQ1005 | 18.5 | 360 | 18.5 | 361 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6216 | 2543.9997 | 194.9249
MBZ-2.RR.390.1 | 24183009143501 | Srimangal, Hobigonj Road, Puran Bazar Point, Sufia Plaza | 2019-07-30 | NQ1005 | 19.4 | 362 | 19.4 | 363 | 2022-01-01 | 2022-09-17 | GS |  |  | 0 |  |  |  |  | 19.4 | 19.4 | 1.164 | 1.164 | 0.0007168 | 100% | 0% | 1.164 | 1.164 | 0.0011869 | 28 | 0.023334 | 0.023334 |  | 0 | 0 | 6216 | 2543.9997 | 204.4077
MBZ-2.RR.391.1 | 24182309143497 | Srimangal, Shaplabug Abashik Alaka, Notun Bazar, Bodoruddin Talukdar | 2019-07-30 | NQ1005 | 12.5 | 364 | 12.6 | 365 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6144 | 2615.9997 | 132.7597
MBZ-2.RR.392.1 | 24182229143506 | Srimangal, Ward # 7, Shaplabug R/A, Shotto Ronjon Pal | 2019-07-31 | NQ1005 | 12.4 | 366 | 12.4 | 367 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6144 | 2615.9997 | 130.6524
MBZ-2.RR.393.1 | 24182109143484 | Srimangal, Ward # 7, Shaplabug R/A, Bisshownath Dhor | 2019-07-31 | NQ1005 | 5.4 | 368 | 5.4 | 369 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6144 | 2615.9997 | 56.897
MBZ-2.RR.394.1 | 24182079143478 | Srimangal, Ward # 7, Shaplabug R/A, Block-B, H # 31, Ram Krisno Debnath | 2019-07-31 | NQ1005 | 7.1 | 370 | 7.1 | 371 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6144 | 2615.9997 | 74.809
MBZ-2.RR.395.1 | 24182119143459 | Srimangal, Ward # 7, Shantibug R/A, H # 147, Aarju Mia | 2019-07-31 | NQ1005 | 14.4 | 372 | 14.4 | 373 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6144 | 2615.9997 | 151.7253
MBZ-2.RR.396.1 | 24182139143445 | Srimangal, Ward # 7, Shantibug R/A, Nantu Pal | 2019-07-31 | NQ1005 | 12.2 | 374 | 11.8 | 375 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6144 | 2615.9997 | 124.3305
MBZ-2.RR.397.1 | 24182139143445 | Srimangal, Ward # 7, Shantibug R/A, Nantu Pal | 2019-07-31 | NQ1005 | 6.6 | 376 | 6.6 | 377 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6144 | 2615.9997 | 69.5408
MBZ-2.RR.398.1 | 24182159143438 | Srimangal, Ward # 7, Shantibug R/A, Shomsher Uddin | 2019-07-31 | NQ1005 | 3.5 | 379 | 3.5 | 380 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6144 | 2615.9997 | 36.8777
MBZ-2.RR.399.1 | 24182689143400 | Srimangal, Ward # 7, Shantibug R/A, Koborsthan Road, Momin Hossen | 2019-07-31 | NQ1005 | 13.9 | 381 | 13.9 | 382 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6144 | 2615.9997 | 146.4571
MBZ-2.RR.400.1 | 24182209143508 | Srimangal, Ward # 7, Shaplabug R/A, H # 21, Tulshi Chouhan | 2019-07-31 | NQ1005 | 14.9 | 383 | 14.9 | 384 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6144 | 2615.9997 | 156.9936
MBZ-2.RR.400.2 | 24182209143508 | Srimangal, Ward # 7, Shaplabug R/A, H # 21, Tulshi Chouhan | 2021-02-01 | NQ1007 | 11.5 | 126 | 11.5 | 127 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6144 | 2615.9997 | 121.1695
MBZ-2.RR.401.1 | 24182139143509 | Srimangal, Ward # 7, Shaplabug R/A, Golam Mostofa | 2019-07-31 | NQ1005 | 12.2 | 385 | 12.2 | 386 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6144 | 2615.9997 | 128.5451
MBZ-2.RR.402.1 | 24182049143496 | Srimangal, Ward # 7, Shaplabug R/A, Block-C, Renu Kuthir, Moni Lal Rai | 2019-07-31 | NQ1005 | 21.4 | 387 | 21.4 | 388 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 6144 | 2615.9997 | 225.4807
MBZ-2.RR.403.1 | 24181899143537 | Srimangal, Ward # 6, Notun Bazar Railgate, Shaplabug R/A, H # 0370-00, Muhibur Rahman | 2019-07-31 | NQ1005 | 96.3 | 389 | 96.3 | 390 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 96.3 | 96.3 | 5.778 | 5.778 | 0.0007168 | 100% | 0% | 5.778 | 5.778 | 0.0011869 | 28 | 0.11583 | 0.11583 |  | 0 | 0 | 6144 | 2615.9997 | 1014.6631
MBZ-2.RR.404.1 | 24180579143504 | Srimangal, Khasgaon, Nabodhara R/A, MD.S.I. House, Sirajul Islam | 2019-08-01 | NQ1005 | 4.1 | 403 | 4.1 | 404 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6120 | 2639.9997 | 43.1996
MBZ-2.RR.405.1 | 24180059143505 | Srimangal, Khasgaon, Nabodhara R/A, Khasgaon Schoo, Road, Nur Islam | 2019-08-01 | NQ1005 | 10 | 405 | 10 | 406 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6144 | 2615.9997 | 105.3648
MBZ-2.RR.406.1 | 24175889143470 | Srimangal, Khasgaon, Sungoir School Back Side Road, Near Sungoir School, Shipon | 2019-08-01 | NQ1005 | 11.6 | 407 | 11.6 | 408 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6120 | 2639.9997 | 122.2232
MBZ-2.RR.407.1 | 24175439143456 | Srimangal, Khasgaon, Sungoir School Back Side Road, Harun-ur-Rashid | 2019-08-01 | NQ1005 | 16.8 | 409 | 16.8 | 410 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6120 | 2639.9997 | 177.0129
MBZ-2.RR.408.1 | 24175399143455 | Srimangal, Khasgaon, Sungoir School Back Side Road, Wahid Shakil Mia | 2019-08-01 | NQ1005 | 15.1 | 411 | 15.1 | 412 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6120 | 2639.9997 | 159.1009
MBZ-2.RR.409.1 | 24175389143457 | Srimangal, Khasgaon, Sungoir School Back Side Road, Mubarok Hossen | 2019-08-01 | NQ1005 | 18.5 | 413 | 18.5 | 414 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6120 | 2639.9997 | 194.9249
MBZ-2.RR.410.1 | 24175319143452 | Srimangal, Khasgaon, Sungoir, Dewan Monjil | 2019-08-01 | NQ1005 | 11.1 | 415 | 11.1 | 416 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6120 | 2639.9997 | 116.9549
MBZ-2.RR.411.1 | 24174939143397 | Srimangal, Ramnagar, South Muslimbug Road, Abdur Shakur | 2019-08-01 | NQ1005 | 14.6 | 417 | 14.6 | 418 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6120 | 2639.9997 | 153.8326
MBZ-2.RR.412.1 | 24174879143404 | Srimangal, Ramnagar, South Muslimbug Road, Dolal Mia | 2019-08-01 | NQ1005 | 12.5 | 419 | 12.5 | 420 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6120 | 2639.9997 | 131.706
MBZ-2.RR.413.1 | 24174809143398 | Srimangal, Ramnagar, South Muslimbug Road, Abdur Hamid | 2019-08-01 | NQ1005 | 12.5 | 421 | 12.6 | 422 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6120 | 2639.9997 | 132.7597
MBZ-2.RR.414.1 | 24174849143420 | Srimangal, Ramnagar, South Muslimbug Road, Chentu Mia | 2019-08-01 | NQ1005 | 3.3 | 423 | 3.3 | 424 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6120 | 2639.9997 | 34.7704
MBZ-2.RR.415.1 | 24180119143569 | Srimangal, Muslimbug R/A, Ward # 4, Road # 2, Lokman Sheikh | 2019-08-03 | NQ1005 | 10.9 | 453 | 10.4 | 454 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6144 | 2615.9997 | 109.5794
MBZ-2.RR.416.1 | 24180129143560 | Srimangal, Muslimbug R/A, Ward # 4, Road # 2, Alom Sheikh | 2019-08-03 | NQ1005 | 2.5 | 455 | 2.5 | 456 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6144 | 2615.9997 | 26.3412
MBZ-2.RR.417.1 | 24174829143525 | Srimangal, Muslimbug R/A, Ward # 4, Road # 2, Shajahan Mia | 2019-08-03 | NQ1005 | 2.5 | 460 | 2.5 | 461 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6120 | 2639.9997 | 26.3412
MBZ-2.RR.418.1 | 24174359143535 | Srimangal, Ramnagar, South Muslimbug R/A, Jabed Square, Shoaib Ali | 2019-08-03 | NQ1005 | 12.8 | 462 | 12.8 | 463 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6120 | 2639.9997 | 134.867
MBZ-2.RR.419.1 | 24174239143518 | Srimangal, Ramnagar, South Muslimbug R/A, Ward # 4, Al-Modina Mosjid Road, Moin Uddin | 2019-08-03 | NQ1005 | 9.1 | 464 | 9.1 | 465 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6120 | 2639.9997 | 95.882
MBZ-2.RR.420.1 | 24173889143507 | Srimangal, Ramnagar, South Muslimbug R/A, Ward # 4, Al-Modina Mosjid Road, Aamir hossain | 2019-08-03 | NQ1005 | 18.1 | 466 | 18.1 | 467 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 6120 | 2639.9997 | 190.7103
MBZ-2.RR.421.1 | 24174399143497 | Srimangal, Ramnagar, South Muslimbug R/A, Ward # 4, Gungpar, Rasel Sumon | 2019-08-03 | NQ1005 | 13.2 | 468 | 12.7 | 469 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6120 | 2639.9997 | 133.8133
MBZ-2.RR.422.1 | 24174389143490 | Srimangal, Ramnagar, South Muslimbug R/A, Ward # 4, Gungpar, Kabir Hossen | 2019-08-03 | NQ1005 | 1.8 | 470 | 1.8 | 471 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6120 | 2639.9997 | 18.9657
MBZ-2.RR.423.1 | 24174389143490 | Srimangal, Ramnagar, South Muslimbug R/A, Ward # 4, Gungpar, Md Abu Mia | 2019-08-03 | NQ1005 | 17.3 | 472 | 17.3 | 473 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 6120 | 2639.9997 | 182.2811
MBZ-2.RR.423.2 | 24174389143490 | Srimangal, Ramnagar, South Muslimbug R/A, Ward # 4, Gungpar, Md Abu Mia | 2021-09-21 | MN1018 | 15.6 | 43 | 15.6 | 44 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6120 | 2639.9997 | 164.3691
MBZ-2.RR.424.1 | 24174579143477 | Srimangal, Ramnagar, South Muslimbug R/A, Ward # 4, Gungpar, Abdul Rashid | 2019-08-03 | NQ1005 | 4.9 | 474 | 4.9 | 475 | 2022-01-01 | [9 empty] | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0
MBZ-2.RR.425.1 | 24181199144034 | Srimangal, Ward # 3, South Jalalia Road, Mojibur Rahman | 2019-08-04 | NQ1005 | 13.6 | 498 | 13.6 | 499 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6144 | 2615.9997 | 143.2961
MBZ-2.RR.426.1 | 24181429144082 | Srimangal, Ward # 3, South Jalalia Road, Robin | 2019-08-04 | NQ1005 | 12.2 | 500 | 11.9 | 501 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6144 | 2615.9997 | 125.3841
MBZ-2.RR.427.1 | 24181489144093 | Srimangal, Ward # 3, South Jalalia Road, Sraboni Cottege, Ashraf Ali | 2019-08-04 | NQ1005 | 12.9 | 502 | 12.9 | 503 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6144 | 2615.9997 | 135.9206
MBZ-2.RR.428.1 | 24181499144151 | Srimangal, Ward # 3, South Jalalia Road, H # 11, Shahinur Rahman | 2019-08-04 | NQ1005 | 18.7 | 504 | 18.5 | 505 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 6144 | 2615.9997 | 194.9249
MBZ-2.RR.429.1 | 24181949144145 | Srimangal, Ward # 3, Jalalia Road, Ashokaloi, Ashim Saha | 2019-08-04 | NQ1005 | 60.8 | 506 | 60.8 | 507 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 60.8 | 60.8 | 3.648 | 3.648 | 0.0007168 | 100% | 0% | 3.648 | 3.648 | 0.0011869 | 28 | 0.07313 | 0.07313 |  | 0 | 0 | 6144 | 2615.9997 | 640.6181
MBZ-2.RR.430.1 | 24181679144094 | Srimangal, Ward # 3, Jalalia Road, Ekbal Khan | 2019-08-04 | NQ1005 | 13.1 | 510 | 13.1 | 511 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6144 | 2615.9997 | 138.0279
MBZ-2.RR.431.1 | 24181599144070 | Srimangal, Ward # 3, Jalalia Road, Somael Uddin | 2019-08-04 | NQ1005 | 15.2 | 512 | 15.2 | 513 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6144 | 2615.9997 | 160.1545
MBZ-2.RR.432.1 | 24181669144065 | Srimangal, Ward # 3, Jalalia Road, Najrul Islam | 2019-08-04 | NQ1005 | 20.4 | 514 | 20.1 | 515 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 20.1 | 20.1 | 1.206 | 1.206 | 0.0007168 | 100% | 0% | 1.206 | 1.206 | 0.0011869 | 28 | 0.024176 | 0.024176 |  | 0 | 0 | 6144 | 2615.9997 | 211.7833
MBZ-2.RR.432.2 | 24181669144065 | Srimangal, Ward # 3, Jalalia Road, Najrul Islam | 2021-02-01 | NQ1007 | 12.3 | 138 | 12.3 | 139 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6144 | 2615.9997 | 129.5987
MBZ-2.RR.433.1 | 24181449144018 | Srimangal, Ward # 3, Jalalia Road, Near Soronika Digital Studio, ujjal Kanon | 2019-08-04 | NQ1005 | 12.5 | 516 | 12.5 | 517 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6144 | 2615.9997 | 131.706
MBZ-2.RR.434.1 | 24184059144275 | Srimangal, Beraimpur R/A, College Road, Road # 7, H # 3, Syed Abdus Samad | 2019-08-05 | NQ1005 | 9.8 | 548 | 9.8 | 549 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6144 | 2615.9997 | 103.2575
MBZ-2.RR.435.1 | 24184679144327 | Srimangal, Beraimpur R/A, Road # 7, H # 15, Azizur Rahman | 2019-08-05 | NQ1005 | 6.5 | 550 | 6.5 | 551 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6144 | 2615.9997 | 68.4871
MBZ-2.RR.435.2 | 24184679144327 | Srimangal, Beraimpur R/A, Road # 7, H # 15, Azizur Rahman | 2021-02-02 | LU1001 | 2.8 | 136 | 2.6 | 137 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6144 | 2615.9997 | 27.3949
MBZ-2.RR.451.1 | 24173349144217 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Hironmoy Shingho | 2019-08-03 | NQ1005 | 9.8 | 478 | 9.8 | 479 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6120 | 2639.9997 | 103.2575
MBZ-2.RR.451.2 | 24173349144217 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Hironmoy Shingho | 2022-09-13 | MN1018 | 7.9 | 5 | 7.9 | 6 | 2022-09-13 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 0 | 2639.9997 | 25.0855
MBZ-2.RR.452.1 | 24173499144211 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Dipok Shingho | 2019-08-03 | NQ1005 | 16.1 | 480 | 16.1 | 481 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6120 | 2639.9997 | 169.6373
MBZ-2.RR.453.1 | 24173489144233 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Nirod Ronjjon Bunadi | 2019-08-03 | NQ1005 | 7.3 | 482 | 7.3 | 483 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6120 | 2639.9997 | 76.9163
MBZ-2.RR.454.1 | 24173569144186 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Churamoni Shingho | 2019-08-03 | NQ1005 | 3.7 | 484 | 3.7 | 485 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6120 | 2639.9997 | 38.985
MBZ-2.RR.455.1 | 24173299144159 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Abul Hossen | 2019-08-03 | NQ1005 | 6.2 | 486 | 6.2 | 487 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6120 | 2639.9997 | 65.3262
MBZ-2.RR.456.1 | 24173439144149 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Ismail Uddin | 2019-08-03 | NQ1005 | 8.4 | 488 | 8.4 | 489 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6120 | 2639.9997 | 88.5064
MBZ-2.RR.457.1 | 24173639144111 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Uttom Pal | 2019-08-03 | NQ1005 | 10.6 | 490 | 10.6 | 491 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6120 | 2639.9997 | 111.6867
MBZ-2.RR.458.1 | 24173959144117 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Bishowkatu Showtal | 2019-08-03 | NQ1005 | 11.3 | 492 | 11.3 | 493 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6120 | 2639.9997 | 119.0622
MBZ-2.RR.459.1 | 24173819144080 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Orjun Shingho | 2019-08-03 | NQ1005 | 17.2 | 494 | 16.6 | 495 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 6120 | 2639.9997 | 174.9056
MBZ-2.RR.460.1 | 24173609144073 | Sreemangal, Purbo Ram Nagar, Monipuri Para, Word # 4, Orun Shingho | 2019-08-03 | NQ1005 | 7.2 | 496 | 7.2 | 497 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6120 | 2639.9997 | 75.8627
MBZ-2.RR.461.1 | 24181039143405 | Sreemangal, Shindurkhan Road, Word # 6, Asraful Islam | 2019-08-04 | NQ1005 | 10.9 | 518 | 10.4 | 519 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6120 | 2639.9997 | 109.5794
MBZ-2.RR.462.1 | 24180929143438 | Sreemangal, Shindurkhan Road, Word # 6, Abdul Bacid | 2019-08-04 | NQ1005 | 9.8 | 520 | 9.8 | 521 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6120 | 2639.9997 | 103.2575
MBZ-2.RR.462.2 | 24180929143438 | Sreemangal, Shindurkhan Road, Word # 6, Abdul Bacid | 2021-02-01 | LU1001 | 9 | 131 | 9 | 132 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6120 | 2639.9997 | 94.8283
MBZ-2.RR.463.1 | 24181199143486 | Sreemangal, Shindurkhan Road, Word # 5, Asad Mia | 2019-08-04 | NQ1005 | 11.9 | 522 | 11.8 | 523 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6120 | 2639.9997 | 124.3305
MBZ-2.RR.464.1 | 24181259143486 | Sreemangal, Shindurkhan Road, Word # 5, Md. Helal Mia | 2019-08-04 | NQ1005 | 4.9 | 524 | 4.9 | 525 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6120 | 2639.9997 | 51.6288
MBZ-2.RR.465.1 | 24181289143495 | Sreemangal, Shindurkhan Road, Word # 5, Tayjul Islam | 2019-08-04 | NQ1005 | 11.6 | 526 | 11.5 | 527 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6120 | 2639.9997 | 121.1695
MBZ-2.RR.465.2 | 24181289143495 | Sreemangal, Shindurkhan Road, Word # 5, Tayjul Islam | 2021-09-21 | MN1018 | 5.6 | 41 | 5.6 | 42 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6120 | 2639.9997 | 59.0043
MBZ-2.RR.466.1 | 24181759144009 | Sreemangal, Kalighat Road, Elias Chowdhury | 2019-08-04 | NQ1005 | 7.5 | 528 | 6.9 | 529 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6144 | 2615.9997 | 72.7017
MBZ-2.RR.467.1 | 24181779144049 | Sreemangal, Kalighat Road, Aftab Uddin Road, Word # 3, Joy Ram Gour | 2019-08-04 | NQ1005 | 24 | 530 | 23.5 | 531 | 2022-01-01 | [9 empty] | 23.5 | 23.5 | 1.41 | 1.41 | 0.0007168 | 100% | 0% | 1.41 | 1.41 | 0.0011869 | 28 | 0.028266 | 0.028266 |  | 0 | 0
MBZ-2.RR.468.1 | 24181989144112 | Sreemangal, Kalighat Road, Jalaliya Road, Word # 3, Sumon Monjil | 2019-08-05 | NQ1005 | 10.5 | 532 | 10.5 | 533 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6144 | 2615.9997 | 110.6331
MBZ-2.RR.469.1 | 24181989144112 | Sreemangal, Kalighat Road, Jalaliya Road, Word # 3, Jahanara Begom | 2019-08-05 | NQ1005 | 6.3 | 534 | 6.3 | 535 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6144 | 2615.9997 | 66.3798
MBZ-2.RR.470.1 | 24182469143522 | Sreemangal, Notun Bazar Jame Mosjid Marchet, Hafejia Madrasa | 2019-08-05 | NQ1005 | 14.2 | 536 | 14.2 | 537 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6144 | 2615.9997 | 149.618
MBZ-2.RR.471.1 | 24184289144186 | Sreemangal, College Road, Birimpur R/A, Road # 2, Abdul Goffar | 2019-08-05 | NQ1005 | 15.2 | 538 | 15.2 | 539 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6144 | 2615.9997 | 160.1545
MBZ-2.RR.472.1 | 24184599144197 | Sreemangal, College Road, Birimpur R/A, Road # 2, Jubaer Ahmed | 2019-08-05 | NQ1005 | 7.3 | 540 | 7.3 | 541 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6144 | 2615.9997 | 76.9163
MBZ-2.RR.473.1 | 24184059144215 | Sreemangal, College Road, Birimpur R/A, Road # 1, Sukur Khan | 2019-08-05 | NQ1005 | 5.8 | 542 | 5.4 | 543 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6144 | 2615.9997 | 56.897
MBZ-2.RR.474.1 | 24184099144243 | Sreemangal, College Road, Birimpur R/A, Road # 1, Rosid Master | 2019-08-05 | NQ1005 | 12.7 | 544 | 12.7 | 545 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6144 | 2615.9997 | 133.8133
MBZ-2.RR.475.1 | 24184119144245 | Sreemangal, College Road, Birimpur R/A, Road # 1, Nasim Mia | 2019-08-05 | NQ1005 | 6.9 | 546 | 6.9 | 547 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6144 | 2615.9997 | 72.7017
MBZ-2.RR.476.1 | 24174189143558 | Sreemangal, South Muslibag, Mohibur Rahman | 2019-08-17 | NQ1007 | 2.1 | 53 | 2.1 | 54 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6120 | 2639.9997 | 22.1266
MBZ-2.RR.477.1 | 24174329144021 | Sreemangal, South Muslimbug, Rohim Gazi | 2019-08-17 | NQ1007 | 6.6 | 55 | 6.6 | 56 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6120 | 2639.9997 | 69.5408
MBZ-2.RR.478.1 | 24174329144021 | Sreemangal, South Muslimbug, Shimu Mia | 2019-08-17 | NQ1007 | 5 | 57 | 5 | 58 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6120 | 2639.9997 | 52.6824
MBZ-2.RR.479.1 | 24174219144059 | Sreemangal, South Muslimbag, Mohammad Karim | 2019-08-17 | NQ1007 | 3.9 | 59 | 3.9 | 60 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6120 | 2639.9997 | 41.0923
MBZ-2.RR.480.1 | 24173949144058 | Sreemangal, Ramnagar, Monipuripara, Upendra Bhaban, Horendra Shingho | 2019-08-17 | NQ1007 | 4.9 | 61 | 4.9 | 62 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6120 | 2639.9997 | 51.6288
MBZ-2.RR.481.1 | 24173929144053 | Sreemangal, Ramnagar, Monipuripara, Shochib Bhushon | 2019-08-17 | NQ1007 | 7 | 63 | 7 | 64 | 2022-01-01 | 2022-09-13 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6120 | 2639.9997 | 73.7554
MBZ-2.RR.501.1 | 24175879142210 | Sreemangal, South Uttorsur, Chayan Secratry | 2019-08-04 | MP1032 | 15.3 | 595 | 15.3 | 596 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6168 | 2591.9997 | 161.2082
MBZ-2.RR.502.1 | 24175879142210 | Sreemangal, South Uttorsur, Rana | 2019-08-04 | MP1032 | 13.4 | 597 | 13.4 | 598 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6168 | 2591.9997 | 141.1888
MBZ-2.RR.503.1 | 24175919142168 | Sreemangal, South Uttorsur, Sonjit | 2019-08-04 | MP1032 | 8.9 | 599 | 8.9 | 600 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6168 | 2591.9997 | 93.7747
MBZ-2.RR.504.1 | 24175919142168 | Sreemangal, South Uttorsur, Sonjit | 2019-08-04 | MP1032 | 11.9 | 601 | 11.9 | 602 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6168 | 2591.9997 | 125.3841
MBZ-2.RR.505.1 | 24175919142168 | Sreemangal, South Uttorsur, Sonjit | 2019-08-04 | MP1032 | 11.4 | 603 | 11.4 | 604 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6168 | 2591.9997 | 120.1159
MBZ-2.RR.506.1 | 24175889142161 | Sreemangal, South Uttorsur, Gosai Bari | 2019-08-04 | MP1032 | 9.7 | 605 | 9.7 | 606 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6168 | 2591.9997 | 102.2039
MBZ-2.RR.507.1 | 24175819142147 | Sreemangal, South Uttorsur, Banu Debnath | 2019-08-04 | MP1032 | 6.8 | 607 | 6.8 | 608 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6168 | 2591.9997 | 71.6481
MBZ-2.RR.508.1 | 24175819142147 | Sreemangal, South Uttorsur, Banu Debnath | 2019-08-04 | MP1032 | 11.3 | 609 | 11.3 | 610 | 2022-01-01 | 2022-09-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6168 | 2591.9997 | 119.0622
MBZ-2.RR.509.1 | 24183499144116 | Seermangal, Court Rood, Upazila Complex Rood, Suleman Khan | 2019-08-05 | MP1032 | 2.6 | 615 | 2.6 | 616 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6144 | 2615.9997 | 27.3949
MBZ-2.RR.510.1 | 24183549144116 | Seermangal, Court Rood, Upazila Complex Rood, Majedul Islam | 2019-08-05 | MP1032 | 4.1 | 617 | 4.1 | 618 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6144 | 2615.9997 | 43.1996
MBZ-2.RR.511.1 | 24183359144098 | Seermangal, Court Rood, Upazila Complex Rood, Ramjan Ali | 2019-08-05 | MP1032 | 13.1 | 619 | 13.2 | 620 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6144 | 2615.9997 | 139.0816
MBZ-2.RR.512.1 | 24183359144098 | Seermangal, Court Rood, Upazila Complex Rood, Lokiyat ullah | 2019-08-05 | MP1032 | 11.3 | 621 | 11.3 | 622 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6144 | 2615.9997 | 119.0622
MBZ-2.RR.513.1 | 24184029144362 | Seermangal, Purbo Berahimpur, Outsignal, Abdul Mannan | 2019-08-05 | MP1032 | 10.9 | 623 | 10.9 | 624 | 2022-01-01 | 2022-09-14 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6144 | 2615.9997 | 114.8476
MBZ-3.RR.1.1 | 24223909153512 | Shamser Nagar, College Road, Shengraule R/A, Md.Latfur Rahman ( Master) | 2019-08-07 | MP1032 | 10.8 | 33 | 10.8 | 34 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6072 | 2687.9997 | 113.794
MBZ-3.RR.2.1 | 24223889153536 | Shamser Nagar, College Road, Shengraule R/A, Abdul Kaium | 2019-08-07 | MP1032 | 2.3 | 35 | 2.3 | 36 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6072 | 2687.9997 | 24.2339
MBZ-3.RR.3.1 | 24220999153311 | Shamser Nagar, Barcheg R/A, Aklesur Rahman | 2019-08-07 | MP1032 | 13.1 | 37 | 13.1 | 38 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 6072 | 2687.9997 | 138.0279
MBZ-3.RR.4.1 | 24220999153311 | Shamser Nagar, Barcheg R/A, Aklesur Rahman | 2019-08-07 | MP1032 | 7.1 | 39 | 7.1 | 40 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6072 | 2687.9997 | 74.809
MBZ-3.RR.5.1 | 24221009153320 | Shamser Nagar, Barcheg R/A, Nurujaman | 2019-08-07 | MP1032 | 11.9 | 41 | 11.6 | 42 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6072 | 2687.9997 | 122.2232
MBZ-3.RR.5.2 | 24221009153320 | Shamser Nagar, Barcheg R/A, Nurujaman | 2021-01-31 | NQ1007 | 12.1 | 123 | 12.1 | 124 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6072 | 2687.9997 | 127.4914
MBZ-3.RR.6.1 | 24220939153342 | Shamser Nagar, Barcheg R/A, Afiya Bagum | 2019-08-07 | MP1032 | 11.5 | 47 | 11.5 | 48 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6072 | 2687.9997 | 121.1695
MBZ-3.RR.7.1 | 24225799154077 | Shamsher Nagar, Airport Road, Joynal Chakder Villa (Joglu), H # 17 | 2019-08-08 | NQ1009 | 9.2 | 18 | 9.2 | 19 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6072 | 2687.9997 | 96.9356
MBZ-3.RR.51.1 | 24205109150252 | Kamalgong, Bhanugach, Station Road, Mir Mujahed Ali | 2019-08-05 | MP1032 | 5.5 | 627 | 5.5 | 628 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6096 | 2663.9997 | 57.9506
MBZ-3.RR.52.1 | 24205109150252 | Kamalgong, Bhanugach, Station Road, Mir Mujahed Ali | 2019-08-05 | MP1032 | 9.9 | 629 | 9.9 | 630 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6096 | 2663.9997 | 104.3112
MBZ-3.RR.53.1 | 24205399150266 | Kamalgong, Bhanugach, Station Road, Shumit Dottho | 2019-08-05 | MP1032 | 66.8 | 631 | 66.9 | 632 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 66.9 | 66.9 | 4.014 | 4.014 | 0.0007168 | 100% | 0% | 4.014 | 4.014 | 0.0011869 | 28 | 0.080467 | 0.080467 |  | 0 | 0 | 6096 | 2663.9997 | 704.8906
MBZ-3.RR.54.1 | 24205659150264 | Kamalgong, Bhanugach, Station Road, Shamim Ahmed | 2019-08-05 | MP1032 | 5.1 | 635 | 5.1 | 636 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6096 | 2663.9997 | 53.7361
MBZ-3.RR.55.1 | 24205929150219 | Kamalgong, Bhanugach, Mokbul Ali Road, Mosarof | 2019-08-05 | MP1032 | 11.1 | 637 | 11.1 | 638 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6096 | 2663.9997 | 116.9549
MBZ-3.RR.56.1 | 24205929150219 | Kamalgong, Bhanugach, Mokbul Ali Road, Mosarof | 2019-08-05 | MP1032 | 4.2 | 639 | 4.2 | 640 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6096 | 2663.9997 | 44.2532
MBZ-3.RR.57.1 | 24210239150289 | Kamalgang, Bhanugach, Station Road, Biplob | 2019-08-06 | MP1032 | 7.4 | 1 | 7.3 | 2 | 2022-01-01 | [9 empty] | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0
MBZ-3.RR.58.1 | 24210239150289 | Kamalgang, Bhanugach, Station Road, Biplob | 2019-08-06 | MP1032 | 5 | 3 | 5 | 4 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6096 | 2663.9997 | 52.6824
MBZ-3.RR.59.1 | 24210239150289 | Kamalgang, Bhanugach, Station Road, Saidul Haque | 2019-08-06 | MP1032 | 14.9 | 5 | 14.9 | 6 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6096 | 2663.9997 | 156.9936
MBZ-3.RR.60.1 | 24225819153492 | Kamalgang, Shamshernagar, Shingraully Road, Sharafa R/A, MD Ibrahim | 2019-08-06 | MP1032 | 10.5 | 9 | 9.8 | 10 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6072 | 2687.9997 | 103.2575
MBZ-3.RR.61.1 | 24225719153441 | Kamalgang, Shamshernagar, Shingraully Road, Sharafa R/A, Rakin | 2019-08-06 | MP1032 | 7.6 | 11 | 7.8 | 12 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6072 | 2687.9997 | 82.1846
MBZ-3.RR.62.1 | 24225709153424 | Kamalgang, Shamshernagar, Shingraully Road, Sharafa R/A, Kader Mia | 2019-08-06 | MP1032 | 5.7 | 13 | 5.7 | 14 | 2022-01-01 | [9 empty] | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 | 2022-02-28 12:00 | 0 | 0
MBZ-3.RR.63.1 | 24224979153441 | Kamalgang, Shamshernagar, Shingraully, Alauddin Mia | 2019-08-07 | MP1032 | 5.4 | 17 | 5.4 | 18 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6072 | 2687.9997 | 56.897
MBZ-3.RR.64.1 | 24224759153445 | Kamalgang, Shamshernagar, Shingraully, Tajub Ali | 2019-08-07 | MP1032 | 12.7 | 19 | 12.7 | 20 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6072 | 2687.9997 | 133.8133
MBZ-3.RR.65.1 | 24224759153445 | Kamalgang, Shamshernagar, Shingraully, Tajub Ali | 2019-08-07 | MP1032 | 5.1 | 23 | 5.1 | 24 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6072 | 2687.9997 | 53.7361
MBZ-3.RR.66.1 | 24223879153412 | Kamalgang, Shamshernagar, Shingraully, Mamun | 2019-08-07 | MP1032 | 7.5 | 25 | 7.5 | 26 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6072 | 2687.9997 | 79.0236
MBZ-3.RR.67.1 | 24223679153405 | Kamalgang, Shamshernagar, Shingraully, Tuakul Mia | 2019-08-07 | MP1032 | 55.5 | 27 | 55.4 | 28 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 55.4 | 55.4 | 3.324 | 3.324 | 0.0007168 | 100% | 0% | 3.324 | 3.324 | 0.0011869 | 28 | 0.066635 | 0.066635 |  | 0 | 0 | 6072 | 2687.9997 | 583.7211
MBZ-3.RR.68.1 | 24223679153405 | Kamalgang, Shamshernagar, Shingraully, Tuakul Mia | 2019-08-07 | MP1032 | 5.3 | 29 | 5.1 | 30 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6072 | 2687.9997 | 53.7361
MBZ-3.RR.69.1 | 24223849153485 | Kamalgang, Shamshernagar, Shingraully, College Road, Hafiza Monjil | 2019-08-07 | MP1032 | 4.4 | 31 | 4.4 | 32 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6072 | 2687.9997 | 46.3605
MBZ-3.RR.69.2 | 24223849153485 | Kamalgang, Shamshernagar, Shingraully, College Road, Hafiza Monjil | 2022-03-03 | NQ1007 | 13.5 | 25 | 13.5 | 26 | 2022-03-03 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 4608 | 2687.9997 | 118.4705
MBZ-3.RR.70.1 | 24225089153347 | Kamalgang, Shamshernagar, Shingraully, Muntaj Mia | 2019-08-08 | MP1032 | 5.1 | 49 | 5.1 | 50 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6072 | 2687.9997 | 53.7361
MBZ-3.RR.71.1 | 24224979153323 | Kamalgang, Shamshernagar, Shingraully, Sherajul | 2019-08-08 | MP1032 | 12.3 | 55 | 12.3 | 56 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6072 | 2687.9997 | 129.5987
MBZ-3.RR.72.1 | 24225899153338 | Kamalgang, Shamshernagar, Shingraully, A.M. Mushahid | 2019-08-08 | MP1032 | 23.1 | 57 | 23.1 | 58 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 23.1 | 23.1 | 1.386 | 1.386 | 0.0007168 | 100% | 0% | 1.386 | 1.386 | 0.0011869 | 28 | 0.027785 | 0.027785 |  | 0 | 0 | 6072 | 2687.9997 | 243.3927
MBZ-3.RR.73.1 | 24225899153338 | Kamalgang, Shamshernagar, Shingraully, A.M. Mushahid | 2019-08-08 | MP1032 | 3.5 | 59 | 3.5 | 60 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6072 | 2687.9997 | 36.8777
MBZ-3.RR.101.1 | 24205489150394 | Kamolgonj, Vanugach, Ward # 6, Thana Road, H # 205, Shornojit Rai | 2019-08-05 | NQ1005 | 5 | 552 | 5 | 553 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6096 | 2663.9997 | 52.6824
MBZ-3.RR.102.1 | 24205419150405 | Kamolgonj, Vanugach, Ward # 6, Thana Road, H # 0168, Binapani Niketon | 2019-08-05 | NQ1005 | 11.5 | 554 | 11.1 | 555 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6096 | 2663.9997 | 116.9549
MBZ-3.RR.103.1 | 24214249151163 | Kamolgonj, Ward # 1, Gopal Nagor, Dewan Abdur Rahim | 2019-08-06 | NQ1005 | 6.9 | 9 | 6.9 | 10 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6096 | 2663.9997 | 72.7017
MBZ-3.RR.104.1 | 24225219154143 | Kamolgonj, Shomshernagor, Bagan Road, Alok Kumar Shaha | 2019-08-07 | NQ1005 | 21.2 | 23 | 21.2 | 24 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 21.2 | 21.2 | 1.272 | 1.272 | 0.0007168 | 100% | 0% | 1.272 | 1.272 | 0.0011869 | 28 | 0.025499 | 0.025499 |  | 0 | 0 | 6072 | 2687.9997 | 223.3734
MBZ-3.RR.105.1 | 24225009154128 | Kamolgonj, Shomshernagor, Shamsur Road, H # 62, Anirban | 2019-08-07 | NQ1005 | 12.2 | 25 | 12.2 | 26 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6072 | 2687.9997 | 128.5451
MBZ-3.RR.106.1 | 24224849154131 | Kamolgonj, Shomshernagor, Shamsur Road, Bani Deb | 2019-08-07 | NQ1005 | 7.2 | 27 | 7.2 | 28 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6072 | 2687.9997 | 75.8627
MBZ-3.RR.107.1 | 24224849154131 | Kamolgonj, Shomshernagor, Shamsur Road, Abdul Gofur | 2019-08-07 | NQ1005 | 7.7 | 29 | 7.7 | 30 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6072 | 2687.9997 | 81.1309
MBZ-3.RR.108.1 | 24224749154131 | Kamolgonj, Shomshernagor, Chatlapur Road, Mesers Auto Rice Mill | 2019-08-07 | NQ1005 | 47.5 | 31 | 47.5 | 32 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 47.5 | 47.5 | 2.85 | 2.85 | 0.0007168 | 100% | 0% | 2.85 | 2.85 | 0.0011869 | 28 | 0.057133 | 0.057133 |  | 0 | 0 | 6072 | 2687.9997 | 500.4829
MBZ-3.RR.109.1 | 24225769154141 | Kamolgonj, Shaheenbug College Road, Sobujbug R/ A,Block -A, H # 114/1 | 2019-08-08 | NQ1005 | 20.2 | 33 | 20.3 | 34 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 20.3 | 20.3 | 1.218 | 1.218 | 0.0007168 | 100% | 0% | 1.218 | 1.218 | 0.0011869 | 28 | 0.024417 | 0.024417 |  | 0 | 0 | 6072 | 2687.9997 | 213.8906
MBZ-3.RR.110.1 | 24225599154138 | Kamolgonj, Shaheenbug College Road, Sobujbug R/ A,Block -A, H # 120, Billal Khan | 2019-08-08 | NQ1005 | 12.1 | 35 | 12.1 | 36 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6072 | 2687.9997 | 127.4914
MBZ-3.RR.111.1 | 24225599154138 | Kamolgonj, Shaheenbug College Road, Sobujbug R/ A,Block -A, H # 121, Abdul Kayum | 2019-08-08 | NQ1005 | 11 | 37 | 10.7 | 38 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6072 | 2687.9997 | 112.7403
MBZ-3.RR.111.2 | 24225599154138 | Kamolgonj, Shaheenbug College Road, Sobujbug R/ A,Block -A, H # 121, Abdul Kayum | 2021-01-31 | NQ1003 | 6.4 | 170 | 6.4 | 171 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6072 | 2687.9997 | 67.4335
MBZ-3.RR.112.1 | 24225349154102 | Kamolgonj, Shomshernagar, Bagan Road, Annapurna Bhaban, Kanai Pal | 2019-08-08 | NQ1005 | 7.4 | 39 | 7.4 | 40 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6072 | 2687.9997 | 77.97
MBZ-3.RR.113.1 | 24225359154081 | Kamolgonj, Shomshernagar, Bagan Road, Sadhon Kanunjna | 2019-08-08 | NQ1005 | 15 | 41 | 15 | 42 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6072 | 2687.9997 | 158.0472
MBZ-3.RR.113.2 | 24225359154081 | Kamolgonj, Shomshernagar, Bagan Road, Sadhon Kanunjna | 2021-01-31 | NQ1003 | 12.5 | 166 | 12.6 | 167 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6072 | 2687.9997 | 132.7597
MBZ-3.RR.151.1 | 24205959150497 | Moulvibazar, Komolgonj, Pouro Alaka, Word # 5, Gujari Villa, Sirajul Haque | 2019-08-06 | NQ1005 | 5.7 | 1 | 5.7 | 2 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6096 | 2663.9997 | 60.0579
MBZ-3.RR.152.1 | 24205959150497 | Moulvibazar, Komolgonj, Pouro Alaka, Word # 5, Rowsonara Begom | 2019-08-06 | NQ1005 | 7.8 | 3 | 7.8 | 4 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6096 | 2663.9997 | 82.1846
MBZ-3.RR.153.1 | 24210359150536 | Moulvibazar, Komolgonj, Word # 5, Radhanath Shingho | 2019-08-06 | NQ1005 | 22.5 | 5 | 21.7 | 6 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 6096 | 2663.9997 | 228.6416
MBZ-3.RR.153.2 | 24210359150536 | Moulvibazar, Komolgonj, Word # 5, Radhanath Shingho | 2022-03-05 | NQ1007 | 10.3 | 27 | 10.3 | 28 | 2022-03-05 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 4584 | 2663.9997 | 89.7939
MBZ-3.RR.154.1 | 24211369151035 | Moulvibazar, Komolgonj, Word # 5, Mobarok Hossen Master | 2019-08-06 | NQ1005 | 12 | 7 | 12 | 8 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6096 | 2663.9997 | 126.4378
MBZ-3.RR.155.1 | 24230049153551 | Moulvibazar, Kamalgonj, Somsher Nagar, Moulvibazar Road, Word # 4, Abdul Kaium | 2019-08-07 | NQ1005 | 12.7 | 11 | 12.7 | 12 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6072 | 2687.9997 | 133.8133
MBZ-3.RR.156.1 | 24230589153544 | Moulvibazar, Kamalgonj, Somsher Nagar, Moulvibazar Road, Word # 4, Matin & Khanam Villa | 2019-08-07 | NQ1005 | 7.4 | 13 | 6.9 | 14 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6072 | 2687.9997 | 72.7017
MBZ-3.RR.157.1 | 24230469153559 | Moulvibazar, Kamalgonj, Somsher Nagar, Abdul Mosabbir Road, Word # 4, Sultana Bagom | 2019-08-07 | NQ1005 | 11.1 | 15 | 11.1 | 16 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6072 | 2687.9997 | 116.9549
MBZ-3.RR.158.1 | 24231059154001 | Moulvibazar, kamalgonj, Somsher Nagar, Vadael Dhuil, Sirajul Islam | 2019-08-07 | NQ1005 | 20.7 | 17 | 20.2 | 18 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 20.2 | 20.2 | 1.212 | 1.212 | 0.0007168 | 100% | 0% | 1.212 | 1.212 | 0.0011869 | 28 | 0.024296 | 0.024296 |  | 0 | 0 | 6072 | 2687.9997 | 212.8369
MBZ-3.RR.159.1 | 24231099153582 | Moulvibazar, kamalgonj, Somsher Nagar, Vadael Dhuil, Jorun Nesha | 2019-08-07 | NQ1005 | 8.1 | 19 | 8.1 | 20 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6072 | 2687.9997 | 85.3455
MBZ-3.RR.160.1 | 24231009153550 | Moulvibazar, Kamalgonj, Somsher Nagar, Moulvibazar Road, Rohij Mia | 2019-08-07 | NQ1005 | 12.8 | 21 | 12.8 | 22 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6072 | 2687.9997 | 134.867
MBZ-3.RR.161.1 | 24235479154260 | Kamalgonj, Shamsher Nagar, Dhulotpur, Aiarport Road, Aiarmans Quarter, Surma-2 | 2019-08-08 | NQ1005 | 25 | 46 | 25 | 47 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 25 | 25 | 1.5 | 1.5 | 0.0007168 | 100% | 0% | 1.5 | 1.5 | 0.0011869 | 28 | 0.03007 | 0.03007 |  | 0 | 0 | 6072 | 2687.9997 | 263.412
MBZ-3.RR.201.1 | 24204779151159 | Kamalganj, Kushalpur, Salimbazar Road, Syed Ziaul Islam | 2019-08-05 | LX1011 | 33.8 | 573 | 33.8 | 574 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 33.8 | 33.8 | 2.028 | 2.028 | 0.0007168 | 100% | 0% | 2.028 | 2.028 | 0.0011869 | 28 | 0.040654 | 0.040654 |  | 0 | 0 | 6096 | 2663.9997 | 356.1331
MBZ-3.RR.202.1 | 24212509151048 | Kamalganj, Ward # 2, Borgach, Borgach Road, Chowdhury Bari, Nazrul Islam Chowdhury | 2019-08-06 | LX1011 | 4.3 | 15 | 4.3 | 16 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6096 | 2663.9997 | 45.3069
MBZ-3.RR.203.1 | 24213039151154 | Kamalganj, Borgach, Opposite of Fire Service & Civil Defence Station, Shahjahan | 2019-08-06 | LX1011 | 30.2 | 17 | 30.3 | 18 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 30.3 | 30.3 | 1.818 | 1.818 | 0.0007168 | 100% | 0% | 1.818 | 1.818 | 0.0011869 | 28 | 0.036445 | 0.036445 |  | 0 | 0 | 6096 | 2663.9997 | 319.2554
MBZ-3.RR.204.1 | 24224999154101 | Kamalganj, Shomshernagar, Chatlapur Road, Syed Tofazzal Ali | 2019-08-07 | NQ1009 | 30.1 | 14 | 30.1 | 15 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 30.1 | 30.1 | 1.806 | 1.806 | 0.0007168 | 100% | 0% | 1.806 | 1.806 | 0.0011869 | 28 | 0.036204 | 0.036204 |  | 0 | 0 | 6072 | 2687.9997 | 317.1481
MBZ-3.RR.205.1 | 24224729154106 | Kamalganj, Shomshernagar, Machbazar Road, Jomir Ali | 2019-08-07 | NQ1009 | 5.5 | 16 | 5.4 | 17 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6072 | 2687.9997 | 56.897
MBZ-3.RR.206.1 | 24235629154176 | Kamalganj, Shomshernagar, Kechuluti, Monowara Begum | 2019-08-08 | MP1032 | 6.2 | 61 | 6.2 | 62 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6072 | 2687.9997 | 65.3262
MBZ-3.RR.206.2 | 24235629154176 | Kamalganj, Shomshernagar, Kechuluti, Monowara Begum | 2021-01-31 | NQ1003 | 7 | 161 | 7 | 162 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6072 | 2687.9997 | 73.7554
MBZ-3.RR.251.1 | 24210109150592 | Kamalganj, Chandipur, Panishala, Adampur Road, Sayed Shahjahan | 2019-08-06 | LX1011 | 6.5 | 1 | 6.3 | 2 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6096 | 2663.9997 | 66.3798
MBZ-3.RR.252.1 | 24210109150592 | Kamalganj, Chandipur, Panishala, Adampur Road, Sayed Bakhtixar | 2019-08-06 | LX1011 | 8.4 | 3 | 8.4 | 4 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6096 | 2663.9997 | 88.5064
MBZ-3.RR.253.1 | 24210939151115 | Kamalganj, Chandipur, Borogach, Emdadur Rahman | 2019-08-06 | LX1011 | 10.8 | 5 | 10.8 | 6 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6096 | 2663.9997 | 113.794
MBZ-3.RR.254.1 | 24210939151115 | Kamalganj, Chandipur, Borogach, Eshakuddin | 2019-08-06 | LX1011 | 4.8 | 7 | 4.8 | 8 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6096 | 2663.9997 | 50.5751
MBZ-3.RR.256.1 | 24211239151139 | Kamalganj, Chandipur, Borogach, Abdur Rashid | 2019-08-06 | LX1011 | 6.2 | 11 | 6.2 | 12 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6096 | 2663.9997 | 65.3262
MBZ-3.RR.257.1 | 24211309151155 | Kamalganj, Chandipur, Borogach, Rafiqur Rahman | 2019-08-06 | LX1011 | 3 | 13 | 3.1 | 14 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6096 | 2663.9997 | 32.6631
MBZ-3.RR.258.1 | 24232279153543 | Shamshernagar, Badairdewl, Mukambazar, Moulvibazar Road, Aminul Islam | 2019-08-07 | NQ1009 | 7.3 | 1 | 7.4 | 2 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6072 | 2687.9997 | 77.97
MBZ-3.RR.259.1 | 24231789154041 | Shamshernagar, Badairdewl, Faruk Ahmed | 2019-08-07 | NQ1009 | 8.5 | 3 | 8.5 | 4 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6072 | 2687.9997 | 89.5601
MBZ-3.RR.260.1 | 24231349154079 | Shamshernagar, Badairdewl, Mukambazar Road, Abdur Rahman | 2019-08-07 | NQ1009 | 25 | 5 | 25 | 6 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 25 | 25 | 1.5 | 1.5 | 0.0007168 | 100% | 0% | 1.5 | 1.5 | 0.0011869 | 28 | 0.03007 | 0.03007 |  | 0 | 0 | 6072 | 2687.9997 | 263.412
MBZ-3.RR.261.1 | 24231949153554 | Shamshernagar, Badairdewl, Moulvibazar Road, Abidur Rahman | 2019-08-07 | NQ1009 | 12.2 | 7 | 12.3 | 8 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6072 | 2687.9997 | 129.5987
MBZ-3.RR.262.1 | 24225689154077 | Shamshernagar, Airport Road, Mostofa Mia | 2019-08-07 | NQ1009 | 10.7 | 9 | 10.7 | 10 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6072 | 2687.9997 | 112.7403
MBZ-3.RR.263.1 | 24225689154077 | Shamshernagar, Airport Road, Iliyas Ali | 2019-08-07 | NQ1009 | 5.8 | 11 | 5.3 | 12 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6072 | 2687.9997 | 55.8434
MBZ-3.RR.264.1 | 24235289154214 | Shamshernagar, Airport Road, Swiss Valley Resort Road, Saif Ullah | 2019-08-08 | NQ1009 | 36.4 | 20 | 36.4 | 21 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 36.4 | 36.4 | 2.184 | 2.184 | 0.0007168 | 100% | 0% | 2.184 | 2.184 | 0.0011869 | 28 | 0.043782 | 0.043782 |  | 0 | 0 | 6072 | 2687.9997 | 383.5279
MBZ-3.RR.301.1 | 24205259150260 | Komolgonj, Kumargao, Vanugach Bazar, Station Road, H # 93, Sahjahan Mollah | 2019-08-05 | NQ1007 | 2.5 | 569 | 2.5 | 570 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6096 | 2663.9997 | 26.3412
MBZ-3.RR.302.1 | 24205259150260 | Komolgonj, Kumargao, Vanugach Bazar, Station Road, H # 93/1, Jakir Mollah | 2019-08-05 | NQ1007 | 8 | 571 | 8 | 572 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6096 | 2663.9997 | 84.2919
MBZ-3.RR.303.1 | 24205329150222 | Komolgonj, Baligao, Vanugach Bazar,H # 98, Benu Lal de | 2019-08-05 | NQ1007 | 25.8 | 573 | 25.8 | 574 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 25.8 | 25.8 | 1.548 | 1.548 | 0.0007168 | 100% | 0% | 1.548 | 1.548 | 0.0011869 | 28 | 0.031032 | 0.031032 |  | 0 | 0 | 6096 | 2663.9997 | 271.8412
MBZ-3.RR.303.2 | 24205329150222 | Komolgonj, Baligao, Vanugach Bazar,H # 98, Benu Lal de | 2021-09-16 | MN1018 | 8.7 | 24 | 8.7 | 25 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6096 | 2663.9997 | 91.6674
MBZ-3.RR.304.1 | 24205519150213 | Komolgonj, Baligao, Vanugach Bazar, Onil Kanti Dotto | 2019-08-05 | NQ1007 | 6.8 | 577 | 6.9 | 578 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6096 | 2663.9997 | 72.7017
MBZ-3.RR.305.1 | 24205609150206 | Komolgonj, Baligao, Vanugach Bazar,H # 29, Soiyod Mahamud Ali | 2019-08-05 | NQ1007 | 12.5 | 581 | 12.5 | 582 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6096 | 2663.9997 | 131.706
MBZ-3.RR.306.1 | 24210129150217 | Komolgonj, Baligao, Vanugach Bazar, Kashani | 2019-08-05 | NQ1007 | 3.1 | 583 | 3.1 | 584 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6096 | 2663.9997 | 32.6631
MBZ-3.RR.307.1 | 24225689153562 | Komolgonj, Shamshernagar, Shingraully Road, Md. Ijjot Ali | 2019-08-06 | NQ1007 | 11.6 | 605 | 11.5 | 606 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6072 | 2687.9997 | 121.1695
MBZ-3.RR.308.1 | 24223939153515 | Shamshernagar, Shinraully R/A, College Road, H # 203, Saimon Ahamed | 2019-08-07 | NQ1007 | 11.3 | 19 | 11.3 | 20 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6072 | 2687.9997 | 119.0622
MBZ-3.RR.309.1 | 24224129153528 | Shamshernagar, Shinraully R/A, College Road, H # 642, Shibu Devnath | 2019-08-07 | NQ1007 | 13.7 | 21 | 13.7 | 22 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6072 | 2687.9997 | 144.3498
MBZ-3.RR.310.1 | 24224129153528 | Shamshernagar, Shinraully R/A, College Road, H # 560, Jhahir Mia | 2019-08-07 | NQ1007 | 2.9 | 23 | 2.9 | 24 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6072 | 2687.9997 | 30.5558
MBZ-3.RR.311.1 | 24221659153359 | Shamshernagar, Boroceg, Komolgonj Road, Monir Uddin Mozumdar | 2019-08-07 | NQ1007 | 10.5 | 25 | 10.5 | 26 | 2022-01-01 | 2022-09-11 | MN1018 | 9.6 | 1 | 9.6 | 2 | 2022-09-11 | GS | 0 | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6072 | 2687.9997 | 89.5601
MBZ-3.RR.312.1 | 24220909153273 | Shamshernagar, Shinraully , Itgatila, H # 804, Abdul Malek | 2019-08-07 | NQ1007 | 14.4 | 27 | 14.8 | 28 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6072 | 2687.9997 | 155.9399
MBZ-3.RR.313.1 | 24232319154175 | Shamshernagar, Doulotpur, Airport Road, H # 291, Moksudul | 2019-08-08 | NQ1007 | 18.6 | 47 | 18.6 | 48 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 6072 | 2687.9997 | 195.9786
MBZ-3.RR.314.1 | 24234319154191 | Shamshernagar, Vhada Dewor, Airport Road, H # 278, Kobir Ahamed | 2019-08-08 | NQ1007 | 4.8 | 49 | 4.5 | 50 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6072 | 2687.9997 | 47.4142
MBZ-3.RR.315.1 | 24234309154169 | Shamshernagar, Vhada Dewor, Airport Road, Lokman Mia | 2019-08-08 | NQ1007 | 4.1 | 51 | 4.1 | 52 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6072 | 2687.9997 | 43.1996
MBZ-3.RR.351.1 | 24210239150537 | Komolgonj, Panishala, Ward # 2, Aklus Mia | 2019-08-06 | NQ1007 | 3.6 | 585 | 3.6 | 586 | 2022-01-01 | [9 empty] | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0
MBZ-3.RR.352.1 | 24210209150541 | Komolgonj, Panishala, Ward # 2, Enamul | 2019-08-06 | NQ1007 | 7.5 | 587 | 7.5 | 588 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6096 | 2663.9997 | 79.0236
MBZ-3.RR.352.2 | 24210209150541 | Komolgonj, Panishala, Ward # 2, Enamul | 2021-09-16 | MN1018 | 4.3 | 26 | 4.3 | 27 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6096 | 2663.9997 | 45.3069
MBZ-3.RR.353.1 | 24210119150570 | Komolgonj, Chondipur, Ward # 5, Md. Aiyub Ali | 2019-08-06 | NQ1007 | 6 | 591 | 6 | 592 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6096 | 2663.9997 | 63.2189
MBZ-3.RR.354.1 | 24210009150567 | Komolgonj, Chondipur, Ward # 5, Towfiqul Islam | 2019-08-06 | NQ1007 | 7.9 | 593 | 7.9 | 594 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6096 | 2663.9997 | 83.2382
MBZ-3.RR.354.2 | 24210009150567 | Komolgonj, Chondipur, Ward # 5, Towfiqul Islam | 2022-09-12 | MN1018 | 35.5 | 3 | 35.5 | 4 | 2022-09-12 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 35.5 | 35.5 | 2.13 | 2.13 | 0.0007168 | 100% | 0% | 2.13 | 2.13 | 0.0011869 | 28 | 0.042699 | 0.042699 |  | 0 | 0 | 0 | 2663.9997 | 113.7507
MBZ-3.RR.355.1 | 24205869150559 | Komolgonj, Chondipur, Ward # 5, Moshayed | 2019-08-06 | NQ1007 | 3.2 | 595 | 3.2 | 596 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6096 | 2663.9997 | 33.7167
MBZ-3.RR.356.1 | 24205819150560 | Komolgonj, Chondipur, Ward # 5, Shekh Sayem Ahmed | 2019-08-06 | NQ1007 | 11.7 | 597 | 11.7 | 598 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6096 | 2663.9997 | 123.2768
MBZ-3.RR.357.1 | 24211729151132 | Komolgonj, Nosrotpur, Ward # 3, Dr. Nazrul B Chowdhury | 2019-08-06 | NQ1007 | 3.8 | 599 | 3.8 | 600 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6096 | 2663.9997 | 40.0386
MBZ-3.RR.358.1 | 24211709151154 | Komolgonj, Nosrotpur, Ward # 3, Harunur Rashid | 2019-08-06 | NQ1007 | 12 | 601 | 12.1 | 602 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6096 | 2663.9997 | 127.4914
MBZ-3.RR.359.1 | 24211709151154 | Komolgonj, Nosrotpur, Ward # 3, Harunur Rashid | 2019-08-06 | NQ1007 | 8.4 | 603 | 8.3 | 604 | 2022-01-01 | 2022-09-12 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6096 | 2663.9997 | 87.4528
MBZ-3.RR.360.1 | 24230549153431 | Komolgonj, Shomshernagar, Vadair Deul, Union Porishod Road, Bojlur Rahman | 2019-08-07 | NQ1007 | 6.5 | 1 | 6.5 | 2 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6072 | 2687.9997 | 68.4871
MBZ-3.RR.361.1 | 24230539153447 | Komolgonj, Shomshernagar, Vadair Deul, Union Porishod Road, Mohammad Abdul Basith | 2019-08-07 | NQ1007 | 9.4 | 3 | 9.4 | 4 | 2022-01-01 | [9 empty] | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0
MBZ-3.RR.362.1 | 24230559153463 | Komolgonj, Shomshernagar, Vadair Deul, Union Porishod Road, Showkot Villa | 2019-08-07 | NQ1007 | 16.4 | 5 | 16.4 | 6 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6072 | 2687.9997 | 172.7983
MBZ-3.RR.363.1 | 24230589153464 | Komolgonj, Shomshernagar, Vadair Deul, Union Porishod Road, Dhejendra Pal | 2019-08-07 | NQ1007 | 14.9 | 7 | 14.9 | 8 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 6072 | 2687.9997 | 156.9936
MBZ-3.RR.364.1 | 24230799153479 | Komolgonj, Shomshernagar, Vadair Deul, Union Porishod Road, Subash | 2019-08-07 | NQ1007 | 11.2 | 9 | 11.2 | 10 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6072 | 2687.9997 | 118.0086
MBZ-3.RR.365.1 | 24230759153473 | Komolgonj, Shomshernagar, Vadair Deul, Union Porishod Road, Rokeya Khanom | 2019-08-07 | NQ1007 | 12.7 | 11 | 12.8 | 12 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6072 | 2687.9997 | 134.867
MBZ-3.RR.366.1 | 24230789153446 | Komolgonj, Shomshernagar, Vadair Deul, Union Porishod Road, Hannan Mia | 2019-08-07 | NQ1007 | 34.3 | 13 | 34.6 | 14 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 34.6 | 34.6 | 2.076 | 2.076 | 0.0007168 | 100% | 0% | 2.076 | 2.076 | 0.0011869 | 28 | 0.041617 | 0.041617 |  | 0 | 0 | 6072 | 2687.9997 | 364.5623
MBZ-3.RR.367.1 | 24231019153539 | Komolgonj, Shomshernagar, Moulvibazar Road, Babul Mia | 2019-08-07 | NQ1007 | 7.2 | 15 | 7.2 | 16 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6072 | 2687.9997 | 75.8627
MBZ-3.RR.368.1 | 24231489153569 | Komolgonj, Shomshernagar, Vadair Deul, Hazi Abdus Shohid | 2019-08-07 | NQ1007 | 14.4 | 17 | 14.4 | 18 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 6072 | 2687.9997 | 151.7253
MBZ-3.RR.369.1 | 24231449154161 | Komolgonj, Shomshernaar, Doulotpur, Bimanbondor Road, Jahanara Khanom | 2019-08-08 | NQ1007 | 15.5 | 31 | 15.5 | 32 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 6072 | 2687.9997 | 163.3155
MBZ-3.RR.370.1 | 24231449154161 | Komolgonj, Shomshernaar, Doulotpur, Bimanbondor Road, Jaher Shekh | 2019-08-08 | NQ1007 | 13.3 | 33 | 13.3 | 34 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6072 | 2687.9997 | 140.1352
MBZ-3.RR.371.1 | 24231439154141 | Komolgonj, Shomshernaar, Doulotpur, Bimanbondor Road, U K Gest House | 2019-08-08 | NQ1007 | 46.6 | 35 | 46.6 | 36 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 46.6 | 46.6 | 2.796 | 2.796 | 0.0007168 | 100% | 0% | 2.796 | 2.796 | 0.0011869 | 28 | 0.05605 | 0.05605 |  | 0 | 0 | 6072 | 2687.9997 | 491
MBZ-3.RR.372.1 | 24231969154172 | Komolgonj, Shomshernaar, Doulotpur, Bimanbondor Road, Mukta Tower | 2019-08-08 | NQ1007 | 10.2 | 37 | 10.2 | 38 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6072 | 2687.9997 | 107.4721
MBZ-3.RR.373.1 | 24232269154158 | Komolgonj, Shomshernaar, Doulotpur, Bimanbondor Road, Khatuna Begum | 2019-08-08 | NQ1007 | 5.2 | 41 | 5.2 | 42 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6072 | 2687.9997 | 54.7897
MBZ-3.RR.374.1 | 24232269154158 | Komolgonj, Shomshernaar, Doulotpur, Bimanbondor Road, Khatuna Begum | 2019-08-08 | NQ1007 | 10.5 | 43 | 10.5 | 44 | 2022-01-01 | 2022-09-11 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6072 | 2687.9997 | 110.6331
MBZ-4.CR.1.1 | 24311859202023 | Moulovibazar, Kulaura, South Market, Shaad Bakery Food | 2019-08-19 | NQ1005 | 16.5 | 66 | 16.5 | 67 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 6456 | 2303.9997 | 173.8519
MBZ-4.CR.2.1 | 24313239202103 | Moulovibazar, Kulaura, North Market, Main Road, Ahmed Complex, Golden View Restora | 2019-08-19 | NQ1005 | 10.7 | 86 | 10.7 | 87 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6456 | 2303.9997 | 112.7403
MBZ-4.CR.3.1 | 24353599207161 | Juri, Bhabaniganj Bazar, College Road, Banalata Misti Ghar | 2019-08-22 | NQ1009 | 11.5 | 152 | 11.5 | 153 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6408 | 2351.9997 | 121.1695
MBZ-4.CR.4.1 | 24391609209260 | Barlekha, Chintapur, Azimgonj Road, Hashim Monjil | 2019-08-24 | NQ1007 | 5.7 | 247 | 5.7 | 248 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6336 | 2423.9997 | 60.0579
MBZ-4.CR.5.1 | 24370889208290 | Borolekha, Ward # 2, Pashchim Hatolia, Ator Factory | 2019-08-24 | MP1032 | 13.2 | 223 | 13.2 | 224 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6336 | 2423.9997 | 139.0816
MBZ-4.CR.6.1 | 24390659209528 | Barlekha, Rotuli Bazar, Azimgonj Road, Azizur Rahman | 2019-08-24 | NQ1007 | 9.8 | 227 | 9.8 | 228 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6336 | 2423.9997 | 103.2575
MBZ-4.CR.6.2 | 24390659209528 | Barlekha, Rotuli Bazar, Azimgonj Road, Azizur Rahman | 2019-08-24 | NQ1007 | 1.6 | 229 | 1.6 | 230 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6336 | 2423.9997 | 16.8584
MBZ-4.CR.7.1 | 24390949208317 | Barlekha, Shaldigha,Shaldigha Road, Ward # 5, Abdun Nur | 2019-08-25 | NQ1007 | 8.8 | 279 | 8.8 | 280 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6312 | 2447.9997 | 92.721
MBZ-4.CR.8.1 | 24385729208304 | Barlekha Sujanagar, Shaldigha, Ward # 5, Hazi Moyenuddin | 2019-08-25 | NQ1007 | 5.1 | 289 | 5.1 | 290 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6312 | 2447.9997 | 53.7361
MBZ-4.CR.9.1 | 24393409208425 | Barlekha, North Sujanagar, Ward # 7, Hazi Abdul Gofur | 2019-08-26 | NQ1007 | 11 | 308 | 11 | 309 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6312 | 2447.9997 | 115.9013
MBZ-4.CR.10.1 | 24393879208410 | Barlekha, Sujanagar, Eidgah Bari, Munaf Ali | 2019-08-26 | MP1032 | 50 | 303 | 50 | 304 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 50 | 50 | 3 | 3 | 0.0007168 | 100% | 0% | 3 | 3 | 0.0011869 | 28 | 0.06014 | 0.06014 |  | 0 | 0 | 6312 | 2447.9997 | 526.8241
MBZ-4.CR.11.1 | 24395499208492 | Barlekha, North Sujanagar, Ward # 6, Abdul Aziz | 2019-08-27 | NQ1007 | 4.3 | 354 | 4.3 | 355 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6312 | 2447.9997 | 45.3069
MBZ-4.RR.1.1 | 24303839201481 | Kulaura, Jagannathpur, Syed Md. Tara Mia | 2019-08-18 | MP1032 | 11.1 | 63 | 11 | 64 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6480 | 2279.9997 | 115.9013
MBZ-4.RR.2.1 | 24303839201481 | Kulaura, Jagannathpur, College Road, Riaz Mia | 2019-08-18 | MP1032 | 12.9 | 67 | 12.9 | 68 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6480 | 2279.9997 | 135.9206
MBZ-4.RR.3.1 | 24303069202092 | Kulaura, Ward # 9, Momrejpur, Md. Abdul Latif | 2019-08-18 | MP1032 | 4.1 | 69 | 4.1 | 70 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6480 | 2279.9997 | 43.1996
MBZ-4.RR.4.1 | 24303129202118 | Kulaura, Ward # 9, Loshkorpur, Md. Israb Ali | 2019-08-18 | MP1032 | 6.8 | 73 | 6.8 | 74 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6480 | 2279.9997 | 71.6481
MBZ-4.RR.5.1 | 24312089201555 | Kulaura, Ward # 4, Magura, Abul Hossain Jitu | 2019-08-19 | MP1032 | 12.6 | 89 | 12.2 | 90 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6480 | 2279.9997 | 128.5451
MBZ-4.RR.6.1 | 24312119201531 | Kulaura, Ward # 4, Magura, A.M.S. Zaman (Ex-Chairman) | 2019-08-19 | MP1032 | 5.1 | 91 | 5.1 | 92 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6480 | 2279.9997 | 53.7361
MBZ-4.RR.7.1 | 24312089201521 | Kulaura, Ward # 4, Magura, H # 53, Abdul Hannan | 2019-08-19 | MP1032 | 6.2 | 93 | 6.2 | 94 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6480 | 2279.9997 | 65.3262
MBZ-4.RR.8.1 | 24312469201522 | Kulaura, Ward # 4, Magura, Monsur Road, H # 36, Md. Iqbal Hossain | 2019-08-19 | MP1032 | 8 | 95 | 7.5 | 96 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6480 | 2279.9997 | 79.0236
MBZ-4.RR.9.1 | 24312499201511 | Kulaura, Ward # 4, Magura, Monsur Road, H # 35, Md. Solu Mia | 2019-08-19 | MP1032 | 3.6 | 99 | 3.6 | 100 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6480 | 2279.9997 | 37.9313
MBZ-4.RR.10.1 | 24312629201519 | Kulaura, Ward # 4, Magura, Monsur Road, H # 143, Dipok Pal | 2019-08-19 | MP1032 | 6.5 | 101 | 6.5 | 102 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6480 | 2279.9997 | 68.4871
MBZ-4.RR.11.1 | 24312799201356 | Kulaura, Ward # 8, Kadipur, Monsur Road, Md. Rezaur Rahman | 2019-08-20 | MP1032 | 6.8 | 121 | 6.8 | 122 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6480 | 2279.9997 | 71.6481
MBZ-4.RR.12.1 | 24313329202042 | Kulaura, Ward # 3, Uttar Bazar, M. M. Shahin (Ex- MP) | 2019-08-20 | MP1032 | 10.2 | 123 | 10.2 | 124 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6456 | 2303.9997 | 107.4721
MBZ-4.RR.13.1 | 24313659202009 | Kulaura, Ward # 3, Uttar Bazar, Upzilla Parishad R/A, Mayabon (Upzilla Nirbahi Officer) | 2019-08-20 | MP1032 | 12.6 | 125 | 12.1 | 126 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6456 | 2303.9997 | 127.4914
MBZ-4.RR.14.1 | 24313669202029 | Kulaura, Ward # 3, Uttar Bazar, Upzilla Parishad R/A, Rajanigondha Abashik Bhaban | 2019-08-20 | MP1032 | 11.4 | 127 | 11.4 | 128 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6456 | 2303.9997 | 120.1159
MBZ-4.RR.14.2 | 24313669202029 | Kulaura, Ward # 3, Uttar Bazar, Upzilla Parishad R/A, Rajanigondha Abashik Bhaban | 2022-03-21 | NQ1007 | 6.5 | 56 | 6.5 | 57 | 2022-03-21 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 4560 | 2303.9997 | 53.6639
MBZ-4.RR.15.1 | 24315349202214 | Kulaura, Ward # 2, Bisrakandi, Jubel | 2019-08-20 | MP1032 | 10.9 | 129 | 10.9 | 130 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6432 | 2327.9997 | 114.8476
MBZ-4.RR.16.1 | 24320739202030 | Kulaura, Ward # 1, Sonapur, Lokman Ali | 2019-08-21 | MP1032 | 6.2 | 153 | 6.2 | 154 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6432 | 2327.9997 | 65.3262
MBZ-4.RR.17.1 | 24315869202181 | Kulaura, Ward # 1, Sonapur, Lokman Ali (Commissioner) | 2019-08-21 | MP1032 | 7 | 155 | 7 | 156 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6432 | 2327.9997 | 73.7554
MBZ-4.RR.18.1 | 24315779202165 | Kulaura, Ward # 1, Sonapur, Sultan Khan | 2019-08-21 | MP1032 | 8.5 | 157 | 8.6 | 158 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6432 | 2327.9997 | 90.6137
MBZ-4.RR.19.1 | 24315639202184 | Kulaura, Ward # 1, Sonapur, Abdul Khalek | 2019-08-21 | MP1032 | 12.2 | 159 | 12.2 | 160 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6432 | 2327.9997 | 128.5451
MBZ-4.RR.20.1 | 24315639202184 | Kulaura, Ward # 1, Sonapur, Abdul Motleb | 2019-08-21 | MP1032 | 11.9 | 161 | 11.9 | 162 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6432 | 2327.9997 | 125.3841
MBZ-4.RR.21.1 | 24315469202177 | Kulaura, Ward # 3, Uttar Bazar, Md. Shafiqur Rahman | 2019-08-21 | MP1032 | 6.6 | 163 | 6.6 | 164 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6432 | 2327.9997 | 69.5408
MBZ-4.RR.22.1 | 24315369202173 | Kulaura, Ward # 3, Uttar Bazar, Md. Yousuf Ali | 2019-08-21 | MP1032 | 6.7 | 167 | 6.7 | 168 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6432 | 2327.9997 | 70.5944
MBZ-4.RR.23.1 | 24315269202178 | Kulaura, Ward # 3, Uttar Bazar, Jamal Uddin | 2019-08-21 | MP1032 | 9.9 | 169 | 9.9 | 170 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6432 | 2327.9997 | 104.3112
MBZ-4.RR.24.1 | 24315379202161 | Kulaura, Ward # 3, Uttar Bazar, Gias Beg | 2019-08-21 | MP1032 | 4.8 | 171 | 4.8 | 172 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6432 | 2327.9997 | 50.5751
MBZ-4.RR.25.1 | 24315379202161 | Kulaura, Ward # 3, Uttar Bazar, Azad Beg | 2019-08-21 | MP1032 | 11.4 | 175 | 11.4 | 176 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6432 | 2327.9997 | 120.1159
MBZ-4.RR.26.1 | 24315439202132 | Kulaura, Ward # 3, Uttar Bazar, Abdul Kuddus | 2019-08-21 | MP1032 | 6.9 | 177 | 6.9 | 178 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6432 | 2327.9997 | 72.7017
MBZ-4.RR.27.1 | 24353399206551 | Jury, Kaminiganj Bazar, Monohor Ali Road, Motin Mia | 2019-08-22 | MP1032 | 8.5 | 199 | 8.5 | 200 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6408 | 2351.9997 | 89.5601
MBZ-4.RR.28.1 | 24353389206492 | Jury, Kaminiganj Bazar, Monohor Ali Road, Mujibur Rahman | 2019-08-22 | MP1032 | 6.7 | 201 | 6.7 | 202 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6408 | 2351.9997 | 70.5944
MBZ-4.RR.28.2 | 24353389206492 | Jury, Kaminiganj Bazar, Monohor Ali Road, Mujibur Rahman | 2022-09-25 | MN1018 | 13.3 | 11 | 13.3 | 12 | 2022-09-25 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 0 | 2351.9997 | 37.6253
MBZ-4.RR.29.1 | 24353859207096 | Jury, Bhabaniganj Bazar, High School Road, Nandalal Teli | 2019-08-22 | MP1032 | 12.8 | 203 | 12.8 | 204 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6408 | 2351.9997 | 134.867
MBZ-4.RR.30.1 | 24353719207154 | Jury, Bhabaniganj Bazar, Station Road, Bhai Bhai Tower, Faysal Ahmad | 2019-08-22 | MP1032 | 3.4 | 205 | 3.4 | 206 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6408 | 2351.9997 | 35.824
MBZ-4.RR.31.1 | 24353869207157 | Jury, Bhabaniganj Bazar, Station Road, Late Hazi Abdul Muktadir | 2019-08-22 | MP1032 | 11.8 | 207 | 11.5 | 208 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6408 | 2351.9997 | 121.1695
MBZ-4.RR.32.1 | 24354309207148 | Jury, Bhabaniganj Bazar, Station Road, Dewan Nurul Islam | 2019-08-22 | MP1032 | 11.9 | 209 | 12 | 210 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6408 | 2351.9997 | 126.4378
MBZ-4.RR.33.1 | 24373239208271 | Borolekha, Ward # 2, Pashchim Hatolia, Nurul Islam | 2019-08-24 | MP1032 | 13.6 | 225 | 13.6 | 226 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6336 | 2423.9997 | 143.2961
MBZ-4.RR.34.1 | 24392519208356 | Borolekha, Ward # 9, Sujanagar, Shahidur Rahman | 2019-08-25 | MP1032 | 5.5 | 249 | 5.5 | 250 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6312 | 2447.9997 | 57.9506
MBZ-4.RR.35.1 | 24392519208356 | Borolekha, Ward # 9, Sujanagar, Rezaur Rahman | 2019-08-25 | MP1032 | 6.2 | 251 | 6.2 | 252 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6312 | 2447.9997 | 65.3262
MBZ-4.RR.36.1 | 24392519208356 | Borolekha, Ward # 9, Sujanagar, Zahidul Islam | 2019-08-25 | MP1032 | 11.3 | 255 | 11.3 | 256 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6312 | 2447.9997 | 119.0622
MBZ-4.RR.37.1 | 24392999208359 | Borolekha, Ward # 9, Sujanagar, Hazi Mohurul Islam | 2019-08-25 | MP1032 | 12.9 | 257 | 13 | 258 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6312 | 2447.9997 | 136.9743
MBZ-4.RR.38.1 | 24393179208332 | Borolekha, Ward # 9, Sujanagar, Shaldigha, Shahan Ahmad | 2019-08-25 | MP1032 | 4.5 | 259 | 4.5 | 260 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6312 | 2447.9997 | 47.4142
MBZ-4.RR.39.1 | 24392989208332 | Borolekha, Ward # 9, Sujanagar, Shaldigha, Zahidul Islam | 2019-08-25 | MP1032 | 10.5 | 261 | 10.5 | 262 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6312 | 2447.9997 | 110.6331
MBZ-4.RR.40.1 | 24392759208292 | Borolekha, Ward # 9, Sujanagar, Shaldigha, Babul | 2019-08-25 | MP1032 | 7.4 | 263 | 7.4 | 264 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6312 | 2447.9997 | 77.97
MBZ-4.RR.41.1 | 24393119208278 | Borolekha, Ward # 9, Sujanagar, Shaldigha, Cherag Uddin | 2019-08-25 | MP1032 | 12.6 | 265 | 12.6 | 266 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6312 | 2447.9997 | 132.7597
MBZ-4.RR.42.1 | 24392919208288 | Borolekha, Ward # 9, Sujanagar, Rafinagar, Fariz Uddin | 2019-08-25 | MP1032 | 13.6 | 267 | 13.6 | 268 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6312 | 2447.9997 | 143.2961
MBZ-4.RR.43.1 | 24392729208215 | Borolekha, Ward # 9, Sujanagar, Rafinagar, Fazlu | 2019-08-25 | MP1032 | 4.3 | 269 | 4.4 | 270 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6312 | 2447.9997 | 46.3605
MBZ-4.RR.44.1 | 24392729208215 | Borolekha, Ward # 9, Sujanagar, Rafinagar, Bolon | 2019-08-25 | MP1032 | 5.1 | 271 | 5.1 | 272 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6312 | 2447.9997 | 53.7361
MBZ-4.RR.45.1 | 24393299208249 | Borolekha, Ward # 9, Sujanagar, Rafinagar, Motiur Rahman | 2019-08-25 | MP1032 | 3.1 | 273 | 3.1 | 274 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6312 | 2447.9997 | 32.6631
MBZ-4.RR.46.1 | 24394259208389 | Borolekha, Sujanagar Uttar, Hazi Bari, Sadek Hannan | 2019-08-26 | MP1032 | 3.4 | 309 | 3.4 | 310 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6312 | 2447.9997 | 35.824
MBZ-4.RR.47.1 | 24400699209044 | Borolekha, Sujanagar, Terakuri, Muhibunnesa | 2019-08-26 | MP1032 | 10.2 | 311 | 9.9 | 312 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6312 | 2447.9997 | 104.3112
MBZ-4.RR.48.1 | 24400699209044 | Borolekha, Sujanagar, Terakuri, Elais Mia | 2019-08-26 | MP1032 | 5.8 | 313 | 5.8 | 314 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6312 | 2447.9997 | 61.1116
MBZ-4.RR.49.1 | 24400169209014 | Borolekha, Sujanagar, Terakuri, Fariz Uddin | 2019-08-26 | MP1032 | 6.7 | 315 | 6.7 | 316 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6312 | 2447.9997 | 70.5944
MBZ-4.RR.50.1 | 24391199210008 | Borolekha, Dakshinvagh, Pashchim Gangkul, Abdul Sattar | 2019-08-27 | MP1032 | 4.6 | 319 | 4.6 | 320 | 2022-01-01 | [9 empty] | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0
MBZ-4.RR.51.1 | 24311459201527 | Kulaura, Uslapara, Abdur Rahaman | 2019-08-18 | MP1032 | 8.2 | 75 | 8.2 | 76 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6480 | 2279.9997 | 86.3991
MBZ-4.RR.52.1 | 24311439201515 | Kulaura, Uslapara, Ziaur Hosen | 2019-08-18 | MP1032 | 4.9 | 77 | 4.9 | 78 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6480 | 2279.9997 | 51.6288
MBZ-4.RR.53.1 | 24311439201515 | Kulaura, Uslapara, Ziaur Hosen | 2019-08-18 | MP1032 | 4.3 | 79 | 4.3 | 80 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6480 | 2279.9997 | 45.3069
MBZ-4.RR.54.1 | 24311439201515 | Kulaura, Uslapara, Ziaur Hosen | 2019-08-18 | MP1032 | 8.8 | 81 | 8.8 | 82 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6480 | 2279.9997 | 92.721
MBZ-4.RR.55.1 | 24311479201547 | Kulaura, Uslapara, H # 256 | 2019-08-18 | MP1032 | 12.1 | 83 | 12.1 | 84 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6480 | 2279.9997 | 127.4914
MBZ-4.RR.56.1 | 24312049201568 | Kulaura, Dokhinn Magura, Rahmat Manjil | 2019-08-18 | MP1032 | 16 | 85 | 16.6 | 86 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 6480 | 2279.9997 | 174.9056
MBZ-4.RR.57.1 | 24312039201576 | Kulaura, Dokhinn Magura, Sahanara | 2019-08-18 | MP1032 | 5.5 | 87 | 5.5 | 88 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6480 | 2279.9997 | 57.9506
MBZ-4.RR.58.1 | 24312679201532 | Kulaura, Magura, H# 140 | 2019-08-19 | MP1032 | 9.2 | 103 | 9.2 | 104 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6480 | 2279.9997 | 96.9356
MBZ-4.RR.59.1 | 24312679201532 | Kulaura, Magura, H # 140 | 2019-08-19 | MP1032 | 4.7 | 105 | 4.8 | 106 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6480 | 2279.9997 | 50.5751
MBZ-4.RR.60.1 | 24312969201502 | Kulaura, Magura, H # 111/01 | 2019-08-19 | MP1032 | 11.3 | 107 | 11.3 | 108 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6456 | 2303.9997 | 119.0622
MBZ-4.RR.61.1 | 24312929201486 | Kulaura, Magura, H # 101 | 2019-08-19 | MP1032 | 11.7 | 109 | 11.7 | 110 | 2022-01-01 | [9 empty] | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0
MBZ-4.RR.62.1 | 24312849201482 | Kulaura, Magura, H # 98 | 2019-08-19 | MP1032 | 3.7 | 111 | 3.7 | 112 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6456 | 2303.9997 | 38.985
MBZ-4.RR.63.1 | 24313069201487 | Kulaura, Magura, H # 108/1 | 2019-08-19 | MP1032 | 9.4 | 113 | 9.4 | 114 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6456 | 2303.9997 | 99.0429
MBZ-4.RR.64.1 | 24313129201524 | Kulaura, Magura, H # 134 | 2019-08-19 | MP1032 | 2.2 | 115 | 2.2 | 116 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6456 | 2303.9997 | 23.1803
MBZ-4.RR.65.1 | 24313529201560 | Kulaura, Magura, H # 126 | 2019-08-19 | MP1032 | 13.3 | 117 | 13.8 | 118 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6456 | 2303.9997 | 145.4034
MBZ-4.RR.66.1 | 24312529201461 | Kulaura, Sauth Magura, Monsur Road, Janani Nebas | 2019-08-19 | MP1032 | 39.1 | 119 | 39.1 | 120 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 39.1 | 39.1 | 2.346 | 2.346 | 0.0007168 | 100% | 0% | 2.346 | 2.346 | 0.0011869 | 28 | 0.047029 | 0.047029 |  | 0 | 0 | 6480 | 2279.9997 | 411.9764
MBZ-4.RR.67.1 | 24315819202235 | Kulaura, Bisrakandi, H # 45 | 2019-08-20 | MP1032 | 11.8 | 131 | 11.8 | 132 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6432 | 2327.9997 | 124.3305
MBZ-4.RR.68.1 | 24320019202240 | Kulaura, Bisrakandi, Dola Mia | 2019-08-20 | MP1032 | 5.4 | 133 | 5.4 | 134 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6432 | 2327.9997 | 56.897
MBZ-4.RR.69.1 | 24320019202240 | Kulaura, Bisrakandi, H # 26/1 | 2019-08-20 | MP1032 | 10.7 | 135 | 10.7 | 136 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6432 | 2327.9997 | 112.7403
MBZ-4.RR.70.1 | 24315959202215 | Kulaura, Bisrakandi, Hazi Mannan | 2019-08-20 | MP1032 | 2.5 | 139 | 2.5 | 140 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6432 | 2327.9997 | 26.3412
MBZ-4.RR.71.1 | 24320129202145 | Kulaura, Sonapur, Abdur Rahim | 2019-08-20 | MP1032 | 53.7 | 141 | 52.5 | 142 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 52.5 | 52.5 | 3.15 | 3.15 | 0.0007168 | 100% | 0% | 3.15 | 3.15 | 0.0011869 | 28 | 0.063147 | 0.063147 |  | 0 | 0 | 6432 | 2327.9997 | 553.1653
MBZ-4.RR.72.1 | 24320129202145 | Kulaura, Sonapur, H # 185 | 2019-08-20 | MP1032 | 6.7 | 145 | 6.7 | 146 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6432 | 2327.9997 | 70.5944
MBZ-4.RR.73.1 | 24320199202139 | Kulaura, Sonapur, H # 173 | 2019-08-20 | MP1032 | 5.2 | 147 | 5.2 | 148 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6432 | 2327.9997 | 54.7897
MBZ-4.RR.73.2 | 24320199202139 | Kulaura, Sonapur, H # 173 | 2021-02-07 | MN1032 | 4.4 | 125 | 4.4 | 126 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6432 | 2327.9997 | 46.3605
MBZ-4.RR.74.1 | 24320289202101 | Kulaura, Sonapur, H # 165 | 2019-08-20 | MP1032 | 11.2 | 149 | 11.7 | 150 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6432 | 2327.9997 | 123.2768
MBZ-4.RR.75.1 | 24320289202101 | Kulaura, Sonapur, H # 163 | 2019-08-20 | MP1032 | 19.3 | 151 | 18.7 | 152 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 6432 | 2327.9997 | 197.0322
MBZ-4.RR.76.1 | 24352799206585 | Juri, Kamanigong Bazar, Hazi Mahtab Mia | 2019-08-21 | MP1032 | 3.2 | 179 | 3.2 | 180 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6408 | 2351.9997 | 33.7167
MBZ-4.RR.77.1 | 24352799206585 | Juri, Kamanigong Bazar, Hazi Mahtab Mia | 2019-08-21 | MP1032 | 12.1 | 181 | 11.8 | 182 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6408 | 2351.9997 | 124.3305
MBZ-4.RR.78.1 | 24352799206585 | Juri, Kamanigong Bazar, Tayeb Ali | 2019-08-21 | MP1032 | 6 | 183 | 6 | 184 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6408 | 2351.9997 | 63.2189
MBZ-4.RR.79.1 | 24352889206546 | Juri, Kamanigong Bazar, Mohibor Rahman | 2019-08-21 | MP1032 | 3.5 | 185 | 3.5 | 186 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6408 | 2351.9997 | 36.8777
MBZ-4.RR.80.1 | 24352889206546 | Juri, Kamanigong Bazar, A. Kaium | 2019-08-21 | MP1032 | 24.5 | 187 | 24.5 | 188 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 6408 | 2351.9997 | 258.1438
MBZ-4.RR.81.1 | 24353159206574 | Juri, Kamanigong Bazar, Boro Mosjid Road, Halima Vhoban | 2019-08-21 | MP1032 | 5.1 | 189 | 5.1 | 190 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6408 | 2351.9997 | 53.7361
MBZ-4.RR.82.1 | 24353249207009 | Juri, Kamanigong Bazar, Boro Mosjid Road, Fazlur Rahman | 2019-08-21 | MP1032 | 5 | 193 | 5 | 194 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6408 | 2351.9997 | 52.6824
MBZ-4.RR.83.1 | 24353249207009 | Juri, Kamanigong Bazar, Boro Mosjid Road, Fazlur Rahman | 2019-08-21 | MP1032 | 10.9 | 195 | 10.9 | 196 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6408 | 2351.9997 | 114.8476
MBZ-4.RR.84.1 | 24353589207163 | Juri, Collage Road, Meher Poda Sarker | 2019-08-22 | MP1032 | 12.8 | 213 | 12.9 | 214 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6408 | 2351.9997 | 135.9206
MBZ-4.RR.85.1 | 24352829207273 | Juri, Collage Road, Adour Mia | 2019-08-22 | MP1032 | 19.8 | 215 | 19.9 | 216 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0 | 6408 | 2351.9997 | 209.676
MBZ-4.RR.86.1 | 24352829207273 | Juri, Collage Road, Adour Mia | 2019-08-22 | MP1032 | 11.7 | 217 | 11.7 | 218 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6408 | 2351.9997 | 123.2768
MBZ-4.RR.87.1 | 24352609207337 | Juri, Collage Road, Riaz Uddin | 2019-08-22 | MP1032 | 45 | 219 | 45 | 220 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 45 | 45 | 2.7 | 2.7 | 0.0007168 | 100% | 0% | 2.7 | 2.7 | 0.0011869 | 28 | 0.054126 | 0.054126 |  | 0 | 0 | 6408 | 2351.9997 | 474.1417
MBZ-4.RR.88.1 | 24351849207323 | Juri, Uttar Vobanipur, Forest Office Road, Akram Mia | 2019-08-22 | MP1032 | 9.9 | 221 | 9.7 | 222 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6408 | 2351.9997 | 102.2039
MBZ-4.RR.89.1 | 24391269208399 | Barlekha, Ajimgong Bazar, Hasem Monjil | 2019-08-24 | MP1032 | 20.9 | 227 | 21 | 228 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 21 | 21 | 1.26 | 1.26 | 0.0007168 | 100% | 0% | 1.26 | 1.26 | 0.0011869 | 28 | 0.025259 | 0.025259 |  | 0 | 0 | 6312 | 2447.9997 | 221.2661
MBZ-4.RR.90.1 | 24391269208399 | Barlekha, Ajimgong Bazar, Hasem Monjil | 2019-08-24 | MP1032 | 6.3 | 229 | 6.3 | 230 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6312 | 2447.9997 | 66.3798
MBZ-4.RR.91.1 | 24391269208399 | Barlekha, Ajimgong Bazar, Hasem Monjil | 2019-08-24 | MP1032 | 9.9 | 231 | 9.9 | 232 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6312 | 2447.9997 | 104.3112
MBZ-4.RR.92.1 | 24392019208568 | Barlekha, Borthal, Ajimgong Bazar, Nurul Haq | 2019-08-24 | MP1032 | 3.4 | 233 | 3.4 | 234 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6336 | 2423.9997 | 35.824
MBZ-4.RR.93.1 | 24391479208583 | Barlekha, Sujanagar, Borthal, Abul Kalam | 2019-08-24 | MP1032 | 6.4 | 235 | 6.4 | 236 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6336 | 2423.9997 | 67.4335
MBZ-4.RR.94.1 | 24391399208575 | Barlekha, Sujanagar, Borthal, Rahin Ahmed | 2019-08-24 | MP1032 | 3.2 | 239 | 3.2 | 240 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6336 | 2423.9997 | 33.7167
MBZ-4.RR.95.1 | 24390799208595 | Barlekha, Sujanagar, Borthal, Hazi Nekbor Ali | 2019-08-24 | MP1032 | 6.4 | 243 | 6.4 | 244 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6336 | 2423.9997 | 67.4335
MBZ-4.RR.96.1 | 24390799208595 | Barlekha, Sujanagar, Borthal, Shebul Ahmed | 2019-08-24 | MP1032 | 2.4 | 245 | 2.4 | 246 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6336 | 2423.9997 | 25.2876
MBZ-4.RR.97.1 | 24390569209007 | Barlekha, Sujanagar, Borthal, Alal | 2019-08-24 | MP1032 | 3.5 | 247 | 3.6 | 248 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6336 | 2423.9997 | 37.9313
MBZ-4.RR.98.1 | 24393779208241 | Barlekha, Rofinagar, Nurul Islam | 2019-08-25 | MP1032 | 9.7 | 275 | 9.7 | 276 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6312 | 2447.9997 | 102.2039
MBZ-4.RR.99.1 | 24393779208241 | Barlekha, Rofinagar, Nurul Islam | 2019-08-25 | MP1032 | 11.2 | 277 | 11.2 | 278 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6312 | 2447.9997 | 118.0086
MBZ-4.RR.100.1 | 24393869208237 | Barlekha, Rofinagar, Ziaur | 2019-08-25 | MP1032 | 8 | 279 | 8 | 280 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6312 | 2447.9997 | 84.2919
MBZ-4.RR.101.1 | 24310409201544 | Moulovibazar, Kulaura, Uchlapara, Near Modern Brade and Biscut Factroy, Sabaidullah | 2019-08-18 | NQ1005 | 11.7 | 60 | 11.7 | 61 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6480 | 2279.9997 | 123.2768
MBZ-4.RR.102.1 | 24310799201567 | Moulovibazar, Kulaura, Uchlapara, Surjer Hasi Clinic, Hazi Mohammad Charag Ali | 2019-08-18 | NQ1005 | 14 | 64 | 14.2 | 65 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6480 | 2279.9997 | 149.618
MBZ-4.RR.103.1 | 24312459202095 | Moulovibazar, Kulaura, Station Road, Opposite Gofur Restora, Sultan Mahmud | 2019-08-19 | NQ1005 | 7.2 | 68 | 7.2 | 69 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6456 | 2303.9997 | 75.8627
MBZ-4.RR.104.1 | 24312839202075 | Moulovibazar, Kulaura, Main Road, Al-Modina Market, Near Naborupa Fassion House | 2019-08-19 | NQ1005 | 27.8 | 70 | 27.8 | 71 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 27.8 | 27.8 | 1.668 | 1.668 | 0.0007168 | 100% | 0% | 1.668 | 1.668 | 0.0011869 | 28 | 0.033438 | 0.033438 |  | 0 | 0 | 6456 | 2303.9997 | 292.9142
MBZ-4.RR.105.1 | 24312959202111 | Moulovibazar, Kulaura, Word # 3, Formujabad Uttarbazar, H # 336, Abdul Hai | 2019-08-19 | NQ1005 | 10.7 | 72 | 10.7 | 73 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6456 | 2303.9997 | 112.7403
MBZ-4.RR.105.2 | 24312959202111 | Moulovibazar, Kulaura, Word # 3, Formujabad Uttarbazar, H # 336, Abdul Hai | 2022-09-27 | MN1018 | 14.8 | 17 | 14.8 | 18 | 2022-09-27 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 0 | 2303.9997 | 41.0143
MBZ-4.RR.106.1 | 24312999202111 | Moulovibazar, Kulaura, Word # 3, Formujabad Uttarbazar, H # 359, Babul Ahmed | 2019-08-19 | NQ1005 | 5 | 74 | 5 | 75 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6456 | 2303.9997 | 52.6824
MBZ-4.RR.107.1 | 24312899202103 | Moulovibazar, Kulaura, Formujabad Uttarbazar, Rockles Mia | 2019-08-19 | NQ1005 | 1.1 | 76 | 1.1 | 77 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6456 | 2303.9997 | 11.5901
MBZ-4.RR.108.1 | 24312899202103 | Moulovibazar, Kulaura, Formujabad Uttarbazar, Rokib Mia | 2019-08-19 | NQ1005 | 31.8 | 80 | 31.8 | 81 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 31.8 | 31.8 | 1.908 | 1.908 | 0.0007168 | 100% | 0% | 1.908 | 1.908 | 0.0011869 | 28 | 0.038249 | 0.038249 |  | 0 | 0 | 6456 | 2303.9997 | 335.0601
MBZ-4.RR.109.1 | 24312859202104 | Moulovibazar, Kulaura, Formujabad Uttarbazar, Mostofa | 2019-08-19 | NQ1005 | 7.8 | 82 | 7.8 | 83 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6456 | 2303.9997 | 82.1846
MBZ-4.RR.110.1 | 24313109202124 | Moulovibazar, Kulaura, Formujabad Uttarbazar, H # 347, Md Siraj Mia | 2019-08-19 | NQ1005 | 4.8 | 84 | 4.8 | 85 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6456 | 2303.9997 | 50.5751
MBZ-4.RR.111.1 | 24314469202275 | Moulovibazar, Kulaura, Prantik Abashik Alaka, Abdul Ahad | 2019-08-20 | NQ1005 | 12 | 110 | 11.6 | 111 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6432 | 2327.9997 | 122.2232
MBZ-4.RR.112.1 | 24314419202273 | Moulovibazar, Kulaura, Prantik Abashik Alaka, Hoque Villa, Taijul Islam | 2019-08-20 | NQ1005 | 8.3 | 112 | 8.3 | 113 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6432 | 2327.9997 | 87.4528
MBZ-4.RR.113.1 | 24314189202272 | Moulovibazar, Kulaura, Prantik Abashik Alaka, Mohammad Abdul Khalek | 2019-08-20 | NQ1005 | 8.7 | 116 | 8.7 | 117 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6432 | 2327.9997 | 91.6674
MBZ-4.RR.114.1 | 24314969202297 | Moulovibazar, Kulaura, Bhumi Office Road, Kuwaite House, Haroonur Rashid | 2019-08-20 | NQ1005 | 18.7 | 118 | 18.7 | 119 | 2022-01-01 | [9 empty] | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0
MBZ-4.RR.115.1 | 24315189202297 | Moulovibazar, Kulaura, Bhumi Office Road, Boshir Mia | 2019-08-20 | NQ1005 | 9.8 | 120 | 9.8 | 121 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6432 | 2327.9997 | 103.2575
MBZ-4.RR.116.1 | 24315059202312 | Moulovibazar, Kulaura, Kulauragram, Charag Ali | 2019-08-20 | NQ1005 | 8 | 122 | 8.1 | 123 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 1392 | 0 | 5040 | 2327.9997 | 71.7837
MBZ-4.RR.117.1 | 24315139202326 | Moulovibazar, Kulaura, Kulauragram, Gias Ahmed | 2019-08-20 | NQ1005 | 11.6 | 124 | 11.6 | 125 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6432 | 2327.9997 | 122.2232
MBZ-4.RR.118.1 | 24315419202333 | Moulovibazar, Kulaura, Kulauragram, Momtaz Mia | 2019-08-20 | NQ1005 | 10.7 | 126 | 10.5 | 127 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6432 | 2327.9997 | 110.6331
MBZ-4.RR.119.1 | 24314419202325 | Moulovibazar, Kulaura, Kulauragram, Shibir Road, Hajera Villa, H # 111 | 2019-08-21 | NQ1005 | 11.7 | 150 | 11.7 | 151 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6432 | 2327.9997 | 123.2768
MBZ-4.RR.120.1 | 24313829202277 | Moulovibazar, Kulaura, Joypasha, Taijul Islam, H # 96 | 2019-08-21 | NQ1005 | 11.7 | 152 | 11.6 | 153 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6432 | 2327.9997 | 122.2232
MBZ-4.RR.121.1 | 24313619202261 | Moulovibazar, Kulaura, Joypasha, Eklashur Rahman, H # 99 | 2019-08-21 | NQ1005 | 8.8 | 154 | 8.8 | 155 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6432 | 2327.9997 | 92.721
MBZ-4.RR.122.1 | 24313429202247 | Moulovibazar, Kulaura, Joypasha, Tarek Chowdhury, H # 122 | 2019-08-21 | NQ1005 | 4.6 | 156 | 4.7 | 157 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6432 | 2327.9997 | 49.5215
MBZ-4.RR.123.1 | 24312979202210 | Moulovibazar, Kulaura, Joypasha, Monim Chowdhury | 2019-08-21 | NQ1005 | 9.6 | 158 | 9.6 | 159 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6432 | 2327.9997 | 101.1502
MBZ-4.RR.124.1 | 24360509207136 | Moulovibazar, Zuri, Zangirai, Word # 8, Main Road, Apon Nibash, Hazi Abdus Samad | 2019-08-22 | NQ1005 | 13.2 | 176 | 13.2 | 177 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6336 | 2423.9997 | 139.0816
MBZ-4.RR.125.1 | 24360199207184 | Moulovibazar, Zuri, Horirampur, Gudam Road, Habibullah | 2019-08-22 | NQ1005 | 15.9 | 178 | 15.9 | 179 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6336 | 2423.9997 | 167.5301
MBZ-4.RR.126.1 | 24355189207131 | Moulovibazar, Zuri, Horirampur, Gudam Road, Anowar Ali | 2019-08-22 | NQ1005 | 12.8 | 180 | 12.8 | 181 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6408 | 2351.9997 | 134.867
MBZ-4.RR.127.1 | 24354999207126 | Moulovibazar, Zuri, Horirampur, Gudam Road, Mona Mia | 2019-08-22 | NQ1005 | 9 | 182 | 9 | 183 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6408 | 2351.9997 | 94.8283
MBZ-4.RR.128.1 | 24354409207097 | Moulovibazar, Zuri, Horirampur, Gudam Potti, Moyjon Chairman | 2019-08-22 | NQ1005 | 12.2 | 184 | 12.2 | 185 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6408 | 2351.9997 | 128.5451
MBZ-4.RR.129.1 | 24354619207153 | Moulovibazar, Zuri, Horirampur, Rail Station Road, Samsur Rahman | 2019-08-22 | NQ1005 | 11.1 | 186 | 11.1 | 187 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6408 | 2351.9997 | 116.9549
MBZ-4.RR.130.1 | 24354589207160 | Moulovibazar, Zuri, Horirampur, Rail Station Road, Ma Engineering Workshop | 2019-08-22 | NQ1005 | 12 | 188 | 12 | 189 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6408 | 2351.9997 | 126.4378
MBZ-4.RR.131.1 | 24375929209429 | Moulovibazar, Barolekha, Dokkhinvag, Samonbag Tea Road, Abdur Rahman Monjil | 2019-08-24 | NQ1005 | 9.6 | 199 | 9.6 | 200 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6336 | 2423.9997 | 101.1502
MBZ-4.RR.132.1 | 24375929209429 | Moulovibazar, Barolekha, Dokkhinvag, Samonbag Tea Road, Abdur Rahman Monjil | 2019-08-24 | NQ1005 | 4.6 | 202 | 4.7 | 203 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6336 | 2423.9997 | 49.5215
MBZ-4.RR.133.1 | 24380519209464 | Moulovibazar, Barolekha, Dokkhinvag, Asad Ali Road, Nurul Islam | 2019-08-24 | NQ1005 | 12.1 | 204 | 12 | 205 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6336 | 2423.9997 | 126.4378
MBZ-4.RR.134.1 | 24391769210445 | Moulovibazar, Barolekha, Dokkhinvag, Horipur, Horipur Road, Abdul Khalil | 2019-08-25 | NQ1005 | 14.8 | 226 | 14.8 | 227 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 6288 | 2471.9997 | 155.9399
MBZ-4.RR.135.1 | 24391789210449 | Moulovibazar, Barolekha, Dokkhinvag, Horipur, Horipur Road, Samsul Hoque | 2019-08-25 | NQ1005 | 12.1 | 228 | 12.1 | 229 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6288 | 2471.9997 | 127.4914
MBZ-4.RR.136.1 | 24391869210440 | Moulovibazar, Barolekha, Dokkhinvag, Horipur, Horipur Road, Amir Ali | 2019-08-25 | NQ1005 | 12.7 | 230 | 12.7 | 231 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6288 | 2471.9997 | 133.8133
MBZ-4.RR.137.1 | 24391709210465 | Moulovibazar, Barolekha, Dokkhinvag, Horipur, Horipur Road, Hazi Miajan Ali | 2019-08-25 | NQ1005 | 13.6 | 232 | 13.6 | 233 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6288 | 2471.9997 | 143.2961
MBZ-4.RR.137.2 | 24391709210465 | Moulovibazar, Barolekha, Dokkhinvag, Horipur, Horipur Road, Hazi Miajan Ali | 2021-02-04 | MN1032 | 3.9 | 119 | 3.9 | 120 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6288 | 2471.9997 | 41.0923
MBZ-4.RR.138.1 | 24391699211078 | Moulovibazar, Barolekha, Dokkhinvag, Horipur, Horipur Road, Shib Ronjon | 2019-08-25 | NQ1005 | 21.5 | 234 | 21.5 | 235 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 21.5 | 21.5 | 1.29 | 1.29 | 0.0007168 | 100% | 0% | 1.29 | 1.29 | 0.0011869 | 28 | 0.02586 | 0.02586 |  | 0 | 0 | 6288 | 2471.9997 | 226.5343
MBZ-4.RR.139.1 | 24391489211068 | Moulovibazar, Barolekha, Dokkhinvag, Horipur, Horipur Road, Subudh Chondro | 2019-08-25 | NQ1005 | 26.2 | 236 | 26.2 | 237 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 26.2 | 26.2 | 1.572 | 1.572 | 0.0007168 | 100% | 0% | 1.572 | 1.572 | 0.0011869 | 28 | 0.031513 | 0.031513 |  | 0 | 0 | 6288 | 2471.9997 | 276.0558
MBZ-4.RR.140.1 | 24413119211264 | Moulovibazar, Barolekha, Pakhiola, Rashed Kayes | 2019-08-26 | NQ1005 | 8.1 | 268 | 8.1 | 269 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6288 | 2471.9997 | 85.3455
MBZ-4.RR.141.1 | 24414849211217 | Moulovibazar, Barolekha, Pakhiola, Dimai Road, Hazi Muffazzil Ali Villa | 2019-08-26 | NQ1005 | 12.8 | 270 | 12.8 | 271 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6288 | 2471.9997 | 134.867
MBZ-4.RR.142.1 | 24414399211434 | Moulovibazar, Barolekha, Pakhiola, Dimai Road, Babul | 2019-08-26 | NQ1005 | 12.3 | 272 | 12.4 | 273 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6288 | 2471.9997 | 130.6524
MBZ-4.RR.143.1 | 24421479211431 | Moulovibazar, Barolekha, Hatbond R/A, Moslemuddin | 2019-08-27 | NQ1005 | 5.3 | 282 | 5.3 | 283 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6264 | 2495.9997 | 55.8434
MBZ-4.RR.144.1 | 24421659211433 | Moulovibazar, Barolekha, Hatbond R/A, Jagodish Pal | 2019-08-27 | NQ1005 | 3.5 | 284 | 3.5 | 285 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6264 | 2495.9997 | 36.8777
MBZ-4.RR.145.1 | 24444029209505 | Barolekha, Surikandi, Nir Jungle, Changram Road, Hazi Nur Uddin | 2019-08-28 | NQ1005 | 4.6 | 300 | 4.6 | 301 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6264 | 2495.9997 | 48.4678
MBZ-4.RR.146.1 | 24442819209522 | Barolekha, Surikandi, Nir Jungle, Changram Road, Chulupara, Shad Uddin | 2019-08-28 | NQ1005 | 21.9 | 302 | 21.7 | 303 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 6264 | 2495.9997 | 228.6416
MBZ-4.RR.147.1 | 24320739202403 | Moulovibazar, North Kulaura, Bijoy Road, Shajahan Ali | 2019-08-29 | NQ1005 | 10.9 | 310 | 10.9 | 311 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6432 | 2327.9997 | 114.8476
MBZ-4.RR.148.1 | 24320869202461 | Moulovibazar, North Kulaura, Bijoy Road, Foysal Ahmed | 2019-08-29 | NQ1005 | 15.2 | 312 | 15.4 | 313 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6432 | 2327.9997 | 162.2618
MBZ-4.RR.151.1 | 24303729201530 | Kulaura, School Chumohona, Kachim Nagar, College Road, Sazzad Mia | 2019-08-18 | NQ1005 | 11.5 | 50 | 11.6 | 51 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6480 | 2279.9997 | 122.2232
MBZ-4.RR.152.1 | 24303729201530 | Kulaura, School Chumohona, Kachim Nagar, College Road, Abdul Malek | 2019-08-18 | NQ1005 | 7.9 | 52 | 7.9 | 53 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6480 | 2279.9997 | 83.2382
MBZ-4.RR.153.1 | 24303479201530 | Kulaura, School Chumohona, Kachim Nagar, College Road, Sahed Mia | 2019-08-18 | NQ1005 | 15.3 | 54 | 15.3 | 55 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6480 | 2279.9997 | 161.2082
MBZ-4.RR.154.1 | 24303409202083 | Kulaura, Loskorpur, Word # 7, H # 114, Habib Ullah | 2019-08-18 | NQ1005 | 6.4 | 56 | 6.4 | 57 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6480 | 2279.9997 | 67.4335
MBZ-4.RR.155.1 | 24303409202083 | Kulaura, Loskorpur, Word # 7, H # 114, Habib Ullah | 2019-08-18 | NQ1005 | 9.5 | 58 | 9.4 | 59 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6480 | 2279.9997 | 99.0429
MBZ-4.RR.156.1 | 24313869202179 | Kulaura, Uttor Bazar, Hospital Road, Babul Mia | 2019-08-19 | NQ1005 | 6.7 | 88 | 6.7 | 89 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6456 | 2303.9997 | 70.5944
MBZ-4.RR.157.1 | 24314249202160 | Kulaura, Uttor Bazar, Hospital Road, Upojila Helth Complex | 2019-08-19 | NQ1005 | 13.2 | 90 | 12.7 | 91 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6456 | 2303.9997 | 133.8133
MBZ-4.RR.158.1 | 24314249202160 | Kulaura, Uttor Bazar, Hospital Road, Upojila Helth Complex | 2019-08-19 | NQ1005 | 6.4 | 92 | 6.4 | 93 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6456 | 2303.9997 | 67.4335
MBZ-4.RR.158.2 | 24314249202160 | Kulaura, Uttor Bazar, Hospital Road, Upojila Helth Complex | 2021-02-07 | LU1001 | 35.6 | 160 | 35.6 | 161 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 35.6 | 35.6 | 2.136 | 2.136 | 0.0007168 | 100% | 0% | 2.136 | 2.136 | 0.0011869 | 28 | 0.042819 | 0.042819 |  | 0 | 0 | 6456 | 2303.9997 | 375.0987
MBZ-4.RR.159.1 | 24314309202243 | Kulaura, Uttor Bazar, Islambag R/A, Word # 2, Abdul Kadir | 2019-08-19 | NQ1005 | 13.4 | 94 | 13.4 | 95 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6456 | 2303.9997 | 141.1888
MBZ-4.RR.160.1 | 24314309202243 | Kulaura, Uttor Bazar, Islambag R/A, Word # 2, Abdul Kadir | 2019-08-19 | NQ1005 | 3.9 | 98 | 3.9 | 99 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6456 | 2303.9997 | 41.0923
MBZ-4.RR.161.1 | 24314159202253 | Kulaura, Uttor Bazar, Islambag R/A, Word # 2, H # 148, Lebu Mia | 2019-08-19 | NQ1005 | 5 | 100 | 5.2 | 101 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6456 | 2303.9997 | 54.7897
MBZ-4.RR.162.1 | 24314129202245 | Kulaura, Uttor Bazar, Islambag R/A, Word # 2, Hazi Bari | 2019-08-19 | NQ1005 | 16.5 | 102 | 16.5 | 103 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 6456 | 2303.9997 | 173.8519
MBZ-4.RR.162.2 | 24314129202245 | Kulaura, Uttor Bazar, Islambag R/A, Word # 2, Hazi Bari | 2019-08-19 | NQ1005 | 3 | 104 | 3 | 105 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6456 | 2303.9997 | 31.6094
MBZ-4.RR.163.1 | 24314009202244 | Kulaura, Uttor Bazar, Islambag R/A, Word # 2, Abdul Kadir | 2019-08-19 | NQ1005 | 11.7 | 106 | 11.7 | 107 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6456 | 2303.9997 | 123.2768
MBZ-4.RR.164.1 | 24314009202244 | Kulaura, Uttor Bazar, Islambag R/A, Word # 2, Mijanur Rahman | 2019-08-19 | NQ1005 | 2.8 | 108 | 2.8 | 109 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6456 | 2303.9997 | 29.5021
MBZ-4.RR.165.1 | 24314819202400 | Kulaura, Vumi Office Road, Word # 2, H # 78/1, Ohidul Islam | 2019-08-20 | NQ1005 | 13.7 | 130 | 13.8 | 131 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6432 | 2327.9997 | 145.4034
MBZ-4.RR.166.1 | 24315189202410 | Kulaura, Vumi Office Road, Word # 2, Hafca Begom | 2019-08-20 | NQ1005 | 6.4 | 132 | 6.4 | 133 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6432 | 2327.9997 | 67.4335
MBZ-4.RR.167.1 | 24315759202367 | Kulaura, Bijoya Road, Word # 2, Nasir Ali | 2019-08-20 | NQ1005 | 12 | 134 | 12 | 135 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6432 | 2327.9997 | 126.4378
MBZ-4.RR.167.2 | 24315759202367 | Kulaura, Bijoya Road, Word # 2, Nasir Ali | 2022-09-26 | MN1018 | 8.8 | 15 | 8.8 | 16 | 2022-09-26 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 0 | 2327.9997 | 24.6409
MBZ-4.RR.168.1 | 24315969202364 | Kulaura, Bijoya Road, Word # 2, Abdul Lotib Bari, Abdul Lotib | 2019-08-20 | NQ1005 | 5.9 | 136 | 5.9 | 137 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6432 | 2327.9997 | 62.1652
MBZ-4.RR.169.1 | 24320329202378 | Kulaura, Bijoya Road, Joysondi, Word # 2, Md.Sowkot Ali | 2019-08-20 | NQ1005 | 8.9 | 138 | 8.9 | 139 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6432 | 2327.9997 | 93.7747
MBZ-4.RR.170.1 | 24320329202378 | Kulaura, Bijoya Road, Joysondi, Word # 2, Md.Blue | 2019-08-20 | NQ1005 | 4 | 142 | 4 | 143 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6432 | 2327.9997 | 42.1459
MBZ-4.RR.171.1 | 24315989202300 | Kulaura, Bijoya Road, Word # 2, Hazi Kifat Ullah | 2019-08-20 | NQ1005 | 12.4 | 144 | 12.4 | 145 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6432 | 2327.9997 | 130.6524
MBZ-4.RR.172.1 | 24315799202259 | kulaura, Kulaura Gram, Word # 3, Somir Uddin | 2019-08-20 | NQ1005 | 8.3 | 146 | 8.3 | 147 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6432 | 2327.9997 | 87.4528
MBZ-4.RR.173.1 | 24315669202275 | kulaura, Kulaura Gram, Word # 3, Somir Uddin | 2019-08-20 | NQ1005 | 3.2 | 148 | 3.2 | 149 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6432 | 2327.9997 | 33.7167
MBZ-4.RR.174.1 | 24354319206421 | Juri, Kulaura Road, Upojila Chattor, Word # 5, Rashed Alam | 2019-08-21 | NQ1005 | 24.4 | 160 | 23.7 | 161 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 23.7 | 23.7 | 1.422 | 1.422 | 0.0007168 | 100% | 0% | 1.422 | 1.422 | 0.0011869 | 28 | 0.028506 | 0.028506 |  | 0 | 0 | 6408 | 2351.9997 | 249.7146
MBZ-4.RR.174.2 | 24354319206421 | Juri, Kulaura Road, Upojila Chattor, Word # 5, Rashed Alam | 2021-02-06 | NQ1007 | 1.8 | 157 | 1.7 | 158 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6408 | 2351.9997 | 17.912
MBZ-4.RR.175.1 | 24354319206421 | Juri, Kulaura Road, Upojila Chattor, Word # 5, Rashed Alam | 2019-08-21 | NQ1005 | 3.8 | 162 | 3.8 | 163 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6408 | 2351.9997 | 40.0386
MBZ-4.RR.176.1 | 24354319206421 | Juri, Kulaura Road, Upojila Chattor, Word # 5, Rashed Alam | 2019-08-21 | NQ1005 | 6.9 | 164 | 6.9 | 165 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6408 | 2351.9997 | 72.7017
MBZ-4.RR.177.1 | 24355229206459 | Juri, Kulaura Road, Jangiri, Word # 8, Abdul Ohaed | 2019-08-21 | NQ1005 | 6.6 | 166 | 6.6 | 167 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6336 | 2423.9997 | 69.5408
MBZ-4.RR.178.1 | 24355279206489 | Juri, Kulaura Road, Jangiri, Word # 8, Asoddor | 2019-08-21 | NQ1005 | 4.6 | 168 | 4.6 | 169 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6336 | 2423.9997 | 48.4678
MBZ-4.RR.179.1 | 24355679206584 | Juri, Borolekha Road, Jangiri, Word # 8, Abdul Barek | 2019-08-21 | NQ1005 | 3.2 | 170 | 3.2 | 171 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6336 | 2423.9997 | 33.7167
MBZ-4.RR.180.1 | 24355959207042 | Juri, Borolekha Road, Jangiri, Word # 8, Mosarof Hossen | 2019-08-21 | NQ1005 | 12.6 | 172 | 12.6 | 173 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6336 | 2423.9997 | 132.7597
MBZ-4.RR.181.1 | 24360109207052 | Juri, Borolekha Road, Jangiri, Word # 8, Fojila Khatun | 2019-08-21 | NQ1005 | 8 | 174 | 8 | 175 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6336 | 2423.9997 | 84.2919
MBZ-4.RR.182.1 | 24360529207233 | Juri, Horirampur, Station Road, Word # 5, Nihir Ronjon Dotto | 2019-08-22 | NQ1005 | 4.8 | 190 | 4.8 | 191 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6336 | 2423.9997 | 50.5751
MBZ-4.RR.183.1 | 24351589207499 | Juri, Uttor Vobanipur, Teyobunessa Khanom Govt College, Bodrul Islam | 2019-08-22 | NQ1005 | 11.6 | 192 | 11.6 | 193 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6408 | 2351.9997 | 122.2232
MBZ-4.RR.183.2 | 24351589207499 | Juri, Uttor Vobanipur, Teyobunessa Khanom Govt College, Bodrul Islam | 2022-09-25 | MN1018 | 14.4 | 9 | 14.4 | 10 | 2022-09-25 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 0 | 2351.9997 | 40.7372
MBZ-4.RR.184.1 | 24351179207507 | Juri, Uttor Vobanipur, Teyobunessa Khanom Govt College, Mojor Alli | 2019-08-22 | NQ1005 | 11.9 | 194 | 11.9 | 195 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6408 | 2351.9997 | 125.3841
MBZ-4.RR.185.1 | 24351179207507 | Juri, Uttor Vobanipur, Teyobunessa Khanom Govt College, Kona Mia | 2019-08-22 | NQ1005 | 8 | 197 | 8 | 198 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6408 | 2351.9997 | 84.2919
MBZ-4.RR.185.2 | 24351179207507 | Juri, Uttor Vobanipur, Teyobunessa Khanom Govt College, Kona Mia | 2021-02-06 | NQ1007 | 4.9 | 152 | 4.7 | 153 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6408 | 2351.9997 | 49.5215
MBZ-4.RR.186.1 | 24380089210027 | Borolekha, Dokkhin Bag, Word # 1, Siraj Uddin | 2019-08-24 | NQ1005 | 10.6 | 206 | 10.6 | 207 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6336 | 2423.9997 | 111.6867
MBZ-4.RR.187.1 | 24380089210027 | Borolekha, Dokkhin Bag, 1 No Road, Word # 1, Abdul Malek | 2019-08-24 | NQ1005 | 8.1 | 208 | 8.1 | 209 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6336 | 2423.9997 | 85.3455
MBZ-4.RR.187.2 | 24380089210027 | Borolekha, Dokkhin Bag, 1 No Road, Word # 1, Abdul Malek | 2019-08-24 | NQ1005 | 6.2 | 210 | 6.2 | 211 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6336 | 2423.9997 | 65.3262
MBZ-4.RR.188.1 | 24390699210090 | Borolekha, Horipur Road, Ghangkul, Word # 9, Siraj Uddin | 2019-08-24 | NQ1005 | 11.8 | 212 | 11.5 | 213 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6288 | 2471.9997 | 121.1695
MBZ-4.RR.189.1 | 24391119210165 | Borolekha, Horipur Road, Ghangkul, Word # 9, Misbah Uddin | 2019-08-24 | NQ1005 | 7 | 214 | 7 | 215 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6288 | 2471.9997 | 73.7554
MBZ-4.RR.190.1 | 24391119210165 | Borolekha, Horipur Road, Ghangkul, Word # 9, Misbah Uddin | 2019-08-24 | NQ1005 | 4.5 | 216 | 4.5 | 217 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6288 | 2471.9997 | 47.4142
MBZ-4.RR.191.1 | 24391539210147 | Borolekha, Horipur Road, Ghangkul, Word # 9, Naz Chowdhury | 2019-08-24 | NQ1005 | 5.4 | 218 | 5.4 | 219 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6288 | 2471.9997 | 56.897
MBZ-4.RR.192.1 | 24391349210193 | Borolekha, Horipur Road, Ghangkul, Word # 9, Mostak Ahmad | 2019-08-24 | NQ1005 | 12.2 | 220 | 12.2 | 221 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6288 | 2471.9997 | 128.5451
MBZ-4.RR.192.2 | 24391349210193 | Borolekha, Horipur Road, Ghangkul, Word # 9, Mostak Ahmad | 2022-03-12 | NQ1007 | 5.5 | 46 | 5.5 | 47 | 2022-03-12 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 4608 | 2471.9997 | 46.8368
MBZ-4.RR.193.1 | 24391679210247 | Borolekha, Horipur Road, Ghangkul, Word # 9, Jakaria | 2019-08-24 | NQ1005 | 3.7 | 222 | 3.7 | 223 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6288 | 2471.9997 | 38.985
MBZ-4.RR.194.1 | 24391539210302 | Borolekha, Horipur Road, Ghangkul, Word # 9, Hajera Begom | 2019-08-24 | NQ1005 | 12.8 | 224 | 12.8 | 225 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6288 | 2471.9997 | 134.867
MBZ-4.RR.195.1 | 24411739210571 | Borolekha, Panidar, Word # 6, H # 234, Jalal Uddin | 2019-08-25 | NQ1005 | 12.7 | 238 | 12.7 | 239 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6288 | 2471.9997 | 133.8133
MBZ-4.RR.196.1 | 24412409211030 | Borolekha, Panidar, Word # 6, Cort Chattar, Samsul Haque | 2019-08-25 | NQ1005 | 3 | 240 | 3 | 241 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6288 | 2471.9997 | 31.6094
MBZ-4.RR.197.1 | 24412409211030 | Borolekha, Panidar, Word # 6, Cort Chattar, A.K.M.Helal | 2019-08-25 | NQ1005 | 8.1 | 242 | 8.1 | 243 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6288 | 2471.9997 | 85.3455
MBZ-4.RR.198.1 | 24413809211050 | Borolekha, Panidar, Upojila Helth Complex | 2019-08-25 | NQ1005 | 3.1 | 246 | 3.1 | 247 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6288 | 2471.9997 | 32.6631
MBZ-4.RR.199.1 | 24413809211050 | Borolekha, Panidar, Upojila Helth Complex | 2019-08-25 | NQ1005 | 14.3 | 248 | 13.5 | 249 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6288 | 2471.9997 | 142.2425
MBZ-4.RR.200.1 | 24414769211115 | Borolekha, Pakhiala, Thana Road, Word # 7, Haric Alli | 2019-08-25 | NQ1005 | 9.8 | 250 | 9.8 | 251 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6288 | 2471.9997 | 103.2575
MBZ-4.RR.201.1 | 24305079201419 | Kulaura, School Chowmohona, Ward # 8, H # 324, Rafik Ahmed Khan | 2019-08-18 | NQ1009 | 4.9 | 30 | 4.9 | 31 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6480 | 2279.9997 | 51.6288
MBZ-4.RR.202.1 | 24305079201419 | Kulaura, School Chowmohona, Ward # 8, H # 324, Samsul Islam Khan | 2019-08-18 | NQ1009 | 9.7 | 32 | 9.7 | 33 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6480 | 2279.9997 | 102.2039
MBZ-4.RR.203.1 | 24305079201419 | Kulaura, School Chowmohona, Ward # 8, H # 324, Khosru Jaman Khan | 2019-08-18 | NQ1009 | 7.5 | 34 | 7.5 | 35 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6480 | 2279.9997 | 79.0236
MBZ-4.RR.204.1 | 24305249201424 | Kulaura, Ward # 8, Ushlapara, Anayet Khan | 2019-08-18 | NQ1009 | 10.8 | 36 | 10.8 | 37 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6480 | 2279.9997 | 113.794
MBZ-4.RR.205.1 | 24305249201424 | Kulaura, Ward # 8, Ushlapara, Ustar Khan House | 2019-08-18 | NQ1009 | 12.3 | 38 | 12.3 | 39 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6480 | 2279.9997 | 129.5987
MBZ-4.RR.206.1 | 24311309201590 | Kulaura, Ward # 5,Ushlapara, Shofikur Rahman | 2019-08-19 | NQ1009 | 5.4 | 40 | 5.4 | 41 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6456 | 2303.9997 | 56.897
MBZ-4.RR.207.1 | 24311309201590 | Kulaura, Ward # 5,Ushlapara, Abdul Motin | 2019-08-19 | NQ1009 | 2.8 | 42 | 2.8 | 43 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6456 | 2303.9997 | 29.5021
MBZ-4.RR.208.1 | 24311659202002 | Kulaura, Ward # 5,Ushlapara, Shunil Chandra Dey | 2019-08-19 | NQ1009 | 6.2 | 44 | 6.2 | 45 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6456 | 2303.9997 | 65.3262
MBZ-4.RR.209.1 | 24312429201587 | Kulaura, Ward # 5, Dokhinbazar, Munsur Road, A.Kayom | 2019-08-19 | NQ1009 | 5.6 | 46 | 5.6 | 47 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6456 | 2303.9997 | 59.0043
MBZ-4.RR.210.1 | 24312579201575 | Kulaura, Ward # 5, Dokhinbazar, Magura, Munsur | 2019-08-19 | NQ1009 | 6.4 | 48 | 6.4 | 49 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6456 | 2303.9997 | 67.4335
MBZ-4.RR.211.1 | 24312839201548 | Kulaura, Ward # 5, Dokhinbazar, Magura, A. Hakim (Hakim Villa) | 2019-08-19 | NQ1009 | 6.5 | 50 | 6.5 | 51 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6456 | 2303.9997 | 68.4871
MBZ-4.RR.212.1 | 24312929201586 | Kulaura, Ward # 5, Magura, Adv.Anowara Akter | 2019-08-19 | NQ1009 | 12.4 | 52 | 12.4 | 53 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6456 | 2303.9997 | 130.6524
MBZ-4.RR.212.2 | 24312929201586 | Kulaura, Ward # 5, Magura, Adv.Anowara Akter | 2021-09-13 | MN1018 | 5.7 | 22 | 5.7 | 23 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6456 | 2303.9997 | 60.0579
MBZ-4.RR.213.1 | 24313009201588 | Kulaura, Ward # 5, Magura, H # 7, Masuda Villa | 2019-08-19 | NQ1009 | 37.7 | 54 | 37.7 | 55 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 37.7 | 37.7 | 2.262 | 2.262 | 0.0007168 | 100% | 0% | 2.262 | 2.262 | 0.0011869 | 28 | 0.045345 | 0.045345 |  | 0 | 0 | 6456 | 2303.9997 | 397.2253
MBZ-4.RR.214.1 | 24313989201583 | Kulaura, Ward # 4, Sadekpur Road, Akter Ahmed Chowdhury | 2019-08-20 | NQ1009 | 6 | 85 | 6 | 86 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6456 | 2303.9997 | 63.2189
MBZ-4.RR.215.1 | 24314029201576 | Kulaura, Ward # 4, Sadekpur Road, Islam Monjil - 1 | 2019-08-20 | NQ1009 | 4.3 | 87 | 4.3 | 88 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6456 | 2303.9997 | 45.3069
MBZ-4.RR.216.1 | 24314059201570 | Kulaura, Ward # 4, Sadekpur Road, Hazi Abdul Muktadir (Juber) | 2019-08-20 | NQ1009 | 4 | 89 | 4 | 90 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6456 | 2303.9997 | 42.1459
MBZ-4.RR.217.1 | 24314069201548 | Kulaura, Ward # 4, Sadekpur Road, Iqbal House | 2019-08-20 | NQ1009 | 3.8 | 91 | 3.8 | 92 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6456 | 2303.9997 | 40.0386
MBZ-4.RR.218.1 | 24314269201545 | Kulaura, Ward # 1, Sadekpur Road, Yousuf Monjil, Md. Ibrahim | 2019-08-20 | NQ1009 | 4.1 | 93 | 4.1 | 94 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6456 | 2303.9997 | 43.1996
MBZ-4.RR.219.1 | 24313119202067 | Kulaura, Ward # 3, Uttorbazar, Shahjalal Market, Motiur Rahman | 2019-08-20 | NQ1009 | 5.6 | 95 | 5.6 | 96 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6456 | 2303.9997 | 59.0043
MBZ-4.RR.220.1 | 24315879201566 | Kulaura, Ward # 1, Sonapur, Kuddus Ali | 2019-08-21 | NQ1009 | 11.3 | 97 | 11.3 | 98 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6432 | 2327.9997 | 119.0622
MBZ-4.RR.221.1 | 24320109201556 | Kulaura, Ward # 1, Sonapur, Khanom Villa | 2019-08-21 | NQ1009 | 4.6 | 99 | 4.5 | 100 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6432 | 2327.9997 | 47.4142
MBZ-4.RR.222.1 | 24320179201535 | Kulaura, Ward # 1, Sonapur, Tara mia | 2019-08-21 | NQ1009 | 5.3 | 101 | 5 | 102 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6432 | 2327.9997 | 52.6824
MBZ-4.RR.223.1 | 24320179201508 | Kulaura, Ward # 1, Sadekpur, Maya Monjil | 2019-08-21 | NQ1009 | 7.8 | 103 | 7.8 | 104 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6432 | 2327.9997 | 82.1846
MBZ-4.RR.223.2 | 24320179201508 | Kulaura, Ward # 1, Sadekpur, Maya Monjil | 2021-09-12 | MN1018 | 7.8 | 20 | 7.8 | 21 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6432 | 2327.9997 | 82.1846
MBZ-4.RR.224.1 | 24320179201508 | Kulaura, Ward # 1, Sadekpur, Lutfor Rahman | 2019-08-21 | NQ1009 | 10 | 105 | 10 | 106 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6432 | 2327.9997 | 105.3648
MBZ-4.RR.225.1 | 24320299201495 | Kulaura, Ward # 1, Sadekpur, Shamima Akter | 2019-08-21 | NQ1009 | 10.8 | 107 | 10.8 | 108 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6432 | 2327.9997 | 113.794
MBZ-4.RR.226.1 | 24320489201462 | Kulaura, Ward # 1, Sadekpur, Khondoker Mossabbir Ali | 2019-08-21 | NQ1009 | 10.4 | 109 | 10.4 | 110 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6432 | 2327.9997 | 109.5794
MBZ-4.RR.227.1 | 24320359201457 | Kulaura, Ward # 1, Sadekpur, Khondoker Abdul Kadir | 2019-08-21 | NQ1009 | 3.7 | 111 | 3.7 | 112 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6432 | 2327.9997 | 38.985
MBZ-4.RR.227.2 | 24320359201457 | Kulaura, Ward # 1, Sadekpur, Khondoker Abdul Kadir | 2021-02-07 | MN1032 | 3.4 | 123 | 3.4 | 124 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6432 | 2327.9997 | 35.824
MBZ-4.RR.228.1 | 24352499207060 | Juri, North Vobanipur, Indro Mohon Devnath | 2019-08-22 | NQ1009 | 12.7 | 127 | 12.7 | 128 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6408 | 2351.9997 | 133.8133
MBZ-4.RR.229.1 | 24352559207064 | Juri, North Vobanipur, Jogodis Devnath | 2019-08-22 | NQ1009 | 10.3 | 129 | 10.3 | 130 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6408 | 2351.9997 | 108.5258
MBZ-4.RR.230.1 | 24352559207064 | Juri, North Vobanipur, Anando Vabon | 2019-08-22 | NQ1009 | 13.3 | 131 | 13.3 | 132 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6408 | 2351.9997 | 140.1352
MBZ-4.RR.231.1 | 24352559207064 | Juri, North Vobanipur, Shodoy Day | 2019-08-22 | NQ1009 | 5.8 | 133 | 5.8 | 134 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6408 | 2351.9997 | 61.1116
MBZ-4.RR.232.1 | 24352559207064 | Juri, North Vobanipur, Ronjit Dey | 2019-08-22 | NQ1009 | 10.2 | 135 | 10.2 | 136 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6408 | 2351.9997 | 107.4721
MBZ-4.RR.233.1 | 24352819207103 | Juri, North Vobanipur, Vobanipur Road, Shamol Ghosh | 2019-08-22 | NQ1009 | 9.5 | 137 | 9.5 | 138 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6408 | 2351.9997 | 100.0966
MBZ-4.RR.234.1 | 24352639207107 | Juri, North Vobanipur, Vobanipur Road, Dilip Modok | 2019-08-22 | NQ1009 | 6.2 | 140 | 6.2 | 141 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6408 | 2351.9997 | 65.3262
MBZ-4.RR.235.1 | 24352409207134 | Juri, North Vobanipur, Vobanipur Road, Hazi Abdul Hannan | 2019-08-22 | NQ1009 | 1.4 | 142 | 1.5 | 143 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6408 | 2351.9997 | 15.8047
MBZ-4.RR.236.1 | 24351949207201 | Juri, North Vobanipur, Vobanipur Road, Mir Dotto | 2019-08-22 | NQ1009 | 9.3 | 144 | 9.3 | 145 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6408 | 2351.9997 | 97.9893
MBZ-4.RR.237.1 | 24352779207222 | Juri, North Vobanipur, Collage Road, Sushen Das | 2019-08-22 | NQ1009 | 1.8 | 150 | 1.8 | 151 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6408 | 2351.9997 | 18.9657
MBZ-4.RR.238.1 | 24374689209076 | Borolekha, Shoforpur, Khaled Ahmed | 2019-08-24 | NQ1009 | 13.7 | 164 | 13.7 | 165 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6336 | 2423.9997 | 144.3498
MBZ-4.RR.239.1 | 24374689209076 | Borolekha, Shoforpur, Abdur Rouf | 2019-08-24 | NQ1009 | 11.2 | 166 | 11 | 167 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6336 | 2423.9997 | 115.9013
MBZ-4.RR.240.1 | 24374519209088 | Borolekha, Shoforpur, Mohibur Rahman | 2019-08-24 | NQ1009 | 3.5 | 168 | 3.5 | 169 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6336 | 2423.9997 | 36.8777
MBZ-4.RR.241.1 | 24381319209344 | Borolekha, Dokhinvag, Opposite of Dokhinvag Primary School, johour Uddin | 2019-08-24 | NQ1009 | 11.5 | 170 | 11.5 | 171 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6288 | 2471.9997 | 121.1695
MBZ-4.RR.242.1 | 24381319209344 | Borolekha, Dokhinvag, Opposite of Dokhinvag Primary School, Islam Uddin | 2019-08-24 | NQ1009 | 9 | 172 | 9 | 173 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6288 | 2471.9997 | 94.8283
MBZ-4.RR.242.2 | 24381319209344 | Borolekha, Dokhinvag, Opposite of Dokhinvag Primary School, Islam Uddin | 2022-03-12 | NQ1007 | 8.7 | 44 | 8.7 | 45 | 2022-03-12 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 4608 | 2471.9997 | 74.0873
MBZ-4.RR.243.1 | 24400049210215 | Borlekha, Madhobgul, Main Road, Abdus Shohid | 2019-08-25 | NQ1009 | 9.4 | 194 | 9.4 | 195 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6288 | 2471.9997 | 99.0429
MBZ-4.RR.244.1 | 24400129210246 | Borlekha, Dokhin Kathaltoli, Ward # 5, Helal Ahmed | 2019-08-25 | NQ1009 | 11.5 | 196 | 11.5 | 197 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6288 | 2471.9997 | 121.1695
MBZ-4.RR.245.1 | 24401459210269 | Borlekha, Dokhin Kathaltoli, Ward # 5, Kutub Uddin | 2019-08-25 | NQ1009 | 4.4 | 198 | 4.4 | 199 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6288 | 2471.9997 | 46.3605
MBZ-4.RR.245.2 | 24401459210269 | Borlekha, Dokhin Kathaltoli, Ward # 5, Kutub Uddin | 2021-02-04 | LU1001 | 6.3 | 152 | 6.3 | 153 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6288 | 2471.9997 | 66.3798
MBZ-4.RR.246.1 | 24401459210269 | Borlekha, Dokhin Kathaltoli, Ward # 5, Jamal Uddin | 2019-08-25 | NQ1009 | 6.2 | 200 | 6.2 | 201 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6288 | 2471.9997 | 65.3262
MBZ-4.RR.247.1 | 24401459210269 | Borlekha, Dokhin Kathaltoli, Ward # 5, Sayed Ahmed Hosen | 2019-08-25 | NQ1009 | 10.5 | 202 | 10.5 | 203 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6288 | 2471.9997 | 110.6331
MBZ-4.RR.248.1 | 24401529210286 | Borlekha, Dokhin Kathaltoli, Ward # 5, Md. Belayet | 2019-08-25 | NQ1009 | 10.7 | 204 | 10.7 | 205 | 2022-01-01 | [9 empty] | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0
MBZ-4.RR.249.1 | 24401529210286 | Borlekha, Dokhin Kathaltoli, Ward # 5, Md. Mesalet | 2019-08-25 | NQ1009 | 10.8 | 206 | 10.2 | 207 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6288 | 2471.9997 | 107.4721
MBZ-4.RR.250.1 | 24402149210288 | Borlekha, Kathaltolibazar, Malek Hazi | 2019-08-25 | NQ1009 | 58.2 | 208 | 58.3 | 209 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 58.3 | 58.3 | 3.498 | 3.498 | 0.0007168 | 100% | 0% | 3.498 | 3.498 | 0.0011869 | 28 | 0.070123 | 0.070123 |  | 0 | 0 | 6288 | 2471.9997 | 614.2769
MBZ-4.RR.251.1 | 24304509201159 | Kulauara, Brahman Bazar Road, Chatolgoan, Abu Taleb Mukul | 2019-08-18 | NQ1009 | 10.7 | 22 | 10.7 | 23 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6480 | 2279.9997 | 112.7403
MBZ-4.RR.252.1 | 24304049201268 | Kulauara, Brahman Bazar Road, Chatolgoan, Masud Ahmed (Engineer) | 2019-08-18 | NQ1009 | 5.6 | 24 | 5.6 | 25 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6480 | 2279.9997 | 59.0043
MBZ-4.RR.253.1 | 24304049201268 | Kulauara, Brahman Bazar Road, Chatolgoan, Lili Begum (Ripon) | 2019-08-18 | NQ1009 | 5 | 26 | 5 | 27 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6480 | 2279.9997 | 52.6824
MBZ-4.RR.254.1 | 24304549201349 | Kulauara, Brahman Bazar Road, Chatolgoan, Mamoni Auto, Mustak | 2019-08-18 | NQ1009 | 7 | 28 | 7 | 29 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6480 | 2279.9997 | 73.7554
MBZ-4.RR.255.1 | 24313269201583 | Kulauara, North Magura, Abdul Jabbar | 2019-08-19 | NQ1009 | 4.8 | 57 | 4.8 | 58 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6456 | 2303.9997 | 50.5751
MBZ-4.RR.256.1 | 24313259202017 | Kulauara, North Magura, Jabed | 2019-08-19 | NQ1009 | 11.3 | 61 | 11.3 | 62 | 2022-01-01 | [9 empty] | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0
MBZ-4.RR.257.1 | 24313209202034 | Kulauara, Magura, Thana Road, Rezia Villa, Ali Karim | 2019-08-19 | NQ1009 | 10.7 | 63 | 10.7 | 64 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6456 | 2303.9997 | 112.7403
MBZ-4.RR.258.1 | 24313069202043 | Kulauara, Uttar Bazar, Thana Road, Abdul Hai | 2019-08-19 | NQ1009 | 1.5 | 65 | 1.5 | 66 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6456 | 2303.9997 | 15.8047
MBZ-4.RR.259.1 | 24313059202033 | Kulauara, Dakshin Bazar, Thana Road, Salma Khanan (Sumon) | 2019-08-19 | NQ1009 | 7.8 | 67 | 7.8 | 68 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6456 | 2303.9997 | 82.1846
MBZ-4.RR.260.1 | 24313469201585 | Kulauara, Magura, Jusna Ara Begum (Abdul Kayum) | 2019-08-19 | NQ1009 | 2.9 | 69 | 2.9 | 70 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6456 | 2303.9997 | 30.5558
MBZ-4.RR.261.1 | 24313759201564 | Kulauara, Magura, Kajol Kanti | 2019-08-19 | NQ1009 | 4.6 | 71 | 4.6 | 72 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6456 | 2303.9997 | 48.4678
MBZ-4.RR.262.1 | 24313689201503 | Kulauara, Magura, Hafizur Rahman Sumon | 2019-08-19 | NQ1009 | 5.9 | 73 | 5.9 | 74 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6456 | 2303.9997 | 62.1652
MBZ-4.RR.263.1 | 24314149201393 | Kulaura , Magura Road, Monsur Area, Rumel | 2019-08-20 | NQ1009 | 13 | 75 | 12.8 | 76 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6456 | 2303.9997 | 134.867
MBZ-4.RR.264.1 | 24313859201595 | Kulaura, Magura, TTDC Area, S.S Villa, Abdus Shohid | 2019-08-20 | NQ1009 | 11.5 | 77 | 11.5 | 78 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6456 | 2303.9997 | 121.1695
MBZ-4.RR.265.1 | 24314289201595 | Kulaura, TTDC Area, Mohila Collage Road, Forid Uddin | 2019-08-20 | NQ1009 | 4.8 | 79 | 4.8 | 80 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6456 | 2303.9997 | 50.5751
MBZ-4.RR.266.1 | 24314289201595 | Kulaura, TTDC Area, Mohila Collage Road, Salma Bhaban-2, H # 158 | 2019-08-20 | NQ1009 | 3 | 81 | 3 | 82 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6456 | 2303.9997 | 31.6094
MBZ-4.RR.267.1 | 24314419201581 | Kulaura, Sadekpur, Mohila Collage Road, Sayed Abdus Shohid | 2019-08-20 | NQ1009 | 9.6 | 83 | 9.6 | 84 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6456 | 2303.9997 | 101.1502
MBZ-4.RR.268.1 | 24354709206540 | Juri, Jayfornagar, Upazilla Chattar, Islam Monjil, Mubarak Ali | 2019-08-21 | NQ1009 | 15.3 | 113 | 15 | 114 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6408 | 2351.9997 | 158.0472
MBZ-4.RR.269.1 | 24354529206585 | Juri, Jayfornagar, Kali Bari Road, Badsha Mia | 2019-08-21 | NQ1009 | 10.1 | 115 | 10.1 | 116 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6408 | 2351.9997 | 106.4185
MBZ-4.RR.270.1 | 24354969206573 | Juri, Jayfornagar, Jangirai, Kali Bari Road, Wali Monjil, Abdul Wadud | 2019-08-21 | NQ1009 | 4.4 | 117 | 4.4 | 118 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6408 | 2351.9997 | 46.3605
MBZ-4.RR.271.1 | 24355179206590 | Juri, Jayfornagar, Jangirai, Kali Bari Road, Karunamoy Deb | 2019-08-21 | NQ1009 | 27 | 119 | 27.2 | 120 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 27.2 | 27.2 | 1.632 | 1.632 | 0.0007168 | 100% | 0% | 1.632 | 1.632 | 0.0011869 | 28 | 0.032716 | 0.032716 |  | 0 | 0 | 6408 | 2351.9997 | 286.5923
MBZ-4.RR.272.1 | 24355379206595 | Juri, Jayfornagar, Jangirai, Kali Bari Road, Mamunur Rashid | 2019-08-21 | NQ1009 | 3.8 | 121 | 3.8 | 122 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6408 | 2351.9997 | 40.0386
MBZ-4.RR.273.1 | 24354289207004 | Juri, Jayfornagar, Post Office Road, Khan Monjil, Jamil Ahmed | 2019-08-21 | NQ1009 | 5.4 | 123 | 5.4 | 124 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6408 | 2351.9997 | 56.897
MBZ-4.RR.274.1 | 24353259207085 | Juri, Uttar Bhabanipur, Puler Mukh, Lala Mia | 2019-08-21 | NQ1009 | 7.7 | 125 | 7.3 | 126 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6408 | 2351.9997 | 76.9163
MBZ-4.RR.275.1 | 24353439207201 | Juri, College Road, Beside Sonali Bank, Hossen Ahmed (Shamim) | 2019-08-22 | NQ1009 | 9.1 | 154 | 9.1 | 155 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6408 | 2351.9997 | 95.882
MBZ-4.RR.276.1 | 24353389207214 | Juri, College Road, Japani Tower, Piara Begum | 2019-08-22 | NQ1009 | 4.6 | 156 | 4.6 | 157 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6408 | 2351.9997 | 48.4678
MBZ-4.RR.277.1 | 24352889207268 | Juri, College Road, Beside Dack Banglo, Kishur Roy Chowdhury | 2019-08-22 | NQ1009 | 4.8 | 158 | 4.8 | 159 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6408 | 2351.9997 | 50.5751
MBZ-4.RR.278.1 | 24351949207331 | Juri, Uttar Bhabanipur, Forest Office Road, Keramot Hossen | 2019-08-22 | NQ1009 | 5.2 | 160 | 5.2 | 161 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6408 | 2351.9997 | 54.7897
MBZ-4.RR.279.1 | 24351949207331 | Juri, Uttar Bhabanipur, Forest Office Road, Abdul Malek | 2019-08-22 | NQ1009 | 11.1 | 162 | 11.1 | 163 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6408 | 2351.9997 | 116.9549
MBZ-4.RR.280.1 | 24381789209328 | Barlekha, Niz Dakshinbhag, Binoy Bhuson Das | 2019-08-24 | NQ1009 | 11.9 | 174 | 11.9 | 175 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6288 | 2471.9997 | 125.3841
MBZ-4.RR.281.1 | 24381789209328 | Barlekha, Niz Dakshinbhag, Bidhan Chandra Das | 2019-08-24 | NQ1009 | 2.4 | 176 | 2.4 | 177 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6288 | 2471.9997 | 25.2876
MBZ-4.RR.282.1 | 24381989209331 | Barlekha, Niz Dakshinbhag, Mithu Das | 2019-08-24 | NQ1009 | 5.1 | 178 | 5.1 | 179 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6288 | 2471.9997 | 53.7361
MBZ-4.RR.283.1 | 24382199209295 | Barlekha, Niz Dakshinbhag, Sanjoy Das | 2019-08-24 | NQ1009 | 3.4 | 182 | 3.4 | 183 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6288 | 2471.9997 | 35.824
MBZ-4.RR.284.1 | 24381769209238 | Barlekha, Niz Dakshinbhag, Shomorendro dey | 2019-08-24 | NQ1009 | 3 | 184 | 2.9 | 185 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6288 | 2471.9997 | 30.5558
MBZ-4.RR.285.1 | 24381959209247 | Barlekha, Niz Dakshinbhag, Shubroto Kumar Das | 2019-08-24 | NQ1009 | 10.3 | 186 | 10 | 187 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6288 | 2471.9997 | 105.3648
MBZ-4.RR.286.1 | 24381879209283 | Barlekha, Niz Dakshinbhag, Ranjit Kumar Das | 2019-08-24 | NQ1009 | 9.9 | 188 | 9.9 | 189 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6288 | 2471.9997 | 104.3112
MBZ-4.RR.287.1 | 24382029209287 | Barlekha, Niz Dakshinbhag, Gourango Muhon | 2019-08-24 | NQ1009 | 8.8 | 190 | 8.2 | 191 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6288 | 2471.9997 | 86.3991
MBZ-4.RR.287.2 | 24382029209287 | Barlekha, Niz Dakshinbhag, Gourango Muhon | 2022-09-20 | MN1018 | 27.5 | 7 | 27.5 | 8 | 2022-09-20 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 27.5 | 27.5 | 1.65 | 1.65 | 0.0007168 | 100% | 0% | 1.65 | 1.65 | 0.0011869 | 28 | 0.033077 | 0.033077 |  | 0 | 0 | 0 | 2471.9997 | 81.766
MBZ-4.RR.288.1 | 24382609209291 | Barlekha, Niz Dakshinbhag, Tonu Lal Deb | 2019-08-24 | NQ1009 | 39.9 | 192 | 39.8 | 193 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 39.8 | 39.8 | 2.388 | 2.388 | 0.0007168 | 100% | 0% | 2.388 | 2.388 | 0.0011869 | 28 | 0.047871 | 0.047871 |  | 0 | 0 | 6288 | 2471.9997 | 419.352
MBZ-4.RR.289.1 | 24403699210489 | Barlekha, Kathaltoli (Uttar), Abdul Karim | 2019-08-25 | NQ1009 | 6.1 | 210 | 6.1 | 211 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6288 | 2471.9997 | 64.2725
MBZ-4.RR.290.1 | 24403519210478 | Barlekha, Kathaltoli (Uttar), Ismail | 2019-08-25 | NQ1009 | 2.3 | 212 | 2.3 | 213 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6288 | 2471.9997 | 24.2339
MBZ-4.RR.291.1 | 24404919210408 | Barlekha, Baraitoli, Musegul Road, Khalilur Rahman | 2019-08-25 | NQ1009 | 3.4 | 214 | 3.4 | 215 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6288 | 2471.9997 | 35.824
MBZ-4.RR.292.1 | 24405609210416 | Barlekha, Panidhar, Nasir Uddin | 2019-08-25 | NQ1009 | 11.4 | 216 | 11.4 | 217 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6288 | 2471.9997 | 120.1159
MBZ-4.RR.293.1 | 24411259210513 | Barlekha, Panidhar, Tourist Police Office, Askir Ali | 2019-08-26 | NQ1009 | 20.3 | 218 | 20.3 | 219 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 20.3 | 20.3 | 1.218 | 1.218 | 0.0007168 | 100% | 0% | 1.218 | 1.218 | 0.0011869 | 28 | 0.024417 | 0.024417 |  | 0 | 0 | 6288 | 2471.9997 | 213.8906
MBZ-4.RR.294.1 | 24412219210550 | Barlekha, Panidhar, Akbor Ali | 2019-08-26 | NQ1009 | 11.9 | 220 | 11.9 | 221 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6288 | 2471.9997 | 125.3841
MBZ-4.RR.295.1 | 24412479210528 | Barlekha, Panidhar, Shamim Ahmed | 2019-08-26 | NQ1009 | 2.5 | 222 | 2.5 | 223 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6288 | 2471.9997 | 26.3412
MBZ-4.RR.296.1 | 24412529210518 | Barlekha, Panidhar, Abdul Hasib | 2019-08-26 | NQ1009 | 10.8 | 224 | 10.8 | 225 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6288 | 2471.9997 | 113.794
MBZ-4.RR.297.1 | 24412529210518 | Barlekha, Panidhar, Abdur Rahim | 2019-08-26 | NQ1009 | 6.4 | 226 | 5.9 | 227 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6288 | 2471.9997 | 62.1652
MBZ-4.RR.298.1 | 24413149210576 | Barlekha, Murirgul, Dilip Kumar Bhattacharjo | 2019-08-26 | NQ1009 | 6.5 | 228 | 6.5 | 229 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6288 | 2471.9997 | 68.4871
MBZ-4.RR.299.1 | 24413149210576 | Barlekha, Murirgul, Bijoy Bhuson Chandra | 2019-08-26 | NQ1009 | 9 | 230 | 9 | 231 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6288 | 2471.9997 | 94.8283
MBZ-4.RR.300.1 | 24415349210357 | Barlekha, Murirgul, Baluchar, Asraf Hossen Chowdhury | 2019-08-27 | NQ1009 | 33.4 | 252 | 33.4 | 253 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 33.4 | 33.4 | 2.004 | 2.004 | 0.0007168 | 100% | 0% | 2.004 | 2.004 | 0.0011869 | 28 | 0.040173 | 0.040173 |  | 0 | 0 | 6288 | 2471.9997 | 351.9185
MBZ-4.RR.301.1 | 24310029201481 | Kulaura, Uchlapara, Word # 8, Eidga Road, H # 347/1. Jahanara Begum | 2019-08-18 | NQ1007 | 10.9 | 79 | 11.3 | 80 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6480 | 2279.9997 | 119.0622
MBZ-4.RR.302.1 | 24310029201481 | Kulaura, Uchlapara, Word # 8, Eidga Road, Md. Wahid Khan | 2019-08-18 | NQ1007 | 3.8 | 81 | 3.8 | 82 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6480 | 2279.9997 | 40.0386
MBZ-4.RR.303.1 | 24310559201489 | Kulaura, Uchlapara, Word # 8, Eidga Road, H # 357, Ismit Ahamed | 2019-08-18 | NQ1007 | 5.3 | 83 | 5.3 | 84 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6480 | 2279.9997 | 55.8434
MBZ-4.RR.304.1 | 24310679201483 | Kulaura, Uchlapara, word # 5, Eidga Road, H # 317, Shekh Monjil | 2019-08-19 | NQ1007 | 4.8 | 85 | 4.8 | 86 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6480 | 2279.9997 | 50.5751
MBZ-4.RR.305.1 | 24310599201471 | Kulaura, Uchlapara, word # 8, Eidga Road, H # 358, Abul Kalam | 2019-08-19 | NQ1007 | 10.6 | 87 | 10.6 | 88 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6480 | 2279.9997 | 111.6867
MBZ-4.RR.306.1 | 24310749201433 | Kulaura, Uchlapara, word # 5, Eidga Road, Md. Sojib | 2019-08-19 | NQ1007 | 6.6 | 89 | 6.6 | 90 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6480 | 2279.9997 | 69.5408
MBZ-4.RR.307.1 | 24310749201433 | Kulaura, Uchlapara, word # 5, Eidga Road, Rojob Ali | 2019-08-19 | NQ1007 | 29.9 | 93 | 29.9 | 94 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 29.9 | 29.9 | 1.794 | 1.794 | 0.0007168 | 100% | 0% | 1.794 | 1.794 | 0.0011869 | 28 | 0.035964 | 0.035964 |  | 0 | 0 | 6480 | 2279.9997 | 315.0408
MBZ-4.RR.308.1 | 24311809201316 | Kulaura, Vadha Monsur, Word # 8, Himachol City, Eidga Road, Mohib Ali | 2019-08-19 | NQ1007 | 6.1 | 95 | 6.1 | 96 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6480 | 2279.9997 | 64.2725
MBZ-4.RR.309.1 | 24311809201316 | Kulaura, Vadha Monsur, Word # 8, Eidga Road, H # 254, Siraj Mia | 2019-08-19 | NQ1007 | 5.6 | 97 | 5.6 | 98 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6480 | 2279.9997 | 59.0043
MBZ-4.RR.310.1 | 24312409201316 | Kulaura, Monsur, Word # 8, Eidga Road, H # 112, Md. Shariful Rahman Chowdhory | 2019-08-19 | NQ1007 | 3.4 | 99 | 3.6 | 100 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6480 | 2279.9997 | 37.9313
MBZ-4.RR.311.1 | 24312209201395 | Kulaura, Bade Monsur, Word # 8, H # 217, A.K.M Sorif Ahmod Solman | 2019-08-20 | NQ1007 | 6.5 | 119 | 6.5 | 120 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6480 | 2279.9997 | 68.4871
MBZ-4.RR.312.1 | 24312209201395 | Kulaura, Bade Monsur, Word # 8, Nur Mia | 2019-08-20 | NQ1007 | 9.2 | 123 | 9.4 | 124 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6480 | 2279.9997 | 99.0429
MBZ-4.RR.313.1 | 24314009202145 | Kulaura, Uttar Bazar, Hospital Road, Mozid Mia | 2019-08-20 | NQ1007 | 3.3 | 125 | 3.3 | 126 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6456 | 2303.9997 | 34.7704
MBZ-4.RR.314.1 | 24314129202150 | Kulaura, Uttar Bazar, Hospital Road, Khosru Mia | 2019-08-20 | NQ1007 | 9.2 | 127 | 9.2 | 128 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6456 | 2303.9997 | 96.9356
MBZ-4.RR.315.1 | 24314389202169 | Kulaura, Uttar Bazar, Hospital Road, H # 71, Md. Tochir Ali | 2019-08-20 | NQ1007 | 10.1 | 129 | 10.1 | 130 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6456 | 2303.9997 | 106.4185
MBZ-4.RR.316.1 | 24314689202185 | Kulaura, Uttar Bazar, Hospital Road, Fatir Mia | 2019-08-20 | NQ1007 | 2.2 | 131 | 2.2 | 132 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6456 | 2303.9997 | 23.1803
MBZ-4.RR.317.1 | 24315999202464 | Kulaura, Uttar Kulauragram, Bijoya Road, Sudhir Saronik | 2019-08-21 | NQ1007 | 1.5 | 155 | 1.4 | 156 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6432 | 2327.9997 | 14.7511
MBZ-4.RR.318.1 | 24320199202491 | Kulaura, Uttar Kulauragram, Bijoya Road, A.K Shaker Khan | 2019-08-21 | NQ1007 | 4.2 | 157 | 4.2 | 158 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6432 | 2327.9997 | 44.2532
MBZ-4.RR.319.1 | 24320199202491 | Kulaura, Uttar Kulauragram, Bijoya Road, A.K Shaker Khan | 2019-08-21 | NQ1007 | 9.1 | 159 | 9.1 | 160 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6432 | 2327.9997 | 95.882
MBZ-4.RR.320.1 | 24320349202500 | Kulaura, Uttar Kulauragram, Bijoya Road, Rokkhini Mohon Shorma | 2019-08-21 | NQ1007 | 4.4 | 161 | 4.4 | 162 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6432 | 2327.9997 | 46.3605
MBZ-4.RR.321.1 | 24320699202533 | Kulaura, Uttar Kulauragram, Bijoya Road, Dr. Mohammad Mobashor Ali | 2019-08-21 | NQ1007 | 8.4 | 163 | 8.7 | 164 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6432 | 2327.9997 | 91.6674
MBZ-4.RR.322.1 | 24321229202589 | Kulaura, Uttar Kulauragram, Kulauragram Gov: primary school, Sukhomoy Boddo | 2019-08-21 | NQ1007 | 11.6 | 165 | 11.6 | 166 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6432 | 2327.9997 | 122.2232
MBZ-4.RR.323.1 | 24321529203011 | Kulaura, Uttar Kulauragram, Kulauragram Gov: primary school, Aminur Rashid | 2019-08-21 | NQ1007 | 19 | 167 | 19 | 168 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 6432 | 2327.9997 | 200.1931
MBZ-4.RR.324.1 | 24360619207146 | Jurhi, Jangirai, Borolekha Road, Helal Uddin , Aman Nibas | 2019-08-22 | NQ1007 | 8.7 | 187 | 8.8 | 188 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6336 | 2423.9997 | 92.721
MBZ-4.RR.325.1 | 24360689207136 | Jurhi, Jangirai, Borolekha Road, Md. Sirajul Islam | 2019-08-22 | NQ1007 | 8.3 | 189 | 8.3 | 190 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6336 | 2423.9997 | 87.4528
MBZ-4.RR.326.1 | 24360779207154 | Jurhi, Jangirai, Borolekha Road, Late Dr. Shakhowt Hossen | 2019-08-22 | NQ1007 | 14.1 | 191 | 14.1 | 192 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6336 | 2423.9997 | 148.5644
MBZ-4.RR.327.1 | 24361039207147 | Jurhi, Jangirai, Jangirai Road, Farid Uddin | 2019-08-22 | NQ1007 | 12.1 | 193 | 12.1 | 194 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6336 | 2423.9997 | 127.4914
MBZ-4.RR.328.1 | 24361399207155 | Jurhi, Jangirai, Jangirai Road, Jomshu | 2019-08-22 | NQ1007 | 10.6 | 197 | 10.6 | 198 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6336 | 2423.9997 | 111.6867
MBZ-4.RR.329.1 | 24362539207113 | Jurhi, Jangirai, Jangirai Road, Istekar Ahamed | 2019-08-22 | NQ1007 | 6.7 | 199 | 6.7 | 200 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6336 | 2423.9997 | 70.5944
MBZ-4.RR.330.1 | 24363239207016 | Jurhi, Uttar Jangirai, Uttar Jangirai Road, Md. Abdul Motalib | 2019-08-22 | NQ1007 | 26.7 | 201 | 26.7 | 202 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 26.7 | 26.7 | 1.602 | 1.602 | 0.0007168 | 100% | 0% | 1.602 | 1.602 | 0.0011869 | 28 | 0.032115 | 0.032115 |  | 0 | 0 | 6336 | 2423.9997 | 281.324
MBZ-4.RR.331.1 | 24363529206599 | Jurhi, Uttar Jangirai, Uttar Jangirai Road, Md. Jahirul Islam | 2019-08-22 | NQ1007 | 1.5 | 203 | 1.5 | 204 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6336 | 2423.9997 | 15.8047
MBZ-4.RR.332.1 | 24363849206556 | Jurhi, Uttar Jangirai, Uttar Jangirai Road, Romzan Ali | 2019-08-22 | NQ1007 | 5.1 | 207 | 5.1 | 208 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6336 | 2423.9997 | 53.7361
MBZ-4.RR.333.1 | 24364179206561 | Jurhi, Uttar Jangirai, Uttar Jangirai Road, Toiyob Ali | 2019-08-22 | NQ1007 | 9.4 | 209 | 9.4 | 210 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6336 | 2423.9997 | 99.0429
MBZ-4.RR.334.1 | 24374139209110 | Borolekha, Dokkhinbug, Soperpur, Khanpara, Tipu Mia | 2019-08-24 | NQ1007 | 8.4 | 225 | 8.4 | 226 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6336 | 2423.9997 | 88.5064
MBZ-4.RR.335.1 | 24391349209177 | Borolekha, Suzanagar, Borthol, Md. Habib Ali | 2019-08-25 | NQ1007 | 12.3 | 251 | 12.3 | 252 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6336 | 2423.9997 | 129.5987
MBZ-4.RR.336.1 | 24391349209177 | Borolekha, Suzanagar, Borthol, Mahmudur Rahman | 2019-08-25 | NQ1007 | 3.1 | 253 | 3.1 | 254 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6336 | 2423.9997 | 32.6631
MBZ-4.RR.337.1 | 24391499209101 | Borolekha, Suzanagar, Borthol, Abdul Zobbar | 2019-08-25 | NQ1007 | 10.4 | 255 | 10.4 | 256 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6336 | 2423.9997 | 109.5794
MBZ-4.RR.338.1 | 24392609209051 | Borolekha, Suzanagar, Chintapur, Hazibari, Fakrul Islam | 2019-08-25 | NQ1007 | 9.8 | 257 | 9.8 | 258 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6336 | 2423.9997 | 103.2575
MBZ-4.RR.339.1 | 24392609209051 | Borolekha, Suzanagar, Chintapur, Hazibari, Hafiz | 2019-08-25 | NQ1007 | 4.7 | 259 | 4.7 | 260 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6336 | 2423.9997 | 49.5215
MBZ-4.RR.340.1 | 24393079209032 | Borolekha, Suzanagar, Chintapur, Hazibari, Fojlul Haque | 2019-08-25 | NQ1007 | 8.2 | 261 | 8.2 | 262 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6336 | 2423.9997 | 86.3991
MBZ-4.RR.341.1 | 24393079209032 | Borolekha, Suzanagar, Chintapur, Zubayer | 2019-08-25 | NQ1007 | 10 | 263 | 10 | 264 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6336 | 2423.9997 | 105.3648
MBZ-4.RR.342.1 | 24393079209032 | Borolekha, Suzanagar, Chintapur, Abdul Odud | 2019-08-25 | NQ1007 | 6.8 | 265 | 6.2 | 266 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6336 | 2423.9997 | 65.3262
MBZ-4.RR.343.1 | 24392819208539 | Borolekha, Suzanagar, Hashempur, Shohidul Islam | 2019-08-26 | NQ1007 | 12.1 | 312 | 12.1 | 313 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6336 | 2423.9997 | 127.4914
MBZ-4.RR.343.2 | 24392819208539 | Borolekha, Suzanagar, Hashempur, Shohidul Islam | 2021-02-04 | LU1001 | 13.7 | 150 | 13.4 | 151 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6336 | 2423.9997 | 141.1888
MBZ-4.RR.344.1 | 24392819208539 | Borolekha, Suzanagar, Hashempur, Md. Shirajul Islam | 2019-08-26 | NQ1007 | 11.9 | 318 | 11.6 | 319 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6336 | 2423.9997 | 122.2232
MBZ-4.RR.345.1 | 24393149208537 | Borolekha, Suzanagar, Hashempur, Abdur Rashid | 2019-08-26 | NQ1007 | 11.6 | 320 | 11.6 | 321 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6336 | 2423.9997 | 122.2232
MBZ-4.RR.346.1 | 24393149208537 | Borolekha, Suzanagar, Hashempur, Abdul Motin | 2019-08-26 | NQ1007 | 9.9 | 324 | 9.9 | 325 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6336 | 2423.9997 | 104.3112
MBZ-4.RR.347.1 | 24392949208559 | Borolekha, Suzanagar, Hashempur, Hazi Abdul Hakim | 2019-08-26 | NQ1007 | 11.6 | 328 | 11.6 | 329 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6336 | 2423.9997 | 122.2232
MBZ-4.RR.348.1 | 24392649208493 | Borolekha, Suzanagar, Hashempur, Rois Ali | 2019-08-26 | NQ1007 | 7 | 330 | 7 | 331 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6336 | 2423.9997 | 73.7554
MBZ-4.RR.349.1 | 24392649208493 | Borolekha, Suzanagar, Hashempur, Abdur Rahman | 2019-08-26 | NQ1007 | 13.7 | 332 | 13.7 | 333 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6336 | 2423.9997 | 144.3498
MBZ-4.RR.350.1 | 24392649208493 | Borolekha, Suzanagar, Hashempur, Rakib Ali | 2019-08-26 | NQ1007 | 12.5 | 334 | 12.5 | 335 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6336 | 2423.9997 | 131.706
MBZ-4.RR.351.1 | 24304609201098 | Kulaura, Chatolgaon, Opposite Of Nirbahi Prokousholir Karjaloy, Fokhrul | 2019-08-18 | NQ1007 | 6.8 | 65 | 6.8 | 66 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6480 | 2279.9997 | 71.6481
MBZ-4.RR.352.1 | 24305219201262 | Kulaura, Chatolgaon, Eidgah Road, Shaiyum Hossen | 2019-08-18 | NQ1007 | 15 | 67 | 15 | 68 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6480 | 2279.9997 | 158.0472
MBZ-4.RR.353.1 | 24305259201332 | Kulaura, Kasurkapun, Abdul Basith | 2019-08-18 | NQ1007 | 12.1 | 69 | 12.1 | 70 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6480 | 2279.9997 | 127.4914
MBZ-4.RR.354.1 | 24305299201331 | Kulaura, Kasurkapun, Shahjahan Islam Shaju | 2019-08-18 | NQ1007 | 5.8 | 71 | 5.8 | 72 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6480 | 2279.9997 | 61.1116
MBZ-4.RR.354.2 | 24305299201331 | Kulaura, Kasurkapun, Shahjahan Islam Shaju | 2020-10-13 | NQ1002 | 6.3 | 269 | 6.3 | 270 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6480 | 2279.9997 | 66.3798
MBZ-4.RR.355.1 | 24305369201329 | Kulaura, Kasurkapun, Gias Mia | 2019-08-18 | NQ1007 | 3.3 | 73 | 3.3 | 74 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6480 | 2279.9997 | 34.7704
MBZ-4.RR.356.1 | 24305149201325 | Kulaura, Kasurkapun, Hazi Chomru Mia | 2019-08-18 | NQ1007 | 10.5 | 75 | 10.5 | 76 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6480 | 2279.9997 | 110.6331
MBZ-4.RR.357.1 | 24305019201324 | Kulaura, Kasurkapun, Showkot mia | 2019-08-18 | NQ1007 | 2.9 | 77 | 2.9 | 78 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6480 | 2279.9997 | 30.5558
MBZ-4.RR.358.1 | 24312189201498 | Kulaura, Magura, Ward # 4, H # 30, Abdul Azim | 2019-08-19 | NQ1007 | 10.5 | 101 | 10.5 | 102 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6480 | 2279.9997 | 110.6331
MBZ-4.RR.359.1 | 24312019201490 | Kulaura, Magura, Ward # 4, H # 26, Abdul Muhit Chowdhury | 2019-08-19 | NQ1007 | 3.6 | 103 | 3.6 | 104 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6480 | 2279.9997 | 37.9313
MBZ-4.RR.360.1 | 24312439201448 | Kulaura, Magura, Ward # 8, Shohel Mia | 2019-08-19 | NQ1007 | 2.6 | 105 | 2.6 | 106 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6480 | 2279.9997 | 27.3949
MBZ-4.RR.361.1 | 24312409201441 | Kulaura, Magura, Ward # 8, Atan | 2019-08-19 | NQ1007 | 4.8 | 107 | 4.8 | 108 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6480 | 2279.9997 | 50.5751
MBZ-4.RR.362.1 | 24305499201238 | Kulaura, North Chatolgaon, Abu Sufian Chowdhury | 2019-08-19 | NQ1007 | 3.9 | 109 | 3.9 | 110 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6480 | 2279.9997 | 41.0923
MBZ-4.RR.363.1 | 24305859201229 | Kulaura, North Chatolgaon, Ishak Ali | 2019-08-19 | NQ1007 | 5 | 111 | 5 | 112 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6480 | 2279.9997 | 52.6824
MBZ-4.RR.364.1 | 24305939201301 | Kulaura, Bade Monsur, Saidur Rahman | 2019-08-19 | NQ1007 | 10.5 | 113 | 10.5 | 114 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6480 | 2279.9997 | 110.6331
MBZ-4.RR.366.1 | 24310789201333 | Kulaura, Bade Monsur, Shahanara Begum | 2019-08-19 | NQ1007 | 10.5 | 117 | 10.1 | 118 | 2022-01-01 | 2022-09-28 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6480 | 2279.9997 | 106.4185
MBZ-4.RR.367.1 | 24315029202160 | Kulaura, Ahmadabad, Ward # 3, H # 47, Hazi Tofajjul Ali Villa | 2019-08-20 | NQ1007 | 6.6 | 133 | 6.6 | 134 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6432 | 2327.9997 | 69.5408
MBZ-4.RR.368.1 | 24315059202144 | Kulaura, Ahmadabad, Ward # 3, H # 44, Mohammad Faruk Uddin | 2019-08-20 | NQ1007 | 4.1 | 135 | 4.1 | 136 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6432 | 2327.9997 | 43.1996
MBZ-4.RR.369.1 | 24315089202133 | Kulaura, Ahmadabad, Ward # 3, H # 43, Firoz Cottage | 2019-08-20 | NQ1007 | 6.3 | 137 | 6.3 | 138 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6432 | 2327.9997 | 66.3798
MBZ-4.RR.370.1 | 24315079202111 | Kulaura, Ahmadabad, Ward # 3, Ohidul Islam | 2019-08-20 | NQ1007 | 10.8 | 139 | 10.9 | 140 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6432 | 2327.9997 | 114.8476
MBZ-4.RR.371.1 | 24315199202108 | Kulaura, Ahmadabad, Ward # 3, H # 36, Rowshan Ara Rabeya | 2019-08-20 | NQ1007 | 2.7 | 141 | 2.7 | 142 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6432 | 2327.9997 | 28.4485
MBZ-4.RR.372.1 | 24315219202094 | Kulaura, Ahmadabad, Ward # 3, Ali Bhaban | 2019-08-20 | NQ1007 | 3.7 | 143 | 3.7 | 144 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6432 | 2327.9997 | 38.985
MBZ-4.RR.373.1 | 24314959202017 | Kulaura, North Bazar, Ward # 3, Mohila Callage Road, Shohel | 2019-08-20 | NQ1007 | 9.5 | 145 | 9.5 | 146 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6456 | 2303.9997 | 100.0966
MBZ-4.RR.373.2 | 24314959202017 | Kulaura, North Bazar, Ward # 3, Mohila Callage Road, Shohel | 2021-02-07 | LU1001 | 1.8 | 158 | 1.8 | 159 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6456 | 2303.9997 | 18.9657
MBZ-4.RR.374.1 | 24314959201591 | Kulaura, Sadekpur, Ward # 1, Mohila Callage Road, H 246, Khadija Bhaban | 2019-08-20 | NQ1007 | 9.7 | 147 | 9.7 | 148 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6456 | 2303.9997 | 102.2039
MBZ-4.RR.375.1 | 24314899201589 | Kulaura, Sadekpur, Ward # 1, Mohila Callage Road, Ruksana Monjil | 2019-08-20 | NQ1007 | 10.5 | 149 | 10.5 | 150 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6456 | 2303.9997 | 110.6331
MBZ-4.RR.376.1 | 24314499201583 | Kulaura, Sadekpur, Ward # 1, Mohila Callage Road, Aachia House | 2019-08-20 | NQ1007 | 6.7 | 151 | 6.7 | 152 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6456 | 2303.9997 | 70.5944
MBZ-4.RR.377.1 | 24315009201551 | Kulaura, Sadekpur, Sadekpur Mohila Callage Link Road, H # 242, Chowdhury Villa | 2019-08-20 | NQ1007 | 8.3 | 153 | 8.3 | 154 | 2022-01-01 | 2022-09-27 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6456 | 2303.9997 | 87.4528
MBZ-4.RR.378.1 | 24354279206350 | Juri, East Belagaon, UP Sarak, Alal Mia | 2019-08-21 | NQ1007 | 5 | 169 | 5 | 170 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6408 | 2351.9997 | 52.6824
MBZ-4.RR.379.1 | 24354529206339 | Juri, East Belagaon, Containwala Belagaon Road, Kholil | 2019-08-21 | NQ1007 | 5.3 | 171 | 5.3 | 172 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6408 | 2351.9997 | 55.8434
MBZ-4.RR.380.1 | 24354659206329 | Juri, East Belagaon, Containwala Belagaon Road, Ahad mia | 2019-08-21 | NQ1007 | 11.4 | 173 | 11.4 | 174 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6408 | 2351.9997 | 120.1159
MBZ-4.RR.381.1 | 24354469206405 | Juri, East Belagaon, Kulaura Road, Upojela Chottor, Selim Mia | 2019-08-21 | NQ1007 | 10.8 | 175 | 10.8 | 176 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6408 | 2351.9997 | 113.794
MBZ-4.RR.382.1 | 24354529206425 | Juri, East Belagaon, Kulaura Road, Upojela Chottor, Mosleh Uddin | 2019-08-21 | NQ1007 | 10.5 | 177 | 10.5 | 178 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6408 | 2351.9997 | 110.6331
MBZ-4.RR.383.1 | 24354529206425 | Juri, East Belagaon, Kulaura Road, Upojela Chottor, Liakot Ali | 2019-08-21 | NQ1007 | 3.5 | 179 | 3.5 | 180 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6408 | 2351.9997 | 36.8777
MBZ-4.RR.384.1 | 24354809206462 | Juri, East Belagaon, Kulaura Road, Upojela Chottor, Md Mostofa | 2019-08-21 | NQ1007 | 7.5 | 181 | 7.5 | 182 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6408 | 2351.9997 | 79.0236
MBZ-4.RR.385.1 | 24354849206466 | Juri, East Belagaon, Kulaura Road, Upojela Chottor, Abdur Rahim | 2019-08-21 | NQ1007 | 7.2 | 183 | 7.2 | 184 | 2022-01-01 | 2022-09-25 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6408 | 2351.9997 | 75.8627
MBZ-4.RR.386.1 | 24360759207191 | Juri, Basirpur, Ward # 3, Goriber Dokan, Kuddus Vuiyan | 2019-08-22 | NQ1007 | 8.9 | 211 | 8.8 | 212 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6336 | 2423.9997 | 92.721
MBZ-4.RR.387.1 | 24360759207191 | Juri, Basirpur, Ward # 3, Goriber Dokan, Kalam Vuiyan | 2019-08-22 | NQ1007 | 10.6 | 213 | 10.6 | 214 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6336 | 2423.9997 | 111.6867
MBZ-4.RR.388.1 | 24360769207182 | Juri, Basirpur, Ward # 3, Goriber Dokan, Jolil Vuiyan | 2019-08-22 | NQ1007 | 4.9 | 215 | 4.9 | 216 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6336 | 2423.9997 | 51.6288
MBZ-4.RR.389.1 | 24360889207182 | Juri, Basirpur, Ward # 3, Donunjoy Dey | 2019-08-22 | NQ1007 | 7.2 | 217 | 7.2 | 218 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6336 | 2423.9997 | 75.8627
MBZ-4.RR.390.1 | 24370919208034 | Juri, Chalbond,Ward # 3, Amtoil, Nur Uddin Master | 2019-08-22 | NQ1007 | 13.6 | 219 | 13.3 | 220 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6336 | 2423.9997 | 140.1352
MBZ-4.RR.391.1 | 24370919208034 | Juri, Chalbond,Ward # 3, Amtoil, Nur Uddin Master | 2019-08-22 | NQ1007 | 5.3 | 221 | 5.3 | 222 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6336 | 2423.9997 | 55.8434
MBZ-4.RR.392.1 | 24370469208112 | Juri, Chalbond,Ward # 3, Amtoil, Moklesur Rahman | 2019-08-22 | NQ1007 | 7.1 | 223 | 7.1 | 224 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6336 | 2423.9997 | 74.809
MBZ-4.RR.393.1 | 24390659209528 | Barlekha, Rotuli Bazar, Azimgonj Road, Abdul Motin | 2019-08-24 | NQ1007 | 2.1 | 231 | 2.1 | 232 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6336 | 2423.9997 | 22.1266
MBZ-4.RR.393.2 | 24390659209528 | Barlekha, Rotuli Bazar, Azimgonj Road, Abdul Motin | 2022-03-14 | NQ1007 | 12.2 | 54 | 12.2 | 55 | 2022-03-14 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 4608 | 2423.9997 | 103.1882
MBZ-4.RR.394.1 | 24390849209520 | Barlekha, Rotuli Bazar, Azimgonj Road, Asad Uddin | 2019-08-24 | NQ1007 | 4.3 | 233 | 4.3 | 234 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6336 | 2423.9997 | 45.3069
MBZ-4.RR.395.1 | 24390939209511 | Barlekha, Rotuli Bazar, Azimgonj Road, Abdul Karim | 2019-08-24 | NQ1007 | 12.4 | 235 | 12.4 | 236 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6336 | 2423.9997 | 130.6524
MBZ-4.RR.396.1 | 24391179209492 | Barlekha, Rotuli Bazar, Azimgonj Road, Aamir Hossain | 2019-08-24 | NQ1007 | 11.9 | 237 | 11.9 | 238 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6336 | 2423.9997 | 125.3841
MBZ-4.RR.397.1 | 24391609209410 | Barlekha, Rotuli Bazar, Azimgonj Road, Jamal Uddin | 2019-08-24 | NQ1007 | 4.9 | 239 | 4.9 | 240 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6336 | 2423.9997 | 51.6288
MBZ-4.RR.398.1 | 24391659209335 | Barlekha, Rotuli Bazar, Azimgonj Road, Jomir Uddin | 2019-08-24 | NQ1007 | 9.3 | 241 | 9.3 | 242 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6336 | 2423.9997 | 97.9893
MBZ-4.RR.398.2 | 24391659209335 | Barlekha, Rotuli Bazar, Azimgonj Road, Jomir Uddin | 2021-02-06 | LU1001 | 2.6 | 155 | 2.6 | 156 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6336 | 2423.9997 | 27.3949
MBZ-4.RR.399.1 | 24391799209309 | Barlekha, Rotuli Bazar, Azimgonj Road, Ijjot Ali (Beside Chintapur Prathomik Biddaloy) | 2019-08-24 | NQ1007 | 7.3 | 243 | 7.3 | 244 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6336 | 2423.9997 | 76.9163
MBZ-4.RR.400.1 | 24391799209309 | Barlekha, Rotuli Bazar, Azimgonj Road, Abdul Hamid (Beside Chintapur Prathomik Biddaloy) | 2019-08-24 | NQ1007 | 11.6 | 245 | 11.6 | 246 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6336 | 2423.9997 | 122.2232
MBZ-4.RR.401.1 | 24391199210008 | Borolekha, Dakshinvagh, Pashchim Gangkul, Abdul Sattar | 2019-08-27 | MP1032 | 3.3 | 321 | 3 | 322 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6288 | 2471.9997 | 31.6094
MBZ-4.RR.402.1 | 24424209211426 | Borolekha, Uttor Choumuhoni, College Road, Abdus Salam | 2019-08-27 | MP1032 | 3.5 | 323 | 3.5 | 324 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6264 | 2495.9997 | 36.8777
MBZ-4.RR.403.1 | 24424209211426 | Borolekha, Uttor Choumuhoni, College Road, Abdul Hannan | 2019-08-27 | MP1032 | 6.8 | 325 | 6.8 | 326 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6264 | 2495.9997 | 71.6481
MBZ-4.RR.404.1 | 24435659209304 | Barlekha, Ward # 5, Dakshin Shurikandi, Dasherbazar Road, Mahmud Ali | 2019-08-28 | MP1032 | 4.5 | 333 | 4.4 | 334 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6264 | 2495.9997 | 46.3605
MBZ-4.RR.405.1 | 24435269209336 | Barlekha, Ward # 4, Dasherbazar, Shurikandi, Hazi Alauddin | 2019-08-28 | MP1032 | 4.6 | 335 | 4.6 | 336 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6264 | 2495.9997 | 48.4678
MBZ-4.RR.406.1 | 24434679209395 | Barlekha, Ward # 4, Gowaltabazar, Dakshin Shurikandi, Md. Abdullah | 2019-08-28 | MP1032 | 8.8 | 339 | 8.8 | 340 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6264 | 2495.9997 | 92.721
MBZ-4.RR.407.1 | 24434179209460 | Barlekha, Union # 7, Talimpur, Arab Uddin | 2019-08-28 | MP1032 | 3.9 | 341 | 3.9 | 342 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6264 | 2495.9997 | 41.0923
MBZ-4.RR.408.1 | 24434179209460 | Barlekha, Union # 7, Talimpur, Salek Uddin | 2019-08-28 | MP1032 | 12.1 | 343 | 12.1 | 344 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6264 | 2495.9997 | 127.4914
MBZ-4.RR.409.1 | 24433849209538 | Barlekha, Union # 7, Talimpur, Motin Monjil, Abdul Motin | 2019-08-28 | MP1032 | 5.5 | 345 | 5.5 | 346 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6264 | 2495.9997 | 57.9506
MBZ-4.RR.410.1 | 24434469209520 | Barlekha, Union # 7, Talimpur, Ruel | 2019-08-28 | MP1032 | 5.7 | 347 | 5.7 | 348 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6264 | 2495.9997 | 60.0579
MBZ-4.RR.411.1 | 24391029208188 | Barlekha, Sujanagar, Shaldiga, Md. Rajab Ali | 2019-08-29 | MP1032 | 7 | 373 | 7 | 374 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6312 | 2447.9997 | 73.7554
MBZ-4.RR.412.1 | 24391039208199 | Barlekha, Sujanagar, Shaldiga, Aklas Ali | 2019-08-29 | MP1032 | 3.4 | 375 | 3.4 | 376 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6312 | 2447.9997 | 35.824
MBZ-4.RR.413.1 | 24390599208195 | Barlekha, Sujanagar, Shaldiga, Tazib Ali | 2019-08-29 | MP1032 | 6 | 377 | 6 | 378 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6312 | 2447.9997 | 63.2189
MBZ-4.RR.414.1 | 24390809208138 | Barlekha, Sujanagar, Shaldiga, Hashem Bari, Kutub Uddin | 2019-08-29 | MP1032 | 7.4 | 379 | 7.4 | 380 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6312 | 2447.9997 | 77.97
MBZ-4.RR.415.1 | 24391849208294 | Barlekha, Sujanagar, Rafinagar, Mohammad Naim | 2019-08-29 | MP1032 | 4.7 | 381 | 4.7 | 382 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6312 | 2447.9997 | 49.5215
MBZ-4.RR.416.1 | 24391879208286 | Barlekha, Sujanagar, Rafinagar, Rafiqul Islam | 2019-08-29 | MP1032 | 6 | 383 | 6 | 384 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6312 | 2447.9997 | 63.2189
MBZ-4.RR.451.1 | 24394069208236 | Barlekha, Rofinagar, Idris | 2019-08-25 | MP1032 | 7 | 281 | 7 | 282 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6312 | 2447.9997 | 73.7554
MBZ-4.RR.452.1 | 24394069208236 | Barlekha, Rofinagar, Taherul | 2019-08-25 | MP1032 | 3.4 | 283 | 3.4 | 284 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6312 | 2447.9997 | 35.824
MBZ-4.RR.453.1 | 24394069208236 | Barlekha, Rofinagar, Sekander Ali | 2019-08-25 | MP1032 | 7.6 | 285 | 7.6 | 286 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6312 | 2447.9997 | 80.0773
MBZ-4.RR.454.1 | 24393859208311 | Barlekha, Bagmara, Air Box | 2019-08-25 | MP1032 | 3.4 | 287 | 3.4 | 288 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6312 | 2447.9997 | 35.824
MBZ-4.RR.455.1 | 24393989208303 | Barlekha, South Bagmara, Folu | 2019-08-25 | MP1032 | 6.4 | 289 | 6.4 | 290 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6312 | 2447.9997 | 67.4335
MBZ-4.RR.456.1 | 24393989208303 | Barlekha, South Bagmara, Rafiq | 2019-08-25 | MP1032 | 2.7 | 291 | 2.7 | 292 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6312 | 2447.9997 | 28.4485
MBZ-4.RR.457.1 | 24393989208303 | Barlekha, South Bagmara, Rafiq | 2019-08-25 | MP1032 | 10.9 | 293 | 10.9 | 294 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6312 | 2447.9997 | 114.8476
MBZ-4.RR.458.1 | 24393989208303 | Barlekha, South Bagmara, Rafiq | 2019-08-25 | MP1032 | 11.4 | 295 | 11.4 | 296 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6312 | 2447.9997 | 120.1159
MBZ-4.RR.459.1 | 24393739208368 | Barlekha, Sujanagar, Eidgah Bari, Khililur Rahman | 2019-08-26 | MP1032 | 11.1 | 297 | 11.1 | 298 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6312 | 2447.9997 | 116.9549
MBZ-4.RR.460.1 | 24394039208364 | Barlekha, Sujanagar, Eidgah Bari, Ruhel Malik | 2019-08-26 | MP1032 | 6.3 | 299 | 6.3 | 300 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6312 | 2447.9997 | 66.3798
MBZ-4.RR.461.1 | 24393979208393 | Barlekha, Sujanagar, Eidgah Bari, Abdul Amin | 2019-08-26 | MP1032 | 2.7 | 301 | 2.7 | 302 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6312 | 2447.9997 | 28.4485
MBZ-4.RR.462.1 | 24394339208347 | Barlekha, Sujanagar, Eidgah Bari, Abdul High | 2019-08-26 | MP1032 | 4.2 | 305 | 4.2 | 306 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6312 | 2447.9997 | 44.2532
MBZ-4.RR.463.1 | 24394339208347 | Barlekha, Sujanagar, Eidgah Bari, Abdul High | 2019-08-26 | MP1032 | 6.9 | 307 | 6.9 | 308 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6312 | 2447.9997 | 72.7017
MBZ-4.RR.464.1 | 24423809211442 | Barlekha, Hatbondo, Joporpur Road, Lotfor Rahman | 2019-08-27 | MP1032 | 4.8 | 327 | 4.8 | 328 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6264 | 2495.9997 | 50.5751
MBZ-4.RR.465.1 | 24422069211443 | Barlekha, Hatbondo, Joporpur Road, Sushendra Chondo Nat | 2019-08-27 | MP1032 | 7.3 | 329 | 7.3 | 330 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6264 | 2495.9997 | 76.9163
MBZ-4.RR.466.1 | 24421989211489 | Barlekha, Hatbondo, Joporpur Road, Khokon Devnath | 2019-08-27 | MP1032 | 3.2 | 331 | 3.2 | 332 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6264 | 2495.9997 | 33.7167
MBZ-4.RR.467.1 | 24440999209594 | Barlekha, Surikandi, Hakkul Islam | 2019-08-28 | MP1032 | 12 | 349 | 12 | 350 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6264 | 2495.9997 | 126.4378
MBZ-4.RR.468.1 | 24440999209594 | Barlekha, Surikandi, Araduddin | 2019-08-28 | MP1032 | 4 | 353 | 4 | 354 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6264 | 2495.9997 | 42.1459
MBZ-4.RR.469.1 | 24440889210052 | Barlekha, Surikandi, Abdul Kaium | 2019-08-28 | MP1032 | 2.4 | 357 | 2.4 | 358 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6264 | 2495.9997 | 25.2876
MBZ-4.RR.470.1 | 24440609210056 | Barlekha, Surikandi, Abdur Rakib | 2019-08-28 | MP1032 | 12.8 | 359 | 12.8 | 360 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6264 | 2495.9997 | 134.867
MBZ-4.RR.471.1 | 24440509210070 | Barlekha, Surikandi, Abdur Sukkor | 2019-08-28 | MP1032 | 3.9 | 361 | 3.9 | 362 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6264 | 2495.9997 | 41.0923
MBZ-4.RR.472.1 | 24440929210072 | Barlekha, Surikandi, Mbubur Rahman | 2019-08-28 | MP1032 | 8.6 | 363 | 8.7 | 364 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6264 | 2495.9997 | 91.6674
MBZ-4.RR.473.1 | 24440829210123 | Barlekha, Surikandi, Roshgram, Ayub Ali | 2019-08-28 | MP1032 | 9.9 | 365 | 9.7 | 366 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6264 | 2495.9997 | 102.2039
MBZ-4.RR.474.1 | 24394919208476 | Barlekha, Sujanagar, Baksha Bari, Ansarul Haq | 2019-08-29 | MP1032 | 8.8 | 367 | 8.8 | 368 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6312 | 2447.9997 | 92.721
MBZ-4.RR.474.2 | 24394919208476 | Barlekha, Sujanagar, Baksha Bari, Ansarul Haq | 2022-03-13 | NQ1007 | 4.8 | 50 | 4.9 | 51 | 2022-03-13 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 4608 | 2447.9997 | 41.5859
MBZ-4.RR.475.1 | 24394999208475 | Barlekha, Sujanagar, Baksha Bari, Ala Baksha | 2019-08-29 | MP1032 | 12.7 | 369 | 12.2 | 370 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6312 | 2447.9997 | 128.5451
MBZ-4.RR.476.1 | 24442839209509 | Barlekha, Chulopara, Shankorpur, Moinul | 2019-08-29 | MP1032 | 2.3 | 371 | 2.3 | 372 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6264 | 2495.9997 | 24.2339
MBZ-4.RR.551.1 | 24414949211118 | Borolekha, Pakhiala, Chowmohoni, Word # 7, Jamal Uddin | 2019-08-26 | NQ1005 | 8.9 | 252 | 8.9 | 253 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6288 | 2471.9997 | 93.7747
MBZ-4.RR.552.1 | 24414369211154 | Borolekha, Pakhiala, Word # 7, Tutaur Rahman | 2019-08-26 | NQ1005 | 5.9 | 254 | 5.9 | 255 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6288 | 2471.9997 | 62.1652
MBZ-4.RR.553.1 | 24414019211149 | Borolekha, Pakhiala, Word # 7, Abdul Motin | 2019-08-26 | NQ1005 | 10 | 256 | 10 | 257 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6288 | 2471.9997 | 105.3648
MBZ-4.RR.554.1 | 24413649211146 | Borolekha, Pakhiala, Word # 7, Mewor Bari, Motiur Rahman | 2019-08-26 | NQ1005 | 11.9 | 258 | 11.9 | 259 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6288 | 2471.9997 | 125.3841
MBZ-4.RR.555.1 | 24413649211146 | Borolekha, Pakhiala, Word # 7, Mewor Bari, Motiur Rahman | 2019-08-26 | NQ1005 | 4.8 | 260 | 4.8 | 261 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6288 | 2471.9997 | 50.5751
MBZ-4.RR.556.1 | 24413649211146 | Borolekha, Pakhiala, Word # 7, Mewor Bari, Motiur Rahman | 2019-08-26 | NQ1005 | 8.2 | 264 | 8.2 | 265 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6288 | 2471.9997 | 86.3991
MBZ-4.RR.557.1 | 24412959211215 | Borolekha, Pakhiala, Word # 7, Pakhiala Jame Mosjid Bari, Monojir Alli | 2019-08-26 | NQ1005 | 6.4 | 266 | 6.4 | 267 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6288 | 2471.9997 | 67.4335
MBZ-4.RR.558.1 | 24420399211209 | Borolekha, Dokkhin Bazar, Nijam Shoping Moll, Ohidujjaman | 2019-08-27 | NQ1005 | 12.2 | 274 | 12.2 | 275 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6288 | 2471.9997 | 128.5451
MBZ-4.RR.559.1 | 24420669211290 | Borolekha, Mohobon, PC High School Road, Woard # 8, Bellal Uddin | 2019-08-27 | NQ1005 | 5.2 | 276 | 5.2 | 277 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6264 | 2495.9997 | 54.7897
MBZ-4.RR.560.1 | 24420719211395 | Borolekha, Mohobon, PC High School Road, Woard # 8, Abdul Rohman | 2019-08-27 | NQ1005 | 12.7 | 278 | 12.7 | 279 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6264 | 2495.9997 | 133.8133
MBZ-4.RR.561.1 | 24420719211395 | Borolekha, Mohobon, PC High School Road, Woard # 8, Abdul Rohman | 2019-08-27 | NQ1005 | 7.8 | 280 | 7.8 | 281 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6264 | 2495.9997 | 82.1846
MBZ-4.RR.562.1 | 24435209209430 | Borolekha, Goyalta Bazar, Dokkhin Surikandi, Daser Bazar, Word # 4, Samsul Islam | 2019-08-28 | NQ1005 | 11.8 | 286 | 11.8 | 287 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6264 | 2495.9997 | 124.3305
MBZ-4.RR.563.1 | 24435209209430 | Borolekha, Goyalta Bazar, Dokkhin Surikandi, Daser Bazar, Word # 4, Samsul Islam | 2019-08-28 | NQ1005 | 8.4 | 288 | 8.4 | 289 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6264 | 2495.9997 | 88.5064
MBZ-4.RR.564.1 | 24435479209472 | Borolekha, Goyalta Bazar, Dokkhin Surikandi, Daser Bazar, Ustar Alli | 2019-08-28 | NQ1005 | 11.6 | 290 | 11.6 | 291 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6264 | 2495.9997 | 122.2232
MBZ-4.RR.565.1 | 24435809209485 | Borolekha, Goyalta Bazar, Dokkhin Surikandi, Daser Bazar, Bodrul Islam | 2019-08-28 | NQ1005 | 6.5 | 292 | 6.5 | 293 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6264 | 2495.9997 | 68.4871
MBZ-4.RR.566.1 | 24441079209431 | Borolekha, Goyalta Bazar, Dokkhin Surikandi, Daser Bazar, Abul Hossen | 2019-08-28 | NQ1005 | 10 | 294 | 10 | 295 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6264 | 2495.9997 | 105.3648
MBZ-4.RR.567.1 | 24441079209431 | Borolekha, Goyalta Bazar, Dokkhin Surikandi, Daser Bazar, Fokrul Islam | 2019-08-28 | NQ1005 | 1.7 | 296 | 1.7 | 297 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6264 | 2495.9997 | 17.912
MBZ-4.RR.568.1 | 24441079209431 | Borolekha, Goyalta Bazar, Dokkhin Surikandi, Daser Bazar, Fokrul Islam | 2019-08-28 | NQ1005 | 6.2 | 298 | 6.2 | 299 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6264 | 2495.9997 | 65.3262
MBZ-4.RR.569.1 | 24442999209494 | Borolakha, Goyalta Bazar, Dokkhin Surikandi, Bahar Uddin | 2019-08-29 | NQ1005 | 10.7 | 304 | 10.7 | 305 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6264 | 2495.9997 | 112.7403
MBZ-4.RR.570.1 | 24443939209410 | Borolekha, East Shonkorpur, Word # 2, Hasu Mia | 2019-08-29 | NQ1005 | 5.1 | 306 | 5.1 | 307 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6264 | 2495.9997 | 53.7361
MBZ-4.RR.601.1 | 24413659211025 | Borlekha, Murirgul, Hospital Road, Fokrul Islam | 2019-08-26 | NQ1009 | 9.2 | 232 | 9.2 | 233 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6288 | 2471.9997 | 96.9356
MBZ-4.RR.602.1 | 24414409211074 | Borlekha, Pakhiala, Ward # 7, Hospital Road, Ojoy Lal Nath | 2019-08-26 | NQ1009 | 9.9 | 234 | 9.8 | 235 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6288 | 2471.9997 | 103.2575
MBZ-4.RR.603.1 | 24414629211060 | Borlekha, Murirgul, Ward # 6, Hospital Road, Khayrul Islam | 2019-08-26 | NQ1009 | 11.7 | 236 | 11.7 | 237 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6288 | 2471.9997 | 123.2768
MBZ-4.RR.604.1 | 24415009211110 | Borlekha, Murirgul, Ward # 6, Hospital Road, Hazi Mohammad Assuddar Ali | 2019-08-26 | NQ1009 | 7.9 | 238 | 8 | 239 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6288 | 2471.9997 | 84.2919
MBZ-4.RR.605.1 | 24415179210562 | Borlekha, Murirgul, Ward # 6, Hakaluki Road, Anawar Uddin | 2019-08-26 | NQ1009 | 9.4 | 240 | 8.9 | 241 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6288 | 2471.9997 | 93.7747
MBZ-4.RR.606.1 | 24415179210562 | Borlekha, Murirgul, Ward # 6, Hakaluki Road, Fakoruddin | 2019-08-26 | NQ1009 | 8.5 | 242 | 8.5 | 243 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6288 | 2471.9997 | 89.5601
MBZ-4.RR.607.1 | 24415189210515 | Borlekha, Murirgul, Ward # 6, Hakaluki Road, Idris Ali | 2019-08-26 | NQ1009 | 9.1 | 244 | 8.6 | 245 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6288 | 2471.9997 | 90.6137
MBZ-4.RR.607.2 | 24415189210515 | Borlekha, Murirgul, Ward # 6, Hakaluki Road, Idris Ali | 2021-02-04 | MN1032 | 4.6 | 117 | 4.6 | 118 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6288 | 2471.9997 | 48.4678
MBZ-4.RR.608.1 | 24414509210411 | Borlekha, Murirgul, Ward # 5, Murirgul Road, Abu Taher Chowdhury | 2019-08-26 | NQ1009 | 5.4 | 246 | 5.4 | 247 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6288 | 2471.9997 | 56.897
MBZ-4.RR.609.1 | 24414789210390 | Borlekha, Murirgul, Ward # 5, Murirgul Road, Masud Chowdhury | 2019-08-26 | NQ1009 | 8.4 | 248 | 8.4 | 249 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6288 | 2471.9997 | 88.5064
MBZ-4.RR.610.1 | 24414809210389 | Borlekha, Murirgul, Ward # 5, Murirgul Road, Sohel Chowdhury | 2019-08-26 | NQ1009 | 8.2 | 250 | 8.2 | 251 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6288 | 2471.9997 | 86.3991
MBZ-4.RR.611.1 | 24422119211253 | Borlekha, Baroigram, Ward # 4, Nazmul Hosen | 2019-08-27 | NQ1009 | 8.7 | 264 | 8.7 | 265 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6264 | 2495.9997 | 91.6674
MBZ-4.RR.612.1 | 24422669211109 | Borlekha, Baroigram, Ward # 4, Kamal Uddin | 2019-08-27 | NQ1009 | 8.7 | 266 | 8.7 | 267 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6264 | 2495.9997 | 91.6674
MBZ-4.RR.613.1 | 24424759211267 | Borlekha, Chanda Gram Road, Additar Mohol, Hafiz Ahmed | 2019-08-28 | NQ1009 | 11.3 | 268 | 11.3 | 269 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6264 | 2495.9997 | 119.0622
MBZ-4.RR.614.1 | 24433699209536 | Borlekha, Chanda Gram Road, Talimpur, Md. Nur Uddin | 2019-08-28 | NQ1009 | 9.9 | 270 | 9.9 | 271 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6264 | 2495.9997 | 104.3112
MBZ-4.RR.615.1 | 24441489209521 | Borlekha, Surikandi, Ward # 5, Agotos Ali | 2019-08-28 | NQ1009 | 13.4 | 272 | 13.4 | 273 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6264 | 2495.9997 | 141.1888
MBZ-4.RR.616.1 | 24441489209521 | Borlekha, Surikandi, Ward # 5, Mahtab Uddin | 2019-08-28 | NQ1009 | 12.7 | 274 | 12.7 | 275 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6264 | 2495.9997 | 133.8133
MBZ-4.RR.617.1 | 24442229209561 | Borlekha, Surikandi, Ward # 5, Kotoi Mia | 2019-08-28 | NQ1009 | 4.7 | 276 | 4.7 | 277 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6264 | 2495.9997 | 49.5215
MBZ-4.RR.618.1 | 24442059210064 | Borlekha, Surikandi, Ward # 4, Abdul Ajij | 2019-08-28 | NQ1009 | 10.1 | 278 | 10.1 | 279 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6264 | 2495.9997 | 106.4185
MBZ-4.RR.619.1 | 24442059210064 | Borlekha, Surikandi, Ward # 4, Anam Uddin | 2019-08-28 | NQ1009 | 3.9 | 280 | 3.7 | 281 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6264 | 2495.9997 | 38.985
MBZ-4.RR.620.1 | 24442059210064 | Borlekha, Surikandi, Ward # 4, Mojon Bibi | 2019-08-28 | NQ1009 | 2.3 | 282 | 2.3 | 283 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6264 | 2495.9997 | 24.2339
MBZ-4.RR.621.1 | 24442059210064 | Borlekha, Surikandi, Ward # 4, Abdus Shohid | 2019-08-28 | NQ1009 | 5.3 | 284 | 5.3 | 285 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6264 | 2495.9997 | 55.8434
MBZ-4.RR.622.1 | 24442309210116 | Borlekha, 2 No. Dosher Bazar Union, Ward # 4, Badi Jongol, Abdul Jolil | 2019-08-28 | NQ1009 | 8.8 | 286 | 8.9 | 287 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6264 | 2495.9997 | 93.7747
MBZ-4.RR.623.1 | 24443129210036 | Borlekha, 2 No. Dosher Bazar Union, Ward # 4, Badi Jongol, Ibrahim Ali | 2019-08-28 | NQ1009 | 11 | 288 | 11 | 289 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6264 | 2495.9997 | 115.9013
MBZ-4.RR.624.1 | 24443139210015 | Borlekha, 2 No. Dosher Bazar Union, Ward # 4, Nir Jongol, Joshim Uddin | 2019-08-28 | NQ1009 | 3.1 | 290 | 3.1 | 291 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6264 | 2495.9997 | 32.6631
MBZ-4.RR.625.1 | 24443399210129 | Borlekha, 2 No. Dosher Bazar Union, Ward # 4, Badi Jongol, Abdus Shohid | 2019-08-28 | NQ1009 | 10.2 | 292 | 10.2 | 293 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6264 | 2495.9997 | 107.4721
MBZ-4.RR.626.1 | 24321149202387 | Kulaura, North Kulaura, Juri Road, Mobashir Ali ( Dentist ) | 2019-08-29 | NQ1009 | 1.9 | 300 | 1.9 | 301 | 2022-01-01 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6432 | 2327.9997 | 20.0193
MBZ-4.RR.626.2 | 24321149202387 | Kulaura, North Kulaura, Juri Road, Mobashir Ali ( Dentist ) | 2022-09-26 | MN1018 | 16.3 | 13 | 16.3 | 14 | 2022-09-26 | 2022-09-26 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 0 | 2327.9997 | 45.6417
MBZ-4.RR.651.1 | 24415279210327 | Barlekha, Murirgul, Baluchar, Shamsul Hoque | 2019-08-27 | NQ1009 | 5.2 | 254 | 5.2 | 255 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6288 | 2471.9997 | 54.7897
MBZ-4.RR.652.1 | 24415959211156 | Barlekha, Dakshin Bazar, Teligul Abdul Khalek | 2019-08-27 | NQ1009 | 4.6 | 258 | 4.6 | 259 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6288 | 2471.9997 | 48.4678
MBZ-4.RR.653.1 | 24420209211176 | Barlekha, Dakshin Bazar, Nimar Ali | 2019-08-27 | NQ1009 | 6.7 | 260 | 6.7 | 261 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6288 | 2471.9997 | 70.5944
MBZ-4.RR.654.1 | 24420209211176 | Barlekha, Dakshin Bazar, Tajuddin | 2019-08-27 | NQ1009 | 10 | 262 | 9.5 | 263 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6288 | 2471.9997 | 100.0966
MBZ-4.RR.655.1 | 24443359209450 | Barlekha, Chulopara, Shankorpur, Rahim Uddin | 2019-08-29 | NQ1009 | 5 | 294 | 5 | 295 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6264 | 2495.9997 | 52.6824
MBZ-4.RR.656.1 | 24443359209450 | Barlekha, Chulopara, Shankorpur, Abdus Shukur | 2019-08-29 | NQ1009 | 3.1 | 296 | 3.1 | 297 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6264 | 2495.9997 | 32.6631
MBZ-4.RR.657.1 | 24443609209434 | Barlekha, Chulopara, Shankorpur, Mujaffor Ali | 2019-08-29 | NQ1009 | 3.2 | 298 | 3.2 | 299 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6264 | 2495.9997 | 33.7167
MBZ-4.RR.701.1 | 24393779209039 | Borolekha, Suzanagar, Hashempur, Abdul Jalil | 2019-08-26 | NQ1007 | 5.7 | 338 | 5.7 | 339 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6336 | 2423.9997 | 60.0579
MBZ-4.RR.702.1 | 24393779209039 | Borolekha, Suzanagar, Hashempur, Abdul Rahim | 2019-08-26 | NQ1007 | 8.4 | 340 | 8.4 | 341 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6336 | 2423.9997 | 88.5064
MBZ-4.RR.704.1 | 24393779209039 | Borolekha, Suzanagar, Hashempur, Abdul Atik | 2019-08-26 | NQ1007 | 6.9 | 346 | 6.9 | 347 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6336 | 2423.9997 | 72.7017
MBZ-4.RR.705.1 | 24394009208591 | Borolekha, Suzanagar, Hashempur, Fajlu Mia | 2019-08-26 | NQ1007 | 15.2 | 348 | 15.2 | 349 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 6336 | 2423.9997 | 160.1545
MBZ-4.RR.706.1 | 24423209211331 | Borolekha, Boraigram, Ward # 3, H # 65, Sree Kirpa Sindhu Dotto | 2019-08-27 | NQ1007 | 8.9 | 358 | 8.9 | 359 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6264 | 2495.9997 | 93.7747
MBZ-4.RR.707.1 | 24423119211351 | Borolekha, Boraigram, Ward # 3, H # 65, Manik lal Dotto | 2019-08-27 | NQ1007 | 9.5 | 360 | 9.5 | 361 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6264 | 2495.9997 | 100.0966
MBZ-4.RR.708.1 | 24423369211043 | Borolekha, Boraigram, Gazetaka, Bazar Road, Tajul Islam | 2019-08-27 | NQ1007 | 10.2 | 362 | 10.2 | 363 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6264 | 2495.9997 | 107.4721
MBZ-4.RR.709.1 | 24441049209593 | Borolekha, Surikandi, Rosgram, Monsur Ali | 2019-08-28 | NQ1007 | 5.5 | 378 | 5.5 | 379 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6264 | 2495.9997 | 57.9506
MBZ-4.RR.710.1 | 24441469209591 | Borolekha, Surikandi, Rosgram, Foysal Ahamed | 2019-08-28 | NQ1007 | 2.4 | 382 | 2.4 | 383 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6264 | 2495.9997 | 25.2876
MBZ-4.RR.711.1 | 24441469209591 | Borolekha, Surikandi, Rosgram, Motiur Rahman | 2019-08-28 | NQ1007 | 11.3 | 384 | 11.3 | 385 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6264 | 2495.9997 | 119.0622
MBZ-4.RR.712.1 | 24441179210048 | Borolekha, Surikandi, Rosgram, Abdul Aziz | 2019-08-28 | NQ1007 | 11.3 | 386 | 11.1 | 387 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6264 | 2495.9997 | 116.9549
MBZ-4.RR.713.1 | 24441199210078 | Borolekha, Surikandi, Rosgram, Kabir Ahamed | 2019-08-28 | NQ1007 | 8.7 | 388 | 8.7 | 389 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6264 | 2495.9997 | 91.6674
MBZ-4.RR.714.1 | 24440999210086 | Borolekha, Surikandi, Rosgram, Abdul Hoque | 2019-08-28 | NQ1007 | 7.4 | 390 | 7.4 | 391 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6264 | 2495.9997 | 77.97
MBZ-4.RR.715.1 | 24441089210135 | Borolekha, Surikandi, Rosgram, Forhad Hosen | 2019-08-28 | NQ1007 | 10.4 | 392 | 10.4 | 393 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6264 | 2495.9997 | 109.5794
MBZ-4.RR.716.1 | 24440889210154 | Borolekha, Surikandi, Rosgram, Amir Uddin | 2019-08-28 | NQ1007 | 10.2 | 394 | 10.3 | 395 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6264 | 2495.9997 | 108.5258
MBZ-4.RR.717.1 | 24440889210154 | Borolekha, Surikandi, Rosgram, Foysal Uddin | 2019-08-28 | NQ1007 | 4.6 | 396 | 5 | 397 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6264 | 2495.9997 | 52.6824
MBZ-4.RR.718.1 | 24383409209465 | Borolekha, Dokkhin-Poschimvag, Main Road, Kalam Uddin | 2019-08-29 | NQ1007 | 9.2 | 408 | 9.3 | 409 | 2022-01-01 | 2022-09-20 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6288 | 2471.9997 | 97.9893
MBZ-4.RR.751.1 | 24391649209251 | Barlekha, Chintapur, Azimgonj Road, Shofiq Uddin | 2019-08-24 | NQ1007 | 5.1 | 249 | 5.1 | 250 | 2022-01-01 | 2022-09-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6336 | 2423.9997 | 53.7361
MBZ-4.RR.752.1 | 24391059208330 | Barlekha, Shaldigha,Shaldigha Road, Abdul Mukit | 2019-08-25 | NQ1007 | 3.9 | 267 | 3.9 | 268 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6312 | 2447.9997 | 41.0923
MBZ-4.RR.753.1 | 24391109208325 | Barlekha, Shaldigha,Shaldigha Road, Abdus Shohid | 2019-08-25 | NQ1007 | 7.6 | 269 | 7.6 | 270 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6312 | 2447.9997 | 80.0773
MBZ-4.RR.754.1 | 24391109208325 | Barlekha, Shaldigha,Shaldigha Road, Abdul Gofur | 2019-08-25 | NQ1007 | 4.7 | 271 | 4.7 | 272 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6312 | 2447.9997 | 49.5215
MBZ-4.RR.755.1 | 24390949208317 | Barlekha, Shaldigha,Shaldigha Road, Ward # 5, Monirul Islam Repon | 2019-08-25 | NQ1007 | 4.6 | 273 | 4.6 | 274 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6312 | 2447.9997 | 48.4678
MBZ-4.RR.756.1 | 24390949208317 | Barlekha, Shaldigha,Shaldigha Road, Ward # 5, Monirul Islam Repon | 2019-08-25 | NQ1007 | 27.9 | 275 | 28 | 276 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 28 | 28 | 1.68 | 1.68 | 0.0007168 | 100% | 0% | 1.68 | 1.68 | 0.0011869 | 28 | 0.033678 | 0.033678 |  | 0 | 0 | 6312 | 2447.9997 | 295.0215
MBZ-4.RR.757.1 | 24390949208317 | Barlekha, Shaldigha,Shaldigha Road, Ward # 5, Monirul Islam Repon | 2019-08-25 | NQ1007 | 6.3 | 277 | 6.3 | 278 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6312 | 2447.9997 | 66.3798
MBZ-4.RR.758.1 | 24390639208326 | Barlekha Sujanagar, Shaldigha, Ward # 5, Siddikur Rahman | 2019-08-25 | NQ1007 | 6.2 | 281 | 6.2 | 282 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6312 | 2447.9997 | 65.3262
MBZ-4.RR.759.1 | 24390639208326 | Barlekha Sujanagar, Shaldigha, Ward # 5, Azizur Rahman | 2019-08-25 | NQ1007 | 2.7 | 283 | 2.7 | 284 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6312 | 2447.9997 | 28.4485
MBZ-4.RR.760.1 | 24390519208314 | Barlekha Sujanagar, Shaldigha, Ward # 5, Shofiq Uddin | 2019-08-25 | NQ1007 | 5 | 285 | 5 | 286 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6312 | 2447.9997 | 52.6824
MBZ-4.RR.761.1 | 24390469208312 | Barlekha Sujanagar, Shaldigha, Ward # 5, H # 74, Monu Mia | 2019-08-25 | NQ1007 | 3.3 | 287 | 3.3 | 288 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6312 | 2447.9997 | 34.7704
MBZ-4.RR.762.1 | 24392459208388 | Barlekha, North Sujanagar, Ward # 7, Abdul Munim | 2019-08-26 | NQ1007 | 8.6 | 293 | 8.6 | 294 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6312 | 2447.9997 | 90.6137
MBZ-4.RR.764.1 | 24392909208447 | Barlekha, North Sujanagar, Ward # 7, Sayed Hossen | 2019-08-26 | NQ1007 | 6.2 | 298 | 6.2 | 299 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6312 | 2447.9997 | 65.3262
MBZ-4.RR.765.1 | 24392909208447 | Barlekha, North Sujanagar, Ward # 7, Sayed Hossen | 2019-08-26 | NQ1007 | 5.9 | 300 | 5.9 | 301 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6312 | 2447.9997 | 62.1652
MBZ-4.RR.765.2 | 24392909208447 | Barlekha, North Sujanagar, Ward # 7, Sayed Hossen | 2019-08-26 | NQ1007 | 6.8 | 302 | 6.8 | 303 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6312 | 2447.9997 | 71.6481
MBZ-4.RR.766.1 | 24392909208447 | Barlekha, North Sujanagar, Ward # 7, Abdul Hamid | 2019-08-26 | NQ1007 | 2 | 304 | 1.9 | 305 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6312 | 2447.9997 | 20.0193
MBZ-4.RR.767.1 | 24392949208428 | Barlekha, North Sujanagar, Ward # 7, Bozlur Rahman | 2019-08-26 | NQ1007 | 11.5 | 306 | 11.5 | 307 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6312 | 2447.9997 | 121.1695
MBZ-4.RR.768.1 | 24394129208510 | Barlekha, North Sujanagar, Ward # 7, Dalan Bari | 2019-08-26 | NQ1007 | 4.5 | 310 | 4.6 | 311 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6312 | 2447.9997 | 48.4678
MBZ-4.RR.769.1 | 24394959208589 | Barlekha, North Sujanagar, Ward # 6, Tofayel Ahmed | 2019-08-27 | NQ1007 | 4.3 | 350 | 4.3 | 351 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6312 | 2447.9997 | 45.3069
MBZ-4.RR.770.1 | 24395419208512 | Barlekha, North Sujanagar, Ward # 6, Hazi Mohammad Musabber Ali | 2019-08-27 | NQ1007 | 3.7 | 352 | 3.7 | 353 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6312 | 2447.9997 | 38.985
MBZ-4.RR.771.1 | 24395409209048 | Barlekha, North Sujanagar, Ward # 6, Mobu Mia | 2019-08-27 | NQ1007 | 5.8 | 356 | 5.8 | 357 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6312 | 2447.9997 | 61.1116
MBZ-4.RR.772.1 | 24425099211162 | Barlekha, Gaziteka, Chandrogram Road, Ward # 3, Nurul Islam | 2019-08-28 | NQ1007 | 3.4 | 364 | 3.4 | 365 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6264 | 2495.9997 | 35.824
MBZ-4.RR.773.1 | 24432809209528 | Barlekha, Talimpur, Noabari Road, Ward # 1, Hazi Abdur Rahman | 2019-08-28 | NQ1007 | 7.9 | 366 | 7.9 | 367 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6264 | 2495.9997 | 83.2382
MBZ-4.RR.774.1 | 24432809209528 | Barlekha, Talimpur, Noabari Road, Ward # 1, Hazi Abdur Rahman | 2019-08-28 | NQ1007 | 6.1 | 368 | 6.1 | 369 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6264 | 2495.9997 | 64.2725
MBZ-4.RR.775.1 | 24432559209540 | Barlekha, Talimpur, Noabari Road, Ward # 1, Alimuddin | 2019-08-28 | NQ1007 | 4.6 | 370 | 4.6 | 371 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6264 | 2495.9997 | 48.4678
MBZ-4.RR.776.1 | 24432519209549 | Barlekha, Talimpur, Noabari Road, Ward # 1, Abdul Hannan | 2019-08-28 | NQ1007 | 12.5 | 372 | 12.5 | 373 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6264 | 2495.9997 | 131.706
MBZ-4.RR.777.1 | 24432299209548 | Barlekha, Talimpur, Noabari Road, Ward # 1, Abdus Sukkur | 2019-08-28 | NQ1007 | 6 | 374 | 6.1 | 375 | 2022-01-01 | 2022-09-19 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6264 | 2495.9997 | 64.2725
MBZ-4.RR.778.1 | 24390309208130 | Barlekha, West Shaldigha, Ward # 5, Shofiqur Rahman | 2019-08-29 | NQ1007 | 11.2 | 398 | 11.3 | 399 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6312 | 2447.9997 | 119.0622
MBZ-4.RR.779.1 | 24390309208130 | Barlekha, West Shaldigha, Ward # 5, Shofiqur Rahman | 2019-08-29 | NQ1007 | 9.1 | 400 | 9.1 | 401 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6312 | 2447.9997 | 95.882
MBZ-4.RR.780.1 | 24390329208126 | Barlekha, West Shaldigha, Ward # 5, Abdul Malek | 2019-08-29 | NQ1007 | 6.5 | 402 | 6.5 | 403 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6312 | 2447.9997 | 68.4871
MBZ-4.RR.781.1 | 24390329208126 | Barlekha, West Shaldigha, Ward # 5, Abdul Malek | 2019-08-29 | NQ1007 | 2.3 | 404 | 2.3 | 405 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6312 | 2447.9997 | 24.2339
MBZ-4.RR.782.1 | 24390329208126 | Barlekha, West Shaldigha, Ward # 5, Abdul Malek | 2019-08-29 | NQ1007 | 3.1 | 406 | 3.1 | 407 | 2022-01-01 | 2022-09-21 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6312 | 2447.9997 | 32.6631
SMG-1.CR.1.1 | 25040929123501 | Sunamganj, Old busstand, Nureni Moll Resturent | 2019-01-24 | NQ1000 | 17.9 | 214 | 17.9 | 215 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 7392 | 1367.9997 | 188.603
SMG-1.CR.2.1 | 25035579124446 | Sunamgonj Govt Collage Girls Hostel | 2019-08-04 | LP1002 | 12.3 | 742 | 12.3 | 743 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7248 | 1511.9997 | 129.5987
SMG-1.CR.4.1 | 25040349124026 | Sunamgonj Mohila College, Kushiara Girls Hostel | 2019-08-06 | LP1002 | 19.2 | 823 | 19.7 | 824 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 19.7 | 19.7 | 1.182 | 1.182 | 0.0007168 | 100% | 0% | 1.182 | 1.182 | 0.0011869 | 28 | 0.023695 | 0.023695 |  | 0 | 0 | 7392 | 1367.9997 | 207.5687
SMG-1.CR.4.2 | 25040349124026 | Sunamgonj Mohila College, Kushiara Girls Hostel | 2019-08-06 | LP1002 | 9.4 | 825 | 9.4 | 826 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7392 | 1367.9997 | 99.0429
SMG-1.CR.5.1 | 25041299123574 | Sunamganj, Kali Bari Road, Oitiyho Mishti Ghor | 2019-08-07 | LP1002 | 15.3 | 11 | 15.3 | 12 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 7392 | 1367.9997 | 161.2082
SMG-1.CR.7.1 | 25034949123321 | Sunamganj, Hazi para, Jamia Islamia Darul Ulum Madania, (Opposite Sunamganj Circuit House) | 2019-08-29 | LP1002 | 11 | 495 | 11 | 496 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7320 | 1439.9997 | 115.9013
SMG-1.CR.8.1 | 25034889123360 | Sunamganj Circuit House | 2019-08-29 | LP1002 | 8.8 | 497 | 8.8 | 498 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7320 | 1439.9997 | 92.721
SMG-1.RR.1.1 | 25041659123395 | Sunamganj, Uttar Arphin Nagar, Ward # 06, H # 274, Monir Uddin | 2019-01-24 | NQ1002 | 1.8 | 100 | 1.8 | 101 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7344 | 1415.9997 | 18.9657
SMG-1.RR.2.1 | 25041729123310 | Sunamganj, Tegoria, Morol Hati, Word # 07, Moulana Anawar Hossen | 2019-01-24 | NQ1002 | 24 | 102 | 24 | 103 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 24 | 24 | 1.44 | 1.44 | 0.0007168 | 100% | 0% | 1.44 | 1.44 | 0.0011869 | 28 | 0.028867 | 0.028867 |  | 0 | 0 | 7344 | 1415.9997 | 252.8756
SMG-1.RR.3.1 | 25040959123317 | Sunamganj, Tegoria, Majher Hati, Ward # 07, Iqbal Hossen | 2019-01-24 | NQ1002 | 11.2 | 104 | 11.2 | 105 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7344 | 1415.9997 | 118.0086
SMG-1.RR.4.1 | 25040959123317 | Sunamganj, Tegoria, Majher Hati, Ward # 07, Belal Hossain | 2019-01-24 | NQ1002 | 2.3 | 106 | 2.3 | 107 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7344 | 1415.9997 | 24.2339
SMG-1.RR.5.1 | 25040829123318 | Sunamganj, Tegoria, Majher Hati, Ward # 07, Majharul Islam | 2019-01-24 | NQ1002 | 15 | 108 | 15.1 | 109 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7344 | 1415.9997 | 159.1009
SMG-1.RR.5.2 | 25040829123318 | Sunamganj, Tegoria, Majher Hati, Ward # 07, Majharul Islam | 2019-01-24 | NQ1002 | 31.8 | 110 | 31.8 | 111 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 31.8 | 31.8 | 1.908 | 1.908 | 0.0007168 | 100% | 0% | 1.908 | 1.908 | 0.0011869 | 28 | 0.038249 | 0.038249 |  | 0 | 0 | 7344 | 1415.9997 | 335.0601
SMG-1.RR.6.1 | 25041089123342 | Sunamganj, Tegoria, Lomba Hati, Ward # 07, Md. Joynal Abedin | 2019-01-24 | NQ1002 | 5.9 | 112 | 6 | 113 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7344 | 1415.9997 | 63.2189
SMG-1.RR.7.1 | 25041379124549 | Sunamganj, Alipara, Dhansiri-26, H # 241, Intikhab Alam | 2019-08-03 | LP1002 | 31.8 | 712 | 31.8 | 713 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 31.8 | 31.8 | 1.908 | 1.908 | 0.0007168 | 100% | 0% | 1.908 | 1.908 | 0.0011869 | 28 | 0.038249 | 0.038249 |  | 0 | 0 | 7416 | 1343.9997 | 335.0601
SMG-1.RR.8.1 | 25041529124528 | Sunamganj, Alipara, Dhansiri-30, Abu Sahin quresi | 2019-08-03 | LP1002 | 9 | 714 | 9 | 715 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7416 | 1343.9997 | 94.8283
SMG-1.RR.9.1 | 25041559124519 | Sunamganj, Alipara, Dhansiri-30/1, Md. Kamal uddin | 2019-08-03 | LP1002 | 2.4 | 716 | 2.4 | 717 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7416 | 1343.9997 | 25.2876
SMG-1.RR.10.1 | 25041259124482 | Sunamganj, Shologhar, Bilpar, Udoyon-9, Azmir Villa | 2019-08-03 | LP1002 | 7.2 | 718 | 7.2 | 719 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7248 | 1511.9997 | 75.8627
SMG-1.RR.11.1 | 25041259124482 | Sunamganj, Shologhar, Bilpar, Udoyon-10, Azizur | 2019-08-03 | LP1002 | 9.9 | 720 | 9.9 | 721 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7248 | 1511.9997 | 104.3112
SMG-1.RR.12.1 | 25040979124458 | Sunamganj, Shologhar, Bilpar, Udoyon-49, Haris uddin | 2019-08-03 | LP1002 | 8.9 | 722 | 8.9 | 723 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7248 | 1511.9997 | 93.7747
SMG-1.RR.13.1 | 25034429124472 | Hasan Nagar, East Sultanpur, Morol Bari, Moyna mia,(Kacha Moyna Mia) | 2019-08-04 | LP1002 | 8.5 | 746 | 8.5 | 747 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7248 | 1511.9997 | 89.5601
SMG-1.RR.14.1 | 25034429124472 | Hasan Nagar, East Sultanpur, Morol Bari, Suvas uddin | 2019-08-04 | LP1002 | 8.1 | 748 | 8.2 | 749 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7248 | 1511.9997 | 86.3991
SMG-1.RR.15.1 | 25034429124472 | Hasan Nagar, East Sultanpur, Morol Bari, Hosen Ali | 2019-08-04 | LP1002 | 10.9 | 750 | 10.9 | 751 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7248 | 1511.9997 | 114.8476
SMG-1.RR.16.1 | 25034429124472 | Hasan Nagar, East Sultanpur, Morol Bari, Selim mia | 2019-08-04 | LP1002 | 5.2 | 752 | 5.2 | 753 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7248 | 1511.9997 | 54.7897
SMG-1.RR.17.1 | 25034589124475 | Hasan Nagar, East Sultanpur, Ataul Haq, (Near Government Collage) | 2019-08-04 | LP1002 | 9.8 | 754 | 9.4 | 755 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7248 | 1511.9997 | 99.0429
SMG-1.RR.18.1 | 25034589124475 | Hasan Nagar, East Sultanpur, Mojibor Rahman, (Near Government Collage) | 2019-08-04 | LP1002 | 10.7 | 758 | 10.7 | 759 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7248 | 1511.9997 | 112.7403
SMG-1.RR.19.1 | 25034589124475 | Hasan Nagar, East Sultanpur, Selim Jabed, (Near Government Collage) | 2019-08-04 | LP1002 | 8.9 | 760 | 8.9 | 761 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7248 | 1511.9997 | 93.7747
SMG-1.RR.19.2 | 25034589124475 | Hasan Nagar, East Sultanpur, Selim Jabed, (Near Government Collage) | 2019-08-04 | LP1002 | 1.7 | 762 | 1.7 | 763 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7248 | 1511.9997 | 17.912
SMG-1.RR.19.3 | 25034589124475 | Hasan Nagar, East Sultanpur, Selim Jabed, (Near Government Collage) | 2019-08-04 | LP1002 | 10.1 | 764 | 9.8 | 765 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7248 | 1511.9997 | 103.2575
SMG-1.RR.20.1 | 25034639124445 | Hasan Nagar, East Sultanpur, Chad Bodon, (Near Government Collage) | 2019-08-04 | LP1002 | 5.8 | 766 | 5.8 | 767 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7248 | 1511.9997 | 61.1116
SMG-1.RR.21.1 | 25041869123374 | Sunamganj, North Arfin Nagor, Md. Mohibul Islam, Nearby Surma Nodi | 2019-01-24 | NQ1009 | 7.1 | 50 | 7.1 | 51 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7344 | 1415.9997 | 74.809
SMG-1.RR.22.1 | 25041869123374 | Sunamganj, North Arfin Nagor, Md Nazim Uddin, Nearby Surma Nodi | 2019-01-24 | NQ1009 | 3.5 | 52 | 3.5 | 53 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7344 | 1415.9997 | 36.8777
SMG-1.RR.23.1 | 25041659123380 | Sunamganj, North Arfin Nagor, Lilu Mia, Nearby Surma Nodi | 2019-01-24 | NQ1009 | 14 | 54 | 14 | 55 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 7344 | 1415.9997 | 147.5107
SMG-1.RR.24.1 | 25041659123380 | Sunamganj, North Arfin Nagor, H # 61, MD.Sobzal, Nearby Surma Nodi | 2019-01-24 | NQ1009 | 10.5 | 56 | 10.5 | 57 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7344 | 1415.9997 | 110.6331
SMG-1.RR.24.2 | 25041659123380 | Sunamganj, North Arfin Nagor, H # 61, MD.Sobzal, Nearby Surma Nodi | 2019-01-24 | NQ1009 | 21.4 | 58 | 21.4 | 59 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 7344 | 1415.9997 | 225.4807
SMG-1.RR.25.1 | 25041309123362 | Sunamganj, South Arfin Nagor, Samrun Nur ,Nearby Surma Nodi | 2019-01-24 | NQ1009 | 2 | 60 | 2.1 | 61 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7344 | 1415.9997 | 22.1266
SMG-1.RR.26.1 | 25041309123362 | Sunamganj, South Arfin Nagor, Samrun Nur ,Nearby Surma Nodi | 2019-01-24 | NQ1009 | 6.1 | 62 | 6.1 | 63 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7344 | 1415.9997 | 64.2725
SMG-1.RR.27.1 | 25041239123365 | Sunamganj, South Arfin Nagor, Taghoria, Khaled Mia, Nearby Surma Nodi | 2019-01-24 | NQ1009 | 2.7 | 64 | 2.7 | 65 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7344 | 1415.9997 | 28.4485
SMG-1.RR.28.1 | 25034639124445 | Hasan Nagar, East Sultanpur, A. Hai Chairman | 2019-08-04 | LP1002 | 9 | 768 | 8.4 | 769 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7248 | 1511.9997 | 88.5064
SMG-1.RR.29.1 | 25034719124409 | Hasan Nagar, Sultan Pur R/A, Masuk Mia | 2019-08-04 | LP1002 | 9 | 770 | 9 | 771 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7248 | 1511.9997 | 94.8283
SMG-1.RR.30.1 | 25034719124409 | Hasan Nagar, Sultan Pur R/A, Sayed Anowar Ali | 2019-08-04 | LP1002 | 10.5 | 772 | 10.5 | 773 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7248 | 1511.9997 | 110.6331
SMG-1.RR.31.1 | 25034719124366 | Hasan Nagar, Kuriar Par, Sahidul Kabir Chowdhury | 2019-08-05 | LP1002 | 44.6 | 774 | 44.6 | 775 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 44.6 | 44.6 | 2.676 | 2.676 | 0.0007168 | 100% | 0% | 2.676 | 2.676 | 0.0011869 | 28 | 0.053645 | 0.053645 |  | 0 | 0 | 7248 | 1511.9997 | 469.9271
SMG-1.RR.32.1 | 25035339124343 | Hasan Nagar, Kuriar Par, Beside A. Halk Ukil House | 2019-08-05 | LP1002 | 5.8 | 778 | 6 | 779 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7248 | 1511.9997 | 63.2189
SMG-1.RR.33.1 | 25035469124319 | Hasan Nagar, Kuriar Par, Kolagau Kuthir, Nazrul Islam | 2019-08-05 | LP1002 | 4.8 | 780 | 4.8 | 781 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7248 | 1511.9997 | 50.5751
SMG-1.RR.34.1 | 25035419124298 | Hasan Nagar, Nisorgo- 39, A. Karim | 2019-08-05 | LP1002 | 11.3 | 782 | 11.3 | 783 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7248 | 1511.9997 | 119.0622
SMG-1.RR.35.1 | 25035419124298 | Hasan Nagar, Nisorgo- 38, Asoddar Ali | 2019-08-05 | LP1002 | 12 | 784 | 12 | 785 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7248 | 1511.9997 | 126.4378
SMG-1.RR.35.2 | 25035419124298 | Hasan Nagar, Nisorgo- 38, Asoddar Ali | 2021-10-02 | NQ1007 | 5.5 | 41 | 5.5 | 42 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7248 | 1511.9997 | 57.9506
SMG-1.RR.36.1 | 25035419124298 | Hasan Nagar, Nisorgo- 37, Younus Mohammad | 2019-08-05 | LP1002 | 10.6 | 786 | 10.6 | 787 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7248 | 1511.9997 | 111.6867
SMG-1.RR.37.1 | 25035549124288 | Hasan Nagar, Nisorgo, Saimulla | 2019-08-05 | LP1002 | 12.1 | 788 | 11.9 | 789 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 6144 | 0 | 1104 | 1511.9997 | 37.4435
SMG-1.RR.38.1 | 25035719124279 | Hasan Nagar, Nisorgo- 9/2, Abdul Karim | 2019-08-05 | LP1002 | 4 | 790 | 4 | 791 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7248 | 1511.9997 | 42.1459
SMG-1.RR.39.1 | 25035719124279 | Hasan Nagar, Nisorgo- 11, Abu Nasar | 2019-08-05 | LP1002 | 5.2 | 792 | 5.2 | 793 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7248 | 1511.9997 | 54.7897
SMG-1.RR.40.1 | 25035349124249 | Hasan Nagar, Nisorgo- 24, Saleha Begum | 2019-08-05 | LP1002 | 11.6 | 794 | 11.2 | 795 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7272 | 1487.9997 | 118.0086
SMG-1.RR.41.1 | 25041129123433 | Sunamganj, Middel Arpin Nagor, Saikot-22,Anwour Uddin | 2019-01-24 | NQ1000 | 10.8 | 202 | 10.5 | 203 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7392 | 1367.9997 | 110.6331
SMG-1.RR.42.1 | 25041359123427 | Sunamganj, Middel Arpin Nagor, Word # 06, H # 87, Atiqur Rahman | 2019-01-24 | NQ1000 | 4.6 | 204 | 4.6 | 205 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7392 | 1367.9997 | 48.4678
SMG-1.RR.43.1 | 25041359123427 | Sunamganj, Middel Arpin Nagor, Word # 06, H # 115, Habib ali | 2019-01-24 | NQ1000 | 2.2 | 206 | 2.2 | 207 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7392 | 1367.9997 | 23.1803
SMG-1.RR.44.1 | 25041689123415 | Sunamganj, Middel Arpin Nagor, Word # 06, Sahin Masla Mill (Left) | 2019-01-24 | NQ1000 | 8 | 210 | 8 | 211 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7392 | 1367.9997 | 84.2919
SMG-1.RR.45.1 | 25041689123415 | Sunamganj, Middel Arpin Nagor, Word # 06, Sahin Masla Mill (Right) | 2019-01-24 | NQ1000 | 4.9 | 212 | 4.9 | 213 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7392 | 1367.9997 | 51.6288
SMG-1.RR.46.1 | 25035129124258 | Hasan Nagar, Nisorgo- 26, Md Habibur Rahman | 2019-08-05 | LP1002 | 4 | 796 | 4 | 797 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7272 | 1487.9997 | 42.1459
SMG-1.RR.46.2 | 25035129124258 | Hasan Nagar, Nisorgo- 26, Md Habibur Rahman | 2022-02-27 | LU1001 | 13.1 | 8 | 13.1 | 9 | 2022-02-27 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 5904 | 1487.9997 | 116.4729
SMG-1.RR.47.1 | 25035899124279 | Hasan Nagar, Moynar Point, Tasid Ahmed | 2019-08-05 | LP1002 | 10.1 | 798 | 10.1 | 799 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7272 | 1487.9997 | 106.4185
SMG-1.RR.47.2 | 25035899124279 | Hasan Nagar, Moynar Point, Tasid Ahmed | 2022-10-31 | MN1018 | 5.1 | 108 | 5.1 | 109 | 2022-10-31 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 0 | 1487.9997 | 9.1278
SMG-1.RR.48.1 | 25040139123592 | Sunamganj, Notun Para, Niloy-13/1, Hazi A. Khalek | 2019-08-06 | LP1002 | 6.8 | 835 | 6.8 | 836 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7296 | 1463.9997 | 71.6481
SMG-1.RR.49.1 | 25040139123592 | Sunamganj, Notun Para, Niloy-12, Sajidur Rahaman | 2019-08-06 | LP1002 | 9.5 | 837 | 9.6 | 838 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7296 | 1463.9997 | 101.1502
SMG-1.RR.50.1 | 25040559123598 | Sunamganj, Notun Para, Niloy-5/1, Saydur Rahman | 2019-08-06 | LP1002 | 9.3 | 839 | 9.3 | 840 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7392 | 1367.9997 | 97.9893
SMG-1.RR.51.1 | 25040559123598 | Sunamganj, Notun Para, Niloy-5, Rejaur Rahman Helal | 2019-08-06 | LP1002 | 7.8 | 841 | 7.8 | 842 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7392 | 1367.9997 | 82.1846
SMG-1.RR.52.1 | 25040609123588 | Sunamganj, Jamai Para, Jonosastho Prokausal Vhobon | 2019-08-06 | LP1002 | 4 | 843 | 4 | 844 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7392 | 1367.9997 | 42.1459
SMG-1.RR.53.1 | 25040659123577 | Sunamganj, Jamai Para, Niloy-2, Bablu, (Near Jonosastho Prokausal Vhobon) | 2019-08-06 | LP1002 | 11.1 | 845 | 11.1 | 846 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7392 | 1367.9997 | 116.9549
SMG-1.RR.53.2 | 25040659123577 | Sunamganj, Jamai Para, Niloy-2, Bablu, (Near Jonosastho Prokausal Vhobon) | 2019-08-06 | LP1002 | 8.1 | 847 | 8.2 | 848 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7392 | 1367.9997 | 86.3991
SMG-1.RR.54.1 | 25040919123582 | Sunamganj, Jamai Para, Mohona-5, Safiqul Haque | 2019-08-06 | LP1002 | 7 | 851 | 7 | 852 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7392 | 1367.9997 | 73.7554
SMG-1.RR.55.1 | 25040919123582 | Sunamganj, Jamai Para, Mohona-4, Md Mobarak Hosen | 2019-08-06 | LP1002 | 3.9 | 853 | 3.9 | 854 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7392 | 1367.9997 | 41.0923
SMG-1.RR.56.1 | 25040729123547 | Sunamganj, Jamai Para, Mohona-13, Md Mohibul Islam Chowdhrey | 2019-08-06 | LP1002 | 8.2 | 855 | 8.2 | 856 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7392 | 1367.9997 | 86.3991
SMG-1.RR.57.1 | 25040729123547 | Sunamganj, Jamai Para, Mohona-14, Abdul Hannan | 2019-08-06 | LP1002 | 4.3 | 857 | 4.3 | 858 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7392 | 1367.9997 | 45.3069
SMG-1.RR.58.1 | 25040729123547 | Sunamganj, Jamai Para, Mohona-14, Md Jogolul Haque | 2019-08-06 | LP1002 | 28.5 | 859 | 28.5 | 860 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 28.5 | 28.5 | 1.71 | 1.71 | 0.0007168 | 100% | 0% | 1.71 | 1.71 | 0.0011869 | 28 | 0.03428 | 0.03428 |  | 0 | 0 | 7392 | 1367.9997 | 300.2897
SMG-1.RR.59.1 | 25041069124015 | Sunamganj, Kali Bari Road, Bul Chand High School Gate, Modina Banu | 2019-08-07 | LP1002 | 13.1 | 1 | 13.1 | 2 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7392 | 1367.9997 | 138.0279
SMG-1.RR.60.1 | 25041069124015 | Sunamganj, Kali Bari Road, Bul Chand High School Gate, Searbul Ahmed | 2019-08-07 | LP1002 | 12.3 | 3 | 12.3 | 4 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7392 | 1367.9997 | 129.5987
SMG-1.RR.61.1 | 25041199123392 | Sunamgonj,South Arpin Nagar, Razu Ahmed | 2019-01-24 | NQ1005 | 8.3 | 75 | 8.3 | 76 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7392 | 1367.9997 | 87.4528
SMG-1.RR.62.1 | 25041199123392 | Sunamgonj,South Arpin Nagar, Sonjob Ali | 2019-01-24 | NQ1005 | 8 | 77 | 7.7 | 78 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7392 | 1367.9997 | 81.1309
SMG-1.RR.63.1 | 25041229123394 | Sunamgonj,South Arpin Nagar, Asgar Noor | 2019-01-24 | NQ1005 | 1.7 | 79 | 1.7 | 80 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7392 | 1367.9997 | 17.912
SMG-1.RR.64.1 | 25041399123400 | Sunamgonj,South Arpin Nagar, near by Govt. primary school, Selim Alam | 2019-01-24 | NQ1005 | 10.3 | 81 | 10.2 | 82 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7392 | 1367.9997 | 107.4721
SMG-1.RR.65.1 | 25041499123413 | Sunamgonj,Moddho Arpin Nagar, Rakib Mia | 2019-01-24 | NQ1005 | 11.1 | 83 | 11.1 | 84 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7392 | 1367.9997 | 116.9549
SMG-1.RR.66.1 | 25040929123430 | Sunamgonj,South Arpin Nagar, Abdur Rashid | 2019-01-24 | NQ1005 | 1.4 | 85 | 1.4 | 86 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7392 | 1367.9997 | 14.7511
SMG-1.RR.67.1 | 25040819123438 | Sunamgonj,South Arpin Nagar, Faznur Mia | 2019-01-24 | NQ1005 | 1.9 | 87 | 1.9 | 88 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7392 | 1367.9997 | 20.0193
SMG-1.RR.68.1 | 25040089125005 | Ali Para, Pollobi R/A, Block # H, Collage Road, H # 17, Moniruzzaman | 2019-08-03 | LP1002 | 11.8 | 690 | 11.8 | 691 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7416 | 1343.9997 | 124.3305
SMG-1.RR.68.2 | 25040089125005 | Ali Para, Pollobi R/A, Block # H, Collage Road, H # 17, Moniruzzaman | 2019-08-03 | LP1002 | 21.6 | 692 | 21.6 | 693 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 7416 | 1343.9997 | 227.588
SMG-1.RR.69.1 | 25040409125024 | Ali Para, Pollobi R/A, Word # 1, Collage Road, H # 9/4, Md. Dulal Mia | 2019-08-03 | LP1002 | 13.8 | 694 | 13.8 | 695 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7416 | 1343.9997 | 145.4034
SMG-1.RR.70.1 | 25040489125031 | Ali Para, Pollobi R/A, Collage Road, H # 768, Shohana Bagum | 2019-08-03 | LP1002 | 12.5 | 696 | 12.5 | 697 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7416 | 1343.9997 | 131.706
SMG-1.RR.71.1 | 25040489125031 | Ali Para, Pollobi R/A, Collage Road, H # 8/4, Abul Kalam | 2019-08-03 | LP1002 | 15.3 | 698 | 15.3 | 699 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 7416 | 1343.9997 | 161.2082
SMG-1.RR.72.1 | 25040489125031 | Ali Para, Pollobi R/A, Collage Road, Abul Kasham Khokon | 2019-08-03 | LP1002 | 6.8 | 700 | 6.8 | 701 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7416 | 1343.9997 | 71.6481
SMG-1.RR.73.1 | 25040769125005 | Ali Para, Pollobi R/A, Collage Road, Salma Monjil | 2019-08-03 | LP1002 | 7.5 | 702 | 7.7 | 703 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7416 | 1343.9997 | 81.1309
SMG-1.RR.74.1 | 25040749125019 | Ali Para, Pollobi R/A, Collage Road, H # 3/2, Nurjhan Mohol | 2019-08-03 | LP1002 | 6.6 | 706 | 6.6 | 707 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7416 | 1343.9997 | 69.5408
SMG-1.RR.75.1 | 25040819125013 | Ali Para, Pollobi R/A, Collage Road, H # 2/12, Hazi Amir Uddin | 2019-08-03 | LP1002 | 11.3 | 708 | 11.4 | 709 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7416 | 1343.9997 | 120.1159
SMG-1.RR.76.1 | 25040839125034 | Ali Para, Pollobi R/A, Collage Road, H # 2/10, Hazi Nozrul Islam | 2019-08-03 | LP1002 | 6.9 | 710 | 6.9 | 711 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7416 | 1343.9997 | 72.7017
SMG-1.RR.77.1 | 25040429124453 | Billpar, Udoyon R/A, AbuHanifa Road, Adv. Anichuzzaman H# 36/6 | 2019-08-04 | LP1002 | 8.9 | 724 | 9.5 | 725 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7248 | 1511.9997 | 100.0966
SMG-1.RR.78.1 | 25040309124464 | Billpar, Udoyon R/A, AbuHanifa Road, Abdul Bary Master H#36/3 | 2019-08-04 | LP1002 | 4.3 | 726 | 4.3 | 727 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7248 | 1511.9997 | 45.3069
SMG-1.RR.79.1 | 25040099124488 | Billpar, Udoyon R/A, AbuHanifa Road, Forid Mia,H # 32 | 2019-08-04 | LP1002 | 7.6 | 730 | 7.6 | 731 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7248 | 1511.9997 | 80.0773
SMG-1.RR.80.1 | 25035679124504 | Billpar, Udoyon R/A, AbuHanifa Road, Ajid Ray ,H#36/2 | 2019-08-04 | LP1002 | 5.2 | 732 | 5.2 | 733 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7248 | 1511.9997 | 54.7897
SMG-1.RR.81.1 | 25035679124504 | Billpar, Udoyon R/A, AbuHanifa Road, Shondro Kumar Tarebady | 2019-08-04 | LP1002 | 23.9 | 734 | 22.9 | 735 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 22.9 | 22.9 | 1.374 | 1.374 | 0.0007168 | 100% | 0% | 1.374 | 1.374 | 0.0011869 | 28 | 0.027544 | 0.027544 |  | 0 | 0 | 7248 | 1511.9997 | 241.2854
SMG-1.RR.82.1 | 25035499124522 | Billpar, Udoyon R/A, Back side of Collage ,Shodhangsu Vashon Tenobodi | 2019-08-04 | LP1002 | 12.9 | 736 | 12.9 | 737 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7248 | 1511.9997 | 135.9206
SMG-1.RR.83.1 | 25035499124522 | Billpar, Udoyon R/A, Back side of Collage ,Modon Gopal Day | 2019-08-04 | LP1002 | 5.6 | 738 | 5.6 | 739 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7248 | 1511.9997 | 59.0043
SMG-1.RR.83.2 | 25035499124522 | Billpar, Udoyon R/A, Back side of Collage ,Modon Gopal Day | 2021-01-11 | MN1018 | 9.7 | 7 | 9.7 | 8 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7248 | 1511.9997 | 102.2039
SMG-1.RR.84.1 | 25035339124546 | Billpar, Udoyon R/A, Collage Road, Jamaluddin Ahammed | 2019-08-04 | LP1002 | 6.5 | 740 | 6.2 | 741 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7248 | 1511.9997 | 65.3262
SMG-1.RR.85.1 | 25034839124555 | East Sultanpur ,Beside of Collage Samsul Haque Shohel | 2019-08-04 | LP1002 | 8.5 | 744 | 8.5 | 745 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7248 | 1511.9997 | 89.5601
SMG-1.RR.85.2 | 25034839124555 | East Sultanpur ,Beside of Collage Samsul Haque Shohel | 2021-01-12 | LX1011 | 1.6 | 11 | 1.6 | 12 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7248 | 1511.9997 | 16.8584
SMG-1.RR.86.1 | 25034789124574 | East Sultan Pur, Shonam R/A, Back side of college, H# 967, Shayoda Khirun Nesha | 2019-08-05 | LP1002 | 8.2 | 800 | 8.2 | 801 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7248 | 1511.9997 | 86.3991
SMG-1.RR.87.1 | 25034799124584 | East Sultan Pur, Shonam R/A, Back side of college, Aluddin | 2019-08-05 | LP1002 | 12.8 | 802 | 12.7 | 803 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7248 | 1511.9997 | 133.8133
SMG-1.RR.88.1 | 25034929125004 | East Sultan Pur, Shonam R/A, Beside of Mosjid, Kuddus Ali | 2019-08-05 | LP1002 | 3.2 | 804 | 3.2 | 805 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7248 | 1511.9997 | 33.7167
SMG-1.RR.89.1 | 25035309124592 | Sultan Pur R/A, College Road, Abdul Aowal | 2019-08-05 | LP1002 | 6 | 806 | 5.9 | 807 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7248 | 1511.9997 | 62.1652
SMG-1.RR.90.1 | 25035029124431 | Hoson Nagar, College Road, Forint of College, Nuar Monjil | 2019-08-05 | LP1002 | 9.2 | 808 | 9.2 | 809 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7248 | 1511.9997 | 96.9356
SMG-1.RR.91.1 | 25035119124392 | Hoson Nagar, College Road, Hospatal Get, Hazi Ekbal Hossain | 2019-08-05 | LP1002 | 10.8 | 813 | 10.8 | 814 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7248 | 1511.9997 | 113.794
SMG-1.RR.91.2 | 25035119124392 | Hoson Nagar, College Road, Hospatal Get, Hazi Ekbal Hossain | 2020-10-05 | MN1032 | 2.9 | 5 | 2.9 | 6 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7248 | 1511.9997 | 30.5558
SMG-1.RR.92.1 | 25035119124392 | Hoson Nagar , College Road ,Haspatal Gate, Rosoraz Ali Mondol | 2019-08-05 | LP1002 | 7.3 | 815 | 7.3 | 816 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7248 | 1511.9997 | 76.9163
SMG-1.RR.93.1 | 25040829124023 | Badhon R/A, Block #B, Mohila College Road, H #195, Oyahidur Zaman | 2019-08-06 | LP1002 | 3.6 | 817 | 3.7 | 818 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7392 | 1367.9997 | 38.985
SMG-1.RR.93.2 | 25040829124023 | Badhon R/A, Block #B, Mohila College Road, H #195, Oyahidur Zaman | 2022-11-05 | MN1018 | 4.8 | 125 | 4.8 | 126 | 2022-11-05 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 0 | 1367.9997 | 7.898
SMG-1.RR.94.1 | 25040679124034 | Badhon R/A, Block #B, Mohila College Road, H #198, Mowlana Kutubur Rohaman | 2019-08-06 | LP1002 | 9.5 | 819 | 9.3 | 820 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7392 | 1367.9997 | 97.9893
SMG-1.RR.95.1 | 25040679124034 | Badhon R/A, Block #B, Mohila College Road, H #193, Md Abul Azad | 2019-08-06 | LP1002 | 3.3 | 821 | 3.3 | 822 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7392 | 1367.9997 | 34.7704
SMG-1.RR.96.1 | 25040009124085 | Badhon R/A, Block #B, Mohila College Road, Bonik Kuthir | 2019-08-06 | LP1002 | 5.3 | 827 | 5.3 | 828 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7296 | 1463.9997 | 55.8434
SMG-1.RR.97.1 | 25040009124085 | Badhon R/A, Block #B, Mohila College Road, Shad Mia | 2019-08-06 | LP1002 | 8.1 | 829 | 8.7 | 830 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7296 | 1463.9997 | 91.6674
SMG-1.RR.98.1 | 25035999124053 | Notun Para, Neloy- 29 R/A, H #240, Horipod Roy | 2019-08-06 | LP1002 | 12.6 | 831 | 12.6 | 832 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7296 | 1463.9997 | 132.7597
SMG-1.RR.99.1 | 25035789124016 | Notun Para, Neloy- 19/2 R/A, Adv Samsul Abedin | 2019-08-06 | LP1002 | 7.8 | 833 | 7.8 | 834 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7296 | 1463.9997 | 82.1846
SMG-1.RR.100.1 | 25041629123504 | Raypara, Nirjhor R/A, H # 9, Ajith Kumar Ray | 2019-08-18 | LP1002 | 10.1 | 77 | 10.2 | 78 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7392 | 1367.9997 | 107.4721
SMG-1.RR.101.1 | 25041129124589 | Sunamganj, Alipara Pollobi - 132 R/A, Word # 01, H # 15, Rasheda Akther | 2019-08-03 | MN1018 | 10.1 | 779 | 10.1 | 780 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7416 | 1343.9997 | 106.4185
SMG-1.RR.102.1 | 25041379124553 | Sunamganj, Dhanshiri - 28/2 R/A, Word # 01, Salaha Uddin Aftab | 2019-08-03 | MN1018 | 7.8 | 781 | 7.8 | 782 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7416 | 1343.9997 | 82.1846
SMG-1.RR.103.1 | 25041649124549 | Sunamganj, Dhanshiri- 21/1 R/A, Word # 01, Banane Para, Rabaia Islam Villa | 2019-08-03 | MN1018 | 13.3 | 783 | 13.3 | 784 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7416 | 1343.9997 | 140.1352
SMG-1.RR.104.1 | 25041869124549 | Sunamganj, Dhanshiri - 07 R/A, Word # 01, Junad Ahmed, H # 1018 | 2019-08-03 | MN1018 | 24.8 | 787 | 24.8 | 788 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 24.8 | 24.8 | 1.488 | 1.488 | 0.0007168 | 100% | 0% | 1.488 | 1.488 | 0.0011869 | 28 | 0.029829 | 0.029829 |  | 0 | 0 | 7416 | 1343.9997 | 261.3047
SMG-1.RR.105.1 | 25041959124555 | Sunamganj,Dhanshiri - 20 R/A, Word # 01, Banane Para, Hazi Md. Rajab Ali | 2019-08-03 | MN1018 | 14.9 | 789 | 14.9 | 790 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7416 | 1343.9997 | 156.9936
SMG-1.RR.106.1 | 25042029124556 | Sunamganj, Dhanshiri - 19 R/A, Word # 01, Banani Para, Late Abdul Ahad, H # 1014 | 2019-08-03 | MN1018 | 9 | 791 | 9 | 792 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7416 | 1343.9997 | 94.8283
SMG-1.RR.106.2 | 25042029124556 | Sunamganj, Dhanshiri - 19 R/A, Word # 01, Banani Para, Late Abdul Ahad, H # 1014 | 2021-01-11 | LX1011 | 9.8 | 3 | 9.8 | 4 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7416 | 1343.9997 | 103.2575
SMG-1.RR.107.1 | 25042029124556 | Sunamganj, Dhanshiri - 9/1 R/A, Word # 01, Banani Para, Samimuzzaman, H # 1013 | 2019-08-03 | MN1018 | 3.2 | 796 | 3.2 | 797 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7416 | 1343.9997 | 33.7167
SMG-1.RR.107.2 | 25042029124556 | Sunamganj, Dhanshiri - 9/1 R/A, Word # 01, Banani Para, Samimuzzaman, H # 1013 | 2021-01-11 | LX1011 | 3.2 | 5 | 3.2 | 6 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7416 | 1343.9997 | 33.7167
SMG-1.RR.108.1 | 25042029124556 | Sunamganj, Dhanshiri - 18 R/A, Word # 01, Banani Para, Korom Ali Villa, H # 1011 | 2019-08-03 | MN1018 | 5.8 | 802 | 5.8 | 803 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7416 | 1343.9997 | 61.1116
SMG-1.RR.109.1 | 25042029124556 | Sunamganj, Dhanshiri - 9 R/A, Word # 01, Banani Para, H # 1012 | 2019-08-03 | MN1018 | 2.8 | 804 | 2.8 | 805 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7416 | 1343.9997 | 29.5021
SMG-1.RR.110.1 | 25042179124561 | Sunamganj, Dhanshiri - 17/1 R/A, Word # 01, Banani Para, Uzir Mia | 2019-08-03 | MN1018 | 9.5 | 806 | 9.5 | 807 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7416 | 1343.9997 | 100.0966
SMG-1.RR.111.1 | 25042219124561 | Sunamgonj, Banani Para, Dahanshiri 17/1, Toffazal Hoshen | 2019-08-04 | MN1018 | 0.8 | 852 | 0.8 | 853 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 0.8 | 0.8 | 0.048 | 0.048 | 0.0007168 | 100% | 0% | 0.048 | 0.048 | 0.0011869 | 28 | 0.00096224 | 0.00096224 |  | 0 | 0 | 7416 | 1343.9997 | 8.4292
SMG-1.RR.112.1 | 25042219124561 | Sunamgonj, Banani Para, Dahanshiri 17, Nazrul Islam, H # 1003 | 2019-08-04 | MN1018 | 9.6 | 854 | 9.6 | 855 | 2022-01-01 | [9 empty] | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0
SMG-1.RR.113.1 | 25041769124554 | Sunamgonj, Banani Para, Dahanshiri - 5, Add. Abu Sajjed Hossain, H # 1020 | 2019-08-04 | MN1018 | 7.8 | 856 | 8.4 | 857 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7416 | 1343.9997 | 88.5064
SMG-1.RR.114.1 | 25041519124538 | Sunamgonj, Banani Para, Dahanshiri - 2, MST. Pira Begum, H # 1031 | 2019-08-04 | MN1018 | 5.2 | 858 | 5.2 | 859 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7416 | 1343.9997 | 54.7897
SMG-1.RR.115.1 | 25041919124535 | Sunamgonj, Banani Para, Dahanshiri 17/1, Mahamudul Hasan (Roni), H # 945 | 2019-08-04 | MN1018 | 6.1 | 860 | 6.1 | 861 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7416 | 1343.9997 | 64.2725
SMG-1.RR.116.1 | 25041919124535 | Sunamgonj, Dahanshiri - 6 R/A, BananiPara Mozor Ali Coftage | 2019-08-04 | MN1018 | 5 | 862 | 5 | 863 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7416 | 1343.9997 | 52.6824
SMG-1.RR.117.1 | 25041919124535 | Sunamgonj, Dahanshiri - 09 R/A, Bananipara, Hazi Abdul Malak, H # 1039 | 2019-08-04 | MN1018 | 2.9 | 864 | 3.2 | 865 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7416 | 1343.9997 | 33.7167
SMG-1.RR.118.1 | 25041569124517 | Sunamgonj, Banani Para, Dahanshiri -1, Foized Ahmed | 2019-08-04 | MN1018 | 3.5 | 866 | 3.5 | 867 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7416 | 1343.9997 | 36.8777
SMG-1.RR.119.1 | 25042509124383 | Sunamgonj, Sologhor, Pobon Cominity Center Font Side, Silpe | 2019-08-04 | MN1018 | 9.1 | 868 | 9.1 | 869 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7416 | 1343.9997 | 95.882
SMG-1.RR.120.1 | 25042509124383 | Sunamgonj, Sologhor/ Surma - 125, P DS Road, Saju Mia, H # 1215 | 2019-08-04 | MN1018 | 8 | 870 | 8 | 871 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7416 | 1343.9997 | 84.2919
SMG-1.RR.121.1 | 25042679124401 | Sunamgonj, Sologhor/ Surma - 134, DS Road, MD. Mukthear ali Sogagh, H # 1218 | 2019-08-04 | MN1018 | 10.7 | 872 | 10.3 | 873 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7416 | 1343.9997 | 108.5258
SMG-1.RR.122.1 | 25042679124401 | Sunamgonj, Sologhor/ Surma - 136, DS Road, Sudhir Chondro Das, H # 1234 | 2019-08-04 | MN1018 | 5.6 | 874 | 5.6 | 875 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7416 | 1343.9997 | 59.0043
SMG-1.RR.123.1 | 25042589124416 | Sunamgonj, Sologhor/ Surma - 138/1, DS Road, Tapos Das | 2019-08-04 | MN1018 | 3.7 | 876 | 3.7 | 877 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7416 | 1343.9997 | 38.985
SMG-1.RR.124.1 | 25042789124389 | Sunamganj, Shologhor, D. S Road, Somrat | 2019-08-05 | MN1018 | 8.2 | 878 | 8.6 | 879 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7416 | 1343.9997 | 90.6137
SMG-1.RR.125.1 | 25042789124389 | Sunamganj, Shologhor, D. S Road, Sona Banu | 2019-08-05 | MN1018 | 10.7 | 880 | 10.7 | 881 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7416 | 1343.9997 | 112.7403
SMG-1.RR.126.1 | 25042619124405 | Sunamganj, Shologhor, D. S Road, Bindro Kumar Das | 2019-08-05 | MN1018 | 7.2 | 882 | 7.2 | 883 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7416 | 1343.9997 | 75.8627
SMG-1.RR.127.1 | 25042889124392 | Sunamganj, Shologhor, D. S Road, Salauddin, Pobon Cominity Center Malik | 2019-08-05 | MN1018 | 9.5 | 884 | 9.2 | 885 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7416 | 1343.9997 | 96.9356
SMG-1.RR.128.1 | 25042839124417 | Sunamganj, Shologhor/ Surma - 185/5, Add. Md. Sahajan, H # 1246 | 2019-08-05 | MN1018 | 4.4 | 886 | 4.4 | 887 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7416 | 1343.9997 | 46.3605
SMG-1.RR.129.1 | 25042839124417 | Sunamganj, Shologhor/ Surma - 148/2, H. AM. Roch Ali,, H # 1247 | 2019-08-05 | MN1018 | 3.7 | 888 | 3.7 | 889 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7416 | 1343.9997 | 38.985
SMG-1.RR.130.1 | 25042199124321 | Sunamganj, Shologhor/ Surma - 76, Bisojit Chqrobwroty | 2019-08-05 | MN1018 | 3.9 | 890 | 3.9 | 891 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7416 | 1343.9997 | 41.0923
SMG-1.RR.131.1 | 25042199124321 | Sunamganj, Shologhor/ Surma - 75/1, Sukhomoi Khuter | 2019-08-05 | MN1018 | 13.8 | 892 | 13.8 | 893 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7416 | 1343.9997 | 145.4034
SMG-1.RR.132.1 | 25042199124321 | Sunamganj, Shologhor/ Surma - 75/1, Kajol Nondi | 2019-08-05 | MN1018 | 17 | 894 | 17 | 895 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 7416 | 1343.9997 | 179.1202
SMG-1.RR.133.1 | 25042079124354 | Sunamganj, Shologhor/ Surma - 63, Rowsonora Sultana, H # 1444 | 2019-08-05 | MN1018 | 8.6 | 896 | 8.6 | 897 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7416 | 1343.9997 | 90.6137
SMG-1.RR.134.1 | 25035079123566 | Sunamganj, Niloy - 70, Notun Para, Jitaro Lal Ray , Word # 05, H # 563 | 2019-08-06 | MN1018 | 10.9 | 939 | 10.7 | 940 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7272 | 1487.9997 | 112.7403
SMG-1.RR.134.2 | 25035079123566 | Sunamganj, Niloy - 70, Notun Para, Jitaro Lal Ray , Word # 05, H # 563 | 2019-08-06 | MN1018 | 7.1 | 941 | 7.1 | 942 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7272 | 1487.9997 | 74.809
SMG-1.RR.135.1 | 25034909123578 | Sunamganj, Niloy - 73/3, Notun Para, Faria House | 2019-08-06 | MN1018 | 17.6 | 943 | 17.6 | 944 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 7272 | 1487.9997 | 185.4421
SMG-1.RR.136.1 | 25034899123591 | Sunamganj, Niloy - 73/5 Font side, Notun Para, Rohul Amin/ Jahanira Begum | 2019-08-06 | MN1018 | 6.7 | 945 | 6.7 | 946 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7272 | 1487.9997 | 70.5944
SMG-1.RR.137.1 | 25034899123591 | Sunamganj, Niloy - 73/5, Font Side, Notun Para, Homi Doctor - Runa Day | 2019-08-06 | MN1018 | 21.6 | 947 | 21.7 | 948 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 7272 | 1487.9997 | 228.6416
SMG-1.RR.138.1 | 25034899123591 | Sunamganj, Niloy - 73/5, East Notun Para, Dr . Jotis Kanti Samonto, H # 566 | 2019-08-06 | MN1018 | 12.5 | 949 | 12.5 | 950 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7272 | 1487.9997 | 131.706
SMG-1.RR.139.1 | 25034849124033 | Sunamganj, Niloy - 170, East Notun Para, H # 502, Badol Ray | 2019-08-06 | MN1018 | 4.4 | 951 | 4.4 | 952 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7272 | 1487.9997 | 46.3605
SMG-1.RR.140.1 | 25035269123377 | Sunamganj, Technical School Font Side, Hazi Para, Bashundhara R/A - 32 H # 792, Abdus Sohid | 2019-08-07 | MN1018 | 2.2 | 1 | 2.2 | 2 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7296 | 1463.9997 | 23.1803
SMG-1.RR.141.1 | 25035269123377 | Sunamganj, Technical School Font Side, Hazi Para, Bashundhara R/A - 31 H # 771, Freedom Fighter Late Asrab Ali Bari | 2019-08-07 | MN1018 | 17.7 | 3 | 17.7 | 4 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 7296 | 1463.9997 | 186.4957
SMG-1.RR.142.1 | 25035239123383 | Sunamganj, Technical School Font Side, Hazi Para, Bashundhara R/A - 28, Rabya Begum Choudhury, H # 794 | 2019-08-07 | MN1018 | 5.9 | 5 | 6.3 | 6 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7296 | 1463.9997 | 66.3798
SMG-1.RR.143.1 | 25035219123382 | Sunamganj, Technical School Font Side, Hazi Para, Bashundhara R/A, Add. Abdul Kadir Chowdhury Jilar | 2019-08-07 | MN1018 | 12.7 | 7 | 12.7 | 8 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7296 | 1463.9997 | 133.8133
SMG-1.RR.144.1 | 25035119123397 | Sunamganj, Technical School Font Side, Hazi Para, Bashundhara R/A, Grameen Bank Font Side | 2019-08-07 | MN1018 | 9.7 | 9 | 9.7 | 10 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7296 | 1463.9997 | 102.2039
SMG-1.RR.145.1 | 25034719123444 | Sunamganj, Technical School Font Side, Bashundhara R/A, Hazi Para, Johir Ahmed | 2019-08-07 | MN1018 | 10.4 | 11 | 10.4 | 12 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7296 | 1463.9997 | 109.5794
SMG-1.RR.146.1 | 25034629123458 | Sunamganj, Technical School Font Side, Bashundhara R/A -3/A, Hazi Para, Abul Khir Mithu | 2019-08-07 | MN1018 | 5.5 | 13 | 5.5 | 14 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7296 | 1463.9997 | 57.9506
SMG-1.RR.147.1 | 25034639123427 | Sunamganj, Technical School Font Side, Hazi Para, Bashundhara R/A- 15, H # 752 | 2019-08-07 | MN1018 | 9.6 | 15 | 9.3 | 16 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7296 | 1463.9997 | 97.9893
SMG-1.RR.148.1 | 25034409123430 | Sunamganj, Police Super Office Goli, Hazipara, Bashundhara R /A, Kamrul Hasan Salim, 18/2 | 2019-08-07 | MN1018 | 3.2 | 17 | 3.2 | 18 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7296 | 1463.9997 | 33.7167
SMG-1.RR.149.1 | 25034409123430 | Sunamganj, Police Super Office Goli, Hazipara, Bashundhara R /A -21, Alal Khan | 2019-08-07 | MN1018 | 4.8 | 19 | 4.4 | 20 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7296 | 1463.9997 | 46.3605
SMG-1.RR.150.1 | 25034409123430 | Sunamganj, Police Super Office Goli, Hazipara, Bashundhara R /A -23 H # 747, Morshed Mia | 2019-08-07 | MN1018 | 3.6 | 21 | 3.6 | 22 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7296 | 1463.9997 | 37.9313
SMG-1.RR.151.1 | 25040109125100 | Sunamganj Sadar, Muhammadpur R/A, Ahmod Ali, H # 89/2 | 2019-08-03 | MN1018 | 2.1 | 742 | 2.1 | 743 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7416 | 1343.9997 | 22.1266
SMG-1.RR.152.1 | 25040109125100 | Sunamganj Sadar, Muhammadpur R/A, Abdul Awal Chowdury, H # 89/1 | 2019-08-03 | MN1018 | 3.3 | 746 | 3.3 | 747 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7416 | 1343.9997 | 34.7704
SMG-1.RR.153.1 | 25035779125111 | Sunamganj Sadar, Muhammadpur R/A, Shahab Uddin, H # 91 | 2019-08-03 | MN1018 | 7.7 | 748 | 7.7 | 749 | 2022-01-01 | [9 empty] | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0
SMG-1.RR.154.1 | 25035779125111 | Sunamganj Sadar, Muhammadpur R/A, Shahab Uddin, H # 94 | 2019-08-03 | MN1018 | 4.9 | 750 | 4.9 | 751 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7416 | 1343.9997 | 51.6288
SMG-1.RR.155.1 | 25035719125139 | Sunamganj Sadar, Muhammadpur R/A, Jalal Uddin, H # 98/2 | 2019-08-03 | MN1018 | 3.6 | 752 | 3.6 | 753 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7416 | 1343.9997 | 37.9313
SMG-1.RR.156.1 | 25035809125130 | Sunamganj Sadar, Muhammadpur R/A, Kamrul Islam, H # 98/3 | 2019-08-03 | MN1018 | 16.8 | 754 | 16.8 | 755 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 7416 | 1343.9997 | 177.0129
SMG-1.RR.157.1 | 25035809125130 | Sunamganj Sadar, Muhammadpur R/A, Ashraf Uddin, H # 98 | 2019-08-03 | MN1018 | 7.1 | 756 | 7.1 | 757 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7416 | 1343.9997 | 74.809
SMG-1.RR.158.1 | 25035809125130 | Sunamganj Sadar, Muhammadpur R/A, H # 98/3, Moyna Mia | 2019-08-03 | MN1018 | 4.3 | 758 | 4.3 | 759 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7416 | 1343.9997 | 45.3069
SMG-1.RR.159.1 | 25035929125149 | Sunamganj Sadar, Muhammadpur R/A, H # 100/3 | 2019-08-03 | MN1018 | 5.6 | 766 | 5.6 | 767 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7416 | 1343.9997 | 59.0043
SMG-1.RR.160.1 | 25035899125168 | Sunamganj Sadar, Muhammadpur R/A, Abdur Rahman, H # 103 | 2019-08-03 | MN1018 | 6.5 | 768 | 6.6 | 769 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7416 | 1343.9997 | 69.5408
SMG-1.RR.161.1 | 25035819125185 | Sunamganj Sadar, Muhammadpur R/A, H # 104 | 2019-08-03 | MN1018 | 25.9 | 772 | 25.9 | 773 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 25.9 | 25.9 | 1.554 | 1.554 | 0.0007168 | 100% | 0% | 1.554 | 1.554 | 0.0011869 | 28 | 0.031152 | 0.031152 |  | 0 | 0 | 7416 | 1343.9997 | 272.8949
SMG-1.RR.162.1 | 25035819125185 | Sunamganj Sadar, Muhammadpur R/A, Abul Kalam | 2019-08-03 | MN1018 | 3 | 774 | 3 | 775 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7416 | 1343.9997 | 31.6094
SMG-1.RR.163.1 | 25035819125185 | Sunamganj Sadar, Muhammadpur R/A, Abdul Mossabbir | 2019-08-03 | MN1018 | 3.2 | 777 | 3.2 | 778 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7416 | 1343.9997 | 33.7167
SMG-1.RR.164.1 | 25042189124421 | Sunamganj Sadar, Shuloghor R/A, H #Surma-189, Ruhul Kuddus Pir | 2019-08-04 | MN1018 | 15.2 | 808 | 15.2 | 809 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7416 | 1343.9997 | 160.1545
SMG-1.RR.165.1 | 25042189124421 | Sunamganj Sadar, Shuloghor R/A, H #Surma-188, Achia Khatun | 2019-08-04 | MN1018 | 8.4 | 814 | 8.4 | 815 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7416 | 1343.9997 | 88.5064
SMG-1.RR.166.1 | 25042189124421 | Sunamganj Sadar, Shuloghor R/A, H # Surma-190, Abdul Muyid Pir | 2019-08-04 | MN1018 | 13.4 | 816 | 13.4 | 817 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7416 | 1343.9997 | 141.1888
SMG-1.RR.167.1 | 25042209124430 | Sunamganj Sadar, Shuloghor R/A, H # Surma-222/1, Abdul Bari Chowdury | 2019-08-04 | MN1018 | 2.6 | 818 | 2.6 | 819 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7416 | 1343.9997 | 27.3949
SMG-1.RR.168.1 | 25042209124430 | Sunamganj Sadar, Shuloghor R/A, H # Surma-221/2, Moinul Hoque Chowdury | 2019-08-04 | MN1018 | 3.4 | 820 | 3.4 | 821 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7416 | 1343.9997 | 35.824
SMG-1.RR.169.1 | 25042209124430 | Sunamganj Sadar, Shuloghor R/A, H #Surma-191, Md.Abdul Motalib | 2019-08-04 | MN1018 | 4.3 | 824 | 4.3 | 825 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7416 | 1343.9997 | 45.3069
SMG-1.RR.170.1 | 25042319124430 | Sunamganj Sadar, Shuloghor R/A, H #Surma-192, Md.Fotik Mia | 2019-08-04 | MN1018 | 5.4 | 826 | 5.4 | 827 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7416 | 1343.9997 | 56.897
SMG-1.RR.171.1 | 25042439124416 | Sunamganj Sadar, Shuloghor R/A, H #Surma-198, Mohibur Rahman Khaled | 2019-08-04 | MN1018 | 3.4 | 828 | 3.4 | 829 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7416 | 1343.9997 | 35.824
SMG-1.RR.171.2 | 25042439124416 | Sunamganj Sadar, Shuloghor R/A, H #Surma-198, Mohibur Rahman Khaled | 2021-01-11 | MN1018 | 5.7 | 3 | 5.7 | 4 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7416 | 1343.9997 | 60.0579
SMG-1.RR.172.1 | 25042419124398 | Sunamganj Sadar, Shuloghor R/A, H #Surma-94/3, Iqbal Hossen Sufi | 2019-08-04 | MN1018 | 10 | 830 | 9.5 | 831 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7416 | 1343.9997 | 100.0966
SMG-1.RR.173.1 | 25042309124390 | Sunamganj Sadar, Shuloghor R/A, H #94/3, Iqbal Hossen Sufi | 2019-08-04 | MN1018 | 6.2 | 832 | 6.2 | 833 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7416 | 1343.9997 | 65.3262
SMG-1.RR.174.1 | 25042409124375 | Sunamganj Sadar, Shuloghor R/A, H #Surma-98, Hafiz | 2019-08-04 | MN1018 | 3.3 | 834 | 3.3 | 835 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7416 | 1343.9997 | 34.7704
SMG-1.RR.174.2 | 25042409124375 | Sunamganj Sadar, Shuloghor R/A, H #Surma-98, Hafiz | 2022-02-24 | LU1001 | 13.8 | 6 | 13.8 | 7 | 2022-02-24 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6120 | 1343.9997 | 123.8917
SMG-1.RR.175.1 | 25042469124375 | Sunamganj Sadar, Shuloghor R/A, H #Surma-107, Manna Das | 2019-08-04 | MN1018 | 7.3 | 840 | 7.3 | 841 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7416 | 1343.9997 | 76.9163
SMG-1.RR.176.1 | 25042469124355 | Sunamganj Sadar, Shuloghor R/A, H #Surma-107, Mithu Gosh | 2019-08-04 | MN1018 | 5.4 | 842 | 5.4 | 843 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7416 | 1343.9997 | 56.897
SMG-1.RR.177.1 | 25042349124379 | Sunamganj Sadar, Shuloghor R/A, Opposite to Roham Tithi Cottage, Abdul Kalm | 2019-08-04 | MN1018 | 5.9 | 846 | 5.9 | 847 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7416 | 1343.9997 | 62.1652
SMG-1.RR.178.1 | 25042349124379 | Sunamganj Sadar, Shuloghor R/A, H #1200, Md. Asif Anam Ruhan | 2019-08-04 | MN1018 | 3.2 | 848 | 3.2 | 849 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7416 | 1343.9997 | 33.7167
SMG-1.RR.179.1 | 25042349124379 | Sunamganj Sadar, Shuloghor R/A, Khairul, Opposite to H # 98/1 | 2019-08-04 | MN1018 | 9.9 | 850 | 9.9 | 851 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7416 | 1343.9997 | 104.3112
SMG-1.RR.180.1 | 25041029124440 | Sunamganj Sadar, Shuloghor R/A, Tushon-48, Abul Hashem | 2019-08-05 | MN1018 | 2.1 | 900 | 2.1 | 901 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7248 | 1511.9997 | 22.1266
SMG-1.RR.181.1 | 25040799124436 | Sunamganj Sadar, Shuloghor R/A, Tushon-34/2, Advocate Moynul Islam | 2019-08-05 | MN1018 | 2.1 | 902 | 2.1 | 903 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7248 | 1511.9997 | 22.1266
SMG-1.RR.182.1 | 25040799124436 | Sunamganj Sadar, Shuloghor R/A, Advocate Samsul Hoque | 2019-08-05 | MN1018 | 7.6 | 904 | 7.6 | 905 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7248 | 1511.9997 | 80.0773
SMG-1.RR.183.1 | 25041329124401 | Sunamganj Sadar, Shuloghor R/A, Tushon-28, Ferdousi Begum Lili | 2019-08-05 | MN1018 | 4.5 | 906 | 4.5 | 907 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7248 | 1511.9997 | 47.4142
SMG-1.RR.184.1 | 25042219124376 | Sunamganj Sadar, Shuloghor R/A, Surma-86, Roshid Mia | 2019-08-05 | MN1018 | 6.8 | 908 | 6.8 | 909 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7416 | 1343.9997 | 71.6481
SMG-1.RR.185.1 | 25042129124370 | Sunamganj Sadar, Shuloghor Point, H # Surma-85, Ziku | 2019-08-05 | MN1018 | 5.8 | 910 | 5.8 | 911 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7416 | 1343.9997 | 61.1116
SMG-1.RR.186.1 | 25040049123588 | Sunamganj Sadar, Notunpara, Mujahid | 2019-08-06 | MN1018 | 2.6 | 912 | 2.7 | 913 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7296 | 1463.9997 | 28.4485
SMG-1.RR.188.1 | 25035979123582 | Sunamganj Sadar, Notunpara, Subroto Bonik | 2019-08-06 | MN1018 | 3.5 | 916 | 3.5 | 917 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7296 | 1463.9997 | 36.8777
SMG-1.RR.189.1 | 25035979123582 | Sunamganj Sadar, Notunpara, Sadon Acharjo | 2019-08-06 | MN1018 | 12.5 | 918 | 12.5 | 919 | 2022-01-01 | [9 empty] | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0
SMG-1.RR.190.1 | 25035729123570 | Sunamganj Sadar, Notunpara, Amor Pal, H # Niloy-42/1 | 2019-08-06 | MN1018 | 7.7 | 920 | 7.7 | 921 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7296 | 1463.9997 | 81.1309
SMG-1.RR.191.1 | 25035639123575 | Sunamganj Sadar, Notunpara, Ajoy, H # Niloy-45/1 | 2019-08-06 | MN1018 | 6.1 | 923 | 6.1 | 924 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7296 | 1463.9997 | 64.2725
SMG-1.RR.192.1 | 25035549123578 | Sunamganj Sadar, Notunpara, Ajmol Bokth, H # Niloy-48 | 2019-08-06 | MN1018 | 6.6 | 925 | 6.6 | 926 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7296 | 1463.9997 | 69.5408
SMG-1.RR.193.1 | 25035519124015 | Sunamganj Sadar,Purba Notunpara, Suklal Roy, H # Niloy-140/1 | 2019-08-06 | MN1018 | 11.5 | 927 | 11.5 | 928 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7296 | 1463.9997 | 121.1695
SMG-1.RR.193.2 | 25035519124015 | Sunamganj Sadar,Purba Notunpara, Suklal Roy, H # Niloy-140/1 | 2021-01-13 | MN1018 | 4.9 | 13 | 4.9 | 14 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7296 | 1463.9997 | 51.6288
SMG-1.RR.194.1 | 25035659124031 | Sunamganj Sadar, Purba Notun Para, Gupal Das, H # Niloy-143/3 | 2019-08-06 | MN1018 | 6.3 | 931 | 6.3 | 932 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7296 | 1463.9997 | 66.3798
SMG-1.RR.195.1 | 25035659124031 | Sunamganj Sadar, Purba Notun Para, Konok Chakroborty, H # Niloy-144 | 2019-08-06 | MN1018 | 4.7 | 933 | 4.7 | 934 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7296 | 1463.9997 | 49.5215
SMG-1.RR.196.1 | 25035819124032 | Sunamganj Sadar, Purba Notun Para, Professor Dilip Kumar Mojumdar | 2019-08-06 | MN1018 | 6.9 | 935 | 6.9 | 936 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7296 | 1463.9997 | 72.7017
SMG-1.RR.197.1 | 25035319124017 | Sunamganj Sadar, Purba Notun Para, Sunil Chandra Dey, H # Niloy-154/2 | 2019-08-06 | MN1018 | 3 | 937 | 3 | 938 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7296 | 1463.9997 | 31.6094
SMG-1.RR.198.1 | 25040009123487 | Sunamganj Sadar, Jamtola,Ozobithi R/A, Raton Das | 2019-08-07 | MN1018 | 17.6 | 25 | 17.6 | 26 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 7392 | 1367.9997 | 185.4421
SMG-1.RR.199.1 | 25040149123209 | Sunamganj Sadar, Pochim Teguria, Road # 4, H # Rongdonu-2, Mortuza Ali | 2019-08-07 | MN1018 | 5 | 29 | 5 | 30 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7344 | 1415.9997 | 52.6824
SMG-1.RR.200.1 | 25040179123209 | Sunamganj Sadar, Pochim Teguria, Road # 4, H # Rongdonu-2, Abdul Gafur | 2019-08-07 | MN1018 | 3.4 | 31 | 3.5 | 32 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7344 | 1415.9997 | 36.8777
SMG-1.RR.201.1 | 25042099125026 | Sunamgonj, Balaka-27/3, Banani Para, Salma Ahamad | 2019-08-03 | NQ1002 | 12.7 | 599 | 12.7 | 600 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7224 | 1535.9997 | 133.8133
SMG-1.RR.202.1 | 25041959125022 | Sunamgonj, Balaka-27/3, Banani Para, Sha Taje Uddin | 2019-08-03 | NQ1002 | 6.2 | 601 | 6.2 | 602 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7224 | 1535.9997 | 65.3262
SMG-1.RR.203.1 | 25041959125022 | Sunamgonj, Balaka-27/3, Banani Para, Abdul Jalil | 2019-08-03 | NQ1002 | 10.4 | 603 | 10.4 | 604 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7224 | 1535.9997 | 109.5794
SMG-1.RR.204.1 | 25041869125012 | Sunamgonj, Balaka-25/2, Banani Para, Ali Ahamad | 2019-08-03 | NQ1002 | 19 | 607 | 19 | 608 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 7224 | 1535.9997 | 200.1931
SMG-1.RR.205.1 | 25041869125012 | Sunamgonj, Balaka-25/2, Banani Para, Hasna Aktar | 2019-08-03 | NQ1002 | 7.3 | 609 | 7.3 | 610 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7224 | 1535.9997 | 76.9163
SMG-1.RR.206.1 | 25041789125013 | Sunamgonj, Balaka-25/8, Banani Para, Ali Ahamad | 2019-08-03 | NQ1002 | 12.9 | 611 | 13 | 612 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7224 | 1535.9997 | 136.9743
SMG-1.RR.207.1 | 25041699125026 | Sunamgonj, Balaka-19, Banani Para, Abdul Hak | 2019-08-03 | NQ1002 | 10.8 | 615 | 10.8 | 616 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7224 | 1535.9997 | 113.794
SMG-1.RR.208.1 | 25041669125037 | Sunamgonj, Balaka-19/5, Banani Para, Azijur Rahman | 2019-08-03 | NQ1002 | 10.1 | 617 | 10.1 | 618 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7224 | 1535.9997 | 106.4185
SMG-1.RR.208.2 | 25041669125037 | Sunamgonj, Balaka-19/5, Banani Para, Azijur Rahman | 2019-08-03 | NQ1002 | 4.8 | 619 | 4.8 | 620 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7224 | 1535.9997 | 50.5751
SMG-1.RR.209.1 | 25042249124598 | Sunamgonj, Balaka-33, Banani Para, Safiqul Islam | 2019-08-03 | NQ1002 | 6.9 | 621 | 6.9 | 622 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7224 | 1535.9997 | 72.7017
SMG-1.RR.210.1 | 25042249124598 | Sunamgonj, Balaka-33, Banani Para, Safiqul Islam | 2019-08-03 | NQ1002 | 15.1 | 623 | 15.1 | 624 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7224 | 1535.9997 | 159.1009
SMG-1.RR.211.1 | 25050689125104 | Sunamganj, Nabinagar, Halour Ghat Road, Rokon Uddine | 2019-08-04 | NQ1002 | 8.3 | 649 | 8.3 | 650 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7224 | 1535.9997 | 87.4528
SMG-1.RR.212.1 | 25050639125098 | Sunamganj, Nabinagar, Halour Ghat Road, Feroj | 2019-08-04 | NQ1002 | 3.7 | 653 | 3.7 | 654 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7224 | 1535.9997 | 38.985
SMG-1.RR.213.1 | 25050469125076 | Sunamganj, Nabinagar, Halour Ghat Road, Abdul Halim | 2019-08-04 | NQ1002 | 10.5 | 655 | 10.5 | 656 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7224 | 1535.9997 | 110.6331
SMG-1.RR.213.2 | 25050469125076 | Sunamganj, Nabinagar, Halour Ghat Road, Abdul Halim | 2019-08-04 | NQ1002 | 3.1 | 657 | 3.1 | 658 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7224 | 1535.9997 | 32.6631
SMG-1.RR.214.1 | 25050589125063 | Sunamganj, Nabinagar, Halour Ghat Road, Azijur Rahaman | 2019-08-04 | NQ1002 | 15.9 | 659 | 15.9 | 660 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 7224 | 1535.9997 | 167.5301
SMG-1.RR.215.1 | 25050589125063 | Sunamganj, Nabinagar, Halour Ghat Road, Abdul Salam | 2019-08-04 | NQ1002 | 15.8 | 661 | 15.6 | 662 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7224 | 1535.9997 | 164.3691
SMG-1.RR.216.1 | 25050589125063 | Sunamganj, Nabinagar, Halour Ghat Road, Mohon | 2019-08-04 | NQ1002 | 13.1 | 663 | 13.1 | 664 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7224 | 1535.9997 | 138.0279
SMG-1.RR.216.2 | 25050589125063 | Sunamganj, Nabinagar, Halour Ghat Road, Mohon | 2019-08-04 | NQ1002 | 13.7 | 665 | 13.7 | 666 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7224 | 1535.9997 | 144.3498
SMG-1.RR.217.1 | 25050589125063 | Sunamganj, Nabinagar, Halour Ghat Road, Waskoroni | 2019-08-04 | NQ1002 | 9.7 | 667 | 9.2 | 668 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7224 | 1535.9997 | 96.9356
SMG-1.RR.218.1 | 25050219125056 | Sunamganj, Nabinagar, Halour Ghat Road, Abdul Hak | 2019-08-04 | NQ1002 | 8.4 | 669 | 8.4 | 670 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7224 | 1535.9997 | 88.5064
SMG-1.RR.219.1 | 25050199125051 | Sunamganj, Nabinagar, Halour Ghat Road, Babul | 2019-08-04 | NQ1002 | 5.4 | 671 | 5.4 | 672 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7224 | 1535.9997 | 56.897
SMG-1.RR.219.2 | 25050199125051 | Sunamganj, Nabinagar, Halour Ghat Road, Babul | 2022-02-23 | LU1001 | 9.9 | 1 | 9.9 | 2 | 2022-02-23 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 5952 | 1535.9997 | 89.1646
SMG-1.RR.220.1 | 25050199125051 | Sunamganj, Nabinagar, Halour Ghat Road, Salim | 2019-08-04 | NQ1002 | 5.9 | 673 | 5.9 | 674 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7224 | 1535.9997 | 62.1652
SMG-1.RR.221.1 | 25051449125230 | Sunamganj, Nabinagar, Halour Ghat Road, Abdul Latif | 2019-08-05 | NQ1002 | 12.7 | 675 | 12.7 | 676 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7224 | 1535.9997 | 133.8133
SMG-1.RR.222.1 | 25051559125252 | Sunamganj, Nabinagar, Halour Ghat Road, Abdul Halim | 2019-08-05 | NQ1002 | 5 | 677 | 5 | 678 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7224 | 1535.9997 | 52.6824
SMG-1.RR.223.1 | 25045969125027 | Sunamganj, Nabinagar, Halour Ghat Road, Harun Or Rashid | 2019-08-05 | NQ1002 | 12.4 | 679 | 12.1 | 680 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7224 | 1535.9997 | 127.4914
SMG-1.RR.224.1 | 25045829125014 | Sunamganj, Nabinagar, Halour Ghat Road, Goyas Khan | 2019-08-05 | NQ1002 | 9.8 | 681 | 9.8 | 682 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7224 | 1535.9997 | 103.2575
SMG-1.RR.225.1 | 25045829125014 | Sunamganj, Nabinagar, Halour Ghat Road, Foyjun | 2019-08-05 | NQ1002 | 4.6 | 683 | 4.6 | 684 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7224 | 1535.9997 | 48.4678
SMG-1.RR.226.1 | 25045449124578 | Sunamganj, Nabinagar, Halour Ghat Road, Md. Sobdor Ali | 2019-08-05 | NQ1002 | 13.5 | 685 | 13.5 | 686 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7224 | 1535.9997 | 142.2425
SMG-1.RR.227.1 | 25045449124578 | Sunamganj, Nabinagar, Halour Ghat Road, Mofij | 2019-08-05 | NQ1002 | 10.1 | 687 | 9.4 | 688 | 2022-01-01 | [9 empty] | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 | 2022-10-04 12:00 | 0 | 0
SMG-1.RR.228.1 | 25045449124578 | Sunamganj, Nabinagar, Halour Ghat Road, Sahad Ali | 2019-08-05 | NQ1002 | 3 | 689 | 3 | 690 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7224 | 1535.9997 | 31.6094
SMG-1.RR.229.1 | 25045359124569 | Sunamganj, Nabinagar, Halour Ghat Road, Mojahar | 2019-08-05 | NQ1002 | 6.7 | 691 | 6.6 | 692 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7224 | 1535.9997 | 69.5408
SMG-1.RR.230.1 | 25045199124551 | Sunamganj, Nabinagar, Halour Ghat Road, Borkot | 2019-08-05 | NQ1002 | 12.2 | 693 | 12.2 | 694 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7224 | 1535.9997 | 128.5451
SMG-1.RR.231.1 | 25045009124538 | Sunamganj, Nabinagar, Halour Ghat Road, Rahim Monjil | 2019-08-05 | NQ1002 | 12.4 | 695 | 12.4 | 696 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7224 | 1535.9997 | 130.6524
SMG-1.RR.232.1 | 25040589124375 | Sunamganj, Hasan Nagor Probi, Sha Alam | 2019-08-05 | NQ1002 | 3.7 | 697 | 3.7 | 698 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7272 | 1487.9997 | 38.985
SMG-1.RR.233.1 | 25040839124086 | Sunamganj, Hasan Nagar, Hasan Nagar Road, Doctor Samiul Haque | 2019-08-06 | NQ1002 | 10.8 | 719 | 11.1 | 720 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7296 | 1463.9997 | 116.9549
SMG-1.RR.233.2 | 25040839124086 | Sunamganj, Hasan Nagar, Hasan Nagar Road, Doctor Samiul Haque | 2019-08-06 | NQ1002 | 2.9 | 721 | 2.9 | 722 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7296 | 1463.9997 | 30.5558
SMG-1.RR.234.1 | 25040859124099 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Benoya Bosu | 2019-08-06 | NQ1002 | 9.8 | 723 | 9.8 | 724 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7296 | 1463.9997 | 103.2575
SMG-1.RR.235.1 | 25040499124110 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Azahar Ali Monjil | 2019-08-06 | NQ1002 | 8.4 | 725 | 8.5 | 726 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7296 | 1463.9997 | 89.5601
SMG-1.RR.236.1 | 25040319124121 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Suronjit Sekhor | 2019-08-06 | NQ1002 | 8.4 | 727 | 8.4 | 728 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7296 | 1463.9997 | 88.5064
SMG-1.RR.237.1 | 25040319124121 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Romendro | 2019-08-06 | NQ1002 | 4.4 | 729 | 4.4 | 730 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7296 | 1463.9997 | 46.3605
SMG-1.RR.238.1 | 25040219124101 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Mohassar Pal | 2019-08-06 | NQ1002 | 14.3 | 731 | 14.3 | 732 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7296 | 1463.9997 | 150.6717
SMG-1.RR.239.1 | 25040029124101 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Rupok Talukder | 2019-08-06 | NQ1002 | 11.7 | 733 | 11.7 | 734 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7296 | 1463.9997 | 123.2768
SMG-1.RR.240.1 | 25035779124101 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Maor Aktaruzzaman | 2019-08-06 | NQ1002 | 10.3 | 735 | 10.3 | 736 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7296 | 1463.9997 | 108.5258
SMG-1.RR.240.2 | 25035779124101 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Maor Aktaruzzaman | 2019-08-06 | NQ1002 | 5.9 | 737 | 5.9 | 738 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7296 | 1463.9997 | 62.1652
SMG-1.RR.241.1 | 25035769124092 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Mongol Lal | 2019-08-06 | NQ1002 | 11.4 | 739 | 11.4 | 740 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7296 | 1463.9997 | 120.1159
SMG-1.RR.242.1 | 25035769124092 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Abdul Hi | 2019-08-06 | NQ1002 | 6.4 | 741 | 6.4 | 742 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7296 | 1463.9997 | 67.4335
SMG-1.RR.243.1 | 25035769124092 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Habibur Rahman | 2019-08-06 | NQ1002 | 9.8 | 743 | 9.9 | 744 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7296 | 1463.9997 | 104.3112
SMG-1.RR.243.2 | 25035769124092 | Sunamganj, Hasan Nagar, Upotakka, Shohid Abul Hossain Road, Habibur Rahman | 2019-08-06 | NQ1002 | 8.4 | 745 | 8.4 | 746 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7296 | 1463.9997 | 88.5064
SMG-1.RR.244.1 | 25035079124121 | Sunamganj, Hasan Nagar, Shantibag, H # 156 | 2019-08-07 | NQ1002 | 9.6 | 1 | 9.6 | 2 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7272 | 1487.9997 | 101.1502
SMG-1.RR.245.1 | 25035079124121 | Sunamganj, Hasan Nagar, Shantibag, H # 156/1 | 2019-08-07 | NQ1002 | 7.6 | 3 | 7.6 | 4 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7272 | 1487.9997 | 80.0773
SMG-1.RR.246.1 | 25035069124120 | Sunamganj, Hasan Nagar, Shantibag, H # 157 | 2019-08-07 | NQ1002 | 11.7 | 5 | 11.7 | 6 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7272 | 1487.9997 | 123.2768
SMG-1.RR.247.1 | 25035019124141 | Sunamganj, Hasan Nagar, Shantibag, H # 5/1, Nahara Vaban | 2019-08-07 | NQ1002 | 3.7 | 7 | 3.7 | 8 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7272 | 1487.9997 | 38.985
SMG-1.RR.248.1 | 25035089124181 | Sunamganj, Hasan Nagar, Shantibag, H # 14, Ramanro Chandro Das | 2019-08-07 | NQ1002 | 12.8 | 9 | 12.4 | 10 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7272 | 1487.9997 | 130.6524
SMG-1.RR.248.2 | 25035089124181 | Sunamganj, Hasan Nagar, Shantibag, H # 14, Ramanro Chandro Das | 2022-02-27 | LU1001 | 8.8 | 10 | 8.8 | 11 | 2022-02-27 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 5904 | 1487.9997 | 78.2413
SMG-1.RR.249.1 | 25035089124199 | Sunamganj, Hasan Nagar, Shantibag, Nipanro Narion | 2019-08-07 | NQ1002 | 5 | 11 | 5 | 12 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7272 | 1487.9997 | 52.6824
SMG-1.RR.250.1 | 25035089124199 | Sunamganj, Hasan Nagar, Shantibag, H # 186, Lokkhi Vila | 2019-08-07 | NQ1002 | 9.3 | 15 | 9.3 | 16 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7272 | 1487.9997 | 97.9893
SMG-1.RR.251.1 | 25041059125085 | Sunamganj, Mohammedpur Point, Mohammedpur R/A, H # 07/1 | 2019-08-03 | NQ1002 | 12.5 | 581 | 12.5 | 582 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7416 | 1343.9997 | 131.706
SMG-1.RR.252.1 | 25040839125081 | Sunamganj, Mohammedpur Point, Mohammedpur R/A, H # 47 | 2019-08-03 | NQ1002 | 8.6 | 583 | 8.6 | 584 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7416 | 1343.9997 | 90.6137
SMG-1.RR.253.1 | 25040849125102 | Sunamganj, Mohammedpur Point, Mohammedpur R/A, H # 43 | 2019-08-03 | NQ1002 | 3.7 | 585 | 3.7 | 586 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7416 | 1343.9997 | 38.985
SMG-1.RR.254.1 | 25040769125081 | Sunamganj, Mohammedpur Point, Mohammedpur R/A, H # 48/1 | 2019-08-03 | NQ1002 | 11.6 | 587 | 11.6 | 588 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7416 | 1343.9997 | 122.2232
SMG-1.RR.255.1 | 25040769125081 | Sunamganj, Mohammedpur Point, Mohammedpur R/A, H # 50 | 2019-08-03 | NQ1002 | 3.4 | 591 | 3.4 | 592 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7416 | 1343.9997 | 35.824
SMG-1.RR.257.1 | 25043249124485 | Sunamganj, Shologhor, Shurma R/A, H # 169/1 | 2019-08-04 | NQ1002 | 11.9 | 625 | 11.9 | 626 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7224 | 1535.9997 | 125.3841
SMG-1.RR.258.1 | 25043179124504 | Sunamganj, Shologhor, Shurma R/A, Md. Serajul Islam | 2019-08-04 | NQ1002 | 24 | 627 | 24 | 628 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 24 | 24 | 1.44 | 1.44 | 0.0007168 | 100% | 0% | 1.44 | 1.44 | 0.0011869 | 28 | 0.028867 | 0.028867 |  | 0 | 0 | 7224 | 1535.9997 | 252.8756
SMG-1.RR.259.1 | 25043179124504 | Sunamganj, Shologhor, Shurma R/A, Md. Samsul Hoq (Member) | 2019-08-04 | NQ1002 | 3.3 | 629 | 3.3 | 630 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7224 | 1535.9997 | 34.7704
SMG-1.RR.260.1 | 25043149124518 | Sunamganj, Shologhor, Shurma R/A, Md. Abdul Hannan | 2019-08-04 | NQ1002 | 4.1 | 631 | 4.1 | 632 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7224 | 1535.9997 | 43.1996
SMG-1.RR.261.1 | 25043499124492 | Sunamganj, Shologhor, Shurma R/A, Abdullah Khan | 2019-08-04 | NQ1002 | 6.3 | 633 | 6.3 | 634 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7224 | 1535.9997 | 66.3798
SMG-1.RR.261.2 | 25043499124492 | Sunamganj, Shologhor, Shurma R/A, Abdullah Khan | 2021-01-10 | MN1018 | 11.2 | 1 | 11.2 | 2 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7224 | 1535.9997 | 118.0086
SMG-1.RR.262.1 | 25043519124510 | Sunamganj, Shologhor, Shurma R/A, Shafiq | 2019-08-04 | NQ1002 | 13.4 | 635 | 13.3 | 636 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7224 | 1535.9997 | 140.1352
SMG-1.RR.263.1 | 25043419124507 | Sunamganj, Shologhor, Shurma R/A, Ramijuddin Master | 2019-08-04 | NQ1002 | 2.6 | 637 | 2.6 | 638 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7224 | 1535.9997 | 27.3949
SMG-1.RR.264.1 | 25043519124517 | Sunamganj, Shologhor, Shurma R/A, Atikur Rahaman | 2019-08-04 | NQ1002 | 9 | 639 | 8.5 | 640 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7224 | 1535.9997 | 89.5601
SMG-1.RR.265.1 | 25043379124532 | Sunamganj, Shologhor, Shurma R/A, Nurul Hoq Mia | 2019-08-04 | NQ1002 | 8.7 | 641 | 8.2 | 642 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 24 | 0 | 7200 | 1535.9997 | 86.1624
SMG-1.RR.266.1 | 25043379124532 | Sunamganj, Shologhor, Shurma R/A, Jahur Ali | 2019-08-04 | NQ1002 | 2 | 645 | 2 | 646 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7224 | 1535.9997 | 21.073
SMG-1.RR.267.1 | 25043529124517 | Sunamganj, Shologhor, Shurma R/A, Beside Atikur Rahaman | 2019-08-04 | NQ1002 | 24 | 647 | 24 | 648 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 24 | 24 | 1.44 | 1.44 | 0.0007168 | 100% | 0% | 1.44 | 1.44 | 0.0011869 | 28 | 0.028867 | 0.028867 |  | 0 | 0 | 7224 | 1535.9997 | 252.8756
SMG-1.RR.268.1 | 25043529124500 | Sunamganj, Shologhor, Shurma R/A, Shahid Ahammed | 2019-08-05 | NQ1002 | 12 | 701 | 12 | 702 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7224 | 1535.9997 | 126.4378
SMG-1.RR.269.1 | 25043719124497 | Sunamganj, Shologhor, Shurma, Mofiz Ali | 2019-08-05 | NQ1002 | 3.3 | 703 | 3.3 | 704 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7224 | 1535.9997 | 34.7704
SMG-1.RR.270.1 | 25043719124497 | Sunamganj, Shologhor, Shurma, Ashraf Ali | 2019-08-05 | NQ1002 | 4.8 | 705 | 4.8 | 706 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7224 | 1535.9997 | 50.5751
SMG-1.RR.271.1 | 25043649124508 | Sunamganj, Shologhor, Shurma, Azizul Hoq | 2019-08-05 | NQ1002 | 6.1 | 707 | 6.1 | 708 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7224 | 1535.9997 | 64.2725
SMG-1.RR.272.1 | 25043649124508 | Sunamganj, Shologhor, Shurma, Monaffor Ali | 2019-08-05 | NQ1002 | 12.7 | 709 | 12.7 | 710 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7224 | 1535.9997 | 133.8133
SMG-1.RR.273.1 | 25044019124509 | Sunamganj, Nabinagar, Uttara R/A, Chittoranjon Das | 2019-08-05 | NQ1002 | 7.7 | 711 | 7.7 | 712 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7224 | 1535.9997 | 81.1309
SMG-1.RR.274.1 | 25044029124544 | Sunamganj, Nabinagar, Uttara R/A, Rajon | 2019-08-05 | NQ1002 | 12.7 | 713 | 12.7 | 714 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7224 | 1535.9997 | 133.8133
SMG-1.RR.275.1 | 25043979124587 | Sunamganj, Nabinagar, Uttara R/A, Abdus Sobahan | 2019-08-05 | NQ1002 | 5.1 | 717 | 5.1 | 718 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7224 | 1535.9997 | 53.7361
SMG-1.RR.276.1 | 25035809124079 | Sunamganj, Moratila, Hasan Nagar, Upotoka R/A, Abdul Ahad | 2019-08-06 | NQ1002 | 4.2 | 747 | 4.2 | 748 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7296 | 1463.9997 | 44.2532
SMG-1.RR.277.1 | 25035719124102 | Sunamganj, Moratila, Hasan Nagar, Upotoka R/A, Abu Sofiyan | 2019-08-06 | NQ1002 | 11.1 | 749 | 11.1 | 750 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7296 | 1463.9997 | 116.9549
SMG-1.RR.278.1 | 25035659124103 | Sunamganj, Moratila, Hasan Nagar, Upotoka R/A, Rakabuddin | 2019-08-06 | NQ1002 | 6.7 | 751 | 6.7 | 752 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7296 | 1463.9997 | 70.5944
SMG-1.RR.279.1 | 25035109124071 | Sunamganj, Moratila Point, Miniti Rani Mollick | 2019-08-06 | NQ1002 | 9 | 753 | 9 | 754 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7272 | 1487.9997 | 94.8283
SMG-1.RR.280.1 | 25035109124071 | Sunamganj, Moratila Point, Nikesh Chandra Das | 2019-08-06 | NQ1002 | 10.9 | 755 | 10.9 | 756 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7272 | 1487.9997 | 114.8476
SMG-1.RR.281.1 | 25035049124062 | Sunamganj, Moratila Point, Kanu Ranjon Paul | 2019-08-06 | NQ1002 | 3.8 | 757 | 3.8 | 758 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7272 | 1487.9997 | 40.0386
SMG-1.RR.282.1 | 25034669124071 | Sunamganj, East Notun Para, Jamuna R/A, Manish Kanti Nag | 2019-08-06 | NQ1002 | 1.2 | 759 | 1.2 | 760 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7272 | 1487.9997 | 12.6438
SMG-1.RR.283.1 | 25034519123242 | Sunamganj, West Hazi Para, Khalil Ahammed | 2019-08-07 | NQ1002 | 12.1 | 27 | 12.1 | 28 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7320 | 1439.9997 | 127.4914
SMG-1.RR.284.1 | 25034429123232 | Sunamganj, West Hazi Para, Ibrahim Khalil | 2019-08-07 | NQ1002 | 3.9 | 29 | 3.9 | 30 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7320 | 1439.9997 | 41.0923
SMG-1.RR.285.1 | 25034599123216 | Sunamganj, West Hazi Para, Abul Khayer | 2019-08-07 | NQ1002 | 3.1 | 31 | 3.1 | 32 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7320 | 1439.9997 | 32.6631
SMG-1.RR.285.2 | 25034599123216 | Sunamganj, West Hazi Para, Abul Khayer | 2022-11-02 | MN1018 | 2.1 | 114 | 2.1 | 115 | 2022-11-02 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 0 | 1439.9997 | 3.6373
SMG-1.RR.286.1 | 25035079123231 | Sunamganj, West Hazi Para, Amin Shaheb | 2019-08-07 | NQ1002 | 5.6 | 33 | 5.6 | 34 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7344 | 1415.9997 | 59.0043
SMG-1.RR.287.1 | 25035159123225 | Sunamganj, West Teghoria, Babul Mia | 2019-08-07 | NQ1002 | 10.3 | 35 | 10.3 | 36 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7344 | 1415.9997 | 108.5258
SMG-1.RR.288.1 | 25035159123225 | Sunamganj, West Teghoria, Abdul Wadud Khan | 2019-08-07 | NQ1002 | 15.7 | 37 | 15.7 | 38 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 7344 | 1415.9997 | 165.4228
SMG-1.RR.289.1 | 25035329123223 | Sunamganj, West Teghoria, Hazera Begum | 2019-08-07 | NQ1002 | 3.6 | 39 | 3.6 | 40 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 1296 | 0 | 6048 | 1415.9997 | 32.3196
SMG-1.RR.290.1 | 25035489123240 | Sunamganj, West Teghoria, Rafiqul Islam | 2019-08-07 | NQ1002 | 15 | 41 | 15 | 42 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 7344 | 1415.9997 | 158.0472
SMG-1.RR.291.1 | 25035689123215 | Sunamganj, West Teghoria, Samsul Hoq | 2019-08-07 | NQ1002 | 7.1 | 43 | 7.1 | 44 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7344 | 1415.9997 | 74.809
SMG-1.RR.292.1 | 25035589123214 | Sunamganj, West Teghoria, Ambiya Khatun | 2019-08-07 | NQ1002 | 2.5 | 45 | 2.5 | 46 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7344 | 1415.9997 | 26.3412
SMG-1.RR.293.1 | 25035519123210 | Sunamganj, West Teghoria, Koyarish Ali | 2019-08-07 | NQ1002 | 7.3 | 47 | 7.3 | 48 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7344 | 1415.9997 | 76.9163
SMG-1.RR.294.1 | 25034659123263 | Sunamganj, West Hazi Para, Zahed Hasan | 2019-08-08 | NQ1002 | 3.1 | 63 | 3.1 | 64 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7344 | 1415.9997 | 32.6631
SMG-1.RR.295.1 | 25034759123272 | Sunamganj, West Hazi Para, Shahana M.P | 2019-08-08 | NQ1002 | 7.4 | 67 | 7.4 | 68 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7344 | 1415.9997 | 77.97
SMG-1.RR.296.1 | 25034869123254 | Sunamganj, West Hazi Para, Md. Joynal Abedin | 2019-08-08 | NQ1002 | 11.6 | 69 | 11.4 | 70 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7344 | 1415.9997 | 120.1159
SMG-1.RR.297.1 | 25035019123260 | Sunamganj, West Hazi Para, Kadir Mia | 2019-08-08 | NQ1002 | 2.6 | 71 | 2.6 | 72 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7344 | 1415.9997 | 27.3949
SMG-1.RR.297.2 | 25035019123260 | Sunamganj, West Hazi Para, Kadir Mia | 2020-10-08 | MP1032 | 11.6 | 321 | 11.6 | 322 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7344 | 1415.9997 | 122.2232
SMG-1.RR.298.1 | 25042289125268 | Sunamganj, Maizebari, Bodipur, Mahamud Ali | 2019-08-18 | NQ1002 | 5.1 | 73 | 5.1 | 74 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7224 | 1535.9997 | 53.7361
SMG-1.RR.299.1 | 25042219125253 | Sunamganj, Maizebari, Bodipur, M A Mannan | 2019-08-18 | NQ1002 | 2.7 | 75 | 2.7 | 76 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7224 | 1535.9997 | 28.4485
SMG-1.RR.300.1 | 25032649123175 | Sunamganj Sadar, Upazilla Parishad, Beside Kalni | 2019-08-19 | MN1018 | 10.5 | 157 | 10.3 | 158 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7320 | 1439.9997 | 108.5258
SMG-1.RR.301.1 | 25042369125034 | Sunamganj, Bananipara, Balaka R/A, Md. Jashimuddin | 2019-08-03 | NQ1000 | 12 | 572 | 12 | 573 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7224 | 1535.9997 | 126.4378
SMG-1.RR.302.1 | 25042359124590 | Sunamganj, Bananipara, Balaka R/A, Osman Ali | 2019-08-03 | NQ1000 | 10.3 | 574 | 10.3 | 575 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7224 | 1535.9997 | 108.5258
SMG-1.RR.303.1 | 25042469124580 | Sunamganj, Bananipara, Balaka R/A, Matiur Rahman | 2019-08-03 | NQ1000 | 9.7 | 576 | 10 | 577 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7224 | 1535.9997 | 105.3648
SMG-1.RR.304.1 | 25042469124580 | Sunamganj, Bananipara, Balaka R/A, Siddiqur Rahman | 2019-08-03 | NQ1000 | 14.7 | 580 | 14.4 | 581 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7224 | 1535.9997 | 151.7253
SMG-1.RR.305.1 | 25042779124522 | Sunamganj, Bananipara, Dansiri R/A, Ad. Nesar Ahmed | 2019-08-03 | NQ1000 | 16.3 | 582 | 16.3 | 583 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 7224 | 1535.9997 | 171.7446
SMG-1.RR.306.1 | 25042779124522 | Sunamganj, Bananipara, Dansiri R/A, Md. Abdul Rakib | 2019-08-03 | NQ1000 | 8.6 | 584 | 8.6 | 585 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7224 | 1535.9997 | 90.6137
SMG-1.RR.307.1 | 25042699124532 | Sunamganj, Bananipara, Dansiri R/A, Raj Gagirdar | 2019-08-03 | NQ1000 | 5.9 | 586 | 5.9 | 587 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7224 | 1535.9997 | 62.1652
SMG-1.RR.308.1 | 25042279124550 | Sunamganj, Bananipara, Dansiri R/A, Md. Mujibur Rahman | 2019-08-03 | NQ1000 | 10.1 | 588 | 10.1 | 589 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7224 | 1535.9997 | 106.4185
SMG-1.RR.309.1 | 25042809124512 | Sunamganj, Bananipara, Dansiri R/A, Alhaz Md. Motosir Ali | 2019-08-03 | NQ1000 | 12.9 | 590 | 12.9 | 591 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7224 | 1535.9997 | 135.9206
SMG-1.RR.310.1 | 25042949124480 | Sunamganj, Shologhor, Surma R/A, Shaimun Kabir | 2019-08-03 | NQ1000 | 9.9 | 592 | 9.9 | 593 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7224 | 1535.9997 | 104.3112
SMG-1.RR.311.1 | 25042909124476 | Sunamganj, Shologhor, Surma R/A, Jahanara | 2019-08-03 | NQ1000 | 10.6 | 594 | 10.6 | 595 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7224 | 1535.9997 | 111.6867
SMG-1.RR.312.1 | 25044109124477 | Sunamganj Sadar, Nabinagor, Dopha Khali, Beside Vottu Varieties Shop ,Borkot Chairman | 2019-08-04 | NQ1000 | 5.1 | 621 | 5.1 | 622 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7224 | 1535.9997 | 53.7361
SMG-1.RR.313.1 | 25044109124477 | Sunamganj Sadar, Nabinagor, Dopha Khali, Beside Vottu Varieties Shop , Aminul Haq | 2019-08-04 | NQ1000 | 9.6 | 623 | 9.6 | 624 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7224 | 1535.9997 | 101.1502
SMG-1.RR.314.1 | 25044519124497 | Sunamganj Sadar, Nabinagor, Uttora-77, Hazi Shah Alam | 2019-08-04 | NQ1000 | 8.6 | 627 | 8.6 | 628 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7224 | 1535.9997 | 90.6137
SMG-1.RR.315.1 | 25044549124530 | Sunamganj Sadar, Nabinagor, Uttora-74/2 R/A, Beside Sorkar Villa,Sultan | 2019-08-04 | NQ1000 | 10.7 | 629 | 10.7 | 630 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7224 | 1535.9997 | 112.7403
SMG-1.RR.316.1 | 25044579124532 | Sunamganj Sadar, Nabinagor, Uttora-73/3, Mst. Alia Begum | 2019-08-04 | NQ1000 | 11.2 | 631 | 11.2 | 632 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7224 | 1535.9997 | 118.0086
SMG-1.RR.317.1 | 25044579124532 | Sunamganj Sadar, Nabinagor, Uttora-73/2, Md. Rakib Ali | 2019-08-04 | NQ1000 | 8.2 | 633 | 8.2 | 634 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7224 | 1535.9997 | 86.3991
SMG-1.RR.318.1 | 25044519124537 | Sunamganj Sadar, Nabinagor, Uttora-72, Khorshed | 2019-08-04 | NQ1000 | 9 | 635 | 9 | 636 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7224 | 1535.9997 | 94.8283
SMG-1.RR.319.1 | 25044459124529 | Sunamganj Sadar, Nabinagor, Uttora-72/2, Sahana Kunju, Sahana Malek | 2019-08-04 | NQ1000 | 11.6 | 637 | 11.6 | 638 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7224 | 1535.9997 | 122.2232
SMG-1.RR.320.1 | 25044619124532 | Sunamganj Sadar, Nabinagor, Uttora-74/2, Md. Jamal Hussain | 2019-08-04 | NQ1000 | 10.7 | 639 | 10.7 | 640 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7224 | 1535.9997 | 112.7403
SMG-1.RR.321.1 | 25044719124549 | Sunamganj Sadar, Nabinagor, Holding no: 67, Kabir Ahmad | 2019-08-04 | NQ1000 | 5.3 | 641 | 5.3 | 642 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7224 | 1535.9997 | 55.8434
SMG-1.RR.322.1 | 25044619124549 | Sunamganj, Nabinagar, Billal Hossain | 2019-08-05 | NQ1000 | 10.7 | 643 | 10.7 | 644 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7224 | 1535.9997 | 112.7403
SMG-1.RR.323.1 | 25041119124311 | Sunamganj, Shologhor, Kazir Point, Toson R/A, Genarel Hospital, Sayed Monoyar Ali | 2019-08-05 | NQ1000 | 12 | 645 | 12 | 646 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7272 | 1487.9997 | 126.4378
SMG-1.RR.325.1 | 25040889124302 | Sunamganj, Shologhor, Kazir Point, Toson R/A, Nur Ahmad / Khalil Ahmed | 2019-08-05 | NQ1000 | 11.7 | 649 | 11.7 | 650 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7272 | 1487.9997 | 123.2768
SMG-1.RR.326.1 | 25040729124296 | Sunamganj, Shologhor, Kazir Point, Hasonnagar R/A, Rahmat Ali | 2019-08-05 | NQ1000 | 10.6 | 651 | 10.2 | 652 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7272 | 1487.9997 | 107.4721
SMG-1.RR.327.1 | 25040149124303 | Sunamganj, Shologhor, Hasonnagar, Purbi R/A, Shahabuddin Chairman | 2019-08-05 | NQ1000 | 6.2 | 653 | 6.2 | 654 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7272 | 1487.9997 | 65.3262
SMG-1.RR.328.1 | 25040149124303 | Sunamganj, Shologhor, Hasonnagar, Purbi R/A, Ad. Pronab Kanti | 2019-08-05 | NQ1000 | 9 | 655 | 9 | 656 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7272 | 1487.9997 | 94.8283
SMG-1.RR.329.1 | 25040149124303 | Sunamganj, Shologhor, Hasonnagar, Purbi R/A, Shubimol Chakroborti | 2019-08-05 | NQ1000 | 3.9 | 657 | 3.9 | 658 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7272 | 1487.9997 | 41.0923
SMG-1.RR.330.1 | 25040149124303 | Sunamganj, Shologhor, Hasonnagar, Purbi R/A, Shantimai Chakroborti | 2019-08-05 | NQ1000 | 12.7 | 659 | 12.7 | 660 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7272 | 1487.9997 | 133.8133
SMG-1.RR.331.1 | 25040889124339 | Sunamganj, Shologhor, Hasonnagar, Purbi R/A, Md. Alamin | 2019-08-05 | NQ1000 | 3.1 | 661 | 3.1 | 662 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7272 | 1487.9997 | 32.6631
SMG-1.RR.332.1 | 25040409124328 | Sunamganj, Shologhor, Hasonnagar, Purbi R/A, Dr. Hafizur Rahman | 2019-08-05 | NQ1000 | 10.5 | 663 | 10.5 | 664 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7272 | 1487.9997 | 110.6331
SMG-1.RR.333.1 | 25035889124072 | Sunamganj, Badhonpara, Woman Collage Road, Badhon-11, Anowar | 2019-08-06 | NQ1000 | 11.9 | 681 | 11.9 | 682 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7296 | 1463.9997 | 125.3841
SMG-1.RR.334.1 | 25035889124072 | Sunamganj, Badhonpara, Woman Collage Road, Borhanuddin | 2019-08-06 | NQ1000 | 14.3 | 683 | 14.3 | 684 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7296 | 1463.9997 | 150.6717
SMG-1.RR.335.1 | 25035879124064 | Sunamganj, Badhonpara, Woman Collage Road, Babul Mia | 2019-08-06 | NQ1000 | 8.9 | 685 | 8.9 | 686 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7296 | 1463.9997 | 93.7747
SMG-1.RR.336.1 | 25035689124050 | Sunamganj, Badhonpara, Woman Collage Road, Nipes Talukdar | 2019-08-06 | NQ1000 | 12.8 | 687 | 12.7 | 688 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7296 | 1463.9997 | 133.8133
SMG-1.RR.337.1 | 25035579124063 | Sunamganj, Badhonpara, Woman Collage Road, Aboni Kumar | 2019-08-06 | NQ1000 | 10.1 | 689 | 10.1 | 690 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7296 | 1463.9997 | 106.4185
SMG-1.RR.338.1 | 25035429124078 | Sunamganj, Badhonpara, Woman Collage Road, Roy Talukdar | 2019-08-06 | NQ1000 | 3.4 | 691 | 3.4 | 692 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7296 | 1463.9997 | 35.824
SMG-1.RR.339.1 | 25035459124090 | Sunamganj, Badhonpara, Woman Collage Road, Archana Rani | 2019-08-06 | NQ1000 | 12.9 | 693 | 12.9 | 694 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7296 | 1463.9997 | 135.9206
SMG-1.RR.340.1 | 25035459124090 | Sunamganj, Badhonpara, Woman Collage Road, Ruma Podo Rai | 2019-08-06 | NQ1000 | 8.9 | 695 | 8.5 | 696 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7296 | 1463.9997 | 89.5601
SMG-1.RR.341.1 | 25035319124051 | Sunamganj, Badhonpara, Woman Collage Road, Dinesh Chandro Talukdar | 2019-08-06 | NQ1000 | 9.4 | 697 | 9.4 | 698 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7296 | 1463.9997 | 99.0429
SMG-1.RR.342.1 | 25035329124059 | Sunamganj, Badhonpara, Woman Collage Road, Bina Akter | 2019-08-06 | NQ1000 | 37.2 | 699 | 37.2 | 700 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 37.2 | 37.2 | 2.232 | 2.232 | 0.0007168 | 100% | 0% | 2.232 | 2.232 | 0.0011869 | 28 | 0.044744 | 0.044744 |  | 0 | 0 | 7296 | 1463.9997 | 391.9571
SMG-1.RR.343.1 | 25035289124089 | Sunamganj, Badhonpara, Woman Collage Road, Jaharat Monjil | 2019-08-06 | NQ1000 | 7.7 | 701 | 7.7 | 702 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7296 | 1463.9997 | 81.1309
SMG-1.RR.344.1 | 25040329123542 | Sunamganj, Jamtala, Ajbithi-36, Abdul Rab | 2019-08-07 | NQ1000 | 7.7 | 27 | 7.7 | 28 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7392 | 1367.9997 | 81.1309
SMG-1.RR.345.1 | 25040179123551 | Sunamganj, Jamtala, Ajbithi-39/1, Azir Mia | 2019-08-07 | NQ1000 | 11.1 | 29 | 10.6 | 30 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7392 | 1367.9997 | 111.6867
SMG-1.RR.346.1 | 25035849123523 | Sunamganj, Jamtala, Ajbithi, Chaina Begum | 2019-08-07 | NQ1000 | 10.6 | 31 | 10.6 | 32 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7392 | 1367.9997 | 111.6867
SMG-1.RR.347.1 | 25040039123234 | Sunamganj, West Tagoriya R/A, Rangdhonu-14, Hala Mia | 2019-08-07 | NQ1000 | 8.5 | 33 | 8.5 | 34 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7344 | 1415.9997 | 89.5601
SMG-1.RR.348.1 | 25035799123230 | Sunamganj, West Tagoriya R/A, Rangdhonu-3, Akbar Mia | 2019-08-07 | NQ1000 | 3.6 | 35 | 3.6 | 36 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7344 | 1415.9997 | 37.9313
SMG-1.RR.349.1 | 25035799123230 | Sunamganj, West Tagoriya R/A, Rangdhonu-3, Manik Mia | 2019-08-07 | NQ1000 | 13.2 | 37 | 14.1 | 38 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7344 | 1415.9997 | 148.5644
SMG-1.RR.350.1 | 25035989123197 | Sunamganj, West Tagoriya R/A, Rangdhonu-21, Islam Monjil | 2019-08-07 | NQ1000 | 8.4 | 42 | 8.4 | 43 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7344 | 1415.9997 | 88.5064
SMG-1.RR.351.1 | 25041349125119 | Sunamgong, Mohammadpur, Kawsar Alom | 2019-08-03 | NQ1000 | 16.5 | 558 | 16.5 | 559 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 7416 | 1343.9997 | 173.8519
SMG-1.RR.352.1 | 25041349125119 | Sunamgong, Mohammadpur, Rokon | 2019-08-03 | NQ1000 | 12.2 | 560 | 12.2 | 561 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7416 | 1343.9997 | 128.5451
SMG-1.RR.353.1 | 25041009125116 | Sunamgong, Mohammadpur, Mohammad Ali | 2019-08-03 | NQ1000 | 5.6 | 562 | 5.4 | 563 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7416 | 1343.9997 | 56.897
SMG-1.RR.354.1 | 25040989125094 | Sunamgong, Mohammadpur, Abu Daud Rofiq | 2019-08-03 | NQ1000 | 1.7 | 564 | 1.7 | 565 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7416 | 1343.9997 | 17.912
SMG-1.RR.354.2 | 25040989125094 | Sunamgong, Mohammadpur, Abu Daud Rofiq | 2022-02-24 | LU1001 | 4.7 | 4 | 4.7 | 5 | 2022-02-24 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6120 | 1343.9997 | 42.195
SMG-1.RR.355.1 | 25040679125108 | Sunamgong, Mohammadpur, Mohammad Ali | 2019-08-03 | NQ1000 | 11.5 | 566 | 11.5 | 567 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7416 | 1343.9997 | 121.1695
SMG-1.RR.356.1 | 25040589125110 | Sunamgong, Mohammadpur, Azrot Ali | 2019-08-03 | NQ1000 | 9.3 | 568 | 9.3 | 569 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7416 | 1343.9997 | 97.9893
SMG-1.RR.357.1 | 25041999125082 | Sunamgong, Mohammadpur, Banani Para, Keyas Monjil | 2019-08-03 | NQ1000 | 10.4 | 570 | 10.7 | 571 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7224 | 1535.9997 | 112.7403
SMG-1.RR.358.1 | 25042449124453 | Sunamgonj, Shologhor, Surma R/A, Siraj | 2019-08-04 | NQ1000 | 12.9 | 596 | 12.9 | 597 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7416 | 1343.9997 | 135.9206
SMG-1.RR.359.1 | 25042409124437 | Sunamgonj, Shologhor, Surma R/A, Kamal | 2019-08-04 | NQ1000 | 6.3 | 598 | 6.3 | 599 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7416 | 1343.9997 | 66.3798
SMG-1.RR.360.1 | 25043369124426 | Sunamgonj, Shologhor, Surma R/A, Dudu Miah | 2019-08-04 | NQ1000 | 13.1 | 600 | 13.1 | 601 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7224 | 1535.9997 | 138.0279
SMG-1.RR.361.1 | 25043519124440 | Sunamgonj, Shologhor, Baharul Islam | 2019-08-04 | NQ1000 | 8.4 | 603 | 8.4 | 604 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7224 | 1535.9997 | 88.5064
SMG-1.RR.361.2 | 25043519124440 | Sunamgonj, Shologhor, Baharul Islam | 2022-10-29 | MN1018 | 4 | 106 | 4 | 107 | 2022-10-29 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 0 | 1535.9997 | 7.39
SMG-1.RR.362.1 | 25043629124441 | Sunamgonj, Shologhor, Nurul Islam | 2019-08-04 | NQ1000 | 11.9 | 605 | 11.9 | 606 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7224 | 1535.9997 | 125.3841
SMG-1.RR.363.1 | 25043629124441 | Sunamgonj, Shologhor, D.M. Nurul Islam | 2019-08-04 | NQ1000 | 10.3 | 607 | 10.3 | 608 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7224 | 1535.9997 | 108.5258
SMG-1.RR.364.1 | 25043699124452 | Sunamgonj, Uttor Shologhor, Idris Ali | 2019-08-04 | NQ1000 | 9.8 | 609 | 9.8 | 610 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7224 | 1535.9997 | 103.2575
SMG-1.RR.365.1 | 25043799124525 | Sunamgonj, Uttor Shologhor, Saleya Afrin | 2019-08-04 | NQ1000 | 7.1 | 611 | 7.1 | 612 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7224 | 1535.9997 | 74.809
SMG-1.RR.366.1 | 25043799124525 | Sunamgonj, Shologhor, Dupakhali, Minara Begum | 2019-08-04 | NQ1000 | 9.5 | 615 | 9.5 | 616 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7224 | 1535.9997 | 100.0966
SMG-1.RR.367.1 | 25043889124528 | Sunamgonj, Shologhor, Dupakhali, Bijit Roy | 2019-08-04 | NQ1000 | 4.2 | 617 | 4.2 | 618 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7224 | 1535.9997 | 44.2532
SMG-1.RR.368.1 | 25043889124528 | Sunamgonj, Shologhor, Dupakhali, Lilu Begum | 2019-08-04 | NQ1000 | 6.8 | 619 | 6.7 | 620 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7224 | 1535.9997 | 70.5944
SMG-1.RR.369.1 | 25040179124241 | Sunamgonj, Hason Nagor R/A, Upottoka, Hazi Monowar Begum | 2019-08-05 | NQ1000 | 11 | 665 | 11 | 666 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7272 | 1487.9997 | 115.9013
SMG-1.RR.370.1 | 25040299124250 | Sunamgonj, Hason Nagor R/A, Upottoka, Manik | 2019-08-05 | NQ1000 | 11.7 | 667 | 11.7 | 668 | 2022-01-01 | [9 empty] | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0
SMG-1.RR.371.1 | 25040289124233 | Sunamgonj, Hason Nagor R/A, Upottoka, Sohidullah | 2019-08-05 | NQ1000 | 9.6 | 669 | 9.6 | 670 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7272 | 1487.9997 | 101.1502
SMG-1.RR.372.1 | 25040129124199 | Sunamgonj, Hason Nagor R/A, Upottoka, Josna Rani | 2019-08-05 | NQ1000 | 4.1 | 671 | 4.1 | 672 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7272 | 1487.9997 | 43.1996
SMG-1.RR.373.1 | 25040179124199 | Sunamgonj, Hason Nagor R/A, Upottoka, Khairul | 2019-08-05 | NQ1000 | 10.6 | 673 | 10.5 | 674 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7272 | 1487.9997 | 110.6331
SMG-1.RR.374.1 | 25040409124166 | Sunamgonj, Hason Nagor R/A, Jila Porishod Staff Quarter | 2019-08-05 | NQ1000 | 10.3 | 675 | 10.3 | 676 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7272 | 1487.9997 | 108.5258
SMG-1.RR.375.1 | 25040409124164 | Sunamgonj, Hason Nagor R/A, Ronjona Charjo | 2019-08-05 | NQ1000 | 9.7 | 677 | 9.7 | 678 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7272 | 1487.9997 | 102.2039
SMG-1.RR.376.1 | 25040509124163 | Sunamgonj, Hason Nagor R/A, MA Bosir | 2019-08-05 | NQ1000 | 10.2 | 679 | 9.8 | 680 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7272 | 1487.9997 | 103.2575
SMG-1.RR.377.1 | 25035309123532 | Sunamganj, West Natun para, Sujit | 2019-08-06 | NQ1000 | 10.2 | 703 | 10.2 | 704 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7296 | 1463.9997 | 107.4721
SMG-1.RR.378.1 | 25035239123518 | Sunamganj, West Natun para, Debobroto | 2019-08-06 | NQ1000 | 3.3 | 705 | 3.3 | 706 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7296 | 1463.9997 | 34.7704
SMG-1.RR.379.1 | 25035199123515 | Sunamganj, West Natun para, Uttom Kor | 2019-08-06 | NQ1000 | 7.3 | 707 | 7.4 | 708 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7296 | 1463.9997 | 77.97
SMG-1.RR.380.1 | 25035179123529 | Sunamganj, West Natun para, Ojit Chandro Dey | 2019-08-06 | NQ1000 | 11.7 | 709 | 11.7 | 710 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7296 | 1463.9997 | 123.2768
SMG-1.RR.381.1 | 25035159123537 | Sunamganj, West Natun para, Sudansu Shekhor Das | 2019-08-06 | NQ1000 | 8.9 | 711 | 8.9 | 712 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7296 | 1463.9997 | 93.7747
SMG-1.RR.382.1 | 25035149123520 | Sunamganj, West Natun para, Horendro Kumar Pal | 2019-08-06 | NQ1000 | 4 | 713 | 4 | 714 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7296 | 1463.9997 | 42.1459
SMG-1.RR.383.1 | 25035019123530 | Sunamganj, West Natun para, Bijit Bhushan Roy | 2019-08-06 | NQ1000 | 10.5 | 715 | 10.5 | 716 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7296 | 1463.9997 | 110.6331
SMG-1.RR.384.1 | 25035689123489 | Sunamgonj, West Natun Para, Soshi Bonik | 2019-08-07 | NQ1000 | 5.5 | 1 | 5.8 | 2 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7296 | 1463.9997 | 61.1116
SMG-1.RR.385.1 | 25035689123494 | Sunamgonj, West Natun Para, Rotis | 2019-08-07 | NQ1000 | 3.9 | 3 | 3.9 | 4 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7296 | 1463.9997 | 41.0923
SMG-1.RR.386.1 | 25035859123502 | Sunamgonj, West Natun Para, Bitu Borua | 2019-08-07 | NQ1000 | 12.2 | 5 | 12.2 | 6 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7296 | 1463.9997 | 128.5451
SMG-1.RR.387.1 | 25035859123502 | Sunamgonj, West Natun Para, Fulen Sutrodhor | 2019-08-07 | NQ1000 | 6.3 | 7 | 6.3 | 8 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7296 | 1463.9997 | 66.3798
SMG-1.RR.388.1 | 25035679123523 | Sunamgonj, West Natun Para, Sonkor Roy | 2019-08-07 | NQ1000 | 11.4 | 9 | 11.4 | 10 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7296 | 1463.9997 | 120.1159
SMG-1.RR.389.1 | 25034489123552 | Sunamgonj, South Natun Para, Jotindro Bonik | 2019-08-07 | NQ1000 | 5.6 | 11 | 5.6 | 12 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7296 | 1463.9997 | 59.0043
SMG-1.RR.390.1 | 25034419123553 | Sunamgonj, South Natun Para, Nirod Ronjon | 2019-08-07 | NQ1000 | 2.3 | 13 | 2.2 | 14 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7296 | 1463.9997 | 23.1803
SMG-1.RR.391.1 | 25034379123552 | Sunamgonj, South Natun Para, Suvas Dey | 2019-08-07 | NQ1000 | 69 | 17 | 69.7 | 18 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 69.7 | 69.7 | 4.182 | 4.182 | 0.0007168 | 100% | 0% | 4.182 | 4.182 | 0.0011869 | 28 | 0.083835 | 0.083835 |  | 0 | 0 | 7296 | 1463.9997 | 734.3927
SMG-1.RR.392.1 | 25034229123548 | Sunamgonj, South Natun Para, Laku Talukder | 2019-08-07 | NQ1000 | 6.1 | 19 | 6.1 | 20 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7296 | 1463.9997 | 64.2725
SMG-1.RR.393.1 | 25034229123548 | Sunamgonj, South Natun Para, Poni Vuson | 2019-08-07 | NQ1000 | 4.2 | 21 | 4.2 | 22 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7296 | 1463.9997 | 44.2532
SMG-1.RR.394.1 | 25034159123547 | Sunamgonj, South Natun Para, Pranotos Roy | 2019-08-07 | NQ1000 | 4 | 23 | 4 | 24 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7296 | 1463.9997 | 42.1459
SMG-1.RR.395.1 | 25034159123547 | Sunamgonj, South Natun Para, Gupes Ranjon Sarker | 2019-08-07 | NQ1000 | 5.3 | 25 | 5.3 | 26 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7296 | 1463.9997 | 55.8434
SMG-1.RR.396.1 | 25034359123573 | Sunamganj, South natun Para, Udoy Roy | 2019-08-08 | NQ1000 | 11.2 | 54 | 11.2 | 55 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7296 | 1463.9997 | 118.0086
SMG-1.RR.397.1 | 25034269123585 | Sunamganj, South natun Para, Sukur Ali | 2019-08-08 | NQ1000 | 11.2 | 56 | 11 | 57 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7296 | 1463.9997 | 115.9013
SMG-1.RR.398.1 | 25034109123545 | Sunamganj, South natun Para, Bijoy Talukder | 2019-08-08 | NQ1000 | 4.4 | 58 | 4.4 | 59 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7296 | 1463.9997 | 46.3605
SMG-1.RR.399.1 | 25033989123545 | Sunamganj, South natun Para, Joinal Mia | 2019-08-08 | NQ1000 | 23.6 | 60 | 23.6 | 61 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 23.6 | 23.6 | 1.416 | 1.416 | 0.0007168 | 100% | 0% | 1.416 | 1.416 | 0.0011869 | 28 | 0.028386 | 0.028386 |  | 0 | 0 | 7296 | 1463.9997 | 248.661
SMG-1.RR.399.2 | 25033989123545 | Sunamganj, South natun Para, Joinal Mia | 2021-01-14 | MN1018 | 2.6 | 15 | 2.6 | 16 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7296 | 1463.9997 | 27.3949
SMG-1.RR.400.1 | 25033989123545 | Sunamganj, South natun Para, Chanchol Rani Dey | 2019-08-08 | NQ1000 | 2.3 | 62 | 2.3 | 63 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7296 | 1463.9997 | 24.2339
SMG-1.RR.401.1 | 25041069124015 | Sunamganj, Kali Bari Road, Opposite Praimary School, Mahmudur Rahman | 2019-08-07 | LP1002 | 13.6 | 5 | 13.6 | 6 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7392 | 1367.9997 | 143.2961
SMG-1.RR.402.1 | 25041069124015 | Sunamganj, Kali Bari Road, Opposite Praimary School, Md. Abul Hossain | 2019-08-07 | LP1002 | 9.3 | 7 | 9.3 | 8 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7392 | 1367.9997 | 97.9893
SMG-1.RR.403.1 | 25041099123594 | Sunamganj, Kali Bari Road, Opposite Praimary School, Dr. Bidhan Ronjon | 2019-08-07 | LP1002 | 5.4 | 9 | 5.4 | 10 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7392 | 1367.9997 | 56.897
SMG-1.RR.403.2 | 25041099123594 | Sunamganj, Kali Bari Road, Opposite Praimary School, Dr. Bidhan Ronjon | 2022-11-05 | MN1018 | 2.4 | 127 | 2.4 | 128 | 2022-11-05 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 0 | 1367.9997 | 3.949
SMG-1.RR.404.1 | 25040659124256 | Sunamganj, Hasan Nagar Road, Priangon Market, Faruk Mia | 2019-08-07 | LP1002 | 2.3 | 13 | 2.3 | 14 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7272 | 1487.9997 | 24.2339
SMG-1.RR.405.1 | 25040509124213 | Sunamganj, Hasan Nagar R/A, Upottoka,-80/1, Dulal Dotto | 2019-08-07 | LP1002 | 11.6 | 15 | 11.6 | 16 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7272 | 1487.9997 | 122.2232
SMG-1.RR.406.1 | 25040509124213 | Sunamganj, Hasan Nagar R/A, Upottoka,-81/3, Kibria | 2019-08-07 | LP1002 | 7.3 | 17 | 7.3 | 18 | 2022-01-01 | [9 empty] | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0
SMG-1.RR.407.1 | 25041619124231 | Sunamganj, Ukilpara, Pionear Vhobon | 2019-08-07 | LP1002 | 12.3 | 19 | 11.9 | 20 | 2022-01-01 | 2022-10-31 | MN1018 | 1.4 | 110 | 1.4 | 111 | 2022-10-31 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7272 | 1487.9997
SMG-1.RR.408.1 | 25041389124220 | Sunamganj, Alimbug, Minister Bari R/A, Mokammel Ali | 2019-08-07 | LP1002 | 26.3 | 21 | 26.3 | 22 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 26.3 | 26.3 | 1.578 | 1.578 | 0.0007168 | 100% | 0% | 1.578 | 1.578 | 0.0011869 | 28 | 0.031634 | 0.031634 |  | 0 | 0 | 7272 | 1487.9997 | 277.1095
SMG-1.RR.408.2 | 25041389124220 | Sunamganj, Alimbug, Minister Bari R/A, Mokammel Ali | 2021-01-12 | MN1018 | 7.8 | 11 | 7.8 | 12 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7272 | 1487.9997 | 82.1846
SMG-1.RR.409.1 | 25041749124219 | Sunamganj, Ukilparra R/A, Anabil-26/1, Sonot Das | 2019-08-07 | LP1002 | 5 | 23 | 5 | 24 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7272 | 1487.9997 | 52.6824
SMG-1.RR.410.1 | 25041749124219 | Sunamganj, Ukilparra R/A, Anabil-28, Borendra Chandra | 2019-08-07 | LP1002 | 29.6 | 25 | 29.6 | 26 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 29.6 | 29.6 | 1.776 | 1.776 | 0.0007168 | 100% | 0% | 1.776 | 1.776 | 0.0011869 | 28 | 0.035603 | 0.035603 |  | 120 | 0 | 7152 | 1487.9997 | 307.6075
SMG-1.RR.411.1 | 25041749124219 | Sunamganj, Ukilparra R/A, Anabil-31/1, Aptabunnesa | 2019-08-07 | LP1002 | 3.2 | 27 | 3.2 | 28 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7272 | 1487.9997 | 33.7167
SMG-1.RR.412.1 | 25041749124219 | Sunamganj, Ukilparra R/A, Anabil-30, Samsia | 2019-08-07 | LP1002 | 12.7 | 29 | 12.7 | 30 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7272 | 1487.9997 | 133.8133
SMG-1.RR.413.1 | 25041639124203 | Sunamganj, Ukilparra, A. Hakim Chowdhury, (Opposite Alimbug Jame Masjid) | 2019-08-07 | LP1002 | 10.2 | 31 | 10.2 | 32 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7272 | 1487.9997 | 107.4721
SMG-1.RR.414.1 | 25042099124057 | Sunamganj, Jail Road R/A, Abhijatri-17, Prodip Kumar | 2019-08-07 | LP1002 | 16.1 | 33 | 15.5 | 34 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 7392 | 1367.9997 | 163.3155
SMG-1.RR.414.2 | 25042099124057 | Sunamganj, Jail Road R/A, Abhijatri-17, Prodip Kumar | 2022-03-03 | LU1001 | 11.5 | 16 | 11.5 | 17 | 2022-03-03 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 5928 | 1367.9997 | 100.9193
SMG-1.RR.415.1 | 25042099124057 | Sunamganj, Jail Road R/A, Abhijatri-16, Najmul | 2019-08-07 | LP1002 | 10.5 | 35 | 10.5 | 36 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7392 | 1367.9997 | 110.6331
SMG-1.RR.416.1 | 25042099124057 | Sunamganj, Jail Road R/A, Abhijatri-14, Samsul Abedin | 2019-08-07 | LP1002 | 6.9 | 37 | 6.9 | 38 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7392 | 1367.9997 | 72.7017
SMG-1.RR.417.1 | 25042129124004 | Sunamganj, Jogonnath Bari Road, Rojot Babu | 2019-08-08 | LP1002 | 13.9 | 39 | 13.1 | 40 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7392 | 1367.9997 | 138.0279
SMG-1.RR.418.1 | 25041549123548 | Sunamganj, Moktar Para Road, Nazia Farmecy | 2019-08-08 | LP1002 | 12 | 41 | 11.6 | 42 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7392 | 1367.9997 | 122.2232
SMG-1.RR.419.1 | 25041549123548 | Sunamganj, Moktar Para Road, Latif Plaza | 2019-08-08 | LP1002 | 6.5 | 43 | 6 | 44 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7392 | 1367.9997 | 63.2189
SMG-1.RR.420.1 | 25041619123536 | Sunamganj, Moktar Para, Digonto- 20, Ahnaf Lodge | 2019-08-08 | LP1002 | 7.4 | 45 | 7.4 | 46 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7392 | 1367.9997 | 77.97
SMG-1.RR.421.1 | 25041619123536 | Sunamganj, Moktar Para, Digonto- 21, Gaurango Chandra | 2019-08-08 | LP1002 | 16.3 | 47 | 16.3 | 48 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 7392 | 1367.9997 | 171.7446
SMG-1.RR.422.1 | 25041949124269 | Sunamganj, Ukil Para R/A, Surma-8, Abul Kalam Azad | 2019-08-08 | LP1002 | 13.4 | 49 | 13.4 | 50 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7272 | 1487.9997 | 141.1888
SMG-1.RR.423.1 | 25041839124269 | Sunamganj, Ukil Para R/A, Surma-5, Monoraz Chowdhury | 2019-08-08 | LP1002 | 6.9 | 51 | 6.9 | 52 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7272 | 1487.9997 | 72.7017
SMG-1.RR.424.1 | 25041839124269 | Sunamganj, Ukil Para R/A, Anomil, H # 36/1, Md. Khalekuzzaman | 2019-08-08 | LP1002 | 12 | 53 | 12 | 54 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7272 | 1487.9997 | 126.4378
SMG-1.RR.425.1 | 25041719124271 | Sunamganj, Ukil Para R/A, Surma-3, H # 143, Roushonra Begum Chowdhury | 2019-08-08 | LP1002 | 16.7 | 55 | 16.7 | 56 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 7272 | 1487.9997 | 175.9592
SMG-1.RR.426.1 | 25041719124271 | Sunamganj, Ukil Para R/A, Surma-1, Shonda Rani Talukdar | 2019-08-08 | LP1002 | 4.2 | 57 | 4.2 | 58 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7272 | 1487.9997 | 44.2532
SMG-1.RR.427.1 | 25041999123453 | Sunamganj, West Bazar, Sugondha -24, Horicharan Bonik | 2019-08-17 | LP1002 | 15.2 | 59 | 14.6 | 60 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7392 | 1367.9997 | 153.8326
SMG-1.RR.428.1 | 25041999123453 | Sunamganj, West Bazar, Sugondha -21, Akrom Ali | 2019-08-17 | LP1002 | 14.5 | 61 | 14.5 | 62 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7392 | 1367.9997 | 152.779
SMG-1.RR.429.1 | 25042049123475 | Sunamganj, West Bazar, H# 206, Selim Mia | 2019-08-17 | LP1002 | 23.8 | 63 | 23.8 | 64 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 23.8 | 23.8 | 1.428 | 1.428 | 0.0007168 | 100% | 0% | 1.428 | 1.428 | 0.0011869 | 28 | 0.028627 | 0.028627 |  | 0 | 0 | 7392 | 1367.9997 | 250.7683
SMG-1.RR.430.1 | 25041819123499 | Sunamganj, Rai Para, Nirjhor- 11, Ronju Roy | 2019-08-17 | LP1002 | 13.1 | 65 | 13.1 | 66 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7392 | 1367.9997 | 138.0279
SMG-1.RR.431.1 | 25041819123499 | Sunamganj, Rai Para, Nirjhor- 11, Protib Dev | 2019-08-17 | LP1002 | 4.9 | 67 | 4.9 | 68 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7392 | 1367.9997 | 51.6288
SMG-1.RR.432.1 | 25041819123499 | Sunamganj, Rai Para, Nirjhor- 11, Pronoy Sutra dhor | 2019-08-17 | LP1002 | 11.3 | 69 | 11.3 | 70 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7392 | 1367.9997 | 119.0622
SMG-1.RR.433.1 | 25041759123505 | Sunamganj, Rai Para, Nirjhor- 11, Pronoti Roy | 2019-08-17 | LP1002 | 4.9 | 71 | 4.9 | 72 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7392 | 1367.9997 | 51.6288
SMG-1.RR.434.1 | 25041759123505 | Sunamganj, Rai Para, Goni Bari | 2019-08-17 | LP1002 | 1.8 | 73 | 1.8 | 74 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7392 | 1367.9997 | 18.9657
SMG-1.RR.435.1 | 25042039123501 | Sunamganj, Middle Bazar, Dulu Mia, (Infront Cinema Hall) | 2019-08-17 | LP1002 | 14.6 | 75 | 14.6 | 76 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7392 | 1367.9997 | 153.8326
SMG-1.RR.436.1 | 25031439123220 | Sunamganj, Mollik pur, Mollika R/A, H # 11, Abdullah mia | 2019-08-19 | LP1002 | 17 | 99 | 17 | 100 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 7320 | 1439.9997 | 179.1202
SMG-1.RR.437.1 | 25031439123220 | Sunamganj, Mollik pur, Mollika R/A, H # 10, Moksed Ali | 2019-08-19 | LP1002 | 11.1 | 101 | 11.1 | 102 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7320 | 1439.9997 | 116.9549
SMG-1.RR.438.1 | 25031569123221 | Sunamganj, Mollik pur, Mollika-8/1, Mojumdar Villa | 2019-08-19 | LP1002 | 7.5 | 105 | 7.4 | 106 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7320 | 1439.9997 | 77.97
SMG-1.RR.439.1 | 25031569123221 | Sunamganj, Mollik pur, Mollika-8, Rustom | 2019-08-19 | LP1002 | 11.9 | 107 | 11.9 | 108 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7320 | 1439.9997 | 125.3841
SMG-1.RR.440.1 | 25031819123227 | Sunamganj, Mollik pur, Mollika-6, Gul Rawshan | 2019-08-19 | LP1002 | 2.4 | 109 | 2.4 | 110 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7320 | 1439.9997 | 25.2876
SMG-1.RR.441.1 | 25031819123227 | Sunamganj, Mollik pur, Mollika R/A, Soshan Kali Mandir | 2019-08-19 | LP1002 | 10.9 | 111 | 10.9 | 112 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7320 | 1439.9997 | 114.8476
SMG-1.RR.442.1 | 25031999123235 | Sunamganj, Mollik pur, Mollika-5, Hazi Foroz Ali, (Pir Villa) | 2019-08-19 | LP1002 | 13.5 | 113 | 13.5 | 114 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7320 | 1439.9997 | 142.2425
SMG-1.RR.443.1 | 25032229123234 | Sunamganj, Mollik pur, Mollika-2, Sabad Ali | 2019-08-19 | LP1002 | 13.8 | 115 | 13.4 | 116 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7320 | 1439.9997 | 141.1888
SMG-1.RR.444.1 | 25032599123235 | Sunamganj, Mollik pur, Vai Vai Market, Noyon | 2019-08-19 | LP1002 | 10.9 | 117 | 10.9 | 118 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7320 | 1439.9997 | 114.8476
SMG-1.RR.445.1 | 25032759123244 | Sunamganj, Mollik pur, Soudia Market, Chan Banu | 2019-08-19 | LP1002 | 16.5 | 119 | 16.5 | 120 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 7320 | 1439.9997 | 173.8519
SMG-1.RR.446.1 | 25032899123237 | Sunamganj, Mollik pur, Soudia Market, (Beside Filling Station) | 2019-08-19 | LP1002 | 9.7 | 121 | 9.7 | 122 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7320 | 1439.9997 | 102.2039
SMG-1.RR.447.1 | 25033069123278 | Sunamganj, Mollik pur, Mouchak R/A, Tanvir | 2019-08-19 | LP1002 | 10.4 | 123 | 10.4 | 124 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7320 | 1439.9997 | 109.5794
SMG-1.RR.448.1 | 25032919123304 | Sunamganj, Mollik pur, Mouchak R/A, Zia ul Haq | 2019-08-19 | LP1002 | 14.7 | 127 | 14.4 | 128 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7320 | 1439.9997 | 151.7253
SMG-1.RR.449.1 | 25033479123278 | Sunamganj, North Mollik pur, A. Hakim, (Infront LGED) | 2019-08-19 | LP1002 | 14.8 | 129 | 14.9 | 130 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7320 | 1439.9997 | 156.9936
SMG-1.RR.450.1 | 25033699123291 | Sunamganj, North Mollik pur, Shanti mia, (Infront BGB-28 Camp) | 2019-08-19 | LP1002 | 12.2 | 131 | 12.2 | 132 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7320 | 1439.9997 | 128.5451
SMG-1.RR.451.1 | 25041489123475 | Shompara, Nirjhor R/A, H # 28, Bishojid Babu | 2019-08-18 | LP1002 | 5.1 | 79 | 5.1 | 80 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7392 | 1367.9997 | 53.7361
SMG-1.RR.452.1 | 25041529123469 | Shompara, Nirjhor R/A, H # 31, Noni Gopal Day | 2019-08-18 | LP1002 | 27.1 | 81 | 27.3 | 82 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 27.3 | 27.3 | 1.638 | 1.638 | 0.0007168 | 100% | 0% | 1.638 | 1.638 | 0.0011869 | 28 | 0.032836 | 0.032836 |  | 0 | 0 | 7392 | 1367.9997 | 287.6459
SMG-1.RR.453.1 | 25041529123469 | Shompara, Nirjhor R/A, H # 31 Napal Day | 2019-08-18 | LP1002 | 10.4 | 83 | 10.4 | 84 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7392 | 1367.9997 | 109.5794
SMG-1.RR.454.1 | 25041629123467 | Shompara, Nirjhor R/A, H # 35 , Gita Rani Day | 2019-08-18 | LP1002 | 13.8 | 85 | 13.8 | 86 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7392 | 1367.9997 | 145.4034
SMG-1.RR.455.1 | 25041329123518 | Raypara, Nirjhor R/A, H # 4, Kabari Chowdhory | 2019-08-18 | LP1002 | 20.9 | 87 | 19.9 | 88 | 2022-01-01 | [9 empty] | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0
SMG-1.RR.456.1 | 25041279123523 | Raypara Nirjhor R/A, H # 2 , Rotanungkur Das | 2019-08-18 | LP1002 | 11 | 91 | 11 | 92 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7392 | 1367.9997 | 115.9013
SMG-1.RR.457.1 | 25042059123511 | Modhom Bazar, M P Volanath Ray,Kalpona Electronic | 2019-08-18 | LP1002 | 9.9 | 93 | 9.9 | 94 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7392 | 1367.9997 | 104.3112
SMG-1.RR.458.1 | 25042129123518 | Modhom Bazar, Faizus, Panak, Volanath Enterprice | 2019-08-18 | LP1002 | 10 | 95 | 10 | 96 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7392 | 1367.9997 | 105.3648
SMG-1.RR.458.2 | 25042129123518 | Modhom Bazar, Faizus, Panak, Volanath Enterprice | 2019-08-18 | LP1002 | 6 | 97 | 6 | 98 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7392 | 1367.9997 | 63.2189
SMG-1.RR.459.1 | 25033749123087 | 28 BGB Battalion,Shapla | 2019-08-19 | LP1002 | 14.4 | 133 | 14.4 | 134 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7320 | 1439.9997 | 151.7253
SMG-1.RR.460.1 | 25033749123087 | 28 BGB Battalion, Jumuna | 2019-08-19 | LP1002 | 11.8 | 135 | 11.8 | 136 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7320 | 1439.9997 | 124.3305
SMG-1.RR.460.2 | 25033749123087 | 28 BGB Battalion, Jumuna | 2019-08-19 | LP1002 | 14.9 | 137 | 14.9 | 138 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7320 | 1439.9997 | 156.9936
SMG-1.RR.461.1 | 25033749123087 | 28 BGB Battalion, Surma | 2019-08-19 | LP1002 | 2.2 | 141 | 2.1 | 142 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7320 | 1439.9997 | 22.1266
SMG-1.RR.462.1 | 25034319123091 | 28 BGB Battalion, Shoinik line | 2019-08-19 | LP1002 | 2.4 | 143 | 2.4 | 144 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7320 | 1439.9997 | 25.2876
SMG-1.RR.463.1 | 25033929123199 | 28 BGB Battalion, Offcer's Mass | 2019-08-19 | LP1002 | 4.3 | 145 | 4.3 | 146 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7320 | 1439.9997 | 45.3069
SMG-1.RR.464.1 | 25040799125009 | Ali Para, Pollobi R/A, 22, College Road, H # 797, Md Askon Ali | 2019-08-19 | LP1002 | 1.9 | 147 | 1.9 | 148 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7416 | 1343.9997 | 20.0193
SMG-1.RR.465.1 | 25032959124459 | Notun Hasson Nagar, Prantk R/A, Hahadullah Market, A. Razzak | 2019-08-20 | MN1018 | 60.6 | 183 | 60.6 | 184 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 60.6 | 60.6 | 3.636 | 3.636 | 0.0007168 | 100% | 0% | 3.636 | 3.636 | 0.0011869 | 28 | 0.072889 | 0.072889 |  | 0 | 0 | 7248 | 1511.9997 | 638.5108
SMG-1.RR.466.1 | 25032959124459 | Notun Hasson Nagar, Prantk R/A, Hahadullah Market, A. Sattar | 2019-08-20 | MN1018 | 4.5 | 185 | 4.5 | 186 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7248 | 1511.9997 | 47.4142
SMG-1.RR.467.1 | 25032959124459 | Notun Hasson Nagar, Prantk R/A, Hahadullah Market, A Malak | 2019-08-20 | MN1018 | 2.2 | 187 | 2.1 | 188 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7248 | 1511.9997 | 22.1266
SMG-1.RR.468.1 | 25032379124518 | Notun Hasson Nagar, Prantk R/A, Abbas Uddn | 2019-08-20 | MN1018 | 3.1 | 189 | 3.1 | 190 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7248 | 1511.9997 | 32.6631
SMG-1.RR.469.1 | 25032049124538 | Notun Hasson Nagar, Prantk R/A, Nozrul Islam | 2019-08-20 | MN1018 | 10.5 | 191 | 10.5 | 192 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7248 | 1511.9997 | 110.6331
SMG-1.RR.470.1 | 25040859125006 | Ali Para, Pollobi R/A 1/2, College Road, H # 783, Md Hossan Ali | 2019-08-19 | LP1002 | 4.4 | 154 | 4.4 | 155 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7416 | 1343.9997 | 46.3605
SMG-1.RR.501.1 | 25034409123430 | Sunamganj, Police Super Office Goli, Hazipara, Bashundhara R /A -22, Razia Monzil | 2019-08-07 | MN1018 | 9.5 | 23 | 9.5 | 24 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7296 | 1463.9997 | 100.0966
SMG-1.RR.502.1 | 25034719123513 | Sunamganj, Niloy-116, West Notun Para, W # 05, Azir Uddin | 2019-08-08 | MN1018 | 12.4 | 39 | 12.4 | 40 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7296 | 1463.9997 | 130.6524
SMG-1.RR.503.1 | 25034349123511 | Sunamganj, Niloy R/A, West Notun Para, W # 05, Amirul Islam | 2019-08-08 | MN1018 | 11.8 | 43 | 11.8 | 44 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7296 | 1463.9997 | 124.3305
SMG-1.RR.504.1 | 25034349123511 | Sunamganj, Niloy-133/6, R/A Notun Para, Maya Kutir, Kamal | 2019-08-08 | MN1018 | 7 | 45 | 6.4 | 46 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7296 | 1463.9997 | 67.4335
SMG-1.RR.505.1 | 25034349123511 | Sunamganj, Niloy R/A -133/6,Notun Para, Motin | 2019-08-08 | MN1018 | 5.1 | 49 | 5.1 | 50 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7296 | 1463.9997 | 53.7361
SMG-1.RR.506.1 | 25034349123511 | Sunamganj, Niloy R/A -133/4,Notun Para, Alimuddin | 2019-08-08 | MN1018 | 2 | 51 | 2 | 52 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7296 | 1463.9997 | 21.073
SMG-1.RR.507.1 | 25040879123242 | Sunamganj, West Tagharia, Sonali R/A, Word # 07, Tahir Alom | 2019-08-17 | MN1018 | 4.8 | 65 | 4.5 | 66 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7344 | 1415.9997 | 47.4142
SMG-1.RR.508.1 | 25040879123242 | Sunamganj, West Tagharia, Sonali R/A, Word # 07, Harun Molla | 2019-08-17 | MN1018 | 3.7 | 69 | 3.7 | 70 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7344 | 1415.9997 | 38.985
SMG-1.RR.509.1 | 25040879123242 | Sunamganj, West Tagharia, Sonali R/A, Word # 07, Afjular Nessa | 2019-08-17 | MN1018 | 10.5 | 71 | 10.5 | 72 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7344 | 1415.9997 | 110.6331
SMG-1.RR.510.1 | 25040349123267 | Sunamganj, West Tagharia, Sonali R/A, Word # 07, Dawon Sajur Raja Sumon | 2019-08-17 | MN1018 | 12.3 | 73 | 12.3 | 74 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7344 | 1415.9997 | 129.5987
SMG-1.RR.511.1 | 25041019123276 | Sunamgonj, West Tagoria, Sonali R/A, Word # 07, Ruhena Akter | 2019-08-17 | MN1018 | 4.8 | 75 | 4.8 | 76 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7344 | 1415.9997 | 50.5751
SMG-1.RR.512.1 | 25041389123280 | Sunamganj Sadar, West Teghuria, Mosaddea Hussain Bacchu | 2019-08-18 | MN1018 | 1.9 | 119 | 1.9 | 120 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7344 | 1415.9997 | 20.0193
SMG-1.RR.513.1 | 25041679123280 | Sunamganj Sadar, West Teghuria, Ashak Ali | 2019-08-18 | MN1018 | 8.5 | 121 | 8.5 | 122 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7344 | 1415.9997 | 89.5601
SMG-1.RR.514.1 | 25041679123280 | Sunamganj Sadar, West Teghuria, Mokusur Rahaman | 2019-08-18 | MN1018 | 13.4 | 123 | 13 | 124 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7344 | 1415.9997 | 136.9743
SMG-1.RR.515.1 | 25041679123280 | Sunamganj Sadar, West Teghuria, Abdul Golam Mustafa | 2019-08-18 | MN1018 | 5.4 | 125 | 5.4 | 126 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7344 | 1415.9997 | 56.897
SMG-1.RR.516.1 | 25041149123280 | Sunamganj Sadar, West Teghuria, Shafi Mia | 2019-08-18 | MN1018 | 11.8 | 127 | 11.8 | 128 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7344 | 1415.9997 | 124.3305
SMG-1.RR.517.1 | 25041149123280 | Sunamganj Sadar, West Teghuria, Ropon Mia | 2019-08-18 | MN1018 | 4.9 | 131 | 4.9 | 132 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7344 | 1415.9997 | 51.6288
SMG-1.RR.518.1 | 25031139123205 | Sunamganj, Mollikpur, Notun Bus Stand, Lokman Mia | 2019-08-19 | MN1018 | 10.9 | 133 | 10.9 | 134 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7320 | 1439.9997 | 114.8476
SMG-1.RR.519.1 | 25031059123207 | Sunamganj, Mollikpur R/A, Notun Bus Stand, Mohibur Rahman | 2019-08-19 | MN1018 | 7.9 | 135 | 7.9 | 136 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7320 | 1439.9997 | 83.2382
SMG-1.RR.520.1 | 25031039123200 | Sunamganj, Mollikpur R/A, Notun Bus Stand,H # 47/1, Asad | 2019-08-19 | MN1018 | 18.8 | 137 | 18.8 | 138 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 7320 | 1439.9997 | 198.0858
SMG-1.RR.521.1 | 25030979123203 | Sunamganj, Mollikpur R/A, Notun Bus Stand, M/S Sumia Anter Price | 2019-08-19 | MN1018 | 6.1 | 139 | 6.1 | 140 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7320 | 1439.9997 | 64.2725
SMG-1.RR.521.2 | 25030979123203 | Sunamganj, Mollikpur R/A, Notun Bus Stand, M/S Sumia Anter Price | 2022-03-01 | LU1001 | 4.2 | 14 | 4.2 | 15 | 2022-03-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 5904 | 1439.9997 | 37.1
SMG-1.RR.522.1 | 25023309123217 | Sunamganj, Polli Biddut Office, V.I.P Rast House | 2019-08-19 | MN1018 | 6.5 | 143 | 6 | 144 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7320 | 1439.9997 | 63.2189
SMG-1.RR.523.1 | 25023309123217 | Sunamganj, Polli Biddut Office, G.M House | 2019-08-19 | MN1018 | 11.5 | 145 | 11.5 | 146 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7320 | 1439.9997 | 121.1695
SMG-1.RR.524.1 | 25023309123217 | Sunamganj, Polli Biddut Office, F- Tipe- Vabhon-1 | 2019-08-19 | MN1018 | 6.1 | 147 | 6.1 | 148 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7320 | 1439.9997 | 64.2725
SMG-1.RR.525.1 | 25023899123201 | Sunamganj, Oiajkhali, Sofda CNG Pump Side, Talab Ali | 2019-08-19 | MN1018 | 6.8 | 149 | 6.8 | 150 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7320 | 1439.9997 | 71.6481
SMG-1.RR.526.1 | 25023899123201 | Sunamganj, Oiajkhali, Sofda CNG Pump Side, Manik Mia | 2019-08-19 | MN1018 | 9.4 | 151 | 9.4 | 152 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7320 | 1439.9997 | 99.0429
SMG-1.RR.526.2 | 25023899123201 | Sunamganj, Oiajkhali, Sofda CNG Pump Side, Manik Mia | 2021-01-17 | MN1018 | 10 | 17 | 10 | 18 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7320 | 1439.9997 | 105.3648
SMG-1.RR.526.3 | 25023899123201 | Sunamganj, Oiajkhali, Sofda CNG Pump Side, Manik Mia | 2022-03-01 | LU1001 | 8.9 | 12 | 8.7 | 13 | 2022-03-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 5904 | 1439.9997 | 76.8499
SMG-1.RR.551.1 | 25040129123200 | Sunamganj Sadar, Pochim Teguria, Road # 4, H # Rongdonu-2, Abdur Rahim | 2019-08-07 | MN1018 | 12.1 | 33 | 12.1 | 34 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7344 | 1415.9997 | 127.4914
SMG-1.RR.551.2 | 25040129123200 | Sunamganj Sadar, Pochim Teguria, Road # 4, H # Rongdonu-2, Abdur Rahim | 2022-11-03 | MN1018 | 8.7 | 120 | 8.7 | 121 | 2022-11-03 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 0 | 1415.9997 | 14.8175
SMG-1.RR.552.1 | 25040129123200 | Sunamganj Sadar, Pochim Teguria, Road # 4, H # Rongdonu-2, Abul Hashem | 2019-08-07 | MN1018 | 12.6 | 35 | 12.6 | 36 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7344 | 1415.9997 | 132.7597
SMG-1.RR.553.1 | 25040249123194 | Sunamganj Sadar, Pochim Teguria, Road # 4, H # Rongdonu-4, Moinul Islam | 2019-08-07 | MN1018 | 5 | 37 | 5 | 38 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7344 | 1415.9997 | 52.6824
SMG-1.RR.554.1 | 25035099124027 | Sunamganj Sadar, Purba Notunpara, H # Niloy-159, Katoki Ranjon Dey | 2019-08-08 | MN1018 | 4.6 | 53 | 4.6 | 54 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7272 | 1487.9997 | 48.4678
SMG-1.RR.555.1 | 25034929124024 | Sunamganj Sadar, Purba Notunpara, H # Niloy-168/1,Monju Rani Pal | 2019-08-08 | MN1018 | 5.9 | 55 | 5.9 | 56 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7272 | 1487.9997 | 62.1652
SMG-1.RR.556.1 | 25034929124024 | Sunamganj Sadar, Purba Notunpara, H # Niloy-170/1, Probal Chandra Roy | 2019-08-08 | MN1018 | 9.8 | 57 | 9.5 | 58 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7272 | 1487.9997 | 100.0966
SMG-1.RR.557.1 | 25034929124024 | Sunamganj Sadar, Purba Notunpara, H # Niloy-169, Satish Chandra | 2019-08-08 | MN1018 | 5.9 | 59 | 6 | 60 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7272 | 1487.9997 | 63.2189
SMG-1.RR.558.1 | 25034819124003 | Sunamganj Sadar, Purba Notunpara, H # Niloy-186, Torun Kanti Dey | 2019-08-08 | MN1018 | 12 | 61 | 12 | 62 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7272 | 1487.9997 | 126.4378
SMG-1.RR.559.1 | 25034519123598 | Sunamganj Sadar, Purba Notunpara, Kamruzzaman, H # Niloy-184/3 | 2019-08-08 | MN1018 | 2.8 | 63 | 2.8 | 64 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7272 | 1487.9997 | 29.5021
SMG-1.RR.560.1 | 25040729123145 | Sunamganj Sadar, Baropara, Puraton Mosjid, Abu Sulaiman Kabel | 2019-08-18 | MN1018 | 1.9 | 77 | 1.9 | 78 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7344 | 1415.9997 | 20.0193
SMG-1.RR.560.2 | 25040729123145 | Sunamganj Sadar, Baropara, Puraton Mosjid, Abu Sulaiman Kabel | 2019-08-18 | MN1018 | 8.9 | 79 | 8.9 | 80 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7344 | 1415.9997 | 93.7747
SMG-1.RR.561.1 | 25040419123159 | Sunamganj Sadar, Baropara R/A, H # Shamoly-134/1, Shoyeb Ahmed | 2019-08-18 | MN1018 | 9.4 | 81 | 8.7 | 82 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7344 | 1415.9997 | 91.6674
SMG-1.RR.562.1 | 25040419123159 | Sunamganj Sadar, Baropara R/A, H # Shamoly-135/1, Shoyeb Ahmed | 2019-08-18 | MN1018 | 6.4 | 84 | 6.4 | 85 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7344 | 1415.9997 | 67.4335
SMG-1.RR.562.2 | 25040419123159 | Sunamganj Sadar, Baropara R/A, H # Shamoly-135/1, Shoyeb Ahmed | 2020-10-07 | MP1032 | 4.2 | 211 | 4.2 | 212 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7344 | 1415.9997 | 44.2532
SMG-1.RR.563.1 | 25040419123159 | Sunamganj Sadar, Baropara R/A, H # Shamoly-134/1, Mazaharul Islam | 2019-08-18 | MN1018 | 1.6 | 86 | 1.6 | 87 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7344 | 1415.9997 | 16.8584
SMG-1.RR.564.1 | 25040419123159 | Sunamganj Sadar, Baropara R/A, H # Shamoly-133, Joynul Islam | 2019-08-18 | MN1018 | 5 | 89 | 5 | 90 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7344 | 1415.9997 | 52.6824
SMG-1.RR.565.1 | 25041659123259 | Sunamganj Sadar, West Teghuria, Sarnali-F/18,Yesin Haque | 2019-08-18 | MN1018 | 11.2 | 91 | 11.2 | 92 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7344 | 1415.9997 | 118.0086
SMG-1.RR.565.2 | 25041659123259 | Sunamganj Sadar, West Teghuria, Sarnali-F/18,Yesin Haque | 2019-08-18 | MN1018 | 13.8 | 93 | 13.8 | 94 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7344 | 1415.9997 | 145.4034
SMG-1.RR.566.1 | 25041549123256 | Sunamganj Sadar, West Teghuria, Sarnali-14, Saiful Mia | 2019-08-18 | MN1018 | 18.5 | 95 | 17.8 | 96 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 7344 | 1415.9997 | 187.5494
SMG-1.RR.567.1 | 25041429123259 | Sunamganj Sadar, West Teghuria, Ruhin Mia | 2019-08-18 | MN1018 | 7 | 97 | 7 | 98 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7344 | 1415.9997 | 73.7554
SMG-1.RR.568.1 | 25041429123259 | Sunamganj Sadar, West Teghuria, Sarnali-F/13, Ali Amzad | 2019-08-18 | MN1018 | 13.9 | 99 | 13.9 | 100 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7344 | 1415.9997 | 146.4571
SMG-1.RR.569.1 | 25041429123259 | Sunamganj Sadar, West Teghuria, Late- Abdul Wahid | 2019-08-18 | MN1018 | 5.2 | 101 | 5.2 | 102 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7344 | 1415.9997 | 54.7897
SMG-1.RR.569.2 | 25041429123259 | Sunamganj Sadar, West Teghuria, Late- Abdul Wahid | 2022-11-03 | MN1018 | 2.5 | 122 | 2.5 | 123 | 2022-11-03 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 0 | 1415.9997 | 4.2579
SMG-1.RR.570.1 | 25041429123259 | Sunamganj Sadar, West Teghuria, Sarnali-F-12/1, Md. Azrot Ali | 2019-08-18 | MN1018 | 10.9 | 103 | 11 | 104 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7344 | 1415.9997 | 115.9013
SMG-1.RR.571.1 | 25041249123270 | Sunamganj Sadar, West Teghuria, Sarnali-F/27, Nazmul Hossen | 2019-08-18 | MN1018 | 6.4 | 105 | 6.4 | 106 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7344 | 1415.9997 | 67.4335
SMG-1.RR.572.1 | 25041249123270 | Sunamganj Sadar, West Teghuria, Sarnali-F/27, Hossen Nur | 2019-08-18 | MN1018 | 2.1 | 107 | 2.1 | 108 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7344 | 1415.9997 | 22.1266
SMG-1.RR.573.1 | 25041249123270 | Sunamganj Sadar, West Teghuria, Aleya Khatun (Kala Mia) | 2019-08-18 | MN1018 | 5.6 | 109 | 5.6 | 110 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7344 | 1415.9997 | 59.0043
SMG-1.RR.574.1 | 25041249123270 | Sunamganj Sadar, West Teghuria, Sarnali-F/26/1, Sajjad | 2019-08-18 | MN1018 | 2.9 | 111 | 2.9 | 112 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7344 | 1415.9997 | 30.5558
SMG-1.RR.575.1 | 25041289123281 | Sunamganj Sadar, West Teghuria, Abdur Rahman | 2019-08-18 | MN1018 | 1.5 | 113 | 1.5 | 114 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7344 | 1415.9997 | 15.8047
SMG-1.RR.576.1 | 25041289123281 | Sunamganj Sadar, West Teghuria, Shamsul Haque | 2019-08-18 | MN1018 | 2.7 | 115 | 2.7 | 116 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7344 | 1415.9997 | 28.4485
SMG-1.RR.577.1 | 25041339123280 | Sunamganj Sadar, West Teghuria, Shamim | 2019-08-18 | MN1018 | 2 | 117 | 2 | 118 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7344 | 1415.9997 | 21.073
SMG-1.RR.578.1 | 25032559123192 | Sunamganj Sadar, Upazella Parishad,Beside UNO Basbabhon(Gaspathor) | 2019-08-19 | MN1018 | 8.8 | 153 | 8.8 | 154 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7320 | 1439.9997 | 92.721
SMG-1.RR.579.1 | 25032649123175 | Sunamganj Sadar, Upazella Parishad,Beside Kalni And Chayabithi | 2019-08-19 | MN1018 | 10.2 | 155 | 10.2 | 156 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7320 | 1439.9997 | 107.4721
SMG-1.RR.580.1 | 25023099123159 | Sunamganj Sadar, Pourosova, Gulbagh, Gilman Sahaber Bari, Gilman | 2019-08-19 | MN1018 | 11.9 | 166 | 11.9 | 167 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7320 | 1439.9997 | 125.3841
SMG-1.RR.581.1 | 25033079124472 | Sunamganj Sadar, Natun Hason Nagor,Moyna Mia | 2019-08-20 | MN1018 | 4.1 | 173 | 4.1 | 174 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7248 | 1511.9997 | 43.1996
SMG-1.RR.582.1 | 25033079124472 | Sunamganj Sadar, Natun Hason Nagor, Jahangir Alam Ripon | 2019-08-20 | MN1018 | 2.4 | 175 | 2.4 | 176 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7248 | 1511.9997 | 25.2876
SMG-1.RR.583.1 | 25033079124472 | Sunamganj Sadar, Natun Hason Nagor,Yakub Ali | 2019-08-20 | MN1018 | 8.3 | 177 | 8.2 | 178 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7248 | 1511.9997 | 86.3991
SMG-1.RR.584.1 | 25033129124472 | Sunamganj Sadar, Natun Hason Nagor, Muhammad Ali | 2019-08-20 | MN1018 | 7.5 | 179 | 7.5 | 180 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7248 | 1511.9997 | 79.0236
SMG-1.RR.585.1 | 25033129124472 | Sunamganj Sadar, Natun Hason Nagor, Abdus Samad | 2019-08-20 | MN1018 | 4.1 | 181 | 4.1 | 182 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7248 | 1511.9997 | 43.1996
SMG-1.RR.586.1 | 25034439124414 | Sunamganj Sadar, sultanpur, Hason Nagor, Sapno Chaya Rest House, Hazi Alauddin Cottage | 2019-08-20 | MN1018 | 7.3 | 193 | 7.3 | 194 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7248 | 1511.9997 | 76.9163
SMG-1.RR.587.1 | 25034379124399 | Sunamganj Sadar, sultanpur, Hason Nagor, Abdul Shahid, H # Surovi-34 | 2019-08-20 | MN1018 | 10.5 | 195 | 10.5 | 196 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7248 | 1511.9997 | 110.6331
SMG-1.RR.588.1 | 25034369124385 | Sunamganj Sadar, West sultanpur, Hason Nagor, Surovi-35/4, Abdul Mannan | 2019-08-20 | MN1018 | 14.1 | 197 | 14.1 | 198 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7248 | 1511.9997 | 148.5644
SMG-1.RR.601.1 | 25035089124199 | Sunamganj, Hasan Nagar, Shantibag, H # 203 | 2019-08-07 | NQ1002 | 4.3 | 17 | 4.3 | 18 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7272 | 1487.9997 | 45.3069
SMG-1.RR.602.1 | 25035099124205 | Sunamganj, Hasan Nagar, Shantibag, Nilu Mia | 2019-08-07 | NQ1002 | 5.7 | 19 | 5.7 | 20 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7272 | 1487.9997 | 60.0579
SMG-1.RR.602.2 | 25035099124205 | Sunamganj, Hasan Nagar, Shantibag, Nilu Mia | 2022-10-31 | MN1018 | 5.7 | 112 | 5.7 | 113 | 2022-10-31 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 0 | 1487.9997 | 10.2016
SMG-1.RR.603.1 | 25035289124204 | Sunamganj, Hasan Nagar, Shantibag, Probit | 2019-08-07 | NQ1002 | 12.5 | 21 | 12.5 | 22 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7272 | 1487.9997 | 131.706
SMG-1.RR.604.1 | 25035289124204 | Sunamganj, Hasan Nagar, Shantibag, H # 192, Protima | 2019-08-07 | NQ1002 | 6 | 23 | 6 | 24 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7272 | 1487.9997 | 63.2189
SMG-1.RR.604.2 | 25035289124204 | Sunamganj, Hasan Nagar, Shantibag, H # 192, Protima | 2019-08-07 | NQ1002 | 9.4 | 25 | 9.4 | 26 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7272 | 1487.9997 | 99.0429
SMG-1.RR.605.1 | 25040789124147 | Sunamganj, Hasan Nagar, Upotakka, H # 104, Ponkog Chawdhury | 2019-08-08 | NQ1002 | 13.4 | 49 | 13.4 | 50 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7272 | 1487.9997 | 141.1888
SMG-1.RR.606.1 | 25040789124133 | Sunamganj, Hasan Nagar, Upotakka, H # 108, Sonjita Roy | 2019-08-08 | NQ1002 | 12.3 | 51 | 12.3 | 52 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7272 | 1487.9997 | 129.5987
SMG-1.RR.607.1 | 25040989124164 | Sunamganj, Hasan Nagar, Upotakka, H # 87, Subot Vatta Charjo | 2019-08-08 | NQ1002 | 4.8 | 53 | 4.8 | 54 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7272 | 1487.9997 | 50.5751
SMG-1.RR.608.1 | 25041419124176 | Sunamganj, Hasan Nagar, Ukail Para, H # 61, Sha Fajlul Kuddus | 2019-08-08 | NQ1002 | 5 | 55 | 5 | 56 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7272 | 1487.9997 | 52.6824
SMG-1.RR.609.1 | 25041419124176 | Sunamganj, Hasan Nagar, Ukail Para, Abdul Basir | 2019-08-08 | NQ1002 | 11.8 | 57 | 11.8 | 58 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7272 | 1487.9997 | 124.3305
SMG-1.RR.610.1 | 25041329124194 | Sunamganj, Hasan Nagar, Ukail Para, Tanim | 2019-08-08 | NQ1002 | 10.2 | 59 | 10.2 | 60 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7272 | 1487.9997 | 107.4721
SMG-1.RR.611.1 | 25041709124195 | Sunamganj, Hasan Nagar, Ukail Para, H # 437, Masud Ali | 2019-08-08 | NQ1002 | 7.2 | 61 | 7.2 | 62 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7272 | 1487.9997 | 75.8627
SMG-1.RR.612.1 | 25040409123076 | Sunamganj, Shamoli, Boropara, Jorena Begum | 2019-08-17 | NQ1000 | 10.5 | 66 | 10.8 | 67 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7344 | 1415.9997 | 113.794
SMG-1.RR.613.1 | 25040469123366 | Sunamganj, Sornali, East Taghoria, Tanim | 2019-08-17 | NQ1000 | 5.6 | 68 | 5.6 | 69 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7344 | 1415.9997 | 59.0043
SMG-1.RR.614.1 | 25041149123363 | Sunamganj, Sornali, East Taghoria, Ramjan Ali Vila | 2019-08-17 | NQ1000 | 4.3 | 76 | 4.3 | 77 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7344 | 1415.9997 | 45.3069
SMG-1.RR.615.1 | 25031129123218 | Sunamganj, Mallikpur, Mallikpur Main Road, Samsul Haque | 2019-08-19 | NQ1000 | 11.4 | 86 | 11.4 | 87 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7320 | 1439.9997 | 120.1159
SMG-1.RR.616.1 | 25031129123218 | Sunamganj, Mallikpur, Mallikpur Main Road, Abdul Shahid | 2019-08-19 | NQ1000 | 19.1 | 88 | 19.1 | 89 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 1296 | 0 | 6024 | 1439.9997 | 171.4733
SMG-1.RR.617.1 | 25031189123218 | Sunamganj, Mallikpur, Mallikpur Main Road, Abir Hossain | 2019-08-19 | NQ1000 | 7.5 | 90 | 7.5 | 91 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7320 | 1439.9997 | 79.0236
SMG-1.RR.618.1 | 25031189123218 | Sunamganj, Mallikpur, Mallikpur Main Road, Mia Chan Motor Garage | 2019-08-19 | NQ1000 | 14.7 | 92 | 14.7 | 93 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7320 | 1439.9997 | 154.8863
SMG-1.RR.618.2 | 25031189123218 | Sunamganj, Mallikpur, Mallikpur Main Road, Mia Chan Motor Garage | 2022-11-02 | MN1018 | 5.7 | 116 | 5.7 | 117 | 2022-11-02 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 0 | 1439.9997 | 9.8725
SMG-1.RR.619.1 | 25024799123248 | Sunamganj, Oyaskhali, Police Lines, R I Quarter | 2019-08-19 | NQ1000 | 71.7 | 110 | 71.7 | 111 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 71.7 | 71.7 | 4.302 | 4.302 | 0.0007168 | 100% | 0% | 4.302 | 4.302 | 0.0011869 | 28 | 0.08624 | 0.08624 |  | 0 | 0 | 7320 | 1439.9997 | 755.4657
SMG-1.RR.619.2 | 25024799123248 | Sunamganj, Oyaskhali, Police Lines, R I Quarter | 2019-08-19 | NQ1000 | 11.2 | 112 | 11.3 | 113 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7320 | 1439.9997 | 119.0622
SMG-1.RR.620.1 | 25024209123269 | Sunamganj, Oyaskhali, Oyaskhali Road, Shakil Monjil | 2019-08-19 | NQ1000 | 6.7 | 127 | 6.7 | 128 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7320 | 1439.9997 | 70.5944
SMG-1.RR.620.2 | 25024209123269 | Sunamganj, Oyaskhali, Oyaskhali Road, Shakil Monjil | 2022-11-02 | MN1018 | 4.9 | 118 | 4.9 | 119 | 2022-11-02 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 0 | 1439.9997 | 8.4869
SMG-1.RR.621.1 | 25024119123276 | Sunamganj, Oyaskhali, Oyaskhali Road, Taleb Mia | 2019-08-19 | NQ1000 | 7.5 | 129 | 7.5 | 130 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7320 | 1439.9997 | 79.0236
SMG-1.RR.622.1 | 25024189123281 | Sunamganj, Oyaskhali, Oyaskhali Road, Brac Office | 2019-08-19 | NQ1000 | 11.5 | 131 | 11.5 | 132 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7320 | 1439.9997 | 121.1695
SMG-1.RR.623.1 | 25024279123284 | Sunamganj, Oyaskhali, Oyaskhali Road, Taleb | 2019-08-19 | NQ1000 | 10.6 | 133 | 10.6 | 134 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7320 | 1439.9997 | 111.6867
SMG-1.RR.624.1 | 25024279123281 | Sunamganj, Oyaskhali, Oyaskhali Road, Sobot Ronjon Deb | 2019-08-19 | NQ1000 | 9.4 | 135 | 9.4 | 136 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7320 | 1439.9997 | 99.0429
SMG-1.RR.701.1 | 25035929123190 | Sunamgong, Boropara R/A, Shamoli-4, Anhar Ali | 2019-08-08 | NQ1000 | 10.6 | 44 | 10.6 | 45 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7344 | 1415.9997 | 111.6867
SMG-1.RR.702.1 | 25035929123190 | Sunamgong, Boropara R/A, Shamoli, Shahid Mia | 2019-08-08 | NQ1000 | 7.2 | 46 | 7.2 | 47 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7344 | 1415.9997 | 75.8627
SMG-1.RR.703.1 | 25035969123181 | Sunamgong, Boropara R/A, Shamoli, Mahabur Buildng | 2019-08-08 | NQ1000 | 2.9 | 48 | 2.9 | 49 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7344 | 1415.9997 | 30.5558
SMG-1.RR.704.1 | 25040039123152 | Sunamgong, Boropara R/A, Shamoli, Abdul Motin | 2019-08-08 | NQ1000 | 12.1 | 50 | 12.1 | 51 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7344 | 1415.9997 | 127.4914
SMG-1.RR.705.1 | 25040439123131 | Sunamgong, Boropara R/A, Shamoli, Shanju Bali | 2019-08-08 | NQ1000 | 7.5 | 52 | 7.5 | 53 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7344 | 1415.9997 | 79.0236
SMG-1.RR.706.1 | 25040369123107 | Sunamganj, Boropara, Shaymoli R/A, H # 28/2, Salma Corteg | 2019-08-17 | NQ1000 | 4.7 | 64 | 4.7 | 65 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7344 | 1415.9997 | 49.5215
SMG-1.RR.707.1 | 25040569123358 | Sunamganj, East Taghoriya, Sornali R/A, Arjan Ali | 2019-08-17 | NQ1000 | 9.7 | 70 | 9.7 | 71 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7344 | 1415.9997 | 102.2039
SMG-1.RR.708.1 | 25040529123353 | Sunamganj, East Taghoriya, Sornali R/A, Mojon Mia | 2019-08-17 | NQ1000 | 4.9 | 72 | 4.9 | 73 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7344 | 1415.9997 | 51.6288
SMG-1.RR.709.1 | 25040499123334 | Sunamganj, East Taghoriya, Sornali R/A, Tajon islam | 2019-08-17 | NQ1000 | 9.9 | 74 | 9.9 | 75 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7344 | 1415.9997 | 104.3112
SMG-1.RR.710.1 | 25031149123270 | Sunamganj, Mallikpur, Baganbari, Md. Almas Ali | 2019-08-19 | NQ1000 | 6.2 | 94 | 6.2 | 95 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7320 | 1439.9997 | 65.3262
SMG-1.RR.711.1 | 25031149123270 | Sunamganj, Mallikpur, Baganbari, Md. Almas Ali | 2019-08-19 | NQ1000 | 3.9 | 96 | 3.9 | 97 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7320 | 1439.9997 | 41.0923
SMG-1.RR.712.1 | 25031059123290 | Sunamganj, Mallikpur, Baganbari, Nurul Haque | 2019-08-19 | NQ1000 | 8.6 | 98 | 8.6 | 99 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7320 | 1439.9997 | 90.6137
SMG-1.RR.713.1 | 25030959123281 | Sunamganj, Mallikpur, Baganbari, Solaiman | 2019-08-19 | NQ1000 | 12.2 | 102 | 12.1 | 103 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7320 | 1439.9997 | 127.4914
SMG-1.RR.714.1 | 25030779123277 | Sunamganj, Mallikpur, Baganbari, Alhaz Mohammad Golam Mostofa | 2019-08-19 | NQ1000 | 1.4 | 104 | 1.4 | 105 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7320 | 1439.9997 | 14.7511
SMG-1.RR.715.1 | 25030779123277 | Sunamganj, Mallikpur, Baganbari, Alhaz Mohammad Golam Mostofa | 2019-08-19 | NQ1000 | 55.8 | 106 | 55.8 | 107 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 55.8 | 55.8 | 3.348 | 3.348 | 0.0007168 | 100% | 0% | 3.348 | 3.348 | 0.0011869 | 28 | 0.067116 | 0.067116 |  | 0 | 0 | 7320 | 1439.9997 | 587.9357
SMG-1.RR.716.1 | 25024439123231 | Sunamganj, Waizkhali, Brac Road, Apu Datta | 2019-08-19 | NQ1000 | 10.5 | 114 | 9.8 | 115 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7320 | 1439.9997 | 103.2575
SMG-1.RR.717.1 | 25024439123231 | Sunamganj, Waizkhali, Brac Road, Jitendro Kumar | 2019-08-19 | NQ1000 | 4.1 | 116 | 4.1 | 117 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7320 | 1439.9997 | 43.1996
SMG-1.RR.718.1 | 25024399123248 | Sunamganj, Waizkhali, Brac Road, Putul Rani Dev | 2019-08-19 | NQ1000 | 10.7 | 118 | 10.7 | 119 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7320 | 1439.9997 | 112.7403
SMG-1.RR.719.1 | 25024399123248 | Sunamganj, Waizkhali, Brac Road, Sribas Das | 2019-08-19 | NQ1000 | 8.8 | 120 | 8.8 | 121 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7320 | 1439.9997 | 92.721
SMG-1.RR.720.1 | 25024289123255 | Sunamganj, Waizkhali, Brac Road, Abdul Baten | 2019-08-19 | NQ1000 | 5.9 | 122 | 5.9 | 123 | 2022-01-01 | [9 empty] | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0
SMG-1.RR.721.1 | 25024279123267 | Sunamganj, Waizkhali, Brac Road, Dipti Rani Das | 2019-08-19 | NQ1000 | 5.7 | 124 | 5.6 | 125 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7320 | 1439.9997 | 59.0043
SMG-1.RR.722.1 | 25024059123280 | Sunamganj, Waizkhali, Brac Road, Ambor Ali | 2019-08-19 | NQ1000 | 3.6 | 137 | 3.6 | 138 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7320 | 1439.9997 | 37.9313
SMG-1.RR.723.1 | 25023949123279 | Sunamganj, Waizkhali, Brac Road, Abdul Ahad | 2019-08-19 | NQ1000 | 18.7 | 139 | 18.7 | 140 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 7320 | 1439.9997 | 197.0322
SMG-1.RR.741.1 | 25032519123194 | Sunamganj Sadar, Upazilla Parishad, Front Of Gaspathor | 2019-08-19 | MN1018 | 2.6 | 159 | 2.6 | 160 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7320 | 1439.9997 | 27.3949
SMG-1.RR.742.1 | 25032479123170 | Sunamganj Sadar, Upazilla Parishad, Beside Officer's Mess | 2019-08-19 | MN1018 | 9 | 161 | 9 | 162 | 2022-01-01 | [9 empty] | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0
SMG-1.RR.743.1 | 25023099123159 | Sunamganj Sadar, Pourosova, Gulbag, Gilman Sahaber Bari, Goffer | 2019-08-19 | MN1018 | 13.5 | 163 | 13.1 | 164 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7320 | 1439.9997 | 138.0279
SMG-1.RR.744.1 | 25023099123159 | Sunamganj Sadar, Pourosova, Gulbag, Gilman Sahaber Bari, Nurul Hoq | 2019-08-19 | MN1018 | 2.8 | 171 | 2.8 | 172 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7320 | 1439.9997 | 29.5021
SMG-1.RR.745.1 | 25033579124428 | Sunamganj, Notun Hasan Nagar, Bristol Road, Arshed Ali | 2019-08-20 | NQ1002 | 12.3 | 77 | 12.3 | 78 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7248 | 1511.9997 | 129.5987
SMG-1.RR.746.1 | 25033579124428 | Sunamganj, Notun Hasan Nagar, Bristol Road, Tuhin | 2019-08-20 | NQ1002 | 2.1 | 79 | 2.1 | 80 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7248 | 1511.9997 | 22.1266
SMG-1.RR.746.2 | 25033579124428 | Sunamganj, Notun Hasan Nagar, Bristol Road, Tuhin | 2020-10-06 | MN1032 | 1.2 | 7 | 1.2 | 8 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7248 | 1511.9997 | 12.6438
SMG-1.RR.747.1 | 25033649124422 | Sunamganj, Notun Hasan Nagar, Bristol Road, Md. Shahidur Rahaman | 2019-08-20 | NQ1002 | 10.5 | 81 | 10.5 | 82 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7248 | 1511.9997 | 110.6331
SMG-1.RR.747.2 | 25033649124422 | Sunamganj, Notun Hasan Nagar, Bristol Road, Md. Shahidur Rahaman | 2019-08-20 | NQ1002 | 13.5 | 83 | 13.5 | 84 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7248 | 1511.9997 | 142.2425
SMG-1.RR.748.1 | 25033389124390 | Sunamganj, Notun Hasan Nagar, Bristol Road, Jatindro Biswas | 2019-08-20 | NQ1002 | 12.6 | 85 | 12.5 | 86 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7248 | 1511.9997 | 131.706
SMG-1.RR.749.1 | 25033809124448 | Sunamganj, Notun Hasan Nagar, Bristol Road, Joynal Abedin | 2019-08-20 | NQ1002 | 2 | 89 | 2 | 90 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7248 | 1511.9997 | 21.073
SMG-1.RR.750.1 | 25033809124448 | Sunamganj, Notun Hasan Nagar, Bristol Road, Ahammed Ali | 2019-08-20 | NQ1002 | 13.6 | 91 | 13.6 | 92 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7248 | 1511.9997 | 143.2961
SMG-1.RR.751.1 | 25041879125157 | Sunamgonj, Bodipur Abashik, Bonolota-2, Kadir Villa | 2019-08-18 | NQ1000 | 14 | 78 | 14 | 79 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 7224 | 1535.9997 | 147.5107
SMG-1.RR.752.1 | 25041919125163 | Sunamgonj, Bodipur Abashik, Mofiz Ali | 2019-08-18 | NQ1000 | 12.5 | 80 | 12.5 | 81 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7224 | 1535.9997 | 131.706
SMG-1.RR.753.1 | 25041909125174 | Sunamgonj, Bodipur Abashik, Sha - Alom | 2019-08-18 | NQ1000 | 4 | 82 | 4 | 83 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7224 | 1535.9997 | 42.1459
SMG-1.RR.754.1 | 25042009125177 | Sunamgonj, Bodipur Abashik, Tara Mia | 2019-08-18 | NQ1000 | 2.1 | 84 | 2.1 | 85 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7224 | 1535.9997 | 22.1266
SMG-1.RR.755.1 | 25023779123294 | Sunamganj, Waskhali, Talib Mia | 2019-08-19 | NQ1000 | 12.4 | 141 | 12.4 | 142 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7320 | 1439.9997 | 130.6524
SMG-1.RR.756.1 | 25023779123294 | Sunamganj, Waskhali, Bokrul Mia | 2019-08-19 | NQ1000 | 13 | 143 | 13 | 144 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7320 | 1439.9997 | 136.9743
SMG-1.RR.757.1 | 25023679123288 | Sunamganj, Waskhali, Faruk Mia | 2019-08-19 | NQ1000 | 12.9 | 145 | 12.9 | 146 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7320 | 1439.9997 | 135.9206
SMG-1.RR.758.1 | 25023679123288 | Sunamganj, Waskhali, Gulfor Mia | 2019-08-19 | NQ1000 | 4.4 | 147 | 4.4 | 148 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7320 | 1439.9997 | 46.3605
SMG-1.RR.759.1 | 25023679123288 | Sunamganj, Waskhali, Mohammad Masuk Mia | 2019-08-19 | NQ1000 | 7.6 | 149 | 7.6 | 150 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7320 | 1439.9997 | 80.0773
SMG-1.RR.760.1 | 25023499123292 | Sunamganj, Waskhali, Shofiqul Islam | 2019-08-19 | NQ1000 | 11.5 | 151 | 11.5 | 152 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 4800 | 0 | 2520 | 1439.9997 | 54.7753
SMG-1.RR.761.1 | 25023669123299 | Sunamganj, Waskhali, Jafor Uddin | 2019-08-19 | NQ1000 | 2.9 | 153 | 2.8 | 154 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7320 | 1439.9997 | 29.5021
SMG-1.RR.762.1 | 25023669123299 | Sunamganj, Waskhali, Sahid Ali | 2019-08-19 | NQ1000 | 5.9 | 155 | 5.9 | 156 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7320 | 1439.9997 | 62.1652
SMG-1.RR.763.1 | 25023489123306 | Sunamganj, Waskhali, Joinal Abedin | 2019-08-19 | NQ1000 | 10 | 157 | 10 | 158 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7320 | 1439.9997 | 105.3648
SMG-1.RR.764.1 | 25033349124428 | Sunamganj, Natun Hason Nagor, Sohidullah | 2019-08-20 | NQ1000 | 15.1 | 159 | 15.1 | 160 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7248 | 1511.9997 | 159.1009
SMG-1.RR.765.1 | 25033349124428 | Sunamganj, Natun Hason Nagor, Ali Nur Mia | 2019-08-20 | NQ1000 | 13.6 | 161 | 13.6 | 162 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7248 | 1511.9997 | 143.2961
SMG-1.RR.766.1 | 25033349124428 | Sunamganj, Natun Hason Nagor, Adv Moshahed | 2019-08-20 | NQ1000 | 3.3 | 163 | 3.3 | 164 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7248 | 1511.9997 | 34.7704
SMG-1.RR.767.1 | 25033289124404 | Sunamganj, Natun Hason Nagor, Radha Kanto | 2019-08-20 | NQ1000 | 12.5 | 165 | 12.2 | 166 | 2022-01-01 | [9 empty] | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0
SMG-1.RR.768.1 | 25033349124404 | Sunamganj, Natun Hason Nagor, Sudir Biswas | 2019-08-20 | NQ1000 | 10.8 | 167 | 10.8 | 168 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7248 | 1511.9997 | 113.794
SMG-1.RR.769.1 | 25041509123304 | Sunamganj, Teghoria, Morol Hali, Ashik Mia | 2019-08-20 | NQ1000 | 8.5 | 169 | 8.5 | 170 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7344 | 1415.9997 | 89.5601
SMG-1.RR.770.1 | 25041749123293 | Sunamganj, Teghoria, Morol Hali, Edris Ali | 2019-08-20 | NQ1000 | 10.6 | 172 | 10.6 | 173 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7344 | 1415.9997 | 111.6867
SMG-1.RR.821.1 | 25035409124364 | Sunamganj, Hospital Road, Md. Sonur Ali, (Opposite Civil Sargon Office) | 2019-08-29 | LP1002 | 4.7 | 499 | 4.7 | 500 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7248 | 1511.9997 | 49.5215
SMG-1.RR.822.1 | 25041019123548 | Sunamganj, Jamai para, Golam Jakerin | 2019-08-29 | LP1002 | 12.8 | 501 | 12.8 | 502 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7392 | 1367.9997 | 134.867
SMG-1.RR.823.1 | 25034429124073 | Sunamganj, East Notun para R/A, Shopon | 2019-08-29 | LP1002 | 10.7 | 503 | 10.2 | 504 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7272 | 1487.9997 | 107.4721
SMG-1.RR.824.1 | 25034429124073 | Sunamganj, East Notun para R/A, Jamuna-22, Dhirendra Chandra Kor | 2019-08-29 | LP1002 | 2.3 | 507 | 2.3 | 508 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7272 | 1487.9997 | 24.2339
SMG-1.RR.825.1 | 25034869124032 | Sunamganj, East Notun para, Jibon pal | 2019-08-29 | LP1002 | 15.5 | 509 | 15.5 | 510 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 7272 | 1487.9997 | 163.3155
SMG-1.RR.826.1 | 25034869124032 | Sunamganj, East Notun para, Niloy-171, Himangsu Roy | 2019-08-29 | LP1002 | 9.9 | 511 | 9.9 | 512 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7272 | 1487.9997 | 104.3112
SMG-1.RR.1051.1 | 25033809124448 | Sunamganj, Notun Hasan Nagar, Bristol Road, Goal Ahammed | 2019-08-20 | NQ1002 | 11.6 | 93 | 11.6 | 94 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7248 | 1511.9997 | 122.2232
SMG-1.RR.1052.1 | 25034759123320 | Sunamganj, Islamic Foundation Office | 2019-08-29 | LU1001 | 12.2 | 156 | 12.2 | 157 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7320 | 1439.9997 | 128.5451
SMG-1.RR.1053.1 | 25035449124365 | Sunamganj, Oposite Side Of Civil Surgeon Office | 2019-08-29 | LU1001 | 9.9 | 158 | 9.9 | 159 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7248 | 1511.9997 | 104.3112
SMG-1.RR.1054.1 | 25041019123548 | Sunamganj, Jamai Para, Rahim Badhsha | 2019-08-29 | LU1001 | 5.4 | 160 | 5.7 | 161 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7392 | 1367.9997 | 60.0579
SMG-1.RR.1055.1 | 25034609124067 | Sunamganj, East Notun Para R/A, Mon Mohon Sarker | 2019-08-29 | LU1001 | 10.7 | 162 | 10.7 | 163 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7272 | 1487.9997 | 112.7403
SMG-1.RR.1056.1 | 25034309124063 | Sunamganj, East Notun Para R/A, Niranjan Talukder | 2019-08-29 | LU1001 | 5.6 | 164 | 5.6 | 165 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7272 | 1487.9997 | 59.0043
SMG-1.RR.1057.1 | 25034559124054 | Sunamganj, East Notun Para R/A, Bishnupada Gowshami | 2019-08-29 | LU1001 | 11.1 | 166 | 11.1 | 167 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7272 | 1487.9997 | 116.9549
SMG-1.RR.1058.1 | 25034679124039 | Sunamganj, East Notun Para R/A, Khitish Chandra Talukder | 2019-08-29 | LU1001 | 11 | 168 | 11 | 169 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7272 | 1487.9997 | 115.9013
SMG-1.RR.1058.2 | 25034679124039 | Sunamganj, East Notun Para R/A, Khitish Chandra Talukder | 2019-08-29 | LU1001 | 8.1 | 170 | 8.1 | 171 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7272 | 1487.9997 | 85.3455
SMG-1.RR.1059.1 | 25034679124039 | Sunamganj, East Notun Para R/A, Karuna Shindu Talukder | 2019-08-29 | LU1001 | 9.7 | 172 | 9.9 | 173 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7272 | 1487.9997 | 104.3112
SMG-2.CR.1.1 | 25010789138386 | Chatok, Shampara,Ward# 4, Akij Bazar, Ataur Rahman | 2019-08-21 | MN1018 | 8.2 | 231 | 8.2 | 232 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7896 | 863.9997 | 86.3991
SMG-2.CR.2.1 | 25012499138538 | Chatak, Bazramol, Kuti Mia Store | 2019-08-21 | LP1002 | 12.6 | 188 | 12.6 | 189 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7896 | 863.9997 | 132.7597
SMG-2.CR.3.1 | 25020919139345 | Sunamganj, Chhatak, Bagbari, Porchim Bazar, Lonce Ghat, Khaleda Hotel | 2019-08-24 | NQ1000 | 11.7 | 266 | 11.7 | 267 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7968 | 791.9997 | 123.2768
SMG-2.CR.3.2 | 25020919139345 | Sunamganj, Chhatak, Bagbari, Porchim Bazar, Lonce Ghat, Khaleda Hotel | 2021-02-10 | NQ1003 | 6 | 219 | 6 | 220 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7968 | 791.9997 | 63.2189
SMG-2.CR.4.1 | 25020759139498 | Chhatak, Club Road, Atik Hotel | 2019-08-24 | NQ1000 | 6.1 | 289 | 6.1 | 290 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7944 | 815.9997 | 64.2725
SMG-2.CR.6.1 | 25013649139041 | Chatok, Ferighat Road, Paper Mil Bazar, Achia Hotel, Aminul Haque | 2019-08-29 | MN1018 | 12.8 | 475 | 12.8 | 476 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7896 | 863.9997 | 134.867
SMG-2.RR.1.1 | 25011489139043 | Chatak, Kumna, Keshab Pal, (Beside Paper Mll) | 2019-08-21 | LP1002 | 28.8 | 156 | 28.8 | 157 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 28.8 | 28.8 | 1.728 | 1.728 | 0.0007168 | 100% | 0% | 1.728 | 1.728 | 0.0011869 | 28 | 0.03464 | 0.03464 |  | 0 | 0 | 7896 | 863.9997 | 303.4507
SMG-2.RR.2.1 | 25011489139043 | Chatak, Kumna, Monindra Pal, (Beside Paper Mll) | 2019-08-21 | LP1002 | 14.1 | 158 | 14.1 | 159 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7896 | 863.9997 | 148.5644
SMG-2.RR.3.1 | 25011489139043 | Chatak, Kumna, Rakesh Pal, (Beside Paper Mll) | 2019-08-21 | LP1002 | 7 | 160 | 7 | 161 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7896 | 863.9997 | 73.7554
SMG-2.RR.4.1 | 25011489139043 | Chatak, Kumna, Bokul Pal, (Beside Paper Mll) | 2019-08-21 | LP1002 | 33.9 | 162 | 33.9 | 163 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 33.9 | 33.9 | 2.034 | 2.034 | 0.0007168 | 100% | 0% | 2.034 | 2.034 | 0.0011869 | 28 | 0.040775 | 0.040775 |  | 0 | 0 | 7896 | 863.9997 | 357.1867
SMG-2.RR.5.1 | 25011489139043 | Chatak, Kumna, Gourango Pal, (Beside Paper Mll) | 2019-08-21 | LP1002 | 14.6 | 164 | 14.6 | 165 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7896 | 863.9997 | 153.8326
SMG-2.RR.5.2 | 25011489139043 | Chatak, Kumna, Gourango Pal, (Beside Paper Mll) | 2022-02-23 | NQ1007 | 10.7 | 1 | 10.7 | 2 | 2022-02-23 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6624 | 863.9997 | 96.3698
SMG-2.RR.6.1 | 25011709139043 | Chatak, Kumna, Shibu, (Beside Paper Mll) | 2019-08-21 | LP1002 | 11.1 | 166 | 11.1 | 167 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7896 | 863.9997 | 116.9549
SMG-2.RR.7.1 | 25012019139014 | Chatak, Kumna, Pronob Chakraarti, (Beside Paper Mll) | 2019-08-21 | LP1002 | 5.9 | 168 | 5.9 | 169 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7896 | 863.9997 | 62.1652
SMG-2.RR.7.2 | 25012019139014 | Chatak, Kumna, Pronob Chakraarti, (Beside Paper Mll) | 2021-10-11 | NQ1007 | 5.1 | 47 | 5.1 | 48 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7896 | 863.9997 | 53.7361
SMG-2.RR.8.1 | 25012019139014 | Chatak, Kumna, Mohibur Rahman, (Beside Paper Mll) | 2019-08-21 | LP1002 | 11.1 | 170 | 11.1 | 171 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7896 | 863.9997 | 116.9549
SMG-2.RR.9.1 | 25011849138599 | Chatak, Kumna, Nitai Chandra Das, (Beside Paper Mll) | 2019-08-21 | LP1002 | 4.4 | 172 | 4.4 | 173 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7896 | 863.9997 | 46.3605
SMG-2.RR.10.1 | 25011849138599 | Chatak, Kumna, Sayem Ahmad, (Beside Paper Mll) | 2019-08-21 | LP1002 | 7.1 | 174 | 7.1 | 175 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7896 | 863.9997 | 74.809
SMG-2.RR.11.1 | 25011849138599 | Chatak, Kumna, Shankar Das, (Beside Paper Mll) | 2019-08-21 | LP1002 | 8.9 | 176 | 8.9 | 177 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7896 | 863.9997 | 93.7747
SMG-2.RR.12.1 | 25011849138599 | Chatak, Kumna, Biren Das, (Beside Paper Mll) | 2019-08-21 | LP1002 | 12.2 | 178 | 12.2 | 179 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7896 | 863.9997 | 128.5451
SMG-2.RR.13.1 | 25011849138599 | Chatak, Kumna, A Haq, (Beside Paper Mll) | 2019-08-21 | LP1002 | 5 | 180 | 5 | 181 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7896 | 863.9997 | 52.6824
SMG-2.RR.14.1 | 25011849138599 | Chatak, Kumna, Mohsin, (Beside Paper Mll) | 2019-08-21 | LP1002 | 2.8 | 182 | 2.8 | 183 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7896 | 863.9997 | 29.5021
SMG-2.RR.15.1 | 25012199138587 | Chatak, Kumna, Ukil Das, (Beside Paper Mll) | 2019-08-21 | LP1002 | 11.7 | 184 | 11.7 | 185 | 2022-01-01 | [9 empty] | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0
SMG-2.RR.16.1 | 25012299138575 | Chatak, Kumna, Waris Uddin, (Beside Paper Mll) | 2019-08-21 | LP1002 | 10 | 186 | 10 | 187 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7896 | 863.9997 | 105.3648
SMG-2.RR.17.1 | 25015949140023 | Chatak, South Mondoli Vog, Aroz Mia Chowdhury Road, Sahjalal R/A, A. Motaleb | 2019-08-24 | LP1002 | 11.4 | 236 | 11.4 | 237 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7992 | 767.9997 | 120.1159
SMG-2.RR.18.1 | 25015889140004 | Chatak, South Mondoli Vog, Aroz Mia Chowdhury Road, Sahjalal R/A, Abdullah | 2019-08-24 | LP1002 | 8.2 | 238 | 7.6 | 239 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7992 | 767.9997 | 80.0773
SMG-2.RR.19.1 | 25015889140004 | Chatak, South Mondoli Vog, Aroz Mia Chowdhury Road, Sahjalal R/A, Habib | 2019-08-24 | LP1002 | 2.6 | 240 | 2.6 | 241 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7992 | 767.9997 | 27.3949
SMG-2.RR.20.1 | 25015889140004 | Chatak, South Mondoli Vog, Aroz Mia Chowdhury Road, Sahjalal R/A, Jahangir | 2019-08-24 | LP1002 | 2.2 | 242 | 2.2 | 243 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7992 | 767.9997 | 23.1803
SMG-2.RR.20.2 | 25015889140004 | Chatak, South Mondoli Vog, Aroz Mia Chowdhury Road, Sahjalal R/A, Jahangir | 2022-11-30 | NQ1007 | 7.3 | 232 | 7.4 | 233 | 2022-11-30 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 0 | 767.9997 | 6.8357
SMG-2.RR.21.1 | 25015569139594 | Chatak, South Mondoli Vog, Aroz Mia Chowdhury Road, Sahjalal R/A, A. Sattar | 2019-08-24 | LP1002 | 3.8 | 244 | 3.8 | 245 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7992 | 767.9997 | 40.0386
SMG-2.RR.22.1 | 25015569139594 | Chatak, South Mondoli Vog, Aroz Mia Chowdhury Road, Sahjalal R/A, A. Kuddus | 2019-08-24 | LP1002 | 14.9 | 246 | 14.9 | 247 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7992 | 767.9997 | 156.9936
SMG-2.RR.23.1 | 25015429140024 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, A. Hai | 2019-08-24 | LP1002 | 10.2 | 248 | 10.2 | 249 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7992 | 767.9997 | 107.4721
SMG-2.RR.24.1 | 25015429140024 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Nur Uddin | 2019-08-24 | LP1002 | 15.8 | 250 | 15.8 | 251 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7992 | 767.9997 | 166.4764
SMG-2.RR.25.1 | 25015429140024 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Sumon Ahmed | 2019-08-24 | LP1002 | 7.8 | 252 | 7.8 | 253 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7992 | 767.9997 | 82.1846
SMG-2.RR.26.1 | 25015629140021 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Mortuza Ali | 2019-08-24 | LP1002 | 12.9 | 254 | 12.9 | 255 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7992 | 767.9997 | 135.9206
SMG-2.RR.26.2 | 25015629140021 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Mortuza Ali | 2019-08-24 | LP1002 | 5.8 | 256 | 5.8 | 257 | 2022-01-01 | 2022-11-30 | NQ1007 | 1.3 | 234 | 1.3 | 235 | 2022-11-30 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7992 | 767.9997
SMG-2.RR.27.1 | 25015629140021 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, A. Wadud | 2019-08-24 | LP1002 | 6.7 | 258 | 6.7 | 259 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7992 | 767.9997 | 70.5944
SMG-2.RR.28.1 | 25015929140034 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Delwar | 2019-08-24 | LP1002 | 2.7 | 260 | 2.7 | 261 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7992 | 767.9997 | 28.4485
SMG-2.RR.29.1 | 25015929140034 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Chomok Ali | 2019-08-24 | LP1002 | 8.1 | 262 | 8.1 | 263 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7992 | 767.9997 | 85.3455
SMG-2.RR.30.1 | 25015929140034 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Gias Uddin | 2019-08-24 | LP1002 | 2.8 | 264 | 2.7 | 265 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7992 | 767.9997 | 28.4485
SMG-2.RR.31.1 | 25015929140043 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Fujlur Rahaman | 2019-08-24 | LP1002 | 5.1 | 266 | 5.1 | 267 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7992 | 767.9997 | 53.7361
SMG-2.RR.32.1 | 25015929140043 | Chatak, South Mondoli Vog, Sujon Mia Chowdhury Road, Sahjalal R/A, Somoj Ali | 2019-08-24 | LP1002 | 2.4 | 268 | 2.4 | 269 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7992 | 767.9997 | 25.2876
SMG-2.RR.34.1 | 25021649140062 | Chatak, Mondoli Vog, Thana Road, Zero Point, Anowar Khan | 2019-08-25 | LP1002 | 7.8 | 290 | 7.8 | 291 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 8016 | 743.9997 | 82.1846
SMG-2.RR.35.1 | 25021389140049 | Chatak, Mondoli Vog, Thana Road, Late Somir uddin | 2019-08-25 | LP1002 | 15 | 292 | 15 | 293 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8016 | 743.9997 | 158.0472
SMG-2.RR.36.1 | 25021389140049 | Chatak, Mondoli Vog, Thana Road, Kobir mia | 2019-08-25 | LP1002 | 20.7 | 294 | 20.7 | 295 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 20.7 | 20.7 | 1.242 | 1.242 | 0.0007168 | 100% | 0% | 1.242 | 1.242 | 0.0011869 | 28 | 0.024898 | 0.024898 |  | 0 | 0 | 8016 | 743.9997 | 218.1052
SMG-2.RR.37.1 | 25021389140049 | Chatak, Mondoli Vog, Thana Road, A. Mannan | 2019-08-25 | LP1002 | 11.5 | 296 | 11.5 | 297 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8016 | 743.9997 | 121.1695
SMG-2.RR.38.1 | 25015419140369 | Chatak, Tatikona, Ward # 9, Kayes Ahmed, (Near Tatikona Praimary School) | 2019-08-25 | LP1002 | 3.2 | 298 | 3.2 | 299 | 2022-01-01 | 2022-11-30 | NQ1007 | 1.9 | 228 | 1.9 | 229 | 2022-11-30 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7992 | 767.9997
SMG-2.RR.39.1 | 25015419140369 | Chatak, Tatikona, Ward # 9, Abdur Rahim, (Near Tatikona Praimary School) | 2019-08-25 | LP1002 | 11.1 | 300 | 10.5 | 301 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7992 | 767.9997 | 110.6331
SMG-2.RR.40.1 | 25015239140337 | Chatak, Tatikona, Ward # 9, Abdul Jalil, (Near Tatikona Praimary School) | 2019-08-25 | LP1002 | 10.5 | 302 | 10.5 | 303 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7992 | 767.9997 | 110.6331
SMG-2.RR.41.1 | 25015239140337 | Chatak, Tatikona, Ward # 9 Abdur Rahman, (Near Tatikona Praimary School) | 2019-08-25 | LP1002 | 7.1 | 304 | 7.4 | 305 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7992 | 767.9997 | 77.97
SMG-2.RR.42.1 | 25024499139120 | Chatak, East Noarai, Ward # 3, A. Musabbir, (Tobol) | 2019-08-27 | LP1002 | 15.6 | 423 | 15.6 | 424 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7920 | 839.9997 | 164.3691
SMG-2.RR.43.1 | 25024619139117 | Chatak, East Noarai, Ward # 3, Md. Azob Ali | 2019-08-27 | LP1002 | 7.4 | 425 | 7.4 | 426 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7920 | 839.9997 | 77.97
SMG-2.RR.44.1 | 25020559139117 | Chatak, West Noarai, Ward # 3, Jahangir Alam | 2019-08-27 | LP1002 | 15.6 | 427 | 15.6 | 428 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7920 | 839.9997 | 164.3691
SMG-2.RR.44.2 | 25020559139117 | Chatak, West Noarai, Ward # 3, Jahangir Alam | 2019-08-27 | LP1002 | 10 | 429 | 10 | 430 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7920 | 839.9997 | 105.3648
SMG-2.RR.45.1 | 25020489139077 | Chatak, West Noarai, Ward # 3, Monindra Kumar | 2019-08-27 | LP1002 | 10.4 | 431 | 10.4 | 432 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7920 | 839.9997 | 109.5794
SMG-2.RR.46.1 | 25020489139077 | Chatak, West Noarai, Ward # 3, Nirendra Kumar | 2019-08-27 | LP1002 | 4.6 | 433 | 4.6 | 434 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7920 | 839.9997 | 48.4678
SMG-2.RR.47.1 | 25020489139077 | Chatak, West Noarai, Ward # 3, Mostofa Anowar Enam | 2019-08-27 | LP1002 | 3.7 | 435 | 3.8 | 436 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7920 | 839.9997 | 40.0386
SMG-2.RR.48.1 | 25012859138386 | Chatak, Patibug, Ward # 5, A. Jalil | 2019-08-27 | LP1002 | 13.1 | 437 | 13.1 | 438 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7920 | 839.9997 | 138.0279
SMG-2.RR.49.1 | 25012859138386 | Chatak, Patibug, Ward # 5, A. Kabir | 2019-08-27 | LP1002 | 8.3 | 439 | 8.3 | 440 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7920 | 839.9997 | 87.4528
SMG-2.RR.50.1 | 25012679138364 | Chatak, Patibug, Ward # 5, Nasiruddin | 2019-08-27 | LP1002 | 4.9 | 441 | 4.9 | 442 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7920 | 839.9997 | 51.6288
SMG-2.RR.51.1 | 25020859140016 | Chhatak, Dak Bangla Road, Mondoli Vog, Maya Rani Goush, Back Side Of School | 2019-08-22 | LP1002 | 13.7 | 190 | 13.7 | 191 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7992 | 767.9997 | 144.3498
SMG-2.RR.51.2 | 25020859140016 | Chhatak, Dak Bangla Road, Mondoli Vog, Maya Rani Goush, Back Side Of School | 2021-02-11 | NQ1007 | 7.2 | 179 | 7.2 | 180 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7992 | 767.9997 | 75.8627
SMG-2.RR.52.1 | 25020719139596 | Chhatak, Mondoli Vog, Back Side Of School, Subir Nag Vaskor, Beside ofBagda Bakery | 2019-08-22 | LP1002 | 10.2 | 192 | 10.2 | 193 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7992 | 767.9997 | 107.4721
SMG-2.RR.53.1 | 25020829139581 | Chhatak, Mondoli Vog, Girls School Road, Bethi Das, Beside Loknath Mondir | 2019-08-22 | LP1002 | 4.9 | 194 | 4.9 | 195 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7992 | 767.9997 | 51.6288
SMG-2.RR.53.2 | 25020829139581 | Chhatak, Mondoli Vog, Girls School Road, Bethi Das, Beside Loknath Mondir | 2021-02-09 | NQ1007 | 5.3 | 170 | 5.3 | 171 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7992 | 767.9997 | 55.8434
SMG-2.RR.54.1 | 25020829139581 | Chhatak, Mondoli Vog, Girls School Road, Loknath Mondir | 2019-08-22 | LP1002 | 11.3 | 196 | 11.4 | 197 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7992 | 767.9997 | 120.1159
SMG-2.RR.55.1 | 25020649139581 | Chhatak, Mondoli Vog, Girls School Road, Ronjid Das | 2019-08-22 | LP1002 | 14.3 | 198 | 14.3 | 199 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7992 | 767.9997 | 150.6717
SMG-2.RR.56.1 | 25020639139580 | Chhatak, Mondoli Vog, Girls School Road, Dr. Dijandro | 2019-08-22 | LP1002 | 13.5 | 200 | 13.5 | 201 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7992 | 767.9997 | 142.2425
SMG-2.RR.57.1 | 25020469139573 | Chhatak, Mondoli Vog, Girls School Road, Ronjid. | 2019-08-22 | LP1002 | 9.4 | 202 | 9.4 | 203 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7992 | 767.9997 | 99.0429
SMG-2.RR.57.2 | 25020469139573 | Chhatak, Mondoli Vog, Girls School Road, Ronjid. | 2022-02-26 | NQ1007 | 5.8 | 13 | 5.8 | 14 | 2022-02-26 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6648 | 767.9997 | 51.7356
SMG-2.RR.58.1 | 25020609139561 | Chhatak, Mondoli Vog, Girls School Road, Romas Chondro | 2019-08-22 | LP1002 | 10.1 | 204 | 10.1 | 205 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7992 | 767.9997 | 106.4185
SMG-2.RR.59.1 | 25020619139556 | Chhatak, Mondoli Vog, Girls School Road, Moti Babu | 2019-08-22 | LP1002 | 6.5 | 206 | 6.5 | 207 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7992 | 767.9997 | 68.4871
SMG-2.RR.60.1 | 25020559139579 | Chhatak, Mondoli Vog, Girls School Road, Probasshne | 2019-08-22 | LP1002 | 14.8 | 208 | 15.6 | 209 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7992 | 767.9997 | 164.3691
SMG-2.RR.61.1 | 25020559139579 | Chhatak, Mondoli Vog, Girls School Road, Shonil | 2019-08-22 | LP1002 | 7.2 | 210 | 7.2 | 211 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7992 | 767.9997 | 75.8627
SMG-2.RR.62.1 | 25020529139581 | Chhatak, Mondoli Vog, Girls School Road, Norandro | 2019-08-22 | LP1002 | 3.5 | 212 | 3.5 | 213 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7992 | 767.9997 | 36.8777
SMG-2.RR.63.1 | 25020529139581 | Chhatak, Mondoli Vog, Girls School Road, Nerprondo Esh Rofu | 2019-08-22 | LP1002 | 5.1 | 214 | 5.1 | 215 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7992 | 767.9997 | 53.7361
SMG-2.RR.64.1 | 25020489140017 | Chhatak, Mondoli Vog, Girls School Road, Hassan, Beside of Mosjid | 2019-08-22 | LP1002 | 11.7 | 216 | 11.7 | 217 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7992 | 767.9997 | 123.2768
SMG-2.RR.65.1 | 25020489140017 | Chhatak, Mondoli Vog, Girls School Road, Badsha, Beside of Mosjid | 2019-08-22 | LP1002 | 8.6 | 218 | 8.6 | 219 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7992 | 767.9997 | 90.6137
SMG-2.RR.66.1 | 25020479139588 | Chhatak, Mondoli Vog, Girls School Road, Diponkor | 2019-08-22 | LP1002 | 1.6 | 220 | 1.6 | 221 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7992 | 767.9997 | 16.8584
SMG-2.RR.67.1 | 25020389139590 | Chhatak, Mondoli Vog, Girls School Road, Abu Taher Golam Kibreya | 2019-08-22 | LP1002 | 11.1 | 222 | 11.1 | 223 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7992 | 767.9997 | 116.9549
SMG-2.RR.67.2 | 25020389139590 | Chhatak, Mondoli Vog, Girls School Road, Abu Taher Golam Kibreya | 2019-08-22 | LP1002 | 2.2 | 224 | 2.2 | 225 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7992 | 767.9997 | 23.1803
SMG-2.RR.68.1 | 25020239139584 | Chhatak, Mondoli Vog, Shojon Chowdhory Road, Md. Fozlu Islam | 2019-08-22 | LP1002 | 10.6 | 226 | 10.6 | 227 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7992 | 767.9997 | 111.6867
SMG-2.RR.69.1 | 25020199140010 | Chhatak, Mondoli Vog, Shojon Chowdhory Road, Hazi Mortoza Ali | 2019-08-22 | LP1002 | 12.8 | 228 | 12.8 | 229 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7992 | 767.9997 | 134.867
SMG-2.RR.70.1 | 25020189140027 | Chhatak, Mondoli Vog, Shojon Chowdhory Road, Bosir Mia | 2019-08-22 | LP1002 | 22 | 230 | 22 | 231 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 22 | 22 | 1.32 | 1.32 | 0.0007168 | 100% | 0% | 1.32 | 1.32 | 0.0011869 | 28 | 0.026461 | 0.026461 |  | 0 | 0 | 7992 | 767.9997 | 231.8026
SMG-2.RR.71.1 | 25021069139598 | Chhatak, Dak Bangla Road, Back Side Of Mondoli Vog Primary School, Monnul Hazi | 2019-08-22 | LP1002 | 16.3 | 232 | 16.3 | 233 | 2022-01-01 | 2022-11-30 | NQ1007 | 0.5 | 230 | 0.5 | 231 | 2022-11-30 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7992 | 767.9997
SMG-2.RR.71.2 | 25021069139598 | Chhatak, Dak Bangla Road, Back Side Of Mondoli Vog Primary School, Monnul Hazi | 2022-02-26 | NQ1007 | 8.9 | 11 | 8.9 | 12 | 2022-02-26 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6648 | 767.9997 | 79.3873
SMG-2.RR.72.1 | 25021039140019 | Chhatak, Dak Bangla Road, Kholilur Rohaman | 2019-08-22 | LP1002 | 9.2 | 234 | 9.2 | 235 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7992 | 767.9997 | 96.9356
SMG-2.RR.73.1 | 25021069140079 | Chhatak, Mondoli Vog, Hospital Road, Md.Mokadas Ali | 2019-08-24 | LP1002 | 11.6 | 270 | 11.6 | 271 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8016 | 743.9997 | 122.2232
SMG-2.RR.73.2 | 25021069140079 | Chhatak, Mondoli Vog, Hospital Road, Md.Mokadas Ali | 2019-08-24 | LP1002 | 2.8 | 272 | 2.9 | 273 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 8016 | 743.9997 | 30.5558
SMG-2.RR.74.1 | 25021069140079 | Chhatak, Mondoli Vog, Hospital Road, Shonu Mia | 2019-08-24 | LP1002 | 10.4 | 274 | 10.4 | 275 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8016 | 743.9997 | 109.5794
SMG-2.RR.75.1 | 25021069140079 | Chhatak, Mondoli Vog, Hospital Road, Narayon Chondro | 2019-08-24 | LP1002 | 3.3 | 276 | 3.3 | 277 | 2022-01-01 | [9 empty] | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0
SMG-2.RR.76.1 | 25021239140079 | Chhatak, Mondoli Vog, Hospital Road, Mojib, Brother Of MP Manik | 2019-08-24 | LP1002 | 32.7 | 280 | 30.9 | 281 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 30.9 | 30.9 | 1.854 | 1.854 | 0.0007168 | 100% | 0% | 1.854 | 1.854 | 0.0011869 | 28 | 0.037166 | 0.037166 |  | 0 | 0 | 8016 | 743.9997 | 325.5773
SMG-2.RR.77.1 | 25021319140074 | Chhatak, Mondoli Vog, Hospital Road, Kamal Uddin | 2019-08-24 | LP1002 | 12.6 | 282 | 12.6 | 283 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 8016 | 743.9997 | 132.7597
SMG-2.RR.78.1 | 25021379140087 | Chhatak, Mondoli Vog, Hospital Road, Nirmol Malaker | 2019-08-24 | LP1002 | 7.6 | 284 | 7.6 | 285 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8016 | 743.9997 | 80.0773
SMG-2.RR.78.2 | 25021379140087 | Chhatak, Mondoli Vog, Hospital Road, Nirmol Malaker | 2021-02-11 | NQ1003 | 6.8 | 232 | 6.8 | 233 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 8016 | 743.9997 | 71.6481
SMG-2.RR.79.1 | 25021339140094 | Chhatak, Mondoli Vog, Hospital Road, Upandro Roy | 2019-08-24 | LP1002 | 10.2 | 286 | 10.2 | 287 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8016 | 743.9997 | 107.4721
SMG-2.RR.80.1 | 25015149140381 | Chhatak ,Tati kuna, Akra Bari, Sirazul Haque | 2019-08-25 | LP1002 | 10.5 | 338 | 10.5 | 339 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7992 | 767.9997 | 110.6331
SMG-2.RR.81.1 | 25015149140381 | Chhatak, TatiKuna, Akra Bari, Ounu Mia | 2019-08-25 | LP1002 | 11.6 | 340 | 11.4 | 341 | 2022-01-01 | 2022-11-30 | NQ1007 | 1.8 | 226 | 1.8 | 227 | 2022-11-30 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7992 | 767.9997
SMG-2.RR.82.1 | 25015099140384 | Chhatak, TatiKuna, Abdul Aowel | 2019-08-25 | LP1002 | 22.6 | 344 | 23.6 | 345 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 23.6 | 23.6 | 1.416 | 1.416 | 0.0007168 | 100% | 0% | 1.416 | 1.416 | 0.0011869 | 28 | 0.028386 | 0.028386 |  | 0 | 0 | 7992 | 767.9997 | 248.661
SMG-2.RR.83.1 | 25015119140408 | Chhatak, TatiKuna, Boro Bari, Masuk Mia | 2019-08-25 | LP1002 | 18.5 | 347 | 18.5 | 348 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 7992 | 767.9997 | 194.9249
SMG-2.RR.84.1 | 25015119140408 | Chhatak, TatiKuna, Boro Bari, Gishuddin | 2019-08-25 | LP1002 | 6.1 | 349 | 6.1 | 350 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7992 | 767.9997 | 64.2725
SMG-2.RR.85.1 | 25014869140422 | Chhatak, TatiKuna, Abdur kadir | 2019-08-25 | LP1002 | 7.7 | 351 | 7.7 | 352 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7992 | 767.9997 | 81.1309
SMG-2.RR.86.1 | 25014709140429 | Chhatak, TatiKuna, Shahadat Mia | 2019-08-25 | LP1002 | 10.2 | 353 | 10.2 | 354 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7992 | 767.9997 | 107.4721
SMG-2.RR.86.2 | 25014709140429 | Chhatak, TatiKuna, Shahadat Mia | 2021-10-14 | NQ1007 | 12.9 | 54 | 12.9 | 55 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7992 | 767.9997 | 135.9206
SMG-2.RR.87.1 | 25014539140434 | Chhatak, TatiKuna, Chan Mia | 2019-08-25 | LP1002 | 15.9 | 355 | 15.9 | 356 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 7992 | 767.9997 | 167.5301
SMG-2.RR.88.1 | 25014539140434 | Chhatak, TatiKuna, Shaju | 2019-08-25 | LP1002 | 12.6 | 359 | 13.3 | 360 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7992 | 767.9997 | 140.1352
SMG-2.RR.89.1 | 25014539140434 | Chhatak, TatiKuna, Amin | 2019-08-25 | LP1002 | 9.1 | 364 | 9.1 | 365 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7992 | 767.9997 | 95.882
SMG-2.RR.90.1 | 25021409139180 | Chhatak, Noyarai, Chowdhury para, Hazi Habibur Rahaman | 2019-08-26 | LP1002 | 7.3 | 401 | 7.3 | 402 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7920 | 839.9997 | 76.9163
SMG-2.RR.91.1 | 25021539139214 | Chhatak, Noyarai, Boro bari, Dr.Nazmul & Mokbul villa | 2019-08-26 | LP1002 | 12.1 | 403 | 12 | 404 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7920 | 839.9997 | 126.4378
SMG-2.RR.92.1 | 25021639139212 | Chhatak, Noyarai, Boro bari, Fozor Ali | 2019-08-26 | LP1002 | 10.6 | 405 | 10.6 | 406 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7920 | 839.9997 | 111.6867
SMG-2.RR.93.1 | 25021639139212 | Chhatak, Noyarai, Boro bari, Mojibur Rahaman | 2019-08-26 | LP1002 | 54.5 | 407 | 54.5 | 408 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 54.5 | 54.5 | 3.27 | 3.27 | 0.0007168 | 100% | 0% | 3.27 | 3.27 | 0.0011869 | 28 | 0.065552 | 0.065552 |  | 0 | 0 | 7920 | 839.9997 | 574.2382
SMG-2.RR.94.1 | 25022079139214 | Chhatak, Noyarai, Boro bari, Tohura begum | 2019-08-26 | LP1002 | 9.6 | 409 | 9.6 | 410 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7920 | 839.9997 | 101.1502
SMG-2.RR.95.1 | 25022399139214 | Chhatak, Noyarai, Boro bari, Hafsa begum | 2019-08-26 | LP1002 | 14.6 | 411 | 14.6 | 412 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7920 | 839.9997 | 153.8326
SMG-2.RR.96.1 | 25022399139214 | Chhatak, Noyarai, Harizul | 2019-08-26 | LP1002 | 3.4 | 413 | 3.2 | 414 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7920 | 839.9997 | 33.7167
SMG-2.RR.96.2 | 25022399139214 | Chhatak, Noyarai, Harizul | 2022-02-27 | NQ1007 | 3 | 15 | 3 | 16 | 2022-02-27 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6552 | 839.9997 | 26.6732
SMG-2.RR.97.1 | 25022419139201 | Chhatak, Noyarai, Abdul Rashid Ali | 2019-08-26 | LP1002 | 9.8 | 415 | 9.5 | 416 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7920 | 839.9997 | 100.0966
SMG-2.RR.97.2 | 25022419139201 | Chhatak, Noyarai, Abdul Rashid Ali | 2021-10-10 | NQ1007 | 13.1 | 45 | 13.1 | 46 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7920 | 839.9997 | 138.0279
SMG-2.RR.98.1 | 25022749139139 | Chhatak, Noyarai, Jewel | 2019-08-26 | LP1002 | 9.3 | 417 | 9.3 | 418 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7920 | 839.9997 | 97.9893
SMG-2.RR.99.1 | 25022809139133 | Chhatak, Noyarai, Rewel | 2019-08-26 | LP1002 | 7.8 | 419 | 7.8 | 420 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7920 | 839.9997 | 82.1846
SMG-2.RR.100.1 | 25022609139130 | Chhatak, Noyarai, Noman | 2019-08-26 | LP1002 | 7.5 | 421 | 7.4 | 422 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7920 | 839.9997 | 77.97
SMG-2.RR.101.1 | 25012359138524 | Chatok, Kumna, Baznamohol, Seraj | 2019-08-22 | MN1018 | 10.2 | 239 | 9.6 | 240 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7896 | 863.9997 | 101.1502
SMG-2.RR.102.1 | 25012139138534 | Chatok, Kumna, Baznamohol, Rezaul Karim | 2019-08-22 | MN1018 | 4.1 | 241 | 4.1 | 242 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7896 | 863.9997 | 43.1996
SMG-2.RR.103.1 | 25012089138549 | Chatok, Kumna, Baznamohol, Hasmot Ali | 2019-08-22 | MN1018 | 9.9 | 243 | 9.9 | 244 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7896 | 863.9997 | 104.3112
SMG-2.RR.104.1 | 25012089138549 | Chatok, Kumna, Baznamohol, Rochi mia | 2019-08-22 | MN1018 | 15.5 | 245 | 15.5 | 246 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 7896 | 863.9997 | 163.3155
SMG-2.RR.105.1 | 25012189138514 | Chatok, Kumna, Baznamohol, Sayed Ali | 2019-08-22 | MN1018 | 10.3 | 247 | 10.3 | 248 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7896 | 863.9997 | 108.5258
SMG-2.RR.106.1 | 25012169138514 | Chatok, Kumna, Baznamohol, Asraf | 2019-08-22 | MN1018 | 3.4 | 249 | 3.2 | 250 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7896 | 863.9997 | 33.7167
SMG-2.RR.107.1 | 25012169138514 | Chatok, Kumna, Baznamohol, Nasir uddin | 2019-08-22 | MN1018 | 4.3 | 251 | 4.3 | 252 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7896 | 863.9997 | 45.3069
SMG-2.RR.108.1 | 25012089138515 | Chatok, Kumna, Baznamohol, Akther hossain | 2019-08-22 | MN1018 | 4.9 | 253 | 4.9 | 254 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7896 | 863.9997 | 51.6288
SMG-2.RR.109.1 | 25012089138515 | Chatok, Kumna, Baznamohol, Serajul Islam | 2019-08-22 | MN1018 | 7 | 255 | 7 | 256 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7896 | 863.9997 | 73.7554
SMG-2.RR.109.2 | 25012089138515 | Chatok, Kumna, Baznamohol, Serajul Islam | 2021-02-10 | MN1032 | 8.4 | 136 | 8.5 | 137 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7896 | 863.9997 | 89.5601
SMG-2.RR.110.1 | 25011869138535 | Chatok, Kumna, Baznamohol, Late Zia uddin | 2019-08-22 | MN1018 | 15.6 | 257 | 15.6 | 258 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7896 | 863.9997 | 164.3691
SMG-2.RR.111.1 | 25011869138535 | Chatok, Kumna, Baznamohol, Osman khan | 2019-08-22 | MN1018 | 12.2 | 259 | 12.2 | 260 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7896 | 863.9997 | 128.5451
SMG-2.RR.112.1 | 25011959138483 | Chatok, Kumna, Baznamohol, Gaish uddin | 2019-08-22 | MN1018 | 5.2 | 261 | 5.2 | 262 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7896 | 863.9997 | 54.7897
SMG-2.RR.113.1 | 25011959138483 | Chatok, Kumna, Baznamohol, Alauddin | 2019-08-22 | MN1018 | 4.9 | 263 | 4.9 | 264 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7896 | 863.9997 | 51.6288
SMG-2.RR.114.1 | 25011959138483 | Chatok, Kumna, Baznamohol, Sabuddin | 2019-08-22 | MN1018 | 8 | 265 | 8 | 266 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7896 | 863.9997 | 84.2919
SMG-2.RR.115.1 | 25011979138483 | Chatok, Kumna, Baznamohol, Mosque Goli, Fazul uddin | 2019-08-22 | MN1018 | 10.4 | 267 | 10.4 | 268 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7896 | 863.9997 | 109.5794
SMG-2.RR.116.1 | 25012019138471 | Chatok, Kumna, Baznamohol, Mosque Goli, Abdus Salam | 2019-08-22 | MN1018 | 7 | 269 | 6.4 | 270 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7896 | 863.9997 | 67.4335
SMG-2.RR.117.1 | 25012019138471 | Chatok, Kumna, Baznamohol, Mosque Goli, Jamal uddin | 2019-08-22 | MN1018 | 21 | 271 | 21.1 | 272 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 21.1 | 21.1 | 1.266 | 1.266 | 0.0007168 | 100% | 0% | 1.266 | 1.266 | 0.0011869 | 28 | 0.025379 | 0.025379 |  | 0 | 0 | 7896 | 863.9997 | 222.3198
SMG-2.RR.118.1 | 25012019138471 | Chatok, Kumna, Baznamohol, Mosque Goli, Kawsar Ahmed | 2019-08-22 | MN1018 | 2.5 | 273 | 2.5 | 274 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7896 | 863.9997 | 26.3412
SMG-2.RR.119.1 | 25012019138471 | Chatok, Kumna, Baznamohol, Mosque Goli, Abdul batil | 2019-08-22 | MN1018 | 4.2 | 275 | 4.1 | 276 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7896 | 863.9997 | 43.1996
SMG-2.RR.120.1 | 25011639138473 | Chatok, Kumna, Baznamohol, Hafiz Ahmed | 2019-08-22 | MN1018 | 7 | 277 | 6.4 | 278 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7896 | 863.9997 | 67.4335
SMG-2.RR.121.1 | 25011979138483 | Chatok, Kumna, Baznamohol, Amir Ali | 2019-08-22 | MN1018 | 5.3 | 279 | 5.3 | 280 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7896 | 863.9997 | 55.8434
SMG-2.RR.122.1 | 25011979138483 | Chatok, Kumna, Baznamohol, Abdul Ali | 2019-08-22 | MN1018 | 2.1 | 281 | 2.1 | 282 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7896 | 863.9997 | 22.1266
SMG-2.RR.123.1 | 25011729138450 | Chatok, Kumna, Baznamohol, Faruque mia | 2019-08-22 | MN1018 | 9.5 | 285 | 9.5 | 286 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7896 | 863.9997 | 100.0966
SMG-2.RR.124.1 | 25011459138474 | Chatok, Kumna, Baznamohol, Amin | 2019-08-22 | MN1018 | 3 | 287 | 3 | 288 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7896 | 863.9997 | 31.6094
SMG-2.RR.125.1 | 25011459138474 | Chatok, Kumna, Baznamohol, Samim | 2019-08-22 | MN1018 | 2.4 | 289 | 2.4 | 290 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7896 | 863.9997 | 25.2876
SMG-2.RR.126.1 | 25011409138449 | Chatok, Kumna, Baznamohol, Almas Ali | 2019-08-24 | MN1018 | 12.6 | 291 | 12.6 | 292 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7896 | 863.9997 | 132.7597
SMG-2.RR.126.2 | 25011409138449 | Chatok, Kumna, Baznamohol, Almas Ali | 2021-02-10 | LU1001 | 3.1 | 178 | 3.1 | 179 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7896 | 863.9997 | 32.6631
SMG-2.RR.127.1 | 25011409138449 | Chatok, Kumna, Baznamohol, Abdul Hossain Londone | 2019-08-24 | MN1018 | 3.2 | 293 | 3.2 | 294 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7896 | 863.9997 | 33.7167
SMG-2.RR.128.1 | 25011409138449 | Chatok, Kumna, Baznamohol, Mozafor Ali | 2019-08-24 | MN1018 | 9.4 | 295 | 9.4 | 296 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7896 | 863.9997 | 99.0429
SMG-2.RR.129.1 | 25011249138438 | Chatok, Kumna, Baznamohol, Abdul Khahar | 2019-08-24 | MN1018 | 6.4 | 297 | 6.5 | 298 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7896 | 863.9997 | 68.4871
SMG-2.RR.130.1 | 25011339138416 | Chatok, Kumna, Baznamohol,Abul Hasnat | 2019-08-24 | MN1018 | 8 | 299 | 7.4 | 300 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7896 | 863.9997 | 77.97
SMG-2.RR.131.1 | 25011049138409 | Chatok, Kumna, Baznamohol, Mohommad Hossain | 2019-08-24 | MN1018 | 3.8 | 301 | 3.8 | 302 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7896 | 863.9997 | 40.0386
SMG-2.RR.131.2 | 25011049138409 | Chatok, Kumna, Baznamohol, Mohommad Hossain | 2019-08-24 | MN1018 | 3.7 | 303 | 3.7 | 304 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7896 | 863.9997 | 38.985
SMG-2.RR.132.1 | 25011339138416 | Chatok, Kumna, Baznamohol, Ata Hossain | 2019-08-24 | MN1018 | 4.2 | 309 | 4.2 | 310 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7896 | 863.9997 | 44.2532
SMG-2.RR.133.1 | 25010999138401 | Chatok, Kumna, Baznamohol, Saidur Rahman | 2019-08-24 | MN1018 | 3.7 | 311 | 3.7 | 312 | 2022-01-01 | [9 empty] | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0
SMG-2.RR.134.1 | 25015269139470 | Chatok, Sylet Road, Baghabari, Rowshon Complex Community Center | 2019-08-24 | MN1018 | 6 | 313 | 6 | 314 | 2022-01-01 | [9 empty] | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0
SMG-2.RR.135.1 | 25014779139472 | Chatok, Sylet Road, Baghabari, Samsur Nahar R/A, Faruq Ahmed Chowdhury | 2019-08-24 | MN1018 | 7.5 | 315 | 7.5 | 316 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7944 | 815.9997 | 79.0236
SMG-2.RR.136.1 | 25014699139510 | Chatok, Sylet Road, Baghabari, Samsur Nahar R/A, Odidud Alom Chairman | 2019-08-24 | MN1018 | 4.2 | 317 | 4.2 | 318 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7944 | 815.9997 | 44.2532
SMG-2.RR.137.1 | 25014699139510 | Chatok, Sylet Road, Baghabari, Samsurnahar R/A, Abdul Monaf | 2019-08-24 | MN1018 | 4 | 319 | 4 | 320 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7944 | 815.9997 | 42.1459
SMG-2.RR.138.1 | 25014699139510 | Chatok, Sylet Road, Baghabari, Samsurnahar R/A, Sahajan | 2019-08-24 | MN1018 | 2.9 | 321 | 2.9 | 322 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7944 | 815.9997 | 30.5558
SMG-2.RR.139.1 | 25021249140009 | Chatok, Thana Road, Mondolevhoge, Kobir Ahmed | 2019-08-25 | MN1018 | 10.8 | 351 | 10.8 | 352 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8016 | 743.9997 | 113.794
SMG-2.RR.140.1 | 25021249140009 | Chatok, Thana Road, Mondolevhoge, Abdur Gafur | 2019-08-25 | MN1018 | 34.4 | 353 | 34.4 | 354 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 34.4 | 34.4 | 2.064 | 2.064 | 0.0007168 | 100% | 0% | 2.064 | 2.064 | 0.0011869 | 28 | 0.041376 | 0.041376 |  | 0 | 0 | 8016 | 743.9997 | 362.455
SMG-2.RR.141.1 | 25021249140009 | Chatok, Thana Road, Mondolevhoge, Khair Kuter | 2019-08-25 | MN1018 | 13.7 | 355 | 13.7 | 356 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 8016 | 743.9997 | 144.3498
SMG-2.RR.142.1 | 25021249140009 | Chatok, Thana Road, Mondolevhoge, Hazi M.A Rashid Mansin | 2019-08-25 | MN1018 | 10.8 | 357 | 10.8 | 358 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8016 | 743.9997 | 113.794
SMG-2.RR.143.1 | 25021249140009 | Chatok, Thana Road, Mondolevhoge, Sudep Kor | 2019-08-25 | MN1018 | 2.1 | 359 | 2.1 | 360 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 8016 | 743.9997 | 22.1266
SMG-2.RR.144.1 | 25021249140009 | Chatok, Thana Road, Mondolevhoge, Hazi Nezem Uddin | 2019-08-25 | MN1018 | 3.9 | 361 | 3.9 | 362 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 8016 | 743.9997 | 41.0923
SMG-2.RR.145.1 | 25021249140009 | Chatok, Thana Road, Mondolevhoge, Hazi Belal Mia | 2019-08-25 | MN1018 | 3.3 | 363 | 3.3 | 364 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 8016 | 743.9997 | 34.7704
SMG-2.RR.146.1 | 25021359140024 | Chatok, Thana Road, Iqbal Hossain | 2019-08-25 | MN1018 | 7 | 365 | 7 | 366 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 8016 | 743.9997 | 73.7554
SMG-2.RR.147.1 | 25021359140024 | Chatok, Thana Road, Late Samad Hossain | 2019-08-25 | MN1018 | 5.3 | 367 | 5.3 | 368 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 8016 | 743.9997 | 55.8434
SMG-2.RR.148.1 | 25021399140029 | Chatok, Thana Road, Chad Mia | 2019-08-25 | MN1018 | 7.5 | 369 | 7.5 | 370 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 8016 | 743.9997 | 79.0236
SMG-2.RR.149.1 | 25021399140029 | Chatok, Thana Road, Md. Araz Mia | 2019-08-25 | MN1018 | 3.6 | 373 | 3.6 | 374 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 216 | 0 | 7800 | 743.9997 | 36.996
SMG-2.RR.150.1 | 25021399140029 | Chatok, Thana Road, Alauddin Mia | 2019-08-25 | MN1018 | 6.9 | 375 | 6.3 | 376 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8016 | 743.9997 | 66.3798
SMG-2.RR.151.1 | 25004609138188 | Chatok, Ganokhai, Ward# 4, Ambia, Beside Chatok Roshidia Madrasa | 2019-08-21 | MN1018 | 1.8 | 199 | 1.8 | 200 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7896 | 863.9997 | 18.9657
SMG-2.RR.152.1 | 25004609138188 | Chatok, Ganokhai, Ward# 4, Chatok Roshidia Madrasa | 2019-08-21 | MN1018 | 39.8 | 201 | 39.8 | 202 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 39.8 | 39.8 | 2.388 | 2.388 | 0.0007168 | 100% | 0% | 2.388 | 2.388 | 0.0011869 | 28 | 0.047871 | 0.047871 |  | 0 | 0 | 7896 | 863.9997 | 419.352
SMG-2.RR.153.1 | 25005079138190 | Chatok, Ganokhai, Ward# 4,Chowdury Bari, Abdul Hamid | 2019-08-21 | MN1018 | 5.9 | 203 | 5.9 | 204 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7896 | 863.9997 | 62.1652
SMG-2.RR.154.1 | 25005189138183 | Chatok, Ganokhai, Ward# 4, Hazi Bari, Faruk Ahmed Chowdury | 2019-08-21 | MN1018 | 2.6 | 205 | 2.6 | 206 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7896 | 863.9997 | 27.3949
SMG-2.RR.155.1 | 25004829138208 | Chatok, Ganokhai, Ward# 4,H# 3602, Talukdar Vila | 2019-08-21 | MN1018 | 4.7 | 207 | 4.7 | 208 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7896 | 863.9997 | 49.5215
SMG-2.RR.156.1 | 25005019138232 | Chatok, Ganokhai, Ward# 4, Modina Monjil, Mawlana Mozammel | 2019-08-21 | MN1018 | 3.1 | 209 | 3.1 | 210 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7896 | 863.9997 | 32.6631
SMG-2.RR.157.1 | 25005569138290 | Chatok, Ganokhai, Ward# 4, Aftab Mansion, Azizur Rahman | 2019-08-21 | MN1018 | 11.2 | 211 | 11 | 212 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7896 | 863.9997 | 115.9013
SMG-2.RR.158.1 | 25005849138301 | Chatok, Ganokhai, Ward# 4,Shampara Road, Md. Nojir Ali | 2019-08-21 | MN1018 | 4.2 | 213 | 4.2 | 214 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7896 | 863.9997 | 44.2532
SMG-2.RR.159.1 | 25005809138270 | Chatok, Ganokhai, Ward# 4, Shampara Road, Mithun Store , Nepal Chandra | 2019-08-21 | MN1018 | 10.2 | 215 | 9.8 | 216 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7896 | 863.9997 | 103.2575
SMG-2.RR.160.1 | 25005789138267 | Chatok, Ganokhai, Ward# 4, Shampara Road, Promud Acharzo | 2019-08-21 | MN1018 | 5.9 | 217 | 5.9 | 218 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7896 | 863.9997 | 62.1652
SMG-2.RR.161.1 | 25005889138320 | Chatok, Shampara,Ward# 4, Masum Ahmed | 2019-08-21 | MN1018 | 4.6 | 219 | 4.6 | 220 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7896 | 863.9997 | 48.4678
SMG-2.RR.162.1 | 25005969138326 | Chatok, Shampara,Ward# 4, Terab Ali | 2019-08-21 | MN1018 | 12 | 221 | 12 | 222 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7896 | 863.9997 | 126.4378
SMG-2.RR.163.1 | 25010189138349 | Chatok, Shampara,Ward# 4, Ziaul Haque | 2019-08-21 | MN1018 | 5.2 | 223 | 5.2 | 224 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7896 | 863.9997 | 54.7897
SMG-2.RR.164.1 | 25010169138339 | Chatok, Shampara,Ward# 4, Farid Mia | 2019-08-21 | MN1018 | 1.9 | 225 | 1.9 | 226 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7896 | 863.9997 | 20.0193
SMG-2.RR.165.1 | 25010359138337 | Chatok, Shampara,Ward# 4, Asraf Ali | 2019-08-21 | MN1018 | 2.3 | 227 | 2.3 | 228 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7896 | 863.9997 | 24.2339
SMG-2.RR.166.1 | 25010789138386 | Chatok, Shampara,Ward# 4, Akij Bazar, Aynul Haque | 2019-08-21 | MN1018 | 34 | 229 | 34 | 230 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 34 | 34 | 2.04 | 2.04 | 0.0007168 | 100% | 0% | 2.04 | 2.04 | 0.0011869 | 28 | 0.040895 | 0.040895 |  | 0 | 0 | 7896 | 863.9997 | 358.2404
SMG-2.RR.167.1 | 25010889138396 | Chatok, Bazna Mahol, Akij Bazar, Nazmul Islam | 2019-08-21 | MN1018 | 4.4 | 233 | 4.4 | 234 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7896 | 863.9997 | 46.3605
SMG-2.RR.169.1 | 25010909138400 | Chatok, Bazna Mahol, Akij Bazar, Badrul Islam | 2019-08-21 | MN1018 | 3.2 | 237 | 3.2 | 238 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7896 | 863.9997 | 33.7167
SMG-2.RR.169.2 | 25010909138400 | Chatok, Bazna Mahol, Akij Bazar, Badrul Islam | 2021-02-10 | LU1001 | 3.1 | 176 | 3.1 | 177 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7896 | 863.9997 | 32.6631
SMG-2.RR.170.1 | 25015389139470 | Chatok, Sylhet Road, Afsar, Beside Of Lais Complex | 2019-08-24 | MN1018 | 9.6 | 323 | 9.6 | 324 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7944 | 815.9997 | 101.1502
SMG-2.RR.171.1 | 25015379139442 | Chatok, Sylhet Road, Baganbari, Modina Tower, Jamil Ahmed (Jomir) | 2019-08-24 | MN1018 | 11.9 | 325 | 11.6 | 326 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7944 | 815.9997 | 122.2232
SMG-2.RR.171.2 | 25015379139442 | Chatok, Sylhet Road, Baganbari, Modina Tower, Jamil Ahmed (Jomir) | 2019-08-24 | MN1018 | 5.6 | 329 | 5.6 | 330 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7944 | 815.9997 | 59.0043
SMG-2.RR.172.1 | 25020019139472 | Chatok, Sylhet Road, Baganbari Purbao Mosjid Goli, Tanzir Ahmed Joni | 2019-08-24 | MN1018 | 11.4 | 331 | 11.4 | 332 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7944 | 815.9997 | 120.1159
SMG-2.RR.173.1 | 25020099139464 | Chatok, Sylhet Road, Baganbari Purbao Mosjid Goli, Shamim | 2019-08-24 | MN1018 | 5.3 | 333 | 5.3 | 334 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7944 | 815.9997 | 55.8434
SMG-2.RR.173.2 | 25020099139464 | Chatok, Sylhet Road, Baganbari Purbao Mosjid Goli, Shamim | 2019-08-24 | MN1018 | 6.3 | 335 | 6.3 | 336 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7944 | 815.9997 | 66.3798
SMG-2.RR.174.1 | 25020139139455 | Chatok, Sylhet Road, Baganbari Purbao Mosjid Goli, Sabbir Ahmed | 2019-08-24 | MN1018 | 3.6 | 339 | 3.6 | 340 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7944 | 815.9997 | 37.9313
SMG-2.RR.175.1 | 25020139139455 | Chatok, Sylhet Road, Baganbari Purbao Mosjid Goli, Jalal Uddin | 2019-08-24 | MN1018 | 12.3 | 343 | 12.3 | 344 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7944 | 815.9997 | 129.5987
SMG-2.RR.176.1 | 25020139139455 | Chatok, Sylhet Road, Baganbari Purbao Mosjid Goli, Abdul Ahad Kutu Mia | 2019-08-24 | MN1018 | 3.1 | 345 | 3.1 | 346 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7944 | 815.9997 | 32.6631
SMG-2.RR.177.1 | 25020139139455 | Chatok, Sylhet Road, Baganbari Purbao Mosjid Goli, Abdul Ahad Kutu Mia | 2019-08-24 | MN1018 | 3.4 | 347 | 3.4 | 348 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7944 | 815.9997 | 35.824
SMG-2.RR.178.1 | 25020239139471 | Chatok, Sylhet Road, Front Of Chatok Government Bohumukhi High School, Hazi Fazlu Mia | 2019-08-24 | MN1018 | 6.1 | 349 | 6.1 | 350 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7944 | 815.9997 | 64.2725
SMG-2.RR.179.1 | 25020459139477 | Chatok, Sylhet Road, Bagbari, Angur Mia | 2019-08-25 | MN1018 | 2.9 | 385 | 2.9 | 386 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7944 | 815.9997 | 30.5558
SMG-2.RR.180.1 | 25020459139477 | Chatok, Sylhet Road, Bagbari, Afzal Mia Chowdury | 2019-08-25 | MN1018 | 7.3 | 387 | 7.3 | 388 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7944 | 815.9997 | 76.9163
SMG-2.RR.181.1 | 25020489139479 | Chatok, Sylhet Road, Bagbari, Abu Sayed Chowdury Babul | 2019-08-25 | MN1018 | 3.7 | 389 | 3.7 | 390 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7944 | 815.9997 | 38.985
SMG-2.RR.182.1 | 25020559139483 | Chatok, Sylhet Road, Bagbari, Md. Monsur Alam | 2019-08-25 | MN1018 | 3.4 | 391 | 3.4 | 392 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7944 | 815.9997 | 35.824
SMG-2.RR.182.2 | 25020559139483 | Chatok, Sylhet Road, Bagbari, Md. Monsur Alam | 2020-10-11 | MP1032 | 4.7 | 488 | 4.7 | 489 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7944 | 815.9997 | 49.5215
SMG-2.RR.183.1 | 25020559139483 | Chatok, Sylhet Road, Bagbari, Lahi Mia | 2019-08-25 | MN1018 | 5.4 | 393 | 5.4 | 394 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7944 | 815.9997 | 56.897
SMG-2.RR.183.2 | 25020559139483 | Chatok, Sylhet Road, Bagbari, Lahi Mia | 2021-02-09 | NQ1007 | 17.8 | 168 | 17.9 | 169 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 7944 | 815.9997 | 188.603
SMG-2.RR.184.1 | 25020559139483 | Chatok, Sylhet Road, Bagbari, Md. Hannan Mia | 2019-08-25 | MN1018 | 2.6 | 395 | 2.6 | 396 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7944 | 815.9997 | 27.3949
SMG-2.RR.185.1 | 25020559139483 | Chatok, Sylhet Road, Bagbari, Late Musa Mia | 2019-08-25 | MN1018 | 5.3 | 397 | 5.3 | 398 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7944 | 815.9997 | 55.8434
SMG-2.RR.186.1 | 25020559139483 | Chatok, Sylhet Road, Bagbari, Forid Mia | 2019-08-25 | MN1018 | 5.9 | 399 | 5.9 | 400 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7944 | 815.9997 | 62.1652
SMG-2.RR.187.1 | 25020589139480 | Chatok, Sylhet Road, Bagbari, Mizanur Rahman | 2019-08-25 | LP1002 | 10.2 | 366 | 9.9 | 367 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7944 | 815.9997 | 104.3112
SMG-2.RR.187.2 | 25020589139480 | Chatok, Sylhet Road, Bagbari, Mizanur Rahman | 2019-08-25 | LP1002 | 7.5 | 368 | 7.5 | 369 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7944 | 815.9997 | 79.0236
SMG-2.RR.188.1 | 25020589139480 | Chatok, Sylhet Road, Bagbari, Muktar Hossen | 2019-08-25 | LP1002 | 11.2 | 370 | 11.2 | 371 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7944 | 815.9997 | 118.0086
SMG-2.RR.188.2 | 25020589139480 | Chatok, Sylhet Road, Bagbari, Muktar Hossen | 2019-08-25 | LP1002 | 1.8 | 372 | 1.8 | 373 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7944 | 815.9997 | 18.9657
SMG-2.RR.189.1 | 25015109139310 | Chatok, Sylhet Road, Health Engineering Bhaboner Opposite, Ovi | 2019-08-26 | NQ1000 | 42.4 | 421 | 42.4 | 422 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 42.4 | 42.4 | 2.544 | 2.544 | 0.0007168 | 100% | 0% | 2.544 | 2.544 | 0.0011869 | 28 | 0.050998 | 0.050998 |  | 0 | 0 | 7968 | 791.9997 | 446.7468
SMG-2.RR.190.1 | 25015119139298 | Chatok, Rail Station Road, Court Road, South Bagbari, H # 644, Beside Haq Vila | 2019-08-26 | NQ1000 | 37.1 | 423 | 37.2 | 424 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 37.2 | 37.2 | 2.232 | 2.232 | 0.0007168 | 100% | 0% | 2.232 | 2.232 | 0.0011869 | 28 | 0.044744 | 0.044744 |  | 0 | 0 | 7968 | 791.9997 | 391.9571
SMG-2.RR.191.1 | 25020949139542 | Chatok, Mondolivug, Kalibari, Partho | 2019-08-26 | NQ1000 | 10.3 | 441 | 10.5 | 442 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7992 | 767.9997 | 110.6331
SMG-2.RR.192.1 | 25020949139542 | Chatok, Mondolivug, Kalibari, Otul Ds | 2019-08-26 | NQ1000 | 4.8 | 443 | 5 | 444 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7992 | 767.9997 | 52.6824
SMG-2.RR.193.1 | 25020949139542 | Chatok, Mondolivug, Kalibari, Nibaron Chandra | 2019-08-26 | NQ1000 | 12.4 | 445 | 12.4 | 446 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7992 | 767.9997 | 130.6524
SMG-2.RR.194.1 | 25015049139198 | Chatok, South Bagbari, Ferighat Road, Md. Siraz Uddin | 2019-08-26 | NQ1000 | 9.2 | 447 | 9.2 | 448 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7968 | 791.9997 | 96.9356
SMG-2.RR.194.2 | 25015049139198 | Chatok, South Bagbari, Ferighat Road, Md. Siraz Uddin | 2021-02-10 | NQ1007 | 3.1 | 177 | 3.1 | 178 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7968 | 791.9997 | 32.6631
SMG-2.RR.195.1 | 25015049139198 | Chatok, South Bagbari, Ferighat Road, Sottendra | 2019-08-26 | NQ1000 | 7.5 | 449 | 7.6 | 450 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7968 | 791.9997 | 80.0773
SMG-2.RR.196.1 | 25014269139131 | Chatok, Lafarge Ferighat, South Bagbari, Omit Das | 2019-08-26 | NQ1000 | 3.5 | 463 | 3.5 | 464 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7968 | 791.9997 | 36.8777
SMG-2.RR.197.1 | 25014269139131 | Chatok, Lafarge Ferighat Road, South Bagbari, Jagodish Chandra Dash | 2019-08-26 | NQ1000 | 3.5 | 465 | 3.5 | 466 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7968 | 791.9997 | 36.8777
SMG-2.RR.198.1 | 25014269139131 | Chatok, Lafarge Ferighat Road, South Bagbari, Sitesh Dash | 2019-08-26 | NQ1000 | 11.1 | 467 | 11.1 | 468 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7968 | 791.9997 | 116.9549
SMG-2.RR.199.1 | 25014269139131 | Chatok, Lafarge Ferighat Road, South Bagbari, Binoy Gushon Ghosh | 2019-08-26 | NQ1000 | 6.6 | 469 | 6.6 | 470 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7968 | 791.9997 | 69.5408
SMG-2.RR.200.1 | 25013719139100 | Chatok, Labour Para, South Bagbari, Nurjahan Begum (Rohim Uddin) | 2019-08-26 | NQ1000 | 4 | 477 | 4 | 478 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7968 | 791.9997 | 42.1459
SMG-2.RR.200.2 | 25013719139100 | Chatok, Labour Para, South Bagbari, Nurjahan Begum (Rohim Uddin) | 2019-08-26 | NQ1000 | 5.7 | 481 | 5.7 | 482 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7968 | 791.9997 | 60.0579
SMG-2.RR.201.1 | 25014449139398 | Sunamganj, Chhatak, Collage Road, Latif Chairman | 2019-08-21 | NQ1002 | 33.6 | 95 | 33.7 | 96 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 33.7 | 33.7 | 2.022 | 2.022 | 0.0007168 | 100% | 0% | 2.022 | 2.022 | 0.0011869 | 28 | 0.040534 | 0.040534 |  | 0 | 0 | 7968 | 791.9997 | 355.0794
SMG-2.RR.202.1 | 25014459139404 | Sunamganj, Chhatak, Collage Road, Ayub Ali | 2019-08-21 | NQ1002 | 11.6 | 97 | 11.2 | 98 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7968 | 791.9997 | 118.0086
SMG-2.RR.203.1 | 25014499139418 | Sunamganj, Chhatak, Collage Road, Rabeya Villa | 2019-08-21 | NQ1002 | 6 | 99 | 6 | 100 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7968 | 791.9997 | 63.2189
SMG-2.RR.203.2 | 25014499139418 | Sunamganj, Chhatak, Collage Road, Rabeya Villa | 2019-08-21 | NQ1002 | 7.7 | 101 | 7.7 | 102 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7968 | 791.9997 | 81.1309
SMG-2.RR.204.1 | 25014879139430 | Sunamganj, Chhatak, Cote Road, Babul | 2019-08-21 | NQ1002 | 18.6 | 103 | 18.6 | 104 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 7968 | 791.9997 | 195.9786
SMG-2.RR.205.1 | 25014879139430 | Sunamganj, Chhatak, Cote Road, Foyes | 2019-08-21 | NQ1002 | 36.9 | 105 | 36.9 | 106 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 36.9 | 36.9 | 2.214 | 2.214 | 0.0007168 | 100% | 0% | 2.214 | 2.214 | 0.0011869 | 28 | 0.044383 | 0.044383 |  | 0 | 0 | 7968 | 791.9997 | 388.7962
SMG-2.RR.206.1 | 25014919139385 | Sunamganj, Chhatak, Cote Road, Fokrul | 2019-08-21 | NQ1002 | 8 | 107 | 8 | 108 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7968 | 791.9997 | 84.2919
SMG-2.RR.207.1 | 25015709139368 | Sunamganj, Chhatak, Bagbari, Upozila Porisod Road, Amir Hosen | 2019-08-21 | NQ1002 | 11.5 | 111 | 11.5 | 112 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7968 | 791.9997 | 121.1695
SMG-2.RR.208.1 | 25015669139358 | Sunamganj, Chhatak, Bagbari, Upozila Porisod Road, Fakhar Uddin Ahmed | 2019-08-21 | NQ1002 | 12.7 | 113 | 12.8 | 114 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7968 | 791.9997 | 134.867
SMG-2.RR.209.1 | 25015619139325 | Sunamganj, Chhatak, Bagbari, Upozila Porisod Road, Fatema Vaban | 2019-08-21 | NQ1002 | 14.3 | 115 | 14.3 | 116 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7968 | 791.9997 | 150.6717
SMG-2.RR.209.2 | 25015619139325 | Sunamganj, Chhatak, Bagbari, Upozila Porisod Road, Fatema Vaban | 2019-08-21 | NQ1002 | 10.3 | 117 | 10.3 | 118 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7968 | 791.9997 | 108.5258
SMG-2.RR.210.1 | 25020409139323 | Sunamganj, Chhatak, Bagbari, Bagbari Road, Monir Mia | 2019-08-21 | NQ1002 | 21.4 | 119 | 21.4 | 120 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 7968 | 791.9997 | 225.4807
SMG-2.RR.210.2 | 25020409139323 | Sunamganj, Chhatak, Bagbari, Bagbari Road, Monir Mia | 2019-08-21 | NQ1002 | 14.6 | 121 | 13.7 | 122 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7968 | 791.9997 | 144.3498
SMG-2.RR.211.1 | 25020669139381 | Sunamganj, Chhatak, Bagbari, kutub Ali | 2019-08-21 | NQ1002 | 11.6 | 123 | 11.6 | 124 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7968 | 791.9997 | 122.2232
SMG-2.RR.212.1 | 25020659139467 | Sunamganj, Chhatak, Bagbari, Jahir Mia | 2019-08-24 | NQ1000 | 14.1 | 273 | 13.6 | 274 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7944 | 815.9997 | 143.2961
SMG-2.RR.213.1 | 25020809139497 | Sunamganj, Chhatak, Chaul Hata, Club Road, Abdul Monem | 2019-08-24 | NQ1000 | 15.6 | 277 | 15.6 | 278 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7944 | 815.9997 | 164.3691
SMG-2.RR.213.2 | 25020809139497 | Sunamganj, Chhatak, Chaul Hata, Club Road, Abdul Monem | 2019-08-24 | NQ1000 | 21.4 | 279 | 21.4 | 280 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 7944 | 815.9997 | 225.4807
SMG-2.RR.214.1 | 25020809139497 | Sunamganj, Chhatak, Chaul Hata, Club Road, Abdul Oyadut | 2019-08-24 | NQ1000 | 7.3 | 281 | 7.3 | 282 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7944 | 815.9997 | 76.9163
SMG-2.RR.215.1 | 25020809139497 | Sunamganj, Chhatak, Chaul Hata, Club Road, Taj Uddin | 2019-08-24 | NQ1000 | 6.9 | 283 | 6.9 | 284 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7944 | 815.9997 | 72.7017
SMG-2.RR.216.1 | 25020569140056 | Sunamganj, Chhatak, Mondolivog, Hospital Road, Somen Day | 2019-08-24 | NQ1000 | 10 | 295 | 10 | 296 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8016 | 743.9997 | 105.3648
SMG-2.RR.216.2 | 25020569140056 | Sunamganj, Chhatak, Mondolivog, Hospital Road, Somen Day | 2021-02-11 | NQ1003 | 10.8 | 241 | 10.4 | 242 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8016 | 743.9997 | 109.5794
SMG-2.RR.217.1 | 25020569140056 | Sunamganj, Chhatak, Mondolivog, Hospital Road, Degendro | 2019-08-24 | NQ1000 | 7.4 | 297 | 7.4 | 298 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 8016 | 743.9997 | 77.97
SMG-2.RR.218.1 | 25020569140056 | Sunamganj, Chhatak, Mondolivog, Hospital Road, Satyendra Das | 2019-08-24 | NQ1000 | 13.8 | 299 | 13.8 | 300 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 8016 | 743.9997 | 145.4034
SMG-2.RR.219.1 | 25020569140056 | Sunamganj, Chhatak, Mondolivog, Hospital Road, Shopon Day | 2019-08-24 | NQ1000 | 9.3 | 301 | 9.3 | 302 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 8016 | 743.9997 | 97.9893
SMG-2.RR.220.1 | 25020899140095 | Sunamganj, Chhatak, Mondolivog, Hospital Road, Tajul Islam | 2019-08-24 | NQ1000 | 12.3 | 303 | 13.3 | 304 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 8016 | 743.9997 | 140.1352
SMG-2.RR.220.2 | 25020899140095 | Sunamganj, Chhatak, Mondolivog, Hospital Road, Tajul Islam | 2021-02-11 | NQ1003 | 16.3 | 238 | 16.3 | 239 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 8016 | 743.9997 | 171.7446
SMG-2.RR.221.1 | 25021769140095 | Sunamganj, Chhatak, Mondolivog, Thana Road, Bahar Begum | 2019-08-25 | LP1002 | 7.4 | 306 | 7.4 | 307 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 8016 | 743.9997 | 77.97
SMG-2.RR.222.1 | 25021689140091 | Sunamganj, Chhatak, Mondolivog, Thana Road, Litu Mia | 2019-08-25 | LP1002 | 17.3 | 309 | 17.3 | 310 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 8016 | 743.9997 | 182.2811
SMG-2.RR.223.1 | 25021689140091 | Sunamganj, Chhatak, Mondolivog, Thana Road, Sahanur Ali | 2019-08-25 | LP1002 | 9.2 | 311 | 9.5 | 312 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8016 | 743.9997 | 100.0966
SMG-2.RR.224.1 | 25021879140105 | Sunamganj, Chhatak, Mondolivog, Thana Road, Alfo Mia | 2019-08-25 | LP1002 | 11.1 | 313 | 11.1 | 314 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8016 | 743.9997 | 116.9549
SMG-2.RR.224.2 | 25021879140105 | Sunamganj, Chhatak, Mondolivog, Thana Road, Alfo Mia | 2021-02-11 | NQ1003 | 2.6 | 230 | 2.6 | 231 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 8016 | 743.9997 | 27.3949
SMG-2.RR.225.1 | 25021989140154 | Sunamganj, Chhatak, Mondolivog, Thana Road, Mahatab Mia | 2019-08-25 | LP1002 | 18 | 316 | 18 | 317 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 18 | 18 | 1.08 | 1.08 | 0.0007168 | 100% | 0% | 1.08 | 1.08 | 0.0011869 | 28 | 0.02165 | 0.02165 |  | 0 | 0 | 8016 | 743.9997 | 189.6567
SMG-2.RR.226.1 | 25021939140166 | Sunamganj, Chhatak, Mondolivog, Thana Road, Anowar | 2019-08-25 | LP1002 | 9.7 | 318 | 9.7 | 319 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8016 | 743.9997 | 102.2039
SMG-2.RR.226.2 | 25021939140166 | Sunamganj, Chhatak, Mondolivog, Thana Road, Anowar | 2020-10-10 | MN1032 | 4 | 15 | 4 | 16 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 8016 | 743.9997 | 42.1459
SMG-2.RR.227.1 | 25021899140172 | Sunamganj, Chhatak, Mondolivog, Thana Road, Nejam Hazi | 2019-08-25 | LP1002 | 12.2 | 320 | 12.2 | 321 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 8016 | 743.9997 | 128.5451
SMG-2.RR.228.1 | 25021899140172 | Sunamganj, Chhatak, Mondolivog, Thana Road, Rose Vila | 2019-08-25 | LP1002 | 8.3 | 322 | 8.3 | 323 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 8016 | 743.9997 | 87.4528
SMG-2.RR.229.1 | 25021819140172 | Sunamganj, Chhatak, Mondolivog, Thana Road, Khaled | 2019-08-25 | LP1002 | 15 | 324 | 15 | 325 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8016 | 743.9997 | 158.0472
SMG-2.RR.230.1 | 25021819140172 | Sunamganj, Chhatak, Mondolivog, Thana Road, Nousad Comisonar | 2019-08-25 | LP1002 | 7.6 | 330 | 7.6 | 331 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8016 | 743.9997 | 80.0773
SMG-2.RR.231.1 | 25021819140172 | Sunamganj, Chhatak, Mondolivog, Thana Road, Aiub Ali | 2019-08-25 | LP1002 | 5.3 | 332 | 5.3 | 333 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 8016 | 743.9997 | 55.8434
SMG-2.RR.232.1 | 25021689140214 | Sunamganj, Chhatak, Chorobondo, Thana Road, Hazi Arjot Ali | 2019-08-25 | LP1002 | 25.4 | 334 | 25.4 | 335 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 25.4 | 25.4 | 1.524 | 1.524 | 0.0007168 | 100% | 0% | 1.524 | 1.524 | 0.0011869 | 28 | 0.030551 | 0.030551 |  | 0 | 0 | 8016 | 743.9997 | 267.6266
SMG-2.RR.233.1 | 25021689140214 | Sunamganj, Chhatak, Chorobondo, Thana Road, Hazi Arjot Ali | 2019-08-25 | LP1002 | 6 | 336 | 6 | 337 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 8016 | 743.9997 | 63.2189
SMG-2.RR.234.1 | 25025679139069 | Sunamganj, Chhatak, Norai Islampur, Surma Housing Complex | 2019-08-27 | LU1001 | 4.5 | 82 | 4.5 | 83 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7920 | 839.9997 | 47.4142
SMG-2.RR.235.1 | 25025679139069 | Sunamganj, Chhatak, Norai Islampur, Surma Housing Complex | 2019-08-27 | LU1001 | 4.6 | 84 | 4.6 | 85 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7920 | 839.9997 | 48.4678
SMG-2.RR.236.1 | 25021929139170 | Sunamganj, Chhatak, Porchim Norai, Nojib Ali | 2019-08-27 | LU1001 | 9.2 | 86 | 9.2 | 87 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7920 | 839.9997 | 96.9356
SMG-2.RR.237.1 | 25021929139170 | Sunamganj, Chhatak, Porchim Norai, Asim Sha | 2019-08-27 | LU1001 | 12.1 | 88 | 12.1 | 89 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7920 | 839.9997 | 127.4914
SMG-2.RR.238.1 | 25021619139181 | Sunamganj, Chhatak, Porchim Norai, Jomir Hosen | 2019-08-27 | LU1001 | 1.7 | 90 | 1.7 | 91 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 216 | 0 | 7704 | 839.9997 | 17.4704
SMG-2.RR.239.1 | 25010789138121 | Sunamganj, Chhatak, Bar Kahon, Douara Road, Ekjad Mia | 2019-08-27 | LU1001 | 11.1 | 94 | 11.1 | 95 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7920 | 839.9997 | 116.9549
SMG-2.RR.240.1 | 25010599138114 | Sunamganj, Chhatak, Bar Kahon, Douara Road, Kawsar Mia | 2019-08-27 | LU1001 | 12.6 | 96 | 12.6 | 97 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7920 | 839.9997 | 132.7597
SMG-2.RR.241.1 | 25010599138114 | Sunamganj, Chhatak, Bar Kahon, Douara Road, Serajul Islam | 2019-08-27 | LU1001 | 6.2 | 98 | 6.2 | 99 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7920 | 839.9997 | 65.3262
SMG-2.RR.242.1 | 25010529138105 | Sunamganj, Chhatak, Bar Kahon, Douara Road, Nejamuddin | 2019-08-27 | LU1001 | 10.8 | 100 | 10.8 | 101 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7920 | 839.9997 | 113.794
SMG-2.RR.243.1 | 25010439138096 | Sunamganj, Chhatak, Bar Kahon, Douara Road, Mokso Mia | 2019-08-27 | LU1001 | 11.9 | 102 | 11.5 | 103 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7920 | 839.9997 | 121.1695
SMG-2.RR.244.1 | 25010689138145 | Sunamganj, Chhatak, Bar Kahon, Feroz Mia | 2019-08-27 | LU1001 | 8.1 | 104 | 8.1 | 105 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7920 | 839.9997 | 85.3455
SMG-2.RR.245.1 | 25010699138171 | Sunamganj, Chhatak, Bar Kahon, Rahim Ali | 2019-08-27 | LU1001 | 5.8 | 106 | 5.8 | 107 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7920 | 839.9997 | 61.1116
SMG-2.RR.246.1 | 25010599138177 | Sunamganj, Chhatak, Bar Kahon, Hazi Monir Mia Talukder | 2019-08-27 | LU1001 | 6 | 108 | 6 | 109 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7920 | 839.9997 | 63.2189
SMG-2.RR.247.1 | 25010599138177 | Sunamganj, Chhatak, Bar Kahon, Hazi Monir Mia Talukder | 2019-08-27 | LU1001 | 12 | 110 | 12 | 111 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7920 | 839.9997 | 126.4378
SMG-2.RR.248.1 | 25030079133285 | Sunamganj, Douara Bazar, Duck Bangla Road, Mosaddor | 2019-08-28 | LU1001 | 11.6 | 112 | 11.6 | 113 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7944 | 815.9997 | 122.2232
SMG-2.RR.249.1 | 25025769133270 | Sunamganj, Douara Bazar, Duck Bangla Road, Roise Ali | 2019-08-28 | LU1001 | 11.9 | 114 | 11.9 | 115 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7944 | 815.9997 | 125.3841
SMG-2.RR.250.1 | 25025769133270 | Sunamganj, Douara Bazar, Duck Bangla Road, Gias Monjil | 2019-08-28 | LU1001 | 5.8 | 116 | 5.8 | 117 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7944 | 815.9997 | 61.1116
SMG-2.RR.251.1 | 25021039139393 | Chhatak, Bagbari, West Bazar, Oposite Side Of Islam Villa | 2019-08-22 | NQ1002 | 7.2 | 127 | 7.2 | 128 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7968 | 791.9997 | 75.8627
SMG-2.RR.252.1 | 25021039139393 | Chhatak, Bagbari, West Bazar, Islam Villa | 2019-08-22 | NQ1002 | 11.4 | 129 | 11.4 | 130 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7968 | 791.9997 | 120.1159
SMG-2.RR.253.1 | 25021039139393 | Chhatak, Bagbari, West Bazar, Akramul Hoq | 2019-08-22 | NQ1002 | 15.2 | 131 | 15.2 | 132 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7968 | 791.9997 | 160.1545
SMG-2.RR.254.1 | 25021039139393 | Chhatak, Bagbari, West Bazar, Hazi Mawlana Nur Villa | 2019-08-22 | NQ1002 | 13.7 | 133 | 13.7 | 134 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7968 | 791.9997 | 144.3498
SMG-2.RR.255.1 | 25020769139379 | Chhatak, Bagbari, Boro Bari, Abdul Shahid Mona | 2019-08-22 | NQ1002 | 3.1 | 135 | 3.1 | 136 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7968 | 791.9997 | 32.6631
SMG-2.RR.256.1 | 25021149139410 | Chhatak, Bagbari, West Bazar, Bhanu Protab Datta | 2019-08-22 | NQ1002 | 15 | 137 | 15.2 | 138 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7968 | 791.9997 | 160.1545
SMG-2.RR.257.1 | 25021149139410 | Chhatak, Bagbari, West Bazar, Rajat Kanti Roy | 2019-08-22 | NQ1002 | 6.7 | 139 | 6.7 | 140 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7968 | 791.9997 | 70.5944
SMG-2.RR.258.1 | 25021149139410 | Chhatak, Bagbari, West Bazar, Ajoy Paul | 2019-08-22 | NQ1002 | 5.1 | 141 | 5.1 | 142 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7968 | 791.9997 | 53.7361
SMG-2.RR.259.1 | 25021059139432 | Chhatak, Bagbari, West Bazar, Kayas Vai | 2019-08-22 | NQ1002 | 10.3 | 143 | 10.2 | 144 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7968 | 791.9997 | 107.4721
SMG-2.RR.260.1 | 25021059139432 | Chhatak, Bagbari, West Bazar, Muhi Vai | 2019-08-22 | NQ1002 | 10 | 145 | 10 | 146 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7968 | 791.9997 | 105.3648
SMG-2.RR.261.1 | 25021019139441 | Chhatak, Bagbari, Moddho Bazar, Chowdhury Complex | 2019-08-22 | NQ1002 | 5.3 | 147 | 5.3 | 148 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7968 | 791.9997 | 55.8434
SMG-2.RR.262.1 | 25021019139441 | Chhatak, Bagbari, Moddho Bazar, Jogesh Chandra Dey | 2019-08-22 | NQ1002 | 3 | 149 | 3.1 | 150 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7968 | 791.9997 | 32.6631
SMG-2.RR.262.2 | 25021019139441 | Chhatak, Bagbari, Moddho Bazar, Jogesh Chandra Dey | 2019-08-22 | NQ1002 | 11.1 | 153 | 11.1 | 154 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7968 | 791.9997 | 116.9549
SMG-2.RR.263.1 | 25021039139447 | Chhatak, Bagbari, Moddho Bazar, Emad Mia | 2019-08-22 | NQ1002 | 11.3 | 155 | 11.3 | 156 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7968 | 791.9997 | 119.0622
SMG-2.RR.264.1 | 25021039139447 | Chhatak, Bagbari, Moddho Bazar, Selim Chowdhury | 2019-08-22 | NQ1002 | 10.1 | 157 | 10.3 | 158 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7968 | 791.9997 | 108.5258
SMG-2.RR.265.1 | 25020899139446 | Chhatak, Bagbari, Moddho Bazar, Maruf Ahammed | 2019-08-22 | NQ1002 | 3.4 | 159 | 3.4 | 160 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7968 | 791.9997 | 35.824
SMG-2.RR.266.1 | 25020779139439 | Chhatak, Bagbari, Moddho Bazar, Kabir | 2019-08-22 | NQ1002 | 6.4 | 161 | 6 | 162 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7968 | 791.9997 | 63.2189
SMG-2.RR.267.1 | 25020839139471 | Chhatak, Bagbari, Moddho Bazar, Shikha Rani Roy | 2019-08-24 | NQ1000 | 8.8 | 321 | 8.8 | 322 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7944 | 815.9997 | 92.721
SMG-2.RR.268.1 | 25020639139430 | Chhatak, Bagbari, Moddho Bazar, Rehena Parvin | 2019-08-24 | NQ1000 | 6.4 | 325 | 6.4 | 326 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7968 | 791.9997 | 67.4335
SMG-2.RR.268.2 | 25020639139430 | Chhatak, Bagbari, Moddho Bazar, Rehena Parvin | 2021-02-10 | NQ1003 | 4.3 | 228 | 4.3 | 229 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7968 | 791.9997 | 45.3069
SMG-2.RR.269.1 | 25020639139430 | Chhatak, Bagbari, Moddho Bazar, Amzad Ali | 2019-08-24 | NQ1000 | 3.6 | 327 | 3.6 | 328 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7968 | 791.9997 | 37.9313
SMG-2.RR.270.1 | 25020779139440 | Chhatak, Bagbari, Moddho Bazar, Shahajadi | 2019-08-24 | NQ1000 | 5.8 | 329 | 5.8 | 330 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7968 | 791.9997 | 61.1116
SMG-2.RR.271.1 | 25020809139425 | Chhatak, Bagbari, Moddho Bazar, Abdul Mannan | 2019-08-24 | NQ1000 | 5.5 | 331 | 5.5 | 332 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7968 | 791.9997 | 57.9506
SMG-2.RR.272.1 | 25020289140315 | Chhatak, Moghal Para, Kaoirul Alam | 2019-08-24 | NQ1000 | 11.4 | 341 | 11.4 | 342 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7992 | 767.9997 | 120.1159
SMG-2.RR.273.1 | 25020119140335 | Chhatak, Moghal Para, Shondha Rani Das | 2019-08-24 | NQ1000 | 8.7 | 345 | 8.7 | 346 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7992 | 767.9997 | 91.6674
SMG-2.RR.274.1 | 25020079140316 | Chhatak, Moghal Para, Samsul Hoq | 2019-08-24 | NQ1000 | 3.6 | 347 | 3.6 | 348 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7992 | 767.9997 | 37.9313
SMG-2.RR.275.1 | 25015969140341 | Chhatak, Moghal Para, Mithu Das | 2019-08-25 | NQ1000 | 9.6 | 373 | 9.7 | 374 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7992 | 767.9997 | 102.2039
SMG-2.RR.276.1 | 25015969140341 | Chhatak, Moghal Para, Sonju Deb | 2019-08-25 | NQ1000 | 4.4 | 375 | 4.4 | 376 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7992 | 767.9997 | 46.3605
SMG-2.RR.277.1 | 25015819140339 | Chhatak, Moghal Para, Jotish Das | 2019-08-25 | NQ1000 | 7.7 | 377 | 7.7 | 378 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7992 | 767.9997 | 81.1309
SMG-2.RR.278.1 | 25015789140347 | Chhatak, Moghal Para, Bissojit Purakayasto | 2019-08-25 | NQ1000 | 4.5 | 379 | 4.5 | 380 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7992 | 767.9997 | 47.4142
SMG-2.RR.279.1 | 25015929140372 | Chhatak, Moghal Para, Jushep | 2019-08-25 | NQ1000 | 4.5 | 389 | 4.5 | 390 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7992 | 767.9997 | 47.4142
SMG-2.RR.280.1 | 25021699140210 | Chhatak, Charerbondh, Hazi Md. Arzod Ali Bari, Naziruddin | 2019-08-25 | NQ1000 | 8.2 | 409 | 8.2 | 410 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8016 | 743.9997 | 86.3991
SMG-2.RR.281.1 | 25021699140210 | Chhatak, Charerbondh, Hazi Md. Arzod Ali Bari, Kezai Mia | 2019-08-25 | NQ1000 | 12.6 | 411 | 12.7 | 412 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 8016 | 743.9997 | 133.8133
SMG-2.RR.282.1 | 25021469140247 | Chhatak, Charerbondh, Bodrujamman | 2019-08-25 | NQ1000 | 11.4 | 413 | 11.5 | 414 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8016 | 743.9997 | 121.1695
SMG-2.RR.283.1 | 25021469140247 | Chhatak, Charerbondh, Goribullah | 2019-08-25 | NQ1000 | 5.3 | 415 | 5.3 | 416 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 8016 | 743.9997 | 55.8434
SMG-2.RR.284.1 | 25021339140240 | Chhatak, Charerbondh, Monsur Ali | 2019-08-25 | NQ1000 | 7 | 417 | 7 | 418 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 8016 | 743.9997 | 73.7554
SMG-2.RR.285.1 | 25021339140240 | Chhatak, Charerbondh, Ramizuddin | 2019-08-25 | NQ1000 | 3.5 | 419 | 3.5 | 420 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 8016 | 743.9997 | 36.8777
SMG-2.RR.286.1 | 25020709139171 | Chhatak, Noyarai, Bidhan Babu | 2019-08-26 | LP1002 | 6.9 | 374 | 6.9 | 375 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7920 | 839.9997 | 72.7017
SMG-2.RR.287.1 | 25020709139171 | Chhatak, Noyarai, Suresh Chandra Debnath | 2019-08-26 | LP1002 | 14.7 | 377 | 14.2 | 378 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7920 | 839.9997 | 149.618
SMG-2.RR.288.1 | 25020709139171 | Chhatak, Noyarai, Rakib Mia | 2019-08-26 | LP1002 | 12.3 | 379 | 12.3 | 380 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7920 | 839.9997 | 129.5987
SMG-2.RR.289.1 | 25020819139179 | Chhatak, Noyarai, Mokbul Hossan Chowdhury | 2019-08-26 | LP1002 | 9.7 | 381 | 9.7 | 382 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7920 | 839.9997 | 102.2039
SMG-2.RR.290.1 | 25020819139179 | Chhatak, Noyarai, Moti Mia Chowdhury | 2019-08-26 | LP1002 | 16.3 | 383 | 16.3 | 384 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 7920 | 839.9997 | 171.7446
SMG-2.RR.291.1 | 25020819139179 | Chhatak, Noyarai, Md. Pavel Chowdhury | 2019-08-26 | LP1002 | 10.5 | 385 | 10.9 | 386 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7920 | 839.9997 | 114.8476
SMG-2.RR.292.1 | 25020959139181 | Chhatak, Noyarai, Samsul Hoq Chowdhury | 2019-08-26 | LP1002 | 6.4 | 387 | 6.4 | 388 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7920 | 839.9997 | 67.4335
SMG-2.RR.293.1 | 25021139139174 | Chhatak, Noyarai, Akher House | 2019-08-26 | LP1002 | 2.9 | 391 | 2.9 | 392 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7920 | 839.9997 | 30.5558
SMG-2.RR.294.1 | 25021139139174 | Chhatak, Noyarai, Akher House | 2019-08-26 | LP1002 | 3.9 | 393 | 3.9 | 394 | 2022-01-01 | [9 empty] | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0
SMG-2.RR.295.1 | 25021259139175 | Chhatak, Noyarai, Munaim Chowdhury | 2019-08-26 | LP1002 | 6 | 395 | 6 | 396 | 2022-01-01 | [9 empty] | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0
SMG-2.RR.296.1 | 25021259139175 | Chhatak, Noyarai, Chowdhury Para, Jalaluddin Chowdhury | 2019-08-26 | LP1002 | 60.6 | 397 | 59.2 | 398 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 59.2 | 59.2 | 3.552 | 3.552 | 0.0007168 | 100% | 0% | 3.552 | 3.552 | 0.0011869 | 28 | 0.071205 | 0.071205 |  | 0 | 0 | 7920 | 839.9997 | 623.7597
SMG-2.RR.297.1 | 25021259139175 | Chhatak, Noyarai, Chowdhury Para, Mahabubul Hoq Chowdhury | 2019-08-26 | LP1002 | 18.4 | 399 | 18.4 | 400 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 7920 | 839.9997 | 193.8713
SMG-2.RR.301.1 | 25011799139381 | Chhatak, Muktirgao, Paper Mill''s Front Road, Charibul Villa | 2019-08-21 | NQ1000 | 2.9 | 174 | 2.9 | 175 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7968 | 791.9997 | 30.5558
SMG-2.RR.302.1 | 25011979139433 | Chhatak, West Muktirgao, Suruj Mia | 2019-08-21 | NQ1000 | 19.5 | 178 | 19.5 | 179 | 2022-01-01 | [9 empty] | 19.5 | 19.5 | 1.17 | 1.17 | 0.0007168 | 100% | 0% | 1.17 | 1.17 | 0.0011869 | 28 | 0.023454 | 0.023454 |  | 0 | 0
SMG-2.RR.303.1 | 25011909139442 | Chhatak, West Muktirgao, Nur Jahan | 2019-08-21 | NQ1000 | 11.1 | 180 | 11.1 | 181 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7968 | 791.9997 | 116.9549
SMG-2.RR.304.1 | 25012889139405 | Chhatak, Rahmatbag, Hazi Abdur Rawf | 2019-08-21 | NQ1000 | 9.7 | 182 | 9.7 | 183 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7968 | 791.9997 | 102.2039
SMG-2.RR.305.1 | 25013199139421 | Chhatak, Rahmatbag, Sylhet Road, Rahim Ali | 2019-08-21 | NQ1000 | 3.7 | 184 | 3.7 | 185 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7968 | 791.9997 | 38.985
SMG-2.RR.306.1 | 25013869139427 | Chhatak, Rahmatbag, Sylhet Road, Faruk Ahmad Chairman | 2019-08-21 | NQ1000 | 6.1 | 186 | 6.1 | 187 | 2022-01-01 | 2022-11-29 | NQ1007 | 2 | 223 | 2 | 224 | 2022-11-29 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7968 | 791.9997
SMG-2.RR.306.2 | 25013869139427 | Chhatak, Rahmatbag, Sylhet Road, Faruk Ahmad Chairman | 2022-11-29 | NQ1007 | 6.7 | 221 | 6.7 | 222 | 2022-11-29 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 0 | 791.9997 | 6.3825
SMG-2.RR.307.1 | 25014019139402 | Chhatak, Rahmatbag R/A, Masaraf Ali | 2019-08-21 | NQ1000 | 13.6 | 188 | 13.6 | 189 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7968 | 791.9997 | 143.2961
SMG-2.RR.308.1 | 25013969139393 | Chhatak, Rahmatbag R/A, Atauddin | 2019-08-21 | NQ1000 | 10.3 | 190 | 10.3 | 191 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7968 | 791.9997 | 108.5258
SMG-2.RR.309.1 | 25013999139379 | Chhatak, Rahmatbag R/A, Nur Islam | 2019-08-21 | NQ1000 | 2.1 | 192 | 2.1 | 193 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7968 | 791.9997 | 22.1266
SMG-2.RR.310.1 | 25014009139386 | Chhatak, Rahmatbag R/A, Fatikuddin | 2019-08-21 | NQ1000 | 11 | 194 | 10.9 | 195 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7968 | 791.9997 | 114.8476
SMG-2.RR.311.1 | 25015899139441 | Chhatak, Bagbari R/A, Najim | 2019-08-21 | NQ1000 | 6.5 | 196 | 6.5 | 197 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7968 | 791.9997 | 68.4871
SMG-2.RR.312.1 | 25015899139441 | Chhatak, Bagbari R/A, Mir Md. Alauddin | 2019-08-21 | NQ1000 | 8.5 | 198 | 8.5 | 199 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7968 | 791.9997 | 89.5601
SMG-2.RR.313.1 | 25015899139414 | Chhatak, Bagbari R/A, Badsha Mia | 2019-08-21 | NQ1000 | 14.1 | 200 | 14.1 | 201 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7968 | 791.9997 | 148.5644
SMG-2.RR.313.2 | 25015899139414 | Chhatak, Bagbari R/A, Badsha Mia | 2022-02-28 | NQ1007 | 1.9 | 23 | 1.9 | 24 | 2022-02-28 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6576 | 791.9997 | 16.8382
SMG-2.RR.314.1 | 25015849139399 | Chhatak, Bagbari R/A, Dilip Pal | 2019-08-21 | NQ1000 | 11 | 202 | 11 | 203 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7968 | 791.9997 | 115.9013
SMG-2.RR.315.1 | 25015849139399 | Chhatak, Bagbari R/A, H # 363/1, Sutopa Das | 2019-08-21 | NQ1000 | 7 | 204 | 7 | 205 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7968 | 791.9997 | 73.7554
SMG-2.RR.315.2 | 25015849139399 | Chhatak, Bagbari R/A, H # 363/1, Sutopa Das | 2021-02-10 | NQ1003 | 4.5 | 217 | 4.5 | 218 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7968 | 791.9997 | 47.4142
SMG-2.RR.316.1 | 25020119139386 | Chhatak, Bagbari R/A, Alim Mia | 2019-08-21 | NQ1000 | 14.4 | 206 | 15 | 207 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 7968 | 791.9997 | 158.0472
SMG-2.RR.317.1 | 25020109139363 | Chhatak, Bagbari R/A, Jayanti Acharjo | 2019-08-21 | NQ1000 | 8.5 | 208 | 8.5 | 209 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7968 | 791.9997 | 89.5601
SMG-2.RR.318.1 | 25020109139363 | Chhatak, Bagbari R/A, Shibnarayan Acharjo | 2019-08-21 | NQ1000 | 9.5 | 210 | 9.6 | 211 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7968 | 791.9997 | 101.1502
SMG-2.RR.319.1 | 25020609139465 | Chhatak, Bagbari R/A, Kobir | 2019-08-24 | NQ1000 | 8.1 | 269 | 7.6 | 270 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7944 | 815.9997 | 80.0773
SMG-2.RR.320.1 | 25020609139465 | Chhatak, Bagbari R/A, Abdul Wadud Mia | 2019-08-24 | NQ1000 | 6.9 | 271 | 6.9 | 272 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7944 | 815.9997 | 72.7017
SMG-2.RR.320.2 | 25020609139465 | Chhatak, Bagbari R/A, Abdul Wadud Mia | 2021-02-09 | NQ1007 | 3 | 166 | 3 | 167 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7944 | 815.9997 | 31.6094
SMG-2.RR.321.1 | 25021059139504 | Chhatak, Panahata, Tarun Chadro Dev | 2019-08-24 | NQ1000 | 15.9 | 275 | 15.9 | 276 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 7944 | 815.9997 | 167.5301
SMG-2.RR.322.1 | 25020759139498 | Chhatak, Club Road, Wadud Alam | 2019-08-24 | NQ1000 | 15.4 | 285 | 15.4 | 286 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 7944 | 815.9997 | 162.2618
SMG-2.RR.322.2 | 25020759139498 | Chhatak, Club Road, Wadud Alam | 2019-08-24 | NQ1000 | 7.2 | 287 | 7.2 | 288 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7944 | 815.9997 | 75.8627
SMG-2.RR.323.1 | 25020609140088 | Chhatak, Mandalivog, Hospital Road, Amir Ali | 2019-08-24 | NQ1000 | 9.9 | 291 | 9.9 | 292 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8016 | 743.9997 | 104.3112
SMG-2.RR.324.1 | 25020609140088 | Chhatak, Mandalivog, Hospital Road, Badrul Alam | 2019-08-24 | NQ1000 | 7.3 | 293 | 7.3 | 294 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8016 | 743.9997 | 76.9163
SMG-2.RR.325.1 | 25020569140118 | Chhatak, Mandalivog, Mangolpara, Aftabuddin | 2019-08-24 | NQ1000 | 5.1 | 305 | 4.9 | 306 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 8016 | 743.9997 | 51.6288
SMG-2.RR.326.1 | 25020519140146 | Chhatak, Mandalivog, Mangolpara, Aitera Bibi | 2019-08-24 | NQ1000 | 7.3 | 307 | 7.3 | 308 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8016 | 743.9997 | 76.9163
SMG-2.RR.327.1 | 25020519140146 | Chhatak, Mandalivog, Mangolpara, Mujibur Rahman Academy | 2019-08-24 | NQ1000 | 11.6 | 309 | 11 | 310 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8016 | 743.9997 | 115.9013
SMG-2.RR.327.2 | 25020519140146 | Chhatak, Mandalivog, Mangolpara, Mujibur Rahman Academy | 2022-02-26 | NQ1007 | 4.4 | 9 | 4.4 | 10 | 2022-02-26 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6672 | 743.9997 | 39.2477
SMG-2.RR.328.1 | 25020589140238 | Chhatak, Mandalivog, Mangolpara, Nur Islam | 2019-08-24 | NQ1000 | 14.2 | 311 | 14.1 | 312 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 8016 | 743.9997 | 148.5644
SMG-2.RR.329.1 | 25021359140260 | Chhatak, Mangolpara, Chhatak, Mufizia Islami Acadamy | 2019-08-25 | NQ1000 | 5.9 | 349 | 5.9 | 350 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 8016 | 743.9997 | 62.1652
SMG-2.RR.330.1 | 25021119140246 | Chhatak, Chorerbon, Marfot Ali | 2019-08-25 | NQ1000 | 11.4 | 353 | 11.4 | 354 | 2022-01-01 | [9 empty] | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0
SMG-2.RR.330.2 | 25021119140246 | Chhatak, Chorerbon, Marfot Ali | 2020-10-10 | MN1032 | 8.5 | 19 | 8.5 | 20 | 2022-01-01 | [9 empty] | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0
SMG-2.RR.331.1 | 25021119140246 | Chhatak, Chorerbon, Abdul Hannan | 2019-08-25 | NQ1000 | 10.1 | 355 | 10.1 | 356 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8016 | 743.9997 | 106.4185
SMG-2.RR.332.1 | 25021509140217 | Chhatak, Chorerbon, Arju | 2019-08-25 | NQ1000 | 11.2 | 357 | 11.2 | 358 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8016 | 743.9997 | 118.0086
SMG-2.RR.333.1 | 25021259140211 | Chhatak, Chorerbon, Masuq Mia | 2019-08-25 | NQ1000 | 8.6 | 359 | 8.6 | 360 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 8016 | 743.9997 | 90.6137
SMG-2.RR.334.1 | 25021259140211 | Chhatak, Chorerbon, Ali Alam | 2019-08-25 | NQ1000 | 10.1 | 361 | 10.1 | 362 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8016 | 743.9997 | 106.4185
SMG-2.RR.335.1 | 25021259140211 | Chhatak, Chorerbon, Taher Ali | 2019-08-25 | NQ1000 | 17.9 | 363 | 17.9 | 364 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 8016 | 743.9997 | 188.603
SMG-2.RR.336.1 | 25013019140356 | Chhatak, Bowla, Thanapara, Lal Mia | 2019-08-25 | NQ1000 | 11.2 | 365 | 11.2 | 366 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7992 | 767.9997 | 118.0086
SMG-2.RR.337.1 | 25013159140376 | Chhatak, Bowla, Thanapara, Mawratun Nesa | 2019-08-25 | NQ1000 | 8.9 | 367 | 8.9 | 368 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7992 | 767.9997 | 93.7747
SMG-2.RR.338.1 | 25013039140392 | Chhatak, Bowla, Thanapara, Gedab Ali | 2019-08-25 | NQ1000 | 10.4 | 369 | 10.4 | 370 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7992 | 767.9997 | 109.5794
SMG-2.RR.339.1 | 25012989140415 | Chhatak, Bowla, Thanapara, Abdul Hamid | 2019-08-25 | NQ1000 | 10.3 | 371 | 10.3 | 372 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7992 | 767.9997 | 108.5258
SMG-2.RR.340.1 | 25025459139058 | Chhatak, Noarai, Islampur, Jamil House | 2019-08-27 | NQ1000 | 11 | 538 | 11 | 539 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7920 | 839.9997 | 115.9013
SMG-2.RR.341.1 | 25025409139045 | Chhatak, Noarai, Islampur, Akkas Ali | 2019-08-27 | NQ1000 | 11.5 | 540 | 12.1 | 541 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7920 | 839.9997 | 127.4914
SMG-2.RR.342.1 | 25025359139073 | Chhatak, Noarai, Islampur, Thakur Kuthir, Misu Chakroborti | 2019-08-27 | NQ1000 | 8.7 | 542 | 8.7 | 543 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7920 | 839.9997 | 91.6674
SMG-2.RR.343.1 | 25025309139078 | Chhatak, Noarai, Islampur, Kamrul Mia | 2019-08-27 | NQ1000 | 9.6 | 544 | 9.6 | 545 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7920 | 839.9997 | 101.1502
SMG-2.RR.344.1 | 25014729138519 | Chhatak, Tangargao, Modris Ali | 2019-08-27 | NQ1000 | 21.1 | 546 | 20.2 | 547 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 20.2 | 20.2 | 1.212 | 1.212 | 0.0007168 | 100% | 0% | 1.212 | 1.212 | 0.0011869 | 28 | 0.024296 | 0.024296 |  | 0 | 0 | 7920 | 839.9997 | 212.8369
SMG-2.RR.345.1 | 25014729138519 | Chhatak, Tangargao, Shadeq Mia | 2019-08-27 | NQ1000 | 4.6 | 548 | 4.6 | 549 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7920 | 839.9997 | 48.4678
SMG-2.RR.346.1 | 25014589138506 | Chhatak, Tangargao, Abdul Maleq | 2019-08-27 | NQ1000 | 10.5 | 550 | 10.5 | 551 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7920 | 839.9997 | 110.6331
SMG-2.RR.347.1 | 25014489138493 | Chhatak, Tangargao, Muhibur Rahman | 2019-08-27 | NQ1000 | 7.2 | 552 | 7.2 | 553 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7920 | 839.9997 | 75.8627
SMG-2.RR.348.1 | 25013509138443 | Chhatak, Battirkandi, Rajon Mia | 2019-08-27 | NQ1000 | 11.3 | 554 | 11.3 | 555 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7920 | 839.9997 | 119.0622
SMG-2.RR.349.1 | 25013519138454 | Chhatak, Battirkandi, Ajman Ali | 2019-08-27 | NQ1000 | 10.5 | 556 | 10.5 | 557 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7920 | 839.9997 | 110.6331
SMG-2.RR.350.1 | 25013589138462 | Chhatak, Battirkandi, Abdus Salam | 2019-08-27 | NQ1000 | 10.9 | 558 | 10.9 | 559 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7920 | 839.9997 | 114.8476
SMG-2.RR.351.1 | 25020049139354 | Chhatak, Baghbari, Hamendro Debnath | 2019-08-22 | NQ1000 | 12.4 | 212 | 12.4 | 213 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7968 | 791.9997 | 130.6524
SMG-2.RR.351.2 | 25020049139354 | Chhatak, Baghbari, Hamendro Debnath | 2021-02-10 | NQ1003 | 4.7 | 212 | 4.5 | 213 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7968 | 791.9997 | 47.4142
SMG-2.RR.352.1 | 25020049139354 | Chhatak, Baghbari, Diraj | 2019-08-22 | NQ1000 | 12 | 214 | 12 | 215 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7968 | 791.9997 | 126.4378
SMG-2.RR.353.1 | 25020049139354 | Chhatak, Baghbari, Mohibur Rahman | 2019-08-22 | NQ1000 | 12.4 | 216 | 12.4 | 217 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7968 | 791.9997 | 130.6524
SMG-2.RR.353.2 | 25020049139354 | Chhatak, Baghbari, Mohibur Rahman | 2021-02-10 | NQ1003 | 2.8 | 215 | 2.8 | 216 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7968 | 791.9997 | 29.5021
SMG-2.RR.354.1 | 25015949139354 | Chhatak, Baghbari, Laila Begum | 2019-08-22 | NQ1000 | 9.8 | 218 | 9.8 | 219 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7968 | 791.9997 | 103.2575
SMG-2.RR.355.1 | 25015809139365 | Chhatak, Baghbari, Khalil | 2019-08-22 | NQ1000 | 11 | 220 | 11 | 221 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7968 | 791.9997 | 115.9013
SMG-2.RR.356.1 | 25015909139333 | Chhatak, Baghbari, Abdul Kayum | 2019-08-22 | NQ1000 | 10.4 | 222 | 10.4 | 223 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7968 | 791.9997 | 109.5794
SMG-2.RR.357.1 | 25020289139352 | Chhatok, Baghbari, Abdullah Mia | 2019-08-22 | NQ1000 | 9.2 | 224 | 9.2 | 225 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7968 | 791.9997 | 96.9356
SMG-2.RR.358.1 | 25020289139352 | Chhatak, Baghbari, Abdur Razzak | 2019-08-22 | NQ1000 | 8.6 | 226 | 8.6 | 227 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7968 | 791.9997 | 90.6137
SMG-2.RR.359.1 | 25020259139367 | Chhatak, Baghbari, Romid Ali | 2019-08-22 | NQ1000 | 7.1 | 230 | 7.1 | 231 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7968 | 791.9997 | 74.809
SMG-2.RR.360.1 | 25020369139359 | Chhatak, Baghbari, Ashik Mia | 2019-08-22 | NQ1000 | 12.4 | 232 | 12.4 | 233 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7968 | 791.9997 | 130.6524
SMG-2.RR.361.1 | 25020369139359 | Chhatak, Baghbari, Abdullah Mia | 2019-08-22 | NQ1000 | 8.6 | 234 | 8.6 | 235 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7968 | 791.9997 | 90.6137
SMG-2.RR.362.1 | 25020369139359 | Chhatak, Baghbari, Ahsan Mia | 2019-08-22 | NQ1000 | 10.7 | 236 | 10.7 | 237 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7968 | 791.9997 | 112.7403
SMG-2.RR.363.1 | 25020369139359 | Chhatak, Baghbari, Asa Mia | 2019-08-22 | NQ1000 | 6.2 | 238 | 6.2 | 239 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7968 | 791.9997 | 65.3262
SMG-2.RR.364.1 | 25020339139368 | Chhatak, Baghbari, Alauddin | 2019-08-22 | NQ1000 | 2.9 | 242 | 2.9 | 243 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7968 | 791.9997 | 30.5558
SMG-2.RR.364.2 | 25020339139368 | Chhatak, Baghbari, Alauddin | 2022-02-28 | NQ1007 | 4.7 | 21 | 4.7 | 22 | 2022-02-28 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6576 | 791.9997 | 41.6523
SMG-2.RR.365.1 | 25020259139426 | Chhatak, Baghbari, Rahima Begum | 2019-08-22 | NQ1000 | 21.2 | 246 | 21.2 | 247 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 21.2 | 21.2 | 1.272 | 1.272 | 0.0007168 | 100% | 0% | 1.272 | 1.272 | 0.0011869 | 28 | 0.025499 | 0.025499 |  | 0 | 0 | 7968 | 791.9997 | 223.3734
SMG-2.RR.366.1 | 25020259139421 | Chhatak, Baghbari, Golam Hossain | 2019-08-22 | NQ1000 | 3.9 | 248 | 3.9 | 249 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7968 | 791.9997 | 41.0923
SMG-2.RR.367.1 | 25020369139416 | Chhatak, Baghbari, Jamal | 2019-08-22 | NQ1000 | 11.1 | 250 | 11.1 | 251 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7968 | 791.9997 | 116.9549
SMG-2.RR.368.1 | 25020279139586 | Chhatak, Surab Nagor, Shajalal Abashik, Bodrul Alom | 2019-08-22 | NQ1000 | 8.2 | 252 | 8.2 | 253 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7992 | 767.9997 | 86.3991
SMG-2.RR.369.1 | 25020099139570 | Chhatak, Surab Nagor, Shajalal Abashik, Mojaffor Ali | 2019-08-22 | NQ1000 | 3.2 | 254 | 3.2 | 255 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7992 | 767.9997 | 33.7167
SMG-2.RR.370.1 | 25020099139570 | Chhatak, Surab Nagor, Shajalal Abashik, Jahirul Islam | 2019-08-22 | NQ1000 | 10.2 | 256 | 10.2 | 257 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7992 | 767.9997 | 107.4721
SMG-2.RR.371.1 | 25020479139541 | Chhatak, Surab Nagor, Shajalal Abashik, Forid | 2019-08-22 | NQ1000 | 5.8 | 258 | 5.8 | 259 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 96 | 0 | 7896 | 767.9997 | 60.4419
SMG-2.RR.372.1 | 25020479139541 | Chhatak, Surab Nagor, Shajalal Abashik, Waris Ali | 2019-08-22 | NQ1000 | 4.5 | 260 | 4.5 | 261 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7992 | 767.9997 | 47.4142
SMG-2.RR.373.1 | 25020589139533 | Chhatak, South Mondolivog, Mohammad Awlad Hossain | 2019-08-22 | NQ1000 | 2.2 | 262 | 2.2 | 263 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7992 | 767.9997 | 23.1803
SMG-2.RR.374.1 | 25020589139534 | Chhatak, South Mondolivog, Milik Mia | 2019-08-22 | NQ1000 | 10 | 264 | 10 | 265 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7992 | 767.9997 | 105.3648
SMG-2.RR.375.1 | 25020459140263 | Chhatak, West Moghol Para, Medical Road, Mohammad Nur Mia | 2019-08-24 | NQ1000 | 11.6 | 313 | 11.6 | 314 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8016 | 743.9997 | 122.2232
SMG-2.RR.376.1 | 25020429140279 | Chhatak, West Moghol Para, Medical Road, Aftab Mia | 2019-08-24 | NQ1000 | 14.3 | 315 | 14.3 | 316 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 8016 | 743.9997 | 150.6717
SMG-2.RR.376.2 | 25020429140279 | Chhatak, West Moghol Para, Medical Road, Aftab Mia | 2021-10-14 | NQ1007 | 12.9 | 58 | 12.9 | 59 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 8016 | 743.9997 | 135.9206
SMG-2.RR.377.1 | 25020469140292 | Chhatak, West Moghol Para, Medical Road, Khorshed Mia | 2019-08-24 | NQ1000 | 6.7 | 317 | 7.2 | 318 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 8016 | 743.9997 | 75.8627
SMG-2.RR.378.1 | 25020469140292 | Chhatak, West Moghol Para, Medical Road, Mukul Mia | 2019-08-24 | NQ1000 | 10.1 | 319 | 10.1 | 320 | 2022-01-01 | [9 empty] | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0
SMG-2.RR.379.1 | 25020449140303 | Chhatak, West Moghol Para, Medical Road, Hingi | 2019-08-24 | NQ1000 | 4 | 333 | 4 | 334 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 8016 | 743.9997 | 42.1459
SMG-2.RR.379.2 | 25020449140303 | Chhatak, West Moghol Para, Medical Road, Hingi | 2020-10-10 | MP1032 | 3.6 | 373 | 3.6 | 374 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 8016 | 743.9997 | 37.9313
SMG-2.RR.380.1 | 25020449140303 | Chhatak, West Moghol Para, Medical Road, Rifat | 2019-08-24 | NQ1000 | 10.2 | 335 | 10.2 | 336 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8016 | 743.9997 | 107.4721
SMG-2.RR.381.1 | 25020469140310 | Chhatak, West Moghol Para, Medical Road, Faruk Mia | 2019-08-24 | NQ1000 | 9.9 | 337 | 9.9 | 338 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8016 | 743.9997 | 104.3112
SMG-2.RR.382.1 | 25020569140295 | Chhatak, West Moghol Para, Medical Road, Shamsu Mia | 2019-08-24 | NQ1000 | 13.1 | 339 | 13.1 | 340 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 8016 | 743.9997 | 138.0279
SMG-2.RR.383.1 | 25013289140409 | Chhatak, Boula, Near by Boula Mosjid, Mojjamel Haque | 2019-08-25 | NQ1000 | 3.4 | 381 | 3.4 | 382 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7992 | 767.9997 | 35.824
SMG-2.RR.384.1 | 25013289140409 | Chhatak, Boula, Near by Boula Mosjid, Wakil Mia | 2019-08-25 | NQ1000 | 12.7 | 383 | 12.7 | 384 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7992 | 767.9997 | 133.8133
SMG-2.RR.385.1 | 25013289140409 | Chhatak, Boula, Near by Boula Mosjid, Josim | 2019-08-25 | NQ1000 | 12.9 | 385 | 12.9 | 386 | 2022-01-01 | [9 empty] | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 | 2022-01-01 12:00 | 0 | 0
SMG-2.RR.386.1 | 25013319140443 | Chhatak, Boula, Near by Boula Mosjid, Boktiar | 2019-08-25 | NQ1000 | 53.3 | 387 | 53.3 | 388 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 53.3 | 53.3 | 3.198 | 3.198 | 0.0007168 | 100% | 0% | 3.198 | 3.198 | 0.0011869 | 28 | 0.064109 | 0.064109 |  | 0 | 0 | 7992 | 767.9997 | 561.5945
SMG-2.RR.387.1 | 25020719140318 | Chhatak, Mogolpara, Thana Road, Md. Sohid | 2019-08-25 | NQ1000 | 12.5 | 391 | 12.5 | 392 | 2022-01-01 | [9 empty] | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0
SMG-2.RR.388.1 | 25020719140318 | Chhatak, Mogolpara, Thana Road, Shamim | 2019-08-25 | NQ1000 | 10 | 393 | 10 | 394 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8016 | 743.9997 | 105.3648
SMG-2.RR.388.2 | 25020719140318 | Chhatak, Mogolpara, Thana Road, Shamim | 2021-02-11 | LU1001 | 3 | 182 | 3 | 183 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 8016 | 743.9997 | 31.6094
SMG-2.RR.389.1 | 25020829140309 | Chhatak, Mogolpara, Fozlul Haque Limon | 2019-08-25 | NQ1000 | 8.3 | 395 | 8.3 | 396 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 8016 | 743.9997 | 87.4528
SMG-2.RR.390.1 | 25020659140300 | Chhatak, Mogolpara, Monir Mia | 2019-08-25 | NQ1000 | 7.3 | 397 | 7.3 | 398 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8016 | 743.9997 | 76.9163
SMG-2.RR.391.1 | 25020659140300 | Chhatak, Mogolpara, Kader Mia | 2019-08-25 | NQ1000 | 8.5 | 399 | 8.5 | 400 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 8016 | 743.9997 | 89.5601
SMG-2.RR.391.2 | 25020659140300 | Chhatak, Mogolpara, Kader Mia | 2021-02-11 | LU1001 | 4.3 | 184 | 4.3 | 185 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 8016 | 743.9997 | 45.3069
SMG-2.RR.392.1 | 25020919140294 | Chhatak, Sorobor, Abdur Salek | 2019-08-25 | NQ1000 | 10 | 401 | 10 | 402 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8016 | 743.9997 | 105.3648
SMG-2.RR.392.2 | 25020919140294 | Chhatak, Sorobor, Abdur Salek | 2020-10-10 | MN1032 | 4.8 | 23 | 4.8 | 24 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8016 | 743.9997 | 50.5751
SMG-2.RR.393.1 | 25020889140281 | Chhatak, Sorobor, Jabed | 2019-08-25 | NQ1000 | 5.4 | 403 | 5.4 | 404 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 8016 | 743.9997 | 56.897
SMG-2.RR.393.2 | 25020889140281 | Chhatak, Sorobor, Jabed | 2020-10-10 | MN1032 | 5.8 | 27 | 5.8 | 28 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8016 | 743.9997 | 61.1116
SMG-2.RR.394.1 | 25020889140281 | Chhatak, Sorobor, Khalek | 2019-08-25 | NQ1000 | 10.7 | 407 | 10.7 | 408 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8016 | 743.9997 | 112.7403
SMG-2.RR.395.1 | 25015479139260 | Chhatak, Railway Colony, BR-11 | 2019-08-26 | NQ1000 | 34.6 | 425 | 34.6 | 426 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 34.6 | 34.6 | 2.076 | 2.076 | 0.0007168 | 100% | 0% | 2.076 | 2.076 | 0.0011869 | 28 | 0.041617 | 0.041617 |  | 0 | 0 | 7968 | 791.9997 | 364.5623
SMG-2.RR.396.1 | 25015479139260 | Chhatak, Railway Colony, BR-12 | 2019-08-26 | NQ1000 | 4.2 | 427 | 4.2 | 428 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7968 | 791.9997 | 44.2532
SMG-2.RR.397.1 | 25015479139260 | Chhatak, Railway Colony, BR-10 | 2019-08-26 | NQ1000 | 15.2 | 429 | 15.2 | 430 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7968 | 791.9997 | 160.1545
SMG-2.RR.398.1 | 25015479139260 | Chhatak, Railway Colony, BR-9 | 2019-08-26 | NQ1000 | 13.4 | 431 | 13.4 | 432 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7968 | 791.9997 | 141.1888
SMG-2.RR.399.1 | 25015479139260 | Chhatak, Railway Colony, BR-13 | 2019-08-26 | NQ1000 | 11.2 | 437 | 11.2 | 438 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7968 | 791.9997 | 118.0086
SMG-2.RR.400.1 | 25015629139271 | Chhatak, Railway Colony, BR-15 | 2019-08-26 | NQ1000 | 5.2 | 439 | 5.2 | 440 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7968 | 791.9997 | 54.7897
SMG-2.RR.401.1 | 25012679138364 | Chatak, Patibug, Ward # 5, Azofor Ali | 2019-08-27 | LP1002 | 3.8 | 443 | 3.8 | 444 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7920 | 839.9997 | 40.0386
SMG-2.RR.402.1 | 25012679138364 | Chatak, Patibug, Ward # 5, Angur mia | 2019-08-27 | LP1002 | 13.1 | 445 | 13.1 | 446 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7920 | 839.9997 | 138.0279
SMG-2.RR.403.1 | 25012679138364 | Chatak, Patibug, Ward # 5, Abdus Sahid | 2019-08-27 | LP1002 | 7.8 | 447 | 7.8 | 448 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7920 | 839.9997 | 82.1846
SMG-2.RR.404.1 | 25012679138364 | Chatak, Patibug, Ward # 5, Arob Ali | 2019-08-27 | LP1002 | 6.5 | 449 | 6.5 | 450 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7920 | 839.9997 | 68.4871
SMG-2.RR.404.2 | 25012679138364 | Chatak, Patibug, Ward # 5, Arob Ali | 2021-02-09 | LU1001 | 10.9 | 169 | 10.9 | 170 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7920 | 839.9997 | 114.8476
SMG-2.RR.405.1 | 25012549138350 | Chatak, Patibug, Ward # 5, Jomir Ali | 2019-08-27 | LP1002 | 12.8 | 451 | 12.8 | 452 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7920 | 839.9997 | 134.867
SMG-2.RR.406.1 | 25012549138350 | Chatak, Patibug, Ward # 5, Haris Ali | 2019-08-27 | LP1002 | 4.7 | 453 | 4.7 | 454 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7920 | 839.9997 | 49.5215
SMG-2.RR.407.1 | 25012299138323 | Chatak, Patibug, Ward # 5, Islam uddin | 2019-08-27 | LP1002 | 14.1 | 455 | 14.1 | 456 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7920 | 839.9997 | 148.5644
SMG-2.RR.408.1 | 25012299138323 | Chatak, Patibug, Ward # 5, A. Aahad | 2019-08-27 | LP1002 | 10.3 | 457 | 10.3 | 458 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7920 | 839.9997 | 108.5258
SMG-2.RR.408.2 | 25012299138323 | Chatak, Patibug, Ward # 5, A. Aahad | 2021-10-10 | NQ1007 | 7.4 | 43 | 7.4 | 44 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7920 | 839.9997 | 77.97
SMG-2.RR.409.1 | 25012299138323 | Chatak, Patibug, Ward # 5, Azman Ali | 2019-08-27 | LP1002 | 7.5 | 459 | 7.5 | 460 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7920 | 839.9997 | 79.0236
SMG-2.RR.410.1 | 25012299138323 | Chatak, Patibug, Ward # 5, Ali Nur | 2019-08-27 | LP1002 | 10.2 | 461 | 10.2 | 462 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7920 | 839.9997 | 107.4721
SMG-2.RR.411.1 | 25012299138323 | Chatak, Patibug, Ward # 5, Mojammal Ali | 2019-08-27 | LP1002 | 3.3 | 463 | 3.3 | 464 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7920 | 839.9997 | 34.7704
SMG-2.RR.411.2 | 25012299138323 | Chatak, Patibug, Ward # 5, Mojammal Ali | 2021-02-09 | LU1001 | 2.9 | 171 | 2.9 | 172 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7920 | 839.9997 | 30.5558
SMG-2.RR.412.1 | 25012079138288 | Chatak, Patibug, Ward # 5, Sabajur Rahman | 2019-08-27 | LP1002 | 6.7 | 465 | 6.7 | 466 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7920 | 839.9997 | 70.5944
SMG-2.RR.413.1 | 25012959138394 | Chatak, Patibug, Ward # 5, A. Salam | 2019-08-27 | LP1002 | 9.1 | 467 | 8.7 | 468 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7920 | 839.9997 | 91.6674
SMG-2.RR.414.1 | 25012999138408 | Chatak, Batir Kandi, A. Kahar | 2019-08-27 | LP1002 | 5.7 | 469 | 5.7 | 470 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 288 | 0 | 7632 | 839.9997 | 58.0834
SMG-2.RR.414.2 | 25012999138408 | Chatak, Batir Kandi, A. Kahar | 2022-11-27 | NQ1007 | 10.5 | 215 | 10.5 | 216 | 2022-11-27 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 288 | 0 | -288 | 839.9997 | 6.9714
SMG-2.RR.415.1 | 25012999138408 | Chatak, Batir Kandi, Sahed | 2019-08-27 | LP1002 | 11.4 | 471 | 11.4 | 472 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7920 | 839.9997 | 120.1159
SMG-2.RR.416.1 | 25013019138409 | Chatak, Batir Kandi, A. Halim | 2019-08-27 | LP1002 | 2.2 | 473 | 2.2 | 474 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7920 | 839.9997 | 23.1803
SMG-2.RR.451.1 | 25025269133320 | Doara Bazar, Morad Pur, Kamal | 2019-08-28 | LP1002 | 3.7 | 475 | 3.7 | 476 | 2022-01-01 | [9 empty] | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0
SMG-2.RR.451.2 | 25025269133320 | Doara Bazar, Morad Pur, Kamal | 2021-02-09 | NQ1003 | 5 | 208 | 5 | 209 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7944 | 815.9997 | 52.6824
SMG-2.RR.452.1 | 25025269133320 | Doara Bazar, Morad Pur, Besid Kamal | 2019-08-28 | LP1002 | 25.5 | 477 | 25.5 | 478 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 25.5 | 25.5 | 1.53 | 1.53 | 0.0007168 | 100% | 0% | 1.53 | 1.53 | 0.0011869 | 28 | 0.030671 | 0.030671 |  | 0 | 0 | 7944 | 815.9997 | 268.6803
SMG-2.RR.452.2 | 25025269133320 | Doara Bazar, Morad Pur, Besid Kamal | 2021-02-09 | NQ1003 | 2.2 | 210 | 2.2 | 211 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7944 | 815.9997 | 23.1803
SMG-2.RR.453.1 | 25024849133443 | Doara Bazar, Officer Mass | 2019-08-28 | LP1002 | 6.6 | 481 | 6.6 | 482 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7944 | 815.9997 | 69.5408
SMG-2.RR.454.1 | 25024369133474 | Doara Bazar, Hospital Road, Harunr Roshed | 2019-08-28 | LP1002 | 13.3 | 483 | 12.8 | 484 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7944 | 815.9997 | 134.867
SMG-2.RR.455.1 | 25022289139244 | Chhatak, Noaray, Mst. Hafiz Jamal | 2019-08-28 | LP1002 | 2.1 | 485 | 2.1 | 486 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7920 | 839.9997 | 22.1266
SMG-2.RR.456.1 | 25023099139200 | Chhatak, Noaray, Bangla Bazar Road, Puchon Ali | 2019-08-28 | LP1002 | 24.8 | 489 | 24.8 | 490 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 24.8 | 24.8 | 1.488 | 1.488 | 0.0007168 | 100% | 0% | 1.488 | 1.488 | 0.0011869 | 28 | 0.029829 | 0.029829 |  | 0 | 0 | 7920 | 839.9997 | 261.3047
SMG-2.RR.456.2 | 25023099139200 | Chhatak, Noaray, Bangla Bazar Road, Puchon Ali | 2019-08-28 | LP1002 | 14.2 | 491 | 14.2 | 492 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7920 | 839.9997 | 149.618
SMG-2.RR.457.1 | 25023289139213 | Chhatak, Noaray, Bangla Bazar Road, Koshir Ali | 2019-08-28 | LP1002 | 11.4 | 493 | 11.4 | 494 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7920 | 839.9997 | 120.1159
SMG-2.RR.501.1 | 25021489140029 | Chatok, Thana Road, Lal Mosque Font Side, Hazi Arshad Ali | 2019-08-25 | MN1018 | 4.8 | 377 | 4.8 | 378 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8016 | 743.9997 | 50.5751
SMG-2.RR.502.1 | 25021489140036 | Chatok, Thana Road, Lal Mosque Font Side, Badsha Mia | 2019-08-25 | MN1018 | 2.9 | 379 | 2.9 | 380 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 8016 | 743.9997 | 30.5558
SMG-2.RR.503.1 | 25013099140432 | Chatok, Baula, Word # 9, Md. Nasir | 2019-08-25 | MN1018 | 4 | 381 | 4 | 382 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7992 | 767.9997 | 42.1459
SMG-2.RR.504.1 | 25013099140432 | Chatok, Baula, Word # 9, H # 369, Shayed Ahmed | 2019-08-25 | MN1018 | 5 | 383 | 4.5 | 384 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7992 | 767.9997 | 47.4142
SMG-2.RR.505.1 | 25020279139116 | Chatok, Noyaray, West Side, Kajol Roy | 2019-08-27 | MN1018 | 3.2 | 401 | 3.2 | 402 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7920 | 839.9997 | 33.7167
SMG-2.RR.506.1 | 25020279139116 | Chatok, Noyaray, West Side, Suras Das | 2019-08-27 | MN1018 | 8.7 | 403 | 8.7 | 404 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7920 | 839.9997 | 91.6674
SMG-2.RR.507.1 | 25020339139114 | Chatok, Noyaray, West Side, Motindro Das | 2019-08-27 | MN1018 | 11 | 405 | 11 | 406 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7920 | 839.9997 | 115.9013
SMG-2.RR.508.1 | 25020259139114 | Chatok, Noyaray, West Side, Suchona Das | 2019-08-27 | MN1018 | 2.6 | 407 | 2.6 | 408 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7920 | 839.9997 | 27.3949
SMG-2.RR.509.1 | 25020259139114 | Chatok, Noyaray, West Side, Ragandhoar | 2019-08-27 | MN1018 | 3.3 | 411 | 3.3 | 412 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7920 | 839.9997 | 34.7704
SMG-2.RR.510.1 | 25020369139102 | Chatok, Noyaray, West Side, Rani Das | 2019-08-27 | MN1018 | 21.9 | 413 | 21.9 | 414 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 21.9 | 21.9 | 1.314 | 1.314 | 0.0007168 | 100% | 0% | 1.314 | 1.314 | 0.0011869 | 28 | 0.026341 | 0.026341 |  | 0 | 0 | 7920 | 839.9997 | 230.7489
SMG-2.RR.511.1 | 25020369139102 | Chatok, Noyaray, West Side, Prodes Das | 2019-08-27 | MN1018 | 8.4 | 415 | 8.3 | 416 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7920 | 839.9997 | 87.4528
SMG-2.RR.511.2 | 25020369139102 | Chatok, Noyaray, West Side, Prodes Das | 2021-02-09 | MN1032 | 12.6 | 129 | 12.6 | 130 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7920 | 839.9997 | 132.7597
SMG-2.RR.512.1 | 25020369139102 | Chatok, Noyaray, West Side, Rothrondro Das | 2019-08-27 | MN1018 | 7.7 | 421 | 7.7 | 422 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7920 | 839.9997 | 81.1309
SMG-2.RR.513.1 | 25020219139099 | Chatok, Noyaray, West Side, Hazi Roich Ali | 2019-08-27 | MN1018 | 3.8 | 423 | 3.8 | 424 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7920 | 839.9997 | 40.0386
SMG-2.RR.514.1 | 25020219139099 | Chatok, Noyaray, West Side, Gorongo Doto | 2019-08-27 | MN1018 | 2.3 | 425 | 2.3 | 426 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7920 | 839.9997 | 24.2339
SMG-2.RR.515.1 | 25020219139099 | Chatok, Noyaray, West Side, Sosonko Devnath | 2019-08-27 | MN1018 | 7.5 | 427 | 7.5 | 428 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7920 | 839.9997 | 79.0236
SMG-2.RR.516.1 | 25020319139090 | Chatok, Noyaray, West Side, Poremol Devnath | 2019-08-27 | MN1018 | 12.1 | 429 | 12.1 | 430 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7920 | 839.9997 | 127.4914
SMG-2.RR.517.1 | 25020319139090 | Chatok, Noyaray, West Side, Sonkor Devnath | 2019-08-27 | MN1018 | 8 | 431 | 8 | 432 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7920 | 839.9997 | 84.2919
SMG-2.RR.518.1 | 25020319139090 | Chatok, Noyaray, West Side, Monojoron Devnath | 2019-08-27 | MN1018 | 9 | 435 | 9 | 436 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7920 | 839.9997 | 94.8283
SMG-2.RR.519.1 | 25020319139090 | Chatok, Noyaray, West Side, Boloram Devnath | 2019-08-27 | MN1018 | 21.5 | 437 | 21.5 | 438 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 21.5 | 21.5 | 1.29 | 1.29 | 0.0007168 | 100% | 0% | 1.29 | 1.29 | 0.0011869 | 28 | 0.02586 | 0.02586 |  | 0 | 0 | 7920 | 839.9997 | 226.5343
SMG-2.RR.520.1 | 25010389138141 | Chatok, Baznamohol, Barokohon, Aina Mia | 2019-08-27 | MN1018 | 4.7 | 443 | 4.7 | 444 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7920 | 839.9997 | 49.5215
SMG-2.RR.521.1 | 25010389138141 | Chatok, Baznamohol, Barokohon, Tara Mia | 2019-08-27 | MN1018 | 7.1 | 447 | 7.1 | 448 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7920 | 839.9997 | 74.809
SMG-2.RR.522.1 | 25010389138141 | Chatok, Baznamohol, Barokohon, Siddeique Hasan | 2019-08-27 | MN1018 | 4.9 | 449 | 4.9 | 450 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7920 | 839.9997 | 51.6288
SMG-2.RR.523.1 | 25023299134028 | Sunamganj, Dorabazar, Hospital Front Side, Abdul Mosiber | 2019-08-28 | MN1018 | 19.9 | 451 | 19.9 | 452 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0 | 7944 | 815.9997 | 209.676
SMG-2.RR.524.1 | 25023299134028 | Sunamganj, Dorabazar, Hospital Front Side, Abdul Rob | 2019-08-28 | MN1018 | 1 | 453 | 1 | 454 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7944 | 815.9997 | 10.5365
SMG-2.RR.525.1 | 25023389134017 | Sunamganj, Dorabazar, Hospital Road, Amirunessa | 2019-08-28 | MN1018 | 4.4 | 455 | 4.4 | 456 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7944 | 815.9997 | 46.3605
SMG-2.RR.526.1 | 25023389134017 | Sunamganj, Dorabazar, Hospital Road, Afia Khatun | 2019-08-28 | MN1018 | 10.7 | 457 | 10.7 | 458 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7944 | 815.9997 | 112.7403
SMG-2.RR.527.1 | 25023379133592 | Sunamganj, Dorabazar, Hospital Road, Abdur Rohim | 2019-08-28 | MN1018 | 13 | 459 | 13 | 460 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7944 | 815.9997 | 136.9743
SMG-2.RR.528.1 | 25022909133594 | Sunamganj, Dorabazar, Hospital Road, Md. Abdul Ali | 2019-08-28 | MN1018 | 9.3 | 461 | 9.3 | 462 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7944 | 815.9997 | 97.9893
SMG-2.RR.529.1 | 25022909133594 | Sunamganj, Dorabazar, Hospital Road, Late Romjan Ali | 2019-08-28 | MN1018 | 3.3 | 463 | 3.3 | 464 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7944 | 815.9997 | 34.7704
SMG-2.RR.530.1 | 25022829133599 | Sunamganj, Dorabazar, Hospital Road, Abdul Malak | 2019-08-28 | MN1018 | 29.7 | 465 | 29.8 | 466 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 29.8 | 29.8 | 1.788 | 1.788 | 0.0007168 | 100% | 0% | 1.788 | 1.788 | 0.0011869 | 28 | 0.035843 | 0.035843 |  | 0 | 0 | 7944 | 815.9997 | 313.9871
SMG-2.RR.531.1 | 25023489133567 | Sunamganj, Dorabazar, Hospital Road, Almas Ali | 2019-08-28 | MN1018 | 11.4 | 467 | 11.8 | 468 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7944 | 815.9997 | 124.3305
SMG-2.RR.532.1 | 25023629133559 | Sunamganj, Dorabazar, Hospital Road, Nurul Islam | 2019-08-28 | MN1018 | 2.8 | 469 | 2.8 | 470 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7944 | 815.9997 | 29.5021
SMG-2.RR.533.1 | 25023929133546 | Sunamganj, Dorabazar, Hospital Road, Abdul Bari | 2019-08-28 | MN1018 | 13.6 | 471 | 13.6 | 472 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7944 | 815.9997 | 143.2961
SMG-2.RR.533.2 | 25023929133546 | Sunamganj, Dorabazar, Hospital Road, Abdul Bari | 2022-02-24 | NQ1007 | 4.8 | 4 | 4.8 | 5 | 2022-02-24 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6648 | 815.9997 | 43.0928
SMG-2.RR.551.1 | 25013719139100 | Chatok, Labour Para, South Bagbari, Momtaz Ali | 2019-08-26 | NQ1000 | 3.6 | 483 | 3.6 | 484 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7968 | 791.9997 | 37.9313
SMG-2.RR.552.1 | 25013789139093 | Chatok, Labour Para, South Bagbari, Kibria | 2019-08-26 | NQ1000 | 6.7 | 485 | 6.7 | 486 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7968 | 791.9997 | 70.5944
SMG-2.RR.553.1 | 25013669139089 | Chatok, Labour Para, South Bagbari, Razob Ali | 2019-08-26 | NQ1000 | 4.6 | 497 | 4.6 | 498 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7968 | 791.9997 | 48.4678
SMG-2.RR.554.1 | 25013669139089 | Chatok, Labour Para, South Bagbari, Shamim Mia | 2019-08-26 | NQ1000 | 2.3 | 499 | 2.3 | 500 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7968 | 791.9997 | 24.2339
SMG-2.RR.555.1 | 25013569139119 | Chatok, Labour Para, South Bagbari, Ayub Ali | 2019-08-26 | NQ1000 | 5.4 | 501 | 5.4 | 502 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7968 | 791.9997 | 56.897
SMG-2.RR.556.1 | 25013519139126 | Chatok, Labour Para, South Bagbari, Shohel Mia | 2019-08-26 | NQ1000 | 9.6 | 503 | 9.6 | 504 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7968 | 791.9997 | 101.1502
SMG-2.RR.557.1 | 25013379139159 | Chatok, Labour Para, South Bagbari, Sikandar Ali | 2019-08-26 | NQ1000 | 5 | 505 | 5 | 506 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7968 | 791.9997 | 52.6824
SMG-2.RR.558.1 | 25013149139198 | Chatok, Labour Para, South Bagbari, Mokbul Ali | 2019-08-26 | NQ1000 | 8.3 | 507 | 8.3 | 508 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7968 | 791.9997 | 87.4528
SMG-2.RR.559.1 | 25013159139117 | Chatok, Labour Para, Haris Ali | 2019-08-26 | NQ1000 | 6.3 | 512 | 6.3 | 513 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7896 | 863.9997 | 66.3798
SMG-2.RR.560.1 | 25013239139101 | Chatok, Labour Para, Abidur Rahman | 2019-08-26 | NQ1000 | 5.8 | 526 | 5.8 | 527 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7896 | 863.9997 | 61.1116
SMG-2.RR.561.1 | 25013239139101 | Chatok, Labour Para, Abdul Kabir | 2019-08-26 | NQ1000 | 5.2 | 528 | 5.2 | 529 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7896 | 863.9997 | 54.7897
SMG-2.RR.562.1 | 25013239139101 | Chatok, Labour Para, Abidur Rahman | 2019-08-26 | NQ1000 | 5.6 | 530 | 5.6 | 531 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7896 | 863.9997 | 59.0043
SMG-2.RR.563.1 | 25013389139066 | Chatok, Labourpara, Md. Layek Mia | 2019-08-29 | MN1018 | 6.4 | 477 | 6.4 | 478 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7896 | 863.9997 | 67.4335
SMG-2.RR.564.1 | 25013389139066 | Chatok, Labourpara, Md. Jamal Uddin | 2019-08-29 | MN1018 | 5.4 | 479 | 5.4 | 480 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7896 | 863.9997 | 56.897
SMG-2.RR.565.1 | 25013359139077 | Chatok, Labourpara, Mohi Uddin | 2019-08-29 | MN1018 | 12.5 | 481 | 12.5 | 482 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7896 | 863.9997 | 131.706
SMG-2.RR.565.2 | 25013359139077 | Chatok, Labourpara, Mohi Uddin | 2022-11-26 | NQ1007 | 3.3 | 208 | 3.3 | 209 | 2022-11-26 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 0 | 863.9997 | 3.4294
SMG-2.RR.566.1 | 25013389139061 | Chatok, Labourpara, Late- Fazor Ali | 2019-08-29 | MN1018 | 8.6 | 483 | 8.6 | 484 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7896 | 863.9997 | 90.6137
SMG-2.RR.567.1 | 25013389139061 | Chatok, Labourpara, Sadek Ali | 2019-08-29 | MN1018 | 24 | 485 | 24 | 486 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 24 | 24 | 1.44 | 1.44 | 0.0007168 | 100% | 0% | 1.44 | 1.44 | 0.0011869 | 28 | 0.028867 | 0.028867 |  | 0 | 0 | 7896 | 863.9997 | 252.8756
SMG-2.RR.568.1 | 25013319139079 | Chatok, Labourpara, Fazor Ali | 2019-08-29 | MN1018 | 8.6 | 487 | 8.6 | 488 | 2022-01-01 | [9 empty] | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0
SMG-2.RR.601.1 | 25025639133271 | Sunamganj, Douara Bazar, Duck Bangla Road, Full Mia | 2019-08-28 | LU1001 | 9 | 118 | 9 | 119 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7944 | 815.9997 | 94.8283
SMG-2.RR.602.1 | 25025639133271 | Sunamganj, Douara Bazar, Duck Bangla Road, Monaffor | 2019-08-28 | LU1001 | 5.2 | 120 | 5 | 121 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7944 | 815.9997 | 52.6824
SMG-2.RR.603.1 | 25030509133252 | Sunamganj, Douara Bazar, Bazar Road, Samsuddin | 2019-08-28 | LU1001 | 6 | 124 | 5.5 | 125 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7944 | 815.9997 | 57.9506
SMG-2.RR.604.1 | 25030509133252 | Sunamganj, Douara Bazar, Bazar Road, Toskir Mia | 2019-08-28 | LU1001 | 11.2 | 126 | 11.2 | 127 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7944 | 815.9997 | 118.0086
SMG-2.RR.605.1 | 25030509133252 | Sunamganj, Douara Bazar, Bazar Road, Depok Babu | 2019-08-28 | LU1001 | 7 | 128 | 7 | 129 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7944 | 815.9997 | 73.7554
SMG-2.RR.606.1 | 25030489133241 | Sunamganj, Douara Bazar, Bazar Road, Kadir | 2019-08-28 | LU1001 | 44.7 | 130 | 44.8 | 131 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 44.8 | 44.8 | 2.688 | 2.688 | 0.0007168 | 100% | 0% | 2.688 | 2.688 | 0.0011869 | 28 | 0.053885 | 0.053885 |  | 0 | 0 | 7944 | 815.9997 | 472.0344
SMG-2.RR.607.1 | 25030489133241 | Sunamganj, Douara Bazar, Bazar Road, Jakir | 2019-08-28 | LU1001 | 7.1 | 132 | 7.1 | 133 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7944 | 815.9997 | 74.809
SMG-2.RR.608.1 | 25030489133241 | Sunamganj, Douara Bazar, Bazar Road, Feroj Alam | 2019-08-28 | LU1001 | 6.3 | 134 | 6.3 | 135 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7944 | 815.9997 | 66.3798
SMG-2.RR.609.1 | 25030489133241 | Sunamganj, Douara Bazar, Bazar Road, Pongkoj Ray | 2019-08-28 | LU1001 | 11.1 | 136 | 11.1 | 137 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7944 | 815.9997 | 116.9549
SMG-2.RR.610.1 | 25030489133241 | Sunamganj, Douara Bazar, Bazar Road, Hannan | 2019-08-28 | LU1001 | 4.9 | 138 | 4.9 | 139 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7944 | 815.9997 | 51.6288
SMG-2.RR.611.1 | 25030509133232 | Sunamganj, Douara Bazar, Bazar Road, Shorifuzzaman | 2019-08-28 | LU1001 | 9.6 | 140 | 9.1 | 141 | 2022-01-01 | 2022-11-28 | NQ1007 | 0.6 | 219 | 0.6 | 220 | 2022-11-28 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7944 | 815.9997
SMG-2.RR.611.2 | 25030509133232 | Sunamganj, Douara Bazar, Bazar Road, Shorifuzzaman | 2019-08-28 | LU1001 | 3.5 | 142 | 3.5 | 143 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7944 | 815.9997 | 36.8777
SMG-2.RR.612.1 | 25030509133220 | Sunamganj, Douara Bazar, Bazar Road, Sontos Ray | 2019-08-28 | LU1001 | 9.7 | 144 | 9.7 | 145 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7944 | 815.9997 | 102.2039
SMG-2.RR.613.1 | 25030509133220 | Sunamganj, Douara Bazar, Bazar Road, Abdul Haque | 2019-08-28 | LU1001 | 13.4 | 146 | 13.4 | 147 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7944 | 815.9997 | 141.1888
SMG-2.RR.614.1 | 25030539133219 | Sunamganj, Douara Bazar, Bazar Road, Dulal | 2019-08-28 | LU1001 | 9.8 | 148 | 9.6 | 149 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7944 | 815.9997 | 101.1502
SMG-2.RR.615.1 | 25030539133219 | Sunamganj, Douara Bazar, Bazar Road, Nependro Das | 2019-08-28 | LU1001 | 7.4 | 150 | 7.4 | 151 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7944 | 815.9997 | 77.97
SMG-2.RR.616.1 | 25030539133219 | Sunamganj, Douara Bazar, Bazar Road, Gopika Ronjon | 2019-08-28 | LU1001 | 13.6 | 152 | 13.6 | 153 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7944 | 815.9997 | 143.2961
SMG-2.RR.617.1 | 25030439133201 | Sunamganj, Douara Bazar, Bazar Road, Sonermol Chandro | 2019-08-28 | LU1001 | 11.4 | 154 | 11 | 155 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7944 | 815.9997 | 115.9013
SMG-2.RR.701.1 | 25013359138441 | Chhatak, Battirkandi, Aklasur Rahman | 2019-08-27 | NQ1000 | 11.6 | 560 | 11.6 | 561 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7920 | 839.9997 | 122.2232
SMG-2.RR.702.1 | 25013239138434 | Chhatak, Battirkandi, Mostofa Mia | 2019-08-27 | NQ1000 | 14.2 | 562 | 14.2 | 563 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7920 | 839.9997 | 149.618
SMG-2.RR.703.1 | 25013239138434 | Chhatak, Battirkandi, Hazera | 2019-08-27 | NQ1000 | 9.5 | 564 | 9.5 | 565 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7920 | 839.9997 | 100.0966
SMG-2.RR.704.1 | 25013149138426 | Chhatak, Battirkandi, Kala Mia | 2019-08-27 | NQ1000 | 13.3 | 566 | 13.3 | 567 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7920 | 839.9997 | 140.1352
SMG-2.RR.705.1 | 25012529138273 | Chhatak, Patibag, Ali Akbar | 2019-08-27 | NQ1000 | 14 | 568 | 14.1 | 569 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7920 | 839.9997 | 148.5644
SMG-2.RR.706.1 | 25012529138273 | Chhatak, Patibag, Amjad Ali | 2019-08-27 | NQ1000 | 8.7 | 570 | 8.7 | 571 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7920 | 839.9997 | 91.6674
SMG-2.RR.707.1 | 25020419140093 | Chhatak, Mondolivog, Chhatak Upazila Health Complex | 2019-08-29 | NQ1000 | 25 | 590 | 25.7 | 591 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 25.7 | 25.7 | 1.542 | 1.542 | 0.0007168 | 100% | 0% | 1.542 | 1.542 | 0.0011869 | 28 | 0.030912 | 0.030912 |  | 0 | 0 | 7992 | 767.9997 | 270.7876
SMG-2.RR.708.1 | 25020319140051 | Chhatak, Mondolivog, Chhatak Upazila Health Complex | 2019-08-29 | NQ1000 | 5.9 | 592 | 5.9 | 593 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7992 | 767.9997 | 62.1652
SMG-2.RR.709.1 | 25020199140060 | Chhatak, Mondolivog, Chhatak Upazila Health Complex | 2019-08-29 | NQ1000 | 2.8 | 594 | 2.8 | 595 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7992 | 767.9997 | 29.5021
SMG-2.RR.710.1 | 25020199140060 | Chhatak, Mondolivog, Chhatak Upazila Health Complex | 2019-08-29 | NQ1000 | 10.8 | 596 | 10.8 | 597 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7992 | 767.9997 | 113.794
SMG-2.RR.710.2 | 25020199140060 | Chhatak, Mondolivog, Chhatak Upazila Health Complex | 2021-02-11 | NQ1007 | 2.9 | 181 | 2.9 | 182 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7992 | 767.9997 | 30.5558
SMG-2.RR.751.1 | 25014989139197 | Chhatak, South Baghbari, Railway Road, Binode Behari Das | 2019-08-26 | NQ1000 | 10.1 | 451 | 10.1 | 452 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7968 | 791.9997 | 106.4185
SMG-2.RR.752.1 | 25014989139197 | Chhatak, South Baghbari, Railway Road, Binas Babu | 2019-08-26 | NQ1000 | 3 | 453 | 3 | 454 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7968 | 791.9997 | 31.6094
SMG-2.RR.753.1 | 25014419139110 | Chhatak, South Baghbari, Railway Road, Nazmul | 2019-08-26 | NQ1000 | 10.7 | 455 | 10.6 | 456 | 2022-01-01 | [9 empty] | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0
SMG-2.RR.754.1 | 25014089139114 | Chhatak, South Baghbari, Railway Road, Afroja Monjil | 2019-08-26 | NQ1000 | 9.8 | 457 | 9.8 | 458 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7968 | 791.9997 | 103.2575
SMG-2.RR.755.1 | 25013949139108 | Chhatak, South Baghbari, Railway Road, Kutub | 2019-08-26 | NQ1000 | 4.8 | 461 | 4.8 | 462 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7968 | 791.9997 | 50.5751
SMG-2.RR.756.1 | 25013949139108 | Chhatak, South Baghbari, Railway Road, Shajahan | 2019-08-26 | NQ1000 | 6 | 471 | 6 | 472 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7968 | 791.9997 | 63.2189
SMG-2.RR.757.1 | 25013949139108 | Chhatak, South Baghbari, Railway Road, Delower | 2019-08-26 | NQ1000 | 10.3 | 473 | 10.3 | 474 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7968 | 791.9997 | 108.5258
SMG-2.RR.758.1 | 25013609139106 | Chhatak, South Baghbari, Railway Road, Delower | 2019-08-26 | NQ1000 | 5.3 | 489 | 5.3 | 490 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7968 | 791.9997 | 55.8434
SMG-2.RR.759.1 | 25013609139106 | Chhatak, South Baghbari, Railway Road, Samsuddin | 2019-08-26 | NQ1000 | 9.6 | 491 | 9.6 | 492 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7968 | 791.9997 | 101.1502
SMG-2.RR.760.1 | 25013609139106 | Chhatak, South Baghbari, Railway Road, Bosir Uddin | 2019-08-26 | NQ1000 | 7.8 | 493 | 7.8 | 494 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7968 | 791.9997 | 82.1846
SMG-2.RR.761.1 | 25013609139106 | Chhatak, South Baghbari, Railway Road, Kabir Uddin | 2019-08-26 | NQ1000 | 3.4 | 495 | 3.4 | 496 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7968 | 791.9997 | 35.824
SMG-2.RR.762.1 | 25013009139125 | Chhatak, Laber Para, Near Laber Para Mosque, Amir Ali | 2019-08-26 | NQ1000 | 37.1 | 514 | 37.1 | 515 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 37.1 | 37.1 | 2.226 | 2.226 | 0.0007168 | 100% | 0% | 2.226 | 2.226 | 0.0011869 | 28 | 0.044624 | 0.044624 |  | 0 | 0 | 7896 | 863.9997 | 390.9035
SMG-2.RR.763.1 | 25013139139121 | Chhatak, Laber Para, Modris | 2019-08-26 | NQ1000 | 9.3 | 516 | 9.3 | 517 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7896 | 863.9997 | 97.9893
SMG-2.RR.763.2 | 25013139139121 | Chhatak, Laber Para, Modris | 2019-08-26 | NQ1000 | 4.3 | 518 | 4.3 | 519 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7896 | 863.9997 | 45.3069
SMG-2.RR.764.1 | 25013139139121 | Chhatak, Laber Para, Firoz Ali | 2019-08-26 | NQ1000 | 9.9 | 520 | 10 | 521 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7896 | 863.9997 | 105.3648
SMG-2.RR.765.1 | 25013149139098 | Chhatak, Laber Para, Almain | 2019-08-26 | NQ1000 | 6.7 | 522 | 6.7 | 523 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7896 | 863.9997 | 70.5944
SMG-2.RR.766.1 | 25013149139098 | Chhatak, Laber Para, Rostom Ali | 2019-08-26 | NQ1000 | 5 | 524 | 5 | 525 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7896 | 863.9997 | 52.6824
SMG-2.RR.767.1 | 25013229139097 | Chhatak, Laber Para, Siraj Miia | 2019-08-26 | NQ1000 | 4.1 | 532 | 4.1 | 533 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7896 | 863.9997 | 43.1996
SMG-2.RR.768.1 | 25013289139091 | Chhatak, Laber Para, Wares Ali | 2019-08-26 | NQ1000 | 8.6 | 534 | 8.6 | 535 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7896 | 863.9997 | 90.6137
SMG-2.RR.768.2 | 25013289139091 | Chhatak, Laber Para, Wares Ali | 2022-11-26 | NQ1007 | 11.2 | 210 | 11.2 | 211 | 2022-11-26 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 0 | 863.9997 | 11.6392
SMG-2.RR.769.1 | 25013469139052 | Chhatak, Laber Para, Gaffar Ali | 2019-08-26 | NQ1000 | 8.1 | 536 | 7.8 | 537 | 2022-01-01 | 2022-11-26 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7896 | 863.9997 | 82.1846
SMG-2.RR.770.1 | 25025269133176 | Dowara Bazar, East Muslim Para, Abdul Hakim | 2019-08-28 | NQ1000 | 5.4 | 572 | 5.4 | 573 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7944 | 815.9997 | 56.897
SMG-2.RR.771.1 | 25025269133176 | Dowara Bazar, East Muslim Para, Jolil | 2019-08-28 | NQ1000 | 8.3 | 574 | 8.3 | 575 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7944 | 815.9997 | 87.4528
SMG-2.RR.772.1 | 25025259133164 | Dowara Bazar, East Muslim Para, Kutubuddin | 2019-08-28 | NQ1000 | 13.6 | 576 | 13.6 | 577 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7944 | 815.9997 | 143.2961
SMG-2.RR.772.2 | 25025259133164 | Dowara Bazar, East Muslim Para, Kutubuddin | 2022-11-28 | NQ1007 | 5.3 | 217 | 5.2 | 218 | 2022-11-28 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 0 | 815.9997 | 5.1037
SMG-2.RR.773.1 | 25025259133164 | Dowara Bazar, East Muslim Para, Sattar | 2019-08-28 | NQ1000 | 10.2 | 578 | 10.2 | 579 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7944 | 815.9997 | 107.4721
SMG-2.RR.774.1 | 25030389133232 | Dowara Bazar, Near Loknath Mondir, Babul Roy | 2019-08-28 | NQ1000 | 11.4 | 580 | 11.4 | 581 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7944 | 815.9997 | 120.1159
SMG-2.RR.775.1 | 25030179133229 | Dowara Bazar, Near Loknath Mondir, Adv Sajol | 2019-08-28 | NQ1000 | 11.6 | 582 | 11.6 | 583 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7944 | 815.9997 | 122.2232
SMG-2.RR.776.1 | 25030179133229 | Dowara Bazar, Near Loknath Mondir, Harunur Roshid | 2019-08-28 | NQ1000 | 1.2 | 584 | 1.2 | 585 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7944 | 815.9997 | 12.6438
SMG-2.RR.777.1 | 25030179133229 | Dowara Bazar, Near Loknath Mondir, Sonjoy | 2019-08-28 | NQ1000 | 4.2 | 588 | 4.2 | 589 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7944 | 815.9997 | 44.2532
SYL-B.1.CR.1.1 | 24493519209047 | Biani Bazar, Prosova, Word # 6, Munsi Bakere, Md. Zomir Uddin | 2019-09-18 | MN1018 | 11.5 | 299 | 11.5 | 300 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6984 | 1775.9997 | 121.1695
SYL-B.1.CR.2.1 | 24493039209260 | Biani Bazar, Upozela Point, Vai Vai Bakary, Sofur Uddin | 2019-09-18 | MN1018 | 7.1 | 315 | 7.1 | 316 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6984 | 1775.9997 | 74.809
SYL-B.1.CR.3.1 | 24483549210577 | Biani Bazar, 10 No Muria Union Poroshid | 2019-09-21 | MN1018 | 7.8 | 351 | 7.8 | 352 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6936 | 1823.9997 | 82.1846
SYL-B.1.CR.4.1 | 24482649211095 | Beani Bazar, Sotodesh, Konagram, Konagram Jame Moszid, Aplu Pir | 2019-09-22 | MN1018 | 15.4 | 373 | 15.4 | 374 | 2022-01-01 | [9 empty] | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 | 2022-08-10 12:00 | 0 | 0
SYL-B.1.RR.1.1 | 24534269204097 | Beani Bazar, Kholagram, Liakot Ali | 2019-09-15 | LP1002 | 7.3 | 198 | 6.7 | 199 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7176 | 1583.9997 | 70.5944
SYL-B.1.RR.2.1 | 24534269204097 | Beani Bazar, Kholagram, Monowar mia | 2019-09-15 | LP1002 | 11.2 | 200 | 11.2 | 201 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7176 | 1583.9997 | 118.0086
SYL-B.1.RR.3.1 | 24534689204094 | Beani Bazar, Kholagram, Gias uddin | 2019-09-15 | LP1002 | 6.1 | 202 | 6.1 | 203 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7176 | 1583.9997 | 64.2725
SYL-B.1.RR.4.1 | 24534839204099 | Beani Bazar, Kholagram, Mujir uddin | 2019-09-15 | LP1002 | 12.2 | 204 | 12.2 | 205 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7176 | 1583.9997 | 128.5451
SYL-B.1.RR.5.1 | 24530309204131 | Beani Bazar, Raja pur, Ohab Manjil, Helal Ahmad | 2019-09-15 | LP1002 | 4.1 | 208 | 4.1 | 209 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7176 | 1583.9997 | 43.1996
SYL-B.1.RR.6.1 | 24525499204105 | Beani Bazar, Raja pur, Jaigirdar para, Alaur Rahman | 2019-09-15 | LP1002 | 11 | 210 | 11.1 | 211 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7176 | 1583.9997 | 116.9549
SYL-B.1.RR.7.1 | 24525499204105 | Beani Bazar, Raja pur, Jaigirdar para, Jitu mia | 2019-09-15 | LP1002 | 9.3 | 212 | 8.7 | 213 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7176 | 1583.9997 | 91.6674
SYL-B.1.RR.8.1 | 24524929204131 | Beani Bazar, Raja pur, Laik Ahmad | 2019-09-15 | LP1002 | 8.6 | 214 | 8.6 | 215 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7176 | 1583.9997 | 90.6137
SYL-B.1.RR.9.1 | 24524129204172 | Beani Bazar, Raja pur, Tilla Bari, Amir Ali | 2019-09-15 | LP1002 | 4.8 | 216 | 4.8 | 217 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7176 | 1583.9997 | 50.5751
SYL-B.1.RR.10.1 | 24524129204172 | Beani Bazar, Raja pur, Tilla Bari, Somir Ali | 2019-09-15 | LP1002 | 1.4 | 218 | 1.5 | 219 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 1416 | 0 | 5760 | 1583.9997 | 13.25
SYL-B.1.RR.10.2 | 24524129204172 | Beani Bazar, Raja pur, Tilla Bari, Somir Ali | 2022-10-27 | NQ1007 | 8.1 | 84 | 8.1 | 85 | 2022-10-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 0 | 1583.9997 | 15.4323
SYL-B.1.RR.11.1 | 24524129204172 | Beani Bazar, Raja pur, Tilla Bari, Khaled | 2019-09-15 | LP1002 | 3.6 | 220 | 3.6 | 221 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7176 | 1583.9997 | 37.9313
SYL-B.1.RR.12.1 | 24530699204286 | Beani Bazar, Ali Nagar, Tikor para, Fozol Ahmad | 2019-09-15 | LP1002 | 11.7 | 222 | 11.7 | 223 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7176 | 1583.9997 | 123.2768
SYL-B.1.RR.13.1 | 24530679204407 | Beani Bazar, Kaudia, Uttor Vag, Abul, (Beside Dhaka uttor Mohammad pur High School) | 2019-09-16 | LP1002 | 6.5 | 226 | 6.5 | 227 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7176 | 1583.9997 | 68.4871
SYL-B.1.RR.14.1 | 24530679204407 | Beani Bazar, Kaudia, Uttor Vag, A. Rahim, (Beside Dhaka uttor Mohammad pur High School) | 2019-09-16 | LP1002 | 3.8 | 228 | 3.8 | 229 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7176 | 1583.9997 | 40.0386
SYL-B.1.RR.15.1 | 24530499204407 | Beani Bazar, Kaudia, Uttor Vag, Saleh Ahmad, (Beside Dhaka uttor Mohammad pur High School) | 2019-09-16 | LP1002 | 9.1 | 230 | 9.1 | 231 | 2022-01-01 | [9 empty] | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0
SYL-B.1.RR.16.1 | 24530499204407 | Beani Bazar, Kaudia, Uttor Vag, Emdadul Hay, (Beside Dhaka uttor Mohammad pur High School) | 2019-09-16 | LP1002 | 9.4 | 232 | 9.4 | 233 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7176 | 1583.9997 | 99.0429
SYL-B.1.RR.17.1 | 24524889204458 | Beani Bazar, Tikor Para, Fechu Tilla, Cherag Ali | 2019-09-16 | LP1002 | 2.4 | 234 | 2.4 | 235 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7176 | 1583.9997 | 25.2876
SYL-B.1.RR.18.1 | 24524099204475 | Beani Bazar, Tikor Para, Heno Tilla, Nuruddin | 2019-09-16 | LP1002 | 4.7 | 236 | 4.7 | 237 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7176 | 1583.9997 | 49.5215
SYL-B.1.RR.19.1 | 24524099204475 | Beani Bazar, Tikor Para, Heno Tilla, A. Sahid | 2019-09-16 | LP1002 | 13.7 | 238 | 13.7 | 239 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7176 | 1583.9997 | 144.3498
SYL-B.1.RR.20.1 | 24531239206153 | Beani Bazar, Ramda Bazar, Chondo Gram, Hasnur Rahman | 2019-09-16 | LP1002 | 3.5 | 240 | 3.5 | 241 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7176 | 1583.9997 | 36.8777
SYL-B.1.RR.21.1 | 24531079206148 | Beani Bazar, Ramda Bazar, Chondo Gram, Borhan Uddin | 2019-09-16 | LP1002 | 6.6 | 242 | 6.6 | 243 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7176 | 1583.9997 | 69.5408
SYL-B.1.RR.21.2 | 24531079206148 | Beani Bazar, Ramda Bazar, Chondo Gram, Borhan Uddin | 2019-09-16 | LP1002 | 12.1 | 244 | 12.1 | 245 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7176 | 1583.9997 | 127.4914
SYL-B.1.RR.22.1 | 24553449210248 | Beanibazar, Nateswar, Uttor vag, Mostofa Ahmad, (Tawfiq Elahi gram) | 2019-09-17 | LP1002 | 3.8 | 262 | 3.8 | 263 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7056 | 1703.9997 | 40.0386
SYL-B.1.RR.23.1 | 24553449210248 | Beanibazar, Nateswar, Uttor vag, Selim Ahmad, (Tawfiq Elahi gram) | 2019-09-17 | LP1002 | 3.5 | 264 | 3.6 | 265 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7056 | 1703.9997 | 37.9313
SYL-B.1.RR.24.1 | 24553449210248 | Beanibazar, Nateswar, Uttor vag, Sohid Uddin, (Tawfiq Elahi gram) | 2019-09-17 | LP1002 | 11.8 | 266 | 11.4 | 267 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7056 | 1703.9997 | 120.1159
SYL-B.1.RR.25.1 | 24524729211591 | Beanibazar, Mewa, South Moholla, Lutfor Rahman,(Opposite South Moholla Central Jame Masjid) | 2019-09-17 | LP1002 | 7.8 | 268 | 7.8 | 269 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7056 | 1703.9997 | 82.1846
SYL-B.1.RR.26.1 | 24524459212035 | Beanibazar, Mewa, South Moholla, Siraj Uddin | 2019-09-17 | LP1002 | 12.3 | 270 | 12.3 | 271 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7056 | 1703.9997 | 129.5987
SYL-B.1.RR.27.1 | 24524219212032 | Beanibazar, Mewa, South Moholla, Masuk Ahmad | 2019-09-17 | LP1002 | 11.3 | 272 | 11.3 | 273 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7056 | 1703.9997 | 119.0622
SYL-B.1.RR.28.1 | 24523329212017 | Beanibazar, Mewa, South Moholla, A. Motaleb | 2019-09-17 | LP1002 | 8.3 | 274 | 8.3 | 275 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7056 | 1703.9997 | 87.4528
SYL-B.1.RR.29.1 | 24503159209203 | Beanibazar, Kosba North, Anowar hosen | 2019-09-18 | LP1002 | 3.6 | 312 | 3.6 | 313 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7008 | 1751.9997 | 37.9313
SYL-B.1.RR.30.1 | 24503409209108 | Beanibazar, Kosba, Boro Bari, A. Hasib Jibon, ( Behind Panjegana Masjid ) | 2019-09-18 | LP1002 | 61.6 | 314 | 61.6 | 315 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 61.6 | 61.6 | 3.696 | 3.696 | 0.0007168 | 100% | 0% | 3.696 | 3.696 | 0.0011869 | 28 | 0.074092 | 0.074092 |  | 0 | 0 | 7008 | 1751.9997 | 649.0472
SYL-B.1.RR.31.1 | 24503409209108 | Beanibazar, Kosba, Boro Bari, Jamal Ahmad, ( Beside Panjegana Masjid ) | 2019-09-18 | LP1002 | 12.1 | 316 | 12.1 | 317 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7008 | 1751.9997 | 127.4914
SYL-B.1.RR.31.2 | 24503409209108 | Beanibazar, Kosba, Boro Bari, Jamal Ahmad, ( Beside Panjegana Masjid ) | 2022-04-24 | NQ1007 | 5.3 | 162 | 5.4 | 163 | 2022-04-24 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 4296 | 1751.9997 | 39.2823
SYL-B.1.RR.32.1 | 24502959209063 | Beanibazar, Kosba, Molla Gosti, Nazim uddin | 2019-09-18 | LP1002 | 5.4 | 320 | 5.4 | 321 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7008 | 1751.9997 | 56.897
SYL-B.1.RR.33.1 | 24502959209063 | Beanibazar, Kosba, Molla Gosti, Aisha Khanom | 2019-09-18 | LP1002 | 14.3 | 322 | 14 | 323 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 7008 | 1751.9997 | 147.5107
SYL-B.1.RR.34.1 | 24502489209110 | Beanibazar, Kosba, VIP Road, Daroga Bari, Hasan | 2019-09-18 | LP1002 | 4.3 | 324 | 4.3 | 325 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7008 | 1751.9997 | 45.3069
SYL-B.1.RR.35.1 | 24502489209110 | Beanibazar, Kosba, VIP Road, Daroga Bari, Saifur Rahman | 2019-09-18 | LP1002 | 9.7 | 326 | 9.7 | 327 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7008 | 1751.9997 | 102.2039
SYL-B.1.RR.36.1 | 24501789209072 | Beanibazar, Kosba, Mahbub, ( Near Kosba Government Praimary School ) | 2019-09-18 | LP1002 | 4.3 | 328 | 4.4 | 329 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6984 | 1775.9997 | 46.3605
SYL-B.1.RR.37.1 | 24501499209051 | Beanibazar, Kosba, Chalikona, Manik | 2019-09-19 | LP1002 | 10 | 366 | 9.9 | 367 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6984 | 1775.9997 | 104.3112
SYL-B.1.RR.38.1 | 24501279209029 | Beanibazar, Kosba, Chalikona, Selim uddin, ( Infront Kosba Community Clinic ) | 2019-09-19 | LP1002 | 7 | 368 | 7 | 369 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6984 | 1775.9997 | 73.7554
SYL-B.1.RR.39.1 | 24501279209029 | Beanibazar, Kosba, Chalikona, A. Hannan, ( Infront Kosba Community Clinic ) | 2019-09-19 | LP1002 | 11.8 | 370 | 11.8 | 371 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6984 | 1775.9997 | 124.3305
SYL-B.1.RR.39.2 | 24501279209029 | Beanibazar, Kosba, Chalikona, A. Hannan, ( Infront Kosba Community Clinic ) | 2021-09-25 | NQ1007 | 3.6 | 39 | 3.6 | 40 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6984 | 1775.9997 | 37.9313
SYL-B.1.RR.40.1 | 24501279209029 | Beanibazar, Kosba, Chalikona, Anowara Begum, ( Infront Kosba Community Clinic ) | 2019-09-19 | LP1002 | 6.7 | 372 | 6.7 | 373 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6984 | 1775.9997 | 70.5944
SYL-B.1.RR.41.1 | 24501019208522 | Beanibazar, Kosba, Chalikona, Kawsar | 2019-09-19 | LP1002 | 4.2 | 374 | 4.2 | 375 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7008 | 1751.9997 | 44.2532
SYL-B.1.RR.42.1 | 24501529208557 | Beanibazar, Sreedhara, Ucha Tilla, A. Korim | 2019-09-19 | LP1002 | 14.1 | 376 | 13.6 | 377 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7008 | 1751.9997 | 143.2961
SYL-B.1.RR.43.1 | 24500899208431 | Beanibazar, Nobang, Uttor Side, A. Sohid | 2019-09-19 | LP1002 | 6.8 | 378 | 6.6 | 379 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7008 | 1751.9997 | 69.5408
SYL-B.1.RR.44.1 | 24500899208431 | Beanibazar, Nobang, Uttor Side, Md. Irman Ali | 2019-09-19 | LP1002 | 10.9 | 380 | 10.9 | 381 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7008 | 1751.9997 | 114.8476
SYL-B.1.RR.45.1 | 24495589208414 | Beanibazar, Nobang, Aptab Ali | 2019-09-21 | LP1002 | 7.6 | 382 | 7.6 | 383 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7008 | 1751.9997 | 80.0773
SYL-B.1.RR.46.1 | 24495179208408 | Beanibazar, Nobang, Major potti, A. Rahman | 2019-09-21 | LP1002 | 10.9 | 384 | 10.9 | 385 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7008 | 1751.9997 | 114.8476
SYL-B.1.RR.47.1 | 24494829208402 | Beanibazar, Nobang, Major potti, Monir | 2019-09-21 | LP1002 | 3 | 386 | 3 | 387 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7008 | 1751.9997 | 31.6094
SYL-B.1.RR.48.1 | 24494829208402 | Beanibazar, Nobang, South Side, A. Sukur | 2019-09-21 | LP1002 | 8.9 | 388 | 8.3 | 389 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7008 | 1751.9997 | 87.4528
SYL-B.1.RR.49.1 | 24475229209145 | Beanibazar, Mollapur, Jalal uddin, ( Opposite Mollapur Union Parisad ) | 2019-09-22 | LP1002 | 9.7 | 394 | 9 | 395 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6840 | 1919.9997 | 94.8283
SYL-B.1.RR.50.1 | 24474669209191 | Beanibazar, Mollapur, Mojom Kha, Md. Motiur Rahman | 2019-09-22 | LP1002 | 12 | 396 | 12 | 397 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6840 | 1919.9997 | 126.4378
SYL-B.1.RR.51.1 | 24540859208195 | Beani Bazar, Charkhai, Nej Adinabad, Tazuddin | 2019-09-16 | LP1002 | 3.5 | 246 | 3.5 | 247 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7056 | 1703.9997 | 36.8777
SYL-B.1.RR.52.1 | 24540859208195 | Beani Bazar, Charkhai, Nej Adinabad, Raziya Bagum | 2019-09-16 | LP1002 | 4.6 | 248 | 4.6 | 249 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7056 | 1703.9997 | 48.4678
SYL-B.1.RR.53.1 | 24540949208199 | Beani Bazar, Charkhai, Nej Adinabad, Jamal Uddin | 2019-09-16 | LP1002 | 3.9 | 250 | 4 | 251 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7056 | 1703.9997 | 42.1459
SYL-B.1.RR.54.1 | 24541289208206 | Beani Bazar, Charkhai, Nej Adinabad, Harun-or-Roshid | 2019-09-16 | LP1002 | 1 | 252 | 1 | 253 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7056 | 1703.9997 | 10.5365
SYL-B.1.RR.55.1 | 24541499208216 | Beani Bazar, Charkhai, Nej Adinabad, Late Mostakim Ali | 2019-09-16 | LP1002 | 1.1 | 254 | 1.1 | 255 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7056 | 1703.9997 | 11.5901
SYL-B.1.RR.56.1 | 24535459208226 | Beani Bazar, Charkhai, Adinabad, Modhur Chok, Abdur Rahim | 2019-09-16 | LP1002 | 3.1 | 258 | 3.1 | 259 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7056 | 1703.9997 | 32.6631
SYL-B.1.RR.57.1 | 24535459208226 | Beani Bazar, Charkhai, Adinabad, Modhur Chok, Abul Khayer Khan | 2019-09-16 | LP1002 | 1.2 | 260 | 1.2 | 261 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7056 | 1703.9997 | 12.6438
SYL-B.1.RR.58.1 | 24503299209372 | Beani Bazar, Boiragi Bazar, Khashir Road, Vangi, Noor Uddin | 2019-09-17 | LP1002 | 4 | 276 | 4.3 | 277 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7008 | 1751.9997 | 45.3069
SYL-B.1.RR.59.1 | 24502899209280 | Beani Bazar, Khasha, Imam Bari Road, Rofique Uddin | 2019-09-17 | LP1002 | 6.5 | 278 | 6.5 | 279 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7008 | 1751.9997 | 68.4871
SYL-B.1.RR.60.1 | 24502909209212 | Beani Bazar, Khasha, Imam Bari Road, A. Hakim | 2019-09-17 | LP1002 | 11.1 | 280 | 11.1 | 281 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7008 | 1751.9997 | 116.9549
SYL-B.1.RR.61.1 | 24502909209212 | Beani Bazar, Khasha, Imam Bari Road, Nur Islam | 2019-09-17 | LP1002 | 7.7 | 282 | 7.7 | 283 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7008 | 1751.9997 | 81.1309
SYL-B.1.RR.61.2 | 24502909209212 | Beani Bazar, Khasha, Imam Bari Road, Nur Islam | 2020-10-17 | MN1032 | 8 | 196 | 8 | 197 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7008 | 1751.9997 | 84.2919
SYL-B.1.RR.62.1 | 24502909209212 | Beani Bazar, Khasha, Imam Bari Road, Balal Rasid | 2019-09-17 | LP1002 | 10.5 | 284 | 10 | 285 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7008 | 1751.9997 | 105.3648
SYL-B.1.RR.63.1 | 24533409209010 | Beani Bazar, Charkhai, Jalal Nagar, Mohiuddin | 2019-09-17 | LP1002 | 13.1 | 286 | 13.1 | 287 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7056 | 1703.9997 | 138.0279
SYL-B.1.RR.64.1 | 24533409209010 | Beani Bazar, Charkhai, Jalal Nagar, Parvas Ahamod | 2019-09-17 | LP1002 | 9 | 288 | 9 | 289 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 1848 | 0 | 5208 | 1703.9997 | 74.8234
SYL-B.1.RR.65.1 | 24533409209010 | Beani Bazar, Charkhai, Jalal Nagar, Jamirul Haque | 2019-09-17 | LP1002 | 11.4 | 290 | 11.2 | 291 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7056 | 1703.9997 | 118.0086
SYL-B.1.RR.66.1 | 24533409209010 | Beani Bazar, Charkhai, Jalal Nagar, Ali Ahamod | 2019-09-17 | LP1002 | 20.5 | 292 | 20.5 | 293 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 20.5 | 20.5 | 1.23 | 1.23 | 0.0007168 | 100% | 0% | 1.23 | 1.23 | 0.0011869 | 28 | 0.024657 | 0.024657 |  | 0 | 0 | 7056 | 1703.9997 | 215.9979
SYL-B.1.RR.67.1 | 24533579209034 | Beani Bazar, Charkhai, Jalal Nagar, Ismil Ali | 2019-09-17 | LP1002 | 9.9 | 294 | 9.9 | 295 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7056 | 1703.9997 | 104.3112
SYL-B.1.RR.68.1 | 24533579209034 | Beani Bazar, Charkhai, Jalal Nagar, Joynal | 2019-09-17 | LP1002 | 7.1 | 296 | 7.1 | 297 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7056 | 1703.9997 | 74.809
SYL-B.1.RR.69.1 | 24534369209059 | Beani Bazar, Charkhai, Jalal Nagar, Solaiman | 2019-09-17 | LP1002 | 11.6 | 298 | 11.6 | 299 | 2022-01-01 | [9 empty] | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0
SYL-B.1.RR.70.1 | 24534539209031 | Beani Bazar, Charkhai, Jalal Nagar, Tomsir Ali | 2019-09-17 | LP1002 | 11.6 | 300 | 11.6 | 301 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7056 | 1703.9997 | 122.2232
SYL-B.1.RR.71.1 | 24534979209018 | Beani Bazar, Charkhai, Jalal Nagar, Motiur Rohaman | 2019-09-17 | LP1002 | 5.8 | 302 | 5.8 | 303 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7056 | 1703.9997 | 61.1116
SYL-B.1.RR.72.1 | 24535259209044 | Beani Bazar, Charkhai, Jalal Nagar, Abdul Khalik | 2019-09-17 | LP1002 | 10.6 | 304 | 10.6 | 305 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7056 | 1703.9997 | 111.6867
SYL-B.1.RR.73.1 | 24535679209035 | Beani Bazar, Charkhai, Jalal Nagar, Aub Ahanod | 2019-09-17 | LP1002 | 3.5 | 306 | 3.5 | 307 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7056 | 1703.9997 | 36.8777
SYL-B.1.RR.74.1 | 24540289209035 | Beani Bazar, Charkhai, Jalal Nagar, Shaidur Rohaman | 2019-09-17 | LP1002 | 7.7 | 308 | 7.7 | 309 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7056 | 1703.9997 | 81.1309
SYL-B.1.RR.75.1 | 24540289209035 | Beani Bazar, Charkhai, Jalal Nagar, Late A. Lotif | 2019-09-17 | LP1002 | 3.1 | 310 | 3.1 | 311 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7056 | 1703.9997 | 32.6631
SYL-B.1.RR.76.1 | 24503059209047 | Beani Bazar, Koshba, Thakur Chan | 2019-09-18 | LP1002 | 15 | 330 | 15.8 | 331 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7008 | 1751.9997 | 166.4764
SYL-B.1.RR.77.1 | 24504089209122 | Beani Bazar, Imam Bari, Koshirbon Hazi Bari, Motiur Rohman | 2019-09-18 | LP1002 | 5.2 | 332 | 5.2 | 333 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7008 | 1751.9997 | 54.7897
SYL-B.1.RR.78.1 | 24504089209122 | Beani Bazar, Imam Bari, Koshirbon Hazi Bari, Islamuddin | 2019-09-18 | LP1002 | 15.1 | 334 | 15.1 | 335 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7008 | 1751.9997 | 159.1009
SYL-B.1.RR.79.1 | 24503379208545 | Beani Bazar, Sreedhara, Shabuddin, (Back Side of Primary School) | 2019-09-18 | LP1002 | 4.7 | 336 | 4.7 | 337 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7008 | 1751.9997 | 49.5215
SYL-B.1.RR.80.1 | 24503789208490 | Beani Bazar, Sreedhara, Kurar Bazaer Road, Md. Maruf Ahamod | 2019-09-19 | LP1002 | 3.1 | 340 | 3.1 | 341 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7008 | 1751.9997 | 32.6631
SYL-B.1.RR.80.2 | 24503789208490 | Beani Bazar, Sreedhara, Kurar Bazaer Road, Md. Maruf Ahamod | 2019-09-19 | LP1002 | 11 | 342 | 11 | 343 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7008 | 1751.9997 | 115.9013
SYL-B.1.RR.81.1 | 24504279208552 | Beani Bazar, North Sreedhara, Ucha Bari, Sunam ar Bari, Anower Islam | 2019-09-19 | LP1002 | 10.3 | 344 | 10.3 | 345 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7008 | 1751.9997 | 108.5258
SYL-B.1.RR.82.1 | 24504279208552 | Beani Bazar, North Sreedhara, Ucha Bari, Sunam ar Gusti, Khorul | 2019-09-19 | LP1002 | 3.3 | 346 | 3.3 | 347 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 4224 | 0 | 2784 | 1751.9997 | 18.0044
SYL-B.1.RR.83.1 | 24504279208552 | Beani Bazar, North Sreedhara, Ucha Bari, Sunam ar Gusti, A. Noor | 2019-09-19 | LP1002 | 4.7 | 350 | 4.7 | 351 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7008 | 1751.9997 | 49.5215
SYL-B.1.RR.84.1 | 24504249208543 | Beani Bazar, North Sreedhara, Ucha Bari, Sunam ar Gusti, Nur Hossain | 2019-09-19 | LP1002 | 3.6 | 352 | 3.6 | 353 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7008 | 1751.9997 | 37.9313
SYL-B.1.RR.85.1 | 24504319208539 | Beani Bazar, North Sreedhara, Ucha Bari, Sunam ar Gusti, Late Foysel | 2019-09-19 | LP1002 | 5.9 | 354 | 5.9 | 355 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7152 | 1607.9997 | 62.1652
SYL-B.1.RR.85.2 | 24504319208539 | Beani Bazar, North Sreedhara, Ucha Bari, Sunam ar Gusti, Late Foysel | 2022-10-26 | NQ1007 | 5.5 | 73 | 5.5 | 74 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 0 | 1607.9997 | 10.6375
SYL-B.1.RR.86.1 | 24504319208592 | Beani Bazar, North Sreedhara, Ucha Bari, Sunam ar Gusti, A. Razzak Villa, H# 68 | 2019-09-19 | LP1002 | 6.2 | 356 | 6.2 | 357 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7008 | 1751.9997 | 65.3262
SYL-B.1.RR.87.1 | 24504769208550 | Beani Bazar, Sreedhara, Dorgi Bari, Shamir Mohol | 2019-09-19 | LP1002 | 3.5 | 358 | 3.5 | 359 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7008 | 1751.9997 | 36.8777
SYL-B.1.RR.88.1 | 24504809208525 | Beani Bazar, Sreedhara, Dorgi Bari, Abdul Ahad | 2019-09-19 | LP1002 | 17.1 | 360 | 16.4 | 361 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 7008 | 1751.9997 | 172.7983
SYL-B.1.RR.89.1 | 24504669208533 | Beani Bazar, Sreedhara, Dorgi Bari, Ali villa, Mohammad Ali | 2019-09-19 | LP1002 | 7 | 362 | 7 | 363 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7008 | 1751.9997 | 73.7554
SYL-B.1.RR.89.2 | 24504669208533 | Beani Bazar, Sreedhara, Dorgi Bari, Ali villa, Mohammad Ali | 2021-01-24 | MN1018 | 10 | 18 | 10.7 | 19 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7008 | 1751.9997 | 112.7403
SYL-B.1.RR.89.3 | 24504669208533 | Beani Bazar, Sreedhara, Dorgi Bari, Ali villa, Mohammad Ali | 2021-01-24 | MN1018 | 10.2 | 20 | 10.2 | 21 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7008 | 1751.9997 | 107.4721
SYL-B.1.RR.90.1 | 24502739208402 | Beani Bazar, West Sreedhara, Hosrot Shayod Shaha (R:) Hafazya Madrasha | 2019-09-19 | LP1002 | 9.8 | 364 | 9.8 | 365 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7152 | 1607.9997 | 103.2575
SYL-B.1.RR.90.2 | 24502739208402 | Beani Bazar, West Sreedhara, Hosrot Shayod Shaha (R:) Hafazya Madrasha | 2022-10-26 | NQ1007 | 11.6 | 76 | 11.5 | 77 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 0 | 1607.9997 | 22.2421
SYL-B.1.RR.91.1 | 24494099208311 | Beani Bazar, Suter Kandi, Tohoil Ali | 2019-09-21 | LP1002 | 6.4 | 390 | 6.4 | 391 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7008 | 1751.9997 | 67.4335
SYL-B.1.RR.92.1 | 24494279208122 | Beani Bazar, Suter Kandi, H # 157, Hazi A Shokur Villa | 2019-09-21 | LP1002 | 5.6 | 392 | 5.6 | 393 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7008 | 1751.9997 | 59.0043
SYL-B.1.RR.93.1 | 24472969209218 | Beani Bazar, Pathon, Anamuddin | 2019-09-22 | LP1002 | 4.6 | 404 | 4.6 | 405 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6840 | 1919.9997 | 48.4678
SYL-B.1.RR.94.1 | 24472969209218 | Beani Bazar, Pathon, Nozrul Islam | 2019-09-22 | LP1002 | 31.3 | 406 | 31.3 | 407 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 31.3 | 31.3 | 1.878 | 1.878 | 0.0007168 | 100% | 0% | 1.878 | 1.878 | 0.0011869 | 28 | 0.037647 | 0.037647 |  | 0 | 0 | 6840 | 1919.9997 | 329.7919
SYL-B.1.RR.95.1 | 24472469209230 | Beani Bazar, Pathon, Ucha Para, Zia Uddin | 2019-09-22 | LP1002 | 11.2 | 408 | 11.2 | 409 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6840 | 1919.9997 | 118.0086
SYL-B.1.RR.96.1 | 24472469209230 | Beani Bazar, Pathon, Ucha Para, Hafaz A. Motin | 2019-09-22 | LP1002 | 18.2 | 412 | 18.2 | 413 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 6840 | 1919.9997 | 191.764
SYL-B.1.RR.97.1 | 24472389209257 | Beani Bazar, Pathon, Ucha Para, Nezamuddin | 2019-09-22 | LP1002 | 11 | 414 | 11 | 415 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6840 | 1919.9997 | 115.9013
SYL-B.1.RR.98.1 | 24473349209113 | Beani Bazar, Pathon, Lakhatuk, Shykot | 2019-09-22 | LP1002 | 11.4 | 416 | 11.4 | 417 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6840 | 1919.9997 | 120.1159
SYL-B.1.RR.99.1 | 24470359209264 | Beani Bazar, Abdullhapur, Abdul Kalam | 2019-09-22 | LP1002 | 9.1 | 420 | 9.1 | 421 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6840 | 1919.9997 | 95.882
SYL-B.1.RR.100.1 | 24465969209322 | Beani Bazar, Abdullhapur, Beside of Mosjid, | 2019-09-22 | LP1002 | 4.7 | 422 | 4.7 | 423 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6840 | 1919.9997 | 49.5215
SYL-B.1.RR.101.1 | 24515929211184 | Biani Bazar, Shaola, Kakardia, Hazi Md. Abdus Sabur | 2019-09-17 | MN1018 | 7.5 | 267 | 7.5 | 268 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7056 | 1703.9997 | 79.0236
SYL-B.1.RR.102.1 | 24515929211184 | Biani Bazar, Shaola, Kakardia, Teradal Bazar, Lukman Chowdury Academy, Shahjahan Kabir | 2019-09-17 | MN1018 | 10.1 | 269 | 9.8 | 270 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7056 | 1703.9997 | 103.2575
SYL-B.1.RR.103.1 | 24520169211119 | Biani Bazar, Shaola, Kakardia, Teradal, Nuruddin | 2019-09-17 | MN1018 | 6.5 | 271 | 6.5 | 272 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7056 | 1703.9997 | 68.4871
SYL-B.1.RR.104.1 | 24520169211119 | Biani Bazar, Shaola, Kakardia, Teradal, Abdul Mukit | 2019-09-17 | MN1018 | 3.4 | 273 | 3.4 | 274 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7056 | 1703.9997 | 35.824
SYL-B.1.RR.105.1 | 24515859211105 | Biani Bazar, Shaola, Kakardia, Juber Ahmed | 2019-09-17 | MN1018 | 4.9 | 275 | 4.9 | 276 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7056 | 1703.9997 | 51.6288
SYL-B.1.RR.106.1 | 24515859211105 | Biani Bazar, Shaola, Kakardia, Teradal Bazar, Teradal, Motiur Rahman | 2019-09-17 | MN1018 | 7.1 | 277 | 7.1 | 278 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7056 | 1703.9997 | 74.809
SYL-B.1.RR.107.1 | 24515959211026 | Biani Bazar, Shaola, Kakardia, Teradal, Hazi Shahbuddin Pilot | 2019-09-17 | MN1018 | 10.6 | 279 | 9.9 | 280 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7056 | 1703.9997 | 104.3112
SYL-B.1.RR.108.1 | 24515619211012 | Biani Bazar, Shaola, Kakardia, Teradal, Jamiruddin | 2019-09-17 | MN1018 | 17.8 | 281 | 17.8 | 282 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 7056 | 1703.9997 | 187.5494
SYL-B.1.RR.109.1 | 24492709209238 | Biani Bazar, Prosova, Word # 6, H # 339 | 2019-09-18 | MN1018 | 32.5 | 283 | 32.5 | 284 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 32.5 | 32.5 | 1.95 | 1.95 | 0.0007168 | 100% | 0% | 1.95 | 1.95 | 0.0011869 | 28 | 0.039091 | 0.039091 |  | 0 | 0 | 6984 | 1775.9997 | 342.4356
SYL-B.1.RR.110.1 | 24492889209230 | Biani Bazar, Prosova, Word # 6, Seifot Ali Complex, Md. Gies Uddin | 2019-09-18 | MN1018 | 9.2 | 285 | 9.2 | 286 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6984 | 1775.9997 | 96.9356
SYL-B.1.RR.111.1 | 24492589209182 | Biani Bazar, Prosova, Word # 6, Abdul Korim | 2019-09-18 | MN1018 | 8.5 | 289 | 7.9 | 290 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6984 | 1775.9997 | 83.2382
SYL-B.1.RR.112.1 | 24492519209174 | Biani Bazar, Prosova, Word # 6, Foisal Ahmed | 2019-09-18 | MN1018 | 24 | 291 | 24.1 | 292 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 24.1 | 24.1 | 1.446 | 1.446 | 0.0007168 | 100% | 0% | 1.446 | 1.446 | 0.0011869 | 28 | 0.028987 | 0.028987 |  | 0 | 0 | 6984 | 1775.9997 | 253.9292
SYL-B.1.RR.113.1 | 24492499209178 | Biani Bazar, Prosova, Word # 6, Somir Uddin | 2019-09-18 | MN1018 | 9.6 | 293 | 8.8 | 294 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6984 | 1775.9997 | 92.721
SYL-B.1.RR.114.1 | 24493399209028 | Biani Bazar, Prosova, Word # 6, Sahabuddin | 2019-09-18 | MN1018 | 9.9 | 295 | 9.5 | 296 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6984 | 1775.9997 | 100.0966
SYL-B.1.RR.114.2 | 24493399209028 | Biani Bazar, Prosova, Word # 6, Sahabuddin | 2019-09-18 | MN1018 | 5.7 | 297 | 5.7 | 298 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6984 | 1775.9997 | 60.0579
SYL-B.1.RR.115.1 | 24493749209087 | Biani Bazar, Hazrat Haydor Shah (RH:) Hafizia Madrasha And Atimkhana | 2019-09-18 | MN1018 | 8.1 | 301 | 8.1 | 302 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7152 | 1607.9997 | 85.3455
SYL-B.1.RR.115.2 | 24493749209087 | Biani Bazar, Hazrat Haydor Shah (RH:) Hafizia Madrasha And Atimkhana | 2022-10-26 | NQ1007 | 2.8 | 78 | 2.8 | 79 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 0 | 1607.9997 | 5.4155
SYL-B.1.RR.116.1 | 24493639209081 | Biani Bazar, Prosova, Protipur, Shakh Bari | 2019-09-18 | MN1018 | 7.6 | 303 | 7.6 | 304 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6984 | 1775.9997 | 80.0773
SYL-B.1.RR.117.1 | 24493429209078 | Biani Bazar, Prosova, Protipur, Jomir Hossain | 2019-09-18 | MN1018 | 5.7 | 305 | 5.7 | 306 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6984 | 1775.9997 | 60.0579
SYL-B.1.RR.118.1 | 24493319209076 | Biani Bazar, Prosova, Protipur, Toimosuddin | 2019-09-18 | MN1018 | 10.6 | 307 | 10.6 | 308 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6984 | 1775.9997 | 111.6867
SYL-B.1.RR.119.1 | 24484699210289 | Biani Bazar, Sarpar Road, Chotodesh Point, Font of Ahad Monjil, Md. Moziruddin | 2019-09-19 | MN1018 | 24.4 | 335 | 24.4 | 336 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 24.4 | 24.4 | 1.464 | 1.464 | 0.0007168 | 100% | 0% | 1.464 | 1.464 | 0.0011869 | 28 | 0.029348 | 0.029348 |  | 0 | 0 | 6936 | 1823.9997 | 257.0901
SYL-B.1.RR.120.1 | 24484699210289 | Biani Bazar, Sarpar Road, Chotodesh Point, Font of Ahad Monjil | 2019-09-19 | MN1018 | 11.3 | 337 | 11.3 | 338 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6936 | 1823.9997 | 119.0622
SYL-B.1.RR.121.1 | 24484489210308 | Biani Bazar, Sarpar Road, Chotodesh Point, Ali Monjil, Hazi Suruj Ali | 2019-09-19 | MN1018 | 7.2 | 339 | 7.2 | 340 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 6936 | 1823.9997 | 75.8627
SYL-B.1.RR.122.1 | 24484639210360 | Biani Bazar, Sarpar Road, Chotodesh Point, Monir Mia | 2019-09-19 | MN1018 | 14.9 | 341 | 14.7 | 342 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 6936 | 1823.9997 | 154.8863
SYL-B.1.RR.123.1 | 24484699210395 | Biani Bazar, Sarpar Road, Chotodesh Point, Abdul Manan | 2019-09-19 | MN1018 | 8 | 343 | 8 | 344 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6936 | 1823.9997 | 84.2919
SYL-B.1.RR.124.1 | 24484699210395 | Biani Bazar, Sarpar Road, Chotodesh Point, Abdus Sohid | 2019-09-19 | MN1018 | 5.9 | 345 | 5.9 | 346 | 2022-01-01 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7152 | 1607.9997 | 62.1652
SYL-B.1.RR.124.2 | 24484699210395 | Biani Bazar, Sarpar Road, Chotodesh Point, Abdus Sohid | 2022-10-26 | NQ1007 | 7.6 | 80 | 7.6 | 81 | 2022-10-26 | 2022-10-26 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 0 | 1607.9997 | 14.6991
SYL-B.1.RR.125.1 | 24485719209235 | Biani Bazar, Main Road, Aowal | 2019-09-21 | MN1018 | 2.9 | 347 | 2.9 | 348 | 2022-01-01 | [9 empty] | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 | 2022-08-16 12:00 | 0 | 0
SYL-B.1.RR.126.1 | 24485699209174 | South Biani Bazar, Supatola, Alom Monjil Back Side, K Anter Prise | 2019-09-21 | MN1018 | 2.5 | 349 | 2.5 | 350 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6840 | 1919.9997 | 26.3412
SYL-B.1.RR.127.1 | 24482919211087 | Biani Bazar, Konegram, Zamal Uddin | 2019-09-21 | MN1018 | 2 | 353 | 1.9 | 354 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6936 | 1823.9997 | 20.0193
SYL-B.1.RR.128.1 | 24482849211063 | Biani Bazar, Konegram, Hazi Md. Islam Uddin | 2019-09-21 | MN1018 | 7 | 355 | 7.1 | 356 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6936 | 1823.9997 | 74.809
SYL-B.1.RR.129.1 | 24482779211092 | Beani Bazar, Sotodesh, Konagram, Asraful Hasan | 2019-09-22 | MN1018 | 11 | 371 | 11 | 372 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 3696 | 0 | 3240 | 1823.9997 | 67.0005
SYL-B.1.RR.130.1 | 24481369211104 | Beani Bazar, Sotodesh, Konagram, Ponsa Bari | 2019-09-22 | MN1018 | 7.9 | 375 | 7.9 | 376 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6936 | 1823.9997 | 83.2382
SYL-B.1.RR.131.1 | 24481369211104 | Beani Bazar, Sotodesh, Konagram, Ponsa Bari | 2019-09-22 | MN1018 | 6.7 | 377 | 6.7 | 378 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6936 | 1823.9997 | 70.5944
SYL-B.1.RR.132.1 | 24481369211104 | Beani Bazar, Sotodesh, Konagram, Ponsa Bari | 2019-09-22 | MN1018 | 3.4 | 379 | 3.4 | 380 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6936 | 1823.9997 | 35.824
SYL-B.1.RR.133.1 | 24481369211104 | Beani Bazar, Sotodesh, Konagram, Ponsa Bari | 2019-09-22 | MN1018 | 6.9 | 381 | 6.3 | 382 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6936 | 1823.9997 | 66.3798
SYL-B.1.RR.134.1 | 24481369211129 | Beani Bazar, Sotodesh, Konagram, Moklesur | 2019-09-22 | MN1018 | 7.9 | 383 | 7.3 | 384 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6936 | 1823.9997 | 76.9163
SYL-B.1.RR.135.1 | 24481709211130 | Beani Bazar, Sotodesh, Konagram, Abdul Haque | 2019-09-22 | MN1018 | 5.8 | 385 | 5.4 | 386 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6936 | 1823.9997 | 56.897
SYL-B.1.RR.136.1 | 24481269211120 | Beani Bazar, Sotodesh, Konagram, Mojiruddin | 2019-09-22 | MN1018 | 6.7 | 387 | 6 | 388 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6936 | 1823.9997 | 63.2189
SYL-B.1.RR.137.1 | 24481149211164 | Beani Bazar, Sotodesh, Konagram, Anower Hosen | 2019-09-22 | MN1018 | 7.1 | 389 | 7.1 | 390 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6936 | 1823.9997 | 74.809
SYL-B.1.RR.138.1 | 24481149211164 | Beani Bazar, Sotodesh, Konagram, Abdul Motin | 2019-09-22 | MN1018 | 5.6 | 391 | 5.6 | 392 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6936 | 1823.9997 | 59.0043
SYL-B.1.RR.139.1 | 24482689211223 | Beani Bazar, Sotodesh, Konagram, Monsur | 2019-09-22 | MN1018 | 7.3 | 393 | 7.3 | 394 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6936 | 1823.9997 | 76.9163
SYL-B.1.RR.140.1 | 24502459210568 | Biani Bazar, Gungadesha Boro Mosque, Neazamuddin | 2019-09-23 | MN1018 | 62.8 | 421 | 63 | 422 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 63 | 63 | 3.78 | 3.78 | 0.0007168 | 100% | 0% | 3.78 | 3.78 | 0.0011869 | 28 | 0.075776 | 0.075776 |  | 0 | 0 | 6960 | 1799.9997 | 663.7983
SYL-B.1.RR.141.1 | 24502459210568 | Biani Bazar, Gungadesha Boro Mosque, Bodrul Haque | 2019-09-23 | MN1018 | 6.2 | 423 | 5.8 | 424 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6960 | 1799.9997 | 61.1116
SYL-B.1.RR.141.2 | 24502459210568 | Biani Bazar, Gungadesha Boro Mosque, Bodrul Haque | 2022-04-24 | NQ1007 | 11.8 | 158 | 11.8 | 159 | 2022-04-24 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 4248 | 1799.9997 | 85.8391
SYL-B.1.RR.142.1 | 24502459210568 | Biani Bazar, Gungadesha Boro Mosque, Samsul Haque | 2019-09-23 | MN1018 | 2.4 | 425 | 2.4 | 426 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6960 | 1799.9997 | 25.2876
SYL-B.1.RR.143.1 | 24502419210539 | Biani Bazar, Gungadesha Boro Mosque, Samsur Rahman | 2019-09-23 | MN1018 | 9.1 | 427 | 9.1 | 428 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6960 | 1799.9997 | 95.882
SYL-B.1.RR.144.1 | 24502419210539 | Biani Bazar, Gungadesha Boro Mosque, Moinuddin | 2019-09-23 | MN1018 | 6.2 | 429 | 6.2 | 430 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6960 | 1799.9997 | 65.3262
SYL-B.1.RR.145.1 | 24502419210539 | Biani Bazar, Gungadesha Boro Mosque, Serajuddin | 2019-09-23 | MN1018 | 8 | 433 | 8 | 434 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6960 | 1799.9997 | 84.2919
SYL-B.1.RR.146.1 | 24502359210539 | Biani Bazar, Gungadesha Boro Mosque, Raisuddin | 2019-09-23 | MN1018 | 9.5 | 437 | 9.5 | 438 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6960 | 1799.9997 | 100.0966
SYL-B.1.RR.147.1 | 24502359210539 | Biani Bazar, Gungadesha Boro Mosque, Islamuddin | 2019-09-23 | MN1018 | 7.9 | 439 | 7.9 | 440 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6960 | 1799.9997 | 83.2382
SYL-B.1.RR.148.1 | 24502359210539 | Biani Bazar, Gungadesha Boro Mosque, Nurun Nessa | 2019-09-23 | MN1018 | 7.6 | 441 | 7.6 | 442 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6960 | 1799.9997 | 80.0773
SYL-B.1.RR.149.1 | 24502059210569 | Biani Bazar, Gungadesha Boro Mosque, Mizanur Rahman | 2019-09-23 | MN1018 | 3 | 443 | 3 | 444 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6960 | 1799.9997 | 31.6094
SYL-B.1.RR.150.1 | 24501939210553 | Biani Bazar, Gungadesha Boro Mosque, Abdul Basid | 2019-09-23 | MN1018 | 1.7 | 445 | 1.7 | 446 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6960 | 1799.9997 | 17.912
SYL-B.1.RR.151.1 | 24533309204131 | Biani Bazar, Sherpur Uttorbag, Kholagram Jame Mosjid Road, Anamul Hoque Asan | 2019-09-15 | MN1018 | 19.9 | 225 | 20 | 226 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 7176 | 1583.9997 | 210.7296
SYL-B.1.RR.152.1 | 24533469204126 | Biani Bazar, Sherpur Uttorbag, Kholagram Jame Mosjid Road, Aklis Ali | 2019-09-15 | MN1018 | 13.1 | 227 | 13.1 | 228 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7176 | 1583.9997 | 138.0279
SYL-B.1.RR.153.1 | 24532849204264 | Biani Bazar, Uttorbag Nosirkhani, Nosirkhani Jame Mosjid Road, Nurul Islam | 2019-09-15 | MN1018 | 2 | 229 | 2 | 230 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7176 | 1583.9997 | 21.073
SYL-B.1.RR.154.1 | 24532849204264 | Biani Bazar, Uttorbag Nosirkhani, Nosirkhani Jame Mosjid Road, Sirazul Islam | 2019-09-15 | MN1018 | 11 | 231 | 11 | 232 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7176 | 1583.9997 | 115.9013
SYL-B.1.RR.155.1 | 24532849204264 | Biani Bazar, Uttorbag Nosirkhani, Nosirkhani Jame Mosjid Road, Nazrul Islam | 2019-09-15 | MN1018 | 5.1 | 235 | 4.6 | 236 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7176 | 1583.9997 | 48.4678
SYL-B.1.RR.156.1 | 24531799204381 | Biani Bazar, Uttorbag Nosirkhani, Uttorbag Tikorpara, Tikorpara Jame Mosjid Road, Nazrul Islam | 2019-09-15 | MN1018 | 10.2 | 237 | 10.2 | 238 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7176 | 1583.9997 | 107.4721
SYL-B.1.RR.157.1 | 24531269205289 | Biani Bazar, Niz Muhammadpur, Niz Muhammadpur Jame Mosjid, Mahmud Chowdury | 2019-09-16 | NQ1000 | 10.7 | 242 | 10.4 | 243 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7176 | 1583.9997 | 109.5794
SYL-B.1.RR.158.1 | 24541409208441 | Biani Bazar, Noakhani Puran Bari, Ilias Ali | 2019-09-16 | NQ1000 | 11.2 | 244 | 11.2 | 245 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7056 | 1703.9997 | 118.0086
SYL-B.1.RR.159.1 | 24542209208403 | Biani Bazar, Adinabad Yousuf Khali, Atab Ali | 2019-09-16 | NQ1000 | 5 | 246 | 5 | 247 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7056 | 1703.9997 | 52.6824
SYL-B.1.RR.160.1 | 24525409211546 | Biani Bazar, Dubag, Mewa Poschim, Forid Uddin Chowdury | 2019-09-17 | MN1018 | 50.2 | 259 | 50.2 | 260 | 2022-01-01 | 2022-10-26 | NQ1007 | 0.6 | 71 | 0.6 | 72 | 2022-10-26 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7152 | 1607.9997
SYL-B.1.RR.161.1 | 24524599212081 | Biani Bazar, Dubag, Mewa Poschim, Mubarok Vila, Ataur Rahman | 2019-09-17 | MN1018 | 12.7 | 261 | 12.7 | 262 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7056 | 1703.9997 | 133.8133
SYL-B.1.RR.162.1 | 24525919212094 | Biani Bazar, Dubag, Mewa, Azmal | 2019-09-17 | MN1018 | 4.4 | 263 | 4.4 | 264 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7056 | 1703.9997 | 46.3605
SYL-B.1.RR.163.1 | 24525919212094 | Biani Bazar, Dubag, Mewa, Sumon | 2019-09-17 | MN1018 | 9.4 | 265 | 9.4 | 266 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7056 | 1703.9997 | 99.0429
SYL-B.1.RR.164.1 | 24493999209099 | Biani Bazar, Fotehpur, Fotehpur Jame Mosjid, Late-Abdul Sattar | 2019-09-18 | MN1018 | 10.7 | 309 | 10.7 | 310 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6984 | 1775.9997 | 112.7403
SYL-B.1.RR.165.1 | 24494079209096 | Biani Bazar, Fotehpur, Fotehpur Jame Mosjid, Ahad Ahmed | 2019-09-18 | MN1018 | 10.4 | 311 | 10.4 | 312 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6984 | 1775.9997 | 109.5794
SYL-B.1.RR.166.1 | 24493739209116 | Biani Bazar, Fotehpur, Near By Fotehpur Jame Mosjid,Nazmul Islam | 2019-09-18 | MN1018 | 4.6 | 313 | 4.5 | 314 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6984 | 1775.9997 | 47.4142
SYL-B.1.RR.167.1 | 24493629209264 | Biani Bazar, Upozela Road, Ward # 3, H # 580, Shohid | 2019-09-18 | MN1018 | 4.9 | 317 | 4.9 | 318 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6984 | 1775.9997 | 51.6288
SYL-B.1.RR.168.1 | 24494489209190 | Biani Bazar, Khasa Pondit Para. Zubayer Monjil | 2019-09-18 | MN1018 | 4.6 | 319 | 4.6 | 320 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6984 | 1775.9997 | 48.4678
SYL-B.1.RR.169.1 | 24494489209190 | Biani Bazar, Khasa Pondit Para. Zubayer Monjil | 2019-09-18 | MN1018 | 7.2 | 321 | 6.8 | 322 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6984 | 1775.9997 | 71.6481
SYL-B.1.RR.170.1 | 24494659209166 | Biani Bazar, Khasa Pondit Para, Ward # 3, H # 535 | 2019-09-18 | MN1018 | 14.2 | 323 | 14.2 | 324 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 6984 | 1775.9997 | 149.618
SYL-B.1.RR.171.1 | 24494809209120 | Biani Bazar, Kosba Noyatilla, Noyatilla Mosjid, Fazlul Haque | 2019-09-18 | MN1018 | 11.6 | 325 | 11.6 | 326 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6984 | 1775.9997 | 122.2232
SYL-B.1.RR.172.1 | 24493559209177 | Biani Bazar, Fotehpur, Hasan Ahmed | 2019-09-19 | MN1018 | 3.3 | 327 | 3.3 | 328 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6984 | 1775.9997 | 34.7704
SYL-B.1.RR.173.1 | 24493079209168 | Biani Bazar, Fotehpur, Masu Kazi | 2019-09-19 | MN1018 | 15.9 | 329 | 15.9 | 330 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6984 | 1775.9997 | 167.5301
SYL-B.1.RR.174.1 | 24493619209282 | Biani Bazar, Poschim Noyagram, Onirbarn R/A, Rohmot Ali Nibas | 2019-09-19 | MN1018 | 6.1 | 331 | 6.1 | 332 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6984 | 1775.9997 | 64.2725
SYL-B.1.RR.175.1 | 24493839209328 | Biani Bazar, Poschim Noyagram, Nazim Commissionar | 2019-09-19 | MN1018 | 12.1 | 333 | 12.1 | 334 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6984 | 1775.9997 | 127.4914
SYL-B.1.RR.176.1 | 24483939210207 | Biani Bazar, Fengram, Lombatikor, Khayrul Islam | 2019-09-21 | MN1018 | 9.5 | 357 | 9.5 | 358 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6936 | 1823.9997 | 100.0966
SYL-B.1.RR.176.2 | 24483939210207 | Biani Bazar, Fengram, Lombatikor, Khayrul Islam | 2019-09-21 | MN1018 | 6.2 | 359 | 6.2 | 360 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6936 | 1823.9997 | 65.3262
SYL-B.1.RR.177.1 | 24484239210166 | Biani Bazar, Fengram, Kazir Bari, Sofur Uddin | 2019-09-21 | MN1018 | 10.3 | 361 | 10 | 362 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6936 | 1823.9997 | 105.3648
SYL-B.1.RR.178.1 | 24483309210150 | Biani Bazar, Fengram, Fengram Chandragram Bagon Govt. Primary School, Abdul Salam | 2019-09-21 | MN1018 | 10.6 | 363 | 10.6 | 364 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6936 | 1823.9997 | 111.6867
SYL-B.1.RR.178.2 | 24483309210150 | Biani Bazar, Fengram, Fengram Chandragram Bagon Govt. Primary School, Abdul Salam | 2019-09-21 | MN1018 | 11.2 | 365 | 11.2 | 366 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6936 | 1823.9997 | 118.0086
SYL-B.1.RR.179.1 | 24483309210150 | Biani Bazar, Fengram, Fengram Chandragram Bagon Govt. Primary School, Ibrahim Ali | 2019-09-21 | MN1018 | 10.4 | 367 | 10.4 | 368 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6936 | 1823.9997 | 109.5794
SYL-B.1.RR.180.1 | 24482509210318 | Biani Bazar, Bagon, Mazor Bari, Liakot Ali | 2019-09-21 | MN1018 | 10.6 | 369 | 10.6 | 370 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6936 | 1823.9997 | 111.6867
SYL-B.1.RR.181.1 | 24503279210522 | Biani Bazar, Ghungadia, Dorgatila, Dotor Bari, Kausar(Anowara Begum) | 2019-09-22 | MN1018 | 11.3 | 395 | 11.3 | 396 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6960 | 1799.9997 | 119.0622
SYL-B.1.RR.182.1 | 24503219210527 | Biani Bazar, Ghungadia, Dorgatila, Dotor Bari, Helal Uddin | 2019-09-22 | MN1018 | 4.9 | 399 | 4.9 | 400 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6960 | 1799.9997 | 51.6288
SYL-B.1.RR.183.1 | 24495969210224 | Biani Bazar, Borodesh, Near By Borodesh Central Mosjid, Md Shihab Uddin | 2019-09-23 | MN1018 | 7.8 | 401 | 7.8 | 402 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6960 | 1799.9997 | 82.1846
SYL-B.1.RR.184.1 | 24495969210224 | Biani Bazar, Borodesh, Near By Borodesh Central Mosjid, Emad Uddin | 2019-09-23 | MN1018 | 4.8 | 403 | 4.8 | 404 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6960 | 1799.9997 | 50.5751
SYL-B.1.RR.185.1 | 24500169210182 | Biani Bazar, West Ghungadia, Napiter Bari, Md. Moynul Haque Khan | 2019-09-23 | MN1018 | 9.1 | 405 | 9 | 406 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6960 | 1799.9997 | 94.8283
SYL-B.1.RR.186.1 | 24500359210198 | Biani Bazar, West Ghungadia, Borodesh Major Bari, Islam Vila | 2019-09-23 | MN1018 | 7.3 | 407 | 7.3 | 408 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6960 | 1799.9997 | 76.9163
SYL-B.1.RR.187.1 | 24500459210221 | Biani Bazar, West Ghungadia, Borodesh, Hasan Ali | 2019-09-23 | MN1018 | 10.4 | 409 | 10.4 | 410 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6960 | 1799.9997 | 109.5794
SYL-B.1.RR.188.1 | 24500719210127 | Biani Bazar, West Ghungadia, Chowdury Bari, Asraful Zaman Babul | 2019-09-23 | MN1018 | 10.5 | 411 | 10.5 | 412 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6960 | 1799.9997 | 110.6331
SYL-B.1.RR.189.1 | 24495079210260 | Biani Bazar, Borodesh, Noya Bari, Suzat Bokth | 2019-09-23 | MN1018 | 10.5 | 413 | 10.5 | 414 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6960 | 1799.9997 | 110.6331
SYL-B.1.RR.190.1 | 24495079210260 | Biani Bazar, Borodesh, Noya Bari, Suzat Bokth | 2019-09-23 | MN1018 | 11.2 | 415 | 11.2 | 416 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6960 | 1799.9997 | 118.0086
SYL-B.1.RR.191.1 | 24495349210356 | Biani Bazar, Borodesh, Boro Bari, Ali Ahmed | 2019-09-23 | MN1018 | 3.9 | 417 | 3.9 | 418 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6960 | 1799.9997 | 41.0923
SYL-B.1.RR.192.1 | 24495349210356 | Biani Bazar, Borodesh, Boro Bari, Rafiqul Islam | 2019-09-23 | MN1018 | 8.8 | 419 | 8.8 | 420 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6960 | 1799.9997 | 92.721
SYL-B.1.RR.193.1 | 24492849209145 | Biani Bazar, Fotehpur, Dokshin Tilla, Master Abdul Malik | 2019-09-24 | MN1018 | 4.1 | 450 | 4.1 | 451 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6984 | 1775.9997 | 43.1996
SYL-B.1.RR.194.1 | 24492849209145 | Biani Bazar, Fotehpur, Dokshin Tilla, Master Abdul Malik | 2019-09-24 | MN1018 | 6.3 | 452 | 6.4 | 453 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6984 | 1775.9997 | 67.4335
SYL-B.1.RR.195.1 | 24492849209145 | Biani Bazar, Fotehpur, Dokshin Tilla, Master Abdul Malik | 2019-09-24 | MN1018 | 5.5 | 454 | 5.5 | 455 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6984 | 1775.9997 | 57.9506
SYL-B.1.RR.196.1 | 24492849209145 | Biani Bazar, Fotehpur, Dokshin Tilla, Master Abdul Malik | 2019-09-24 | MN1018 | 5.8 | 456 | 5.8 | 457 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6984 | 1775.9997 | 61.1116
SYL-B.1.RR.197.1 | 24493189209138 | Biani Bazar, Fotehpur, Abdul Khalek | 2019-09-24 | MN1018 | 9.9 | 458 | 9.9 | 459 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6984 | 1775.9997 | 104.3112
SYL-B.1.RR.198.1 | 24493169209136 | Biani Bazar, Fotehpur, Muktadir Ali | 2019-09-24 | MN1018 | 10 | 460 | 10 | 461 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6984 | 1775.9997 | 105.3648
SYL-B.1.RR.199.1 | 24493169209136 | Biani Bazar, Fotehpur, Jamaluddin | 2019-09-24 | MN1018 | 6.5 | 462 | 6.5 | 463 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6984 | 1775.9997 | 68.4871
SYL-B.1.RR.200.1 | 24495479210350 | Biani Bazar, Borodesh, Boro Bari, Block-A, Road# 1, Hazi Samsu Mia | 2019-09-24 | MN1018 | 2.8 | 464 | 2.7 | 465 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6960 | 1799.9997 | 28.4485
SYL-B.1.RR.201.1 | 24532599206091 | Sylhet, Beani Bazar, Alinagar, Uttor Chondrogram, Hosen Ahmed | 2019-09-16 | LU1001 | 11.4 | 233 | 11.4 | 234 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7176 | 1583.9997 | 120.1159
SYL-B.1.RR.202.1 | 24532599206091 | Sylhet, Beani Bazar, Alinagar, Uttor Chondrogram, Alauddin | 2019-09-16 | LU1001 | 5.8 | 235 | 5.8 | 236 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7176 | 1583.9997 | 61.1116
SYL-B.1.RR.203.1 | 24532599206091 | Sylhet, Beani Bazar, Alinagar, Uttor Chondrogram, Suruj | 2019-09-16 | LU1001 | 10.5 | 237 | 10.5 | 238 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7176 | 1583.9997 | 110.6331
SYL-B.1.RR.204.1 | 24524999212336 | Sylhet, Beani Bazar, Dubag Bazar, Main Road, Abdul Rakib | 2019-09-17 | LU1001 | 9.2 | 251 | 9.2 | 252 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7056 | 1703.9997 | 96.9356
SYL-B.1.RR.205.1 | 24524849212375 | Sylhet, Beani Bazar, Uttar Dubag, Bablu Masab | 2019-09-17 | LU1001 | 10.3 | 253 | 10.3 | 254 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7056 | 1703.9997 | 108.5258
SYL-B.1.RR.206.1 | 24524179212419 | Sylhet, Beani Bazar, Uttar Dubag, Harun | 2019-09-17 | LU1001 | 4.5 | 255 | 4.5 | 256 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7056 | 1703.9997 | 47.4142
SYL-B.1.RR.207.1 | 24523199212451 | Sylhet, Beani Bazar, Uttar Dubag, Oized | 2019-09-17 | LU1001 | 8.7 | 257 | 8.7 | 258 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7056 | 1703.9997 | 91.6674
SYL-B.1.RR.208.1 | 24522739212430 | Sylhet, Beani Bazar, Uttar Dubag, Serajul | 2019-09-17 | LU1001 | 12 | 259 | 12 | 260 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7056 | 1703.9997 | 126.4378
SYL-B.1.RR.208.2 | 24522739212430 | Sylhet, Beani Bazar, Uttar Dubag, Serajul | 2021-01-31 | MN1018 | 5.8 | 51 | 5.8 | 52 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7056 | 1703.9997 | 61.1116
SYL-B.1.RR.209.1 | 24521709212477 | Sylhet, Beani Bazar, South Dubag, Tarak | 2019-09-17 | LU1001 | 10.3 | 261 | 10.3 | 262 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7056 | 1703.9997 | 108.5258
SYL-B.1.RR.210.1 | 24485549209171 | Sylhet, Beani Bazar, Supatola, Oyas | 2019-09-18 | LU1001 | 10.5 | 275 | 10.5 | 276 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6840 | 1919.9997 | 110.6331
SYL-B.1.RR.211.1 | 24485549209171 | Sylhet, Beani Bazar, Supatola, Nehar | 2019-09-18 | LU1001 | 6.3 | 277 | 6.3 | 278 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6840 | 1919.9997 | 66.3798
SYL-B.1.RR.212.1 | 24485849209140 | Sylhet, Beani Bazar, Supatola, Nondolal | 2019-09-18 | LU1001 | 10.8 | 279 | 10.8 | 280 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6840 | 1919.9997 | 113.794
SYL-B.1.RR.213.1 | 24485489209039 | Sylhet, Beani Bazar, Supatola, Hamidur Rahman | 2019-09-21 | LU1001 | 6.6 | 299 | 6.6 | 300 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6840 | 1919.9997 | 69.5408
SYL-B.1.RR.214.1 | 24485909209024 | Sylhet, Beani Bazar, Supatola, Asad Uddin | 2019-09-21 | LU1001 | 11.3 | 301 | 11.3 | 302 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6840 | 1919.9997 | 119.0622
SYL-B.1.RR.215.1 | 24485909209024 | Sylhet, Beani Bazar, Supatola, Masuk | 2019-09-21 | LU1001 | 8 | 303 | 8 | 304 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6840 | 1919.9997 | 84.2919
SYL-B.1.RR.216.1 | 24485769209021 | Sylhet, Beani Bazar, Supatola, Aman Uddin | 2019-09-21 | LU1001 | 11.5 | 305 | 11.5 | 306 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6840 | 1919.9997 | 121.1695
SYL-B.1.RR.217.1 | 24490049209002 | Sylhet, Beani Bazar, Supatola, Abdul Oyadut | 2019-09-21 | LU1001 | 5.1 | 307 | 5.1 | 308 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6840 | 1919.9997 | 53.7361
SYL-B.1.RR.218.1 | 24490049209002 | Sylhet, Beani Bazar, Supatola, Abdul Karim | 2019-09-21 | LU1001 | 4.2 | 309 | 4.2 | 310 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6840 | 1919.9997 | 44.2532
SYL-B.1.RR.218.2 | 24490049209002 | Sylhet, Beani Bazar, Supatola, Abdul Karim | 2021-01-27 | MN1018 | 38.1 | 29 | 38.1 | 30 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 38.1 | 38.1 | 2.286 | 2.286 | 0.0007168 | 100% | 0% | 2.286 | 2.286 | 0.0011869 | 28 | 0.045826 | 0.045826 |  | 0 | 0 | 6840 | 1919.9997 | 401.4399
SYL-B.1.RR.219.1 | 24490409208593 | Sylhet, Beani Bazar, Supatola, Akkados Ali | 2019-09-21 | LU1001 | 9.3 | 311 | 9.4 | 312 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6840 | 1919.9997 | 99.0429
SYL-B.1.RR.220.1 | 24485689208573 | Sylhet, Beani Bazar, Supatola, Momsad | 2019-09-21 | LU1001 | 12.1 | 313 | 12.2 | 314 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6840 | 1919.9997 | 128.5451
SYL-B.1.RR.220.2 | 24485689208573 | Sylhet, Beani Bazar, Supatola, Momsad | 2022-10-13 | NQ1007 | 12.6 | 67 | 12.6 | 68 | 2022-10-13 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 0 | 1919.9997 | 29.098
SYL-B.1.RR.221.1 | 24484589209062 | Sylhet, Beani Bazar, Supatola, Hosen Ahmed | 2019-09-21 | LU1001 | 10.7 | 315 | 10.7 | 316 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6840 | 1919.9997 | 112.7403
SYL-B.1.RR.222.1 | 24480659209164 | Sylhet, Beani Bazar, Nedonpur, Jahid | 2019-09-22 | LU1001 | 6.2 | 349 | 6.2 | 350 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6840 | 1919.9997 | 65.3262
SYL-B.1.RR.223.1 | 24480659209164 | Sylhet, Beani Bazar, Nedonpur, Aziruddin | 2019-09-22 | LU1001 | 4.1 | 351 | 4.1 | 352 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6840 | 1919.9997 | 43.1996
SYL-B.1.RR.224.1 | 24484629209267 | Sylhet, Beani Bazar, Supatola, Main Road, Mostafur Rahman | 2019-09-22 | LU1001 | 13.3 | 353 | 12.9 | 354 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6840 | 1919.9997 | 135.9206
SYL-B.1.RR.224.2 | 24484629209267 | Sylhet, Beani Bazar, Supatola, Main Road, Mostafur Rahman | 2019-09-22 | LU1001 | 6.4 | 355 | 6.4 | 356 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6840 | 1919.9997 | 67.4335
SYL-B.1.RR.225.1 | 24484119209250 | Sylhet, Beani Bazar, Supatola, Main Road, Rasal Ahamad | 2019-09-22 | LU1001 | 5.2 | 357 | 5.3 | 358 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6840 | 1919.9997 | 55.8434
SYL-B.1.RR.226.1 | 24484119209250 | Sylhet, Beani Bazar, Supatola, Main Road, Monir Uddin | 2019-09-22 | LU1001 | 10.6 | 359 | 10.4 | 360 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6840 | 1919.9997 | 109.5794
SYL-B.1.RR.227.1 | 24484119209250 | Sylhet, Beani Bazar, Supatola, Main Road, Tarak Hosen | 2019-09-22 | LU1001 | 5.5 | 361 | 5.6 | 362 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6840 | 1919.9997 | 59.0043
SYL-B.1.RR.227.2 | 24484119209250 | Sylhet, Beani Bazar, Supatola, Main Road, Tarak Hosen | 2019-09-22 | LU1001 | 7.8 | 363 | 7.8 | 364 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6840 | 1919.9997 | 82.1846
SYL-B.1.RR.228.1 | 24501259210368 | Sylhet, Beani Bazar, Ghungadia, Samsul Haque | 2019-09-23 | LU1001 | 11.1 | 385 | 11.1 | 386 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6960 | 1799.9997 | 116.9549
SYL-B.1.RR.229.1 | 24501449210386 | Sylhet, Beani Bazar, Ghungadia, Rahman Vila | 2019-09-23 | LU1001 | 8.5 | 387 | 8.5 | 388 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6960 | 1799.9997 | 89.5601
SYL-B.1.RR.230.1 | 24501609210431 | Sylhet, Beani Bazar, Ghungadia, Joynal Uddin | 2019-09-23 | LU1001 | 8.8 | 389 | 8.8 | 390 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6960 | 1799.9997 | 92.721
SYL-B.1.RR.231.1 | 24501609210431 | Sylhet, Beani Bazar, Ghungadia, Raib Ali | 2019-09-23 | LU1001 | 6.5 | 391 | 6.5 | 392 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6960 | 1799.9997 | 68.4871
SYL-B.1.RR.232.1 | 24501609210431 | Sylhet, Beani Bazar, Ghungadia, Abul Kalam | 2019-09-23 | LU1001 | 9.5 | 393 | 9.5 | 394 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6960 | 1799.9997 | 100.0966
SYL-B.1.RR.233.1 | 24501609210431 | Sylhet, Beani Bazar, Ghungadia, Shabu Mia | 2019-09-23 | LU1001 | 6.3 | 395 | 6.3 | 396 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6960 | 1799.9997 | 66.3798
SYL-B.1.RR.234.1 | 24501739210432 | Sylhet, Beani Bazar, Ghungadia, Shibbir | 2019-09-23 | LU1001 | 7.6 | 397 | 7.6 | 398 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6960 | 1799.9997 | 80.0773
SYL-B.1.RR.235.1 | 24501739210432 | Sylhet, Beani Bazar, Ghungadia, Ali Hosen | 2019-09-23 | LU1001 | 7.7 | 401 | 7.7 | 402 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6960 | 1799.9997 | 81.1309
SYL-B.1.RR.236.1 | 24501179210423 | Sylhet, Beani Bazar, Ghungadia, Nazrul Islam | 2019-09-23 | LU1001 | 10.7 | 403 | 10.7 | 404 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6960 | 1799.9997 | 112.7403
SYL-B.1.RR.237.1 | 24501499210459 | Sylhet, Beani Bazar, Ghungadia, Abdul Latif | 2019-09-23 | LU1001 | 11.2 | 405 | 11.2 | 406 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6960 | 1799.9997 | 118.0086
SYL-B.1.RR.238.1 | 24501499210459 | Sylhet, Beani Bazar, Ghungadia, Kuddus | 2019-09-23 | LU1001 | 9.5 | 407 | 9.5 | 408 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6960 | 1799.9997 | 100.0966
SYL-B.1.RR.239.1 | 24491749209162 | Sylhet, Beani Bazar, Fotepur, Dasgram, Roise Ali | 2019-09-23 | LU1001 | 10.2 | 409 | 9.8 | 410 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6840 | 1919.9997 | 103.2575
SYL-B.1.RR.240.1 | 24481909205534 | Sylhet, Beani Bazar, Tilpara, Monjur Ali | 2019-09-24 | LU1001 | 10.3 | 423 | 10.3 | 424 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6888 | 1871.9997 | 108.5258
SYL-B.1.RR.241.1 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2019-09-24 | LU1001 | 10 | 425 | 10 | 426 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6888 | 1871.9997 | 105.3648
SYL-B.1.RR.242.1 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2019-09-24 | LU1001 | 8.7 | 427 | 8.7 | 428 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6888 | 1871.9997 | 91.6674
SYL-B.1.RR.243.1 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2019-09-26 | LU1001 | 9 | 443 | 9 | 444 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6888 | 1871.9997 | 94.8283
SYL-B.1.RR.244.1 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2019-09-26 | LU1001 | 10.4 | 445 | 10.4 | 446 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6888 | 1871.9997 | 109.5794
SYL-B.1.RR.244.2 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2019-09-26 | LU1001 | 39.1 | 447 | 39.3 | 448 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 39.3 | 39.3 | 2.358 | 2.358 | 0.0007168 | 100% | 0% | 2.358 | 2.358 | 0.0011869 | 28 | 0.04727 | 0.04727 |  | 0 | 0 | 6888 | 1871.9997 | 414.0837
SYL-B.1.RR.245.1 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2019-09-26 | LU1001 | 8.4 | 449 | 8.4 | 450 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 6888 | 1871.9997 | 88.5064
SYL-B.1.RR.245.2 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2021-09-20 | LX1011 | 11.1 | 670 | 11.1 | 671 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6888 | 1871.9997 | 116.9549
SYL-B.1.RR.246.1 | 24475029205495 | Sylhet, Beani Bazar, Matijura, Mohajon Bari | 2019-09-26 | LU1001 | 11.3 | 451 | 11.3 | 452 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6888 | 1871.9997 | 119.0622
SYL-B.1.RR.247.1 | 24474659205460 | Sylhet, Beani Bazar, Matijura, Boro Bari Rasta, Hafiz Uddin | 2019-09-26 | LU1001 | 11.9 | 453 | 11.9 | 454 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6888 | 1871.9997 | 125.3841
SYL-B.1.RR.248.1 | 24474649205341 | Sylhet, Beani Bazar, Matijura, Konar Bari, Mosabbir Hosen | 2019-09-26 | LU1001 | 5.5 | 455 | 5.5 | 456 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6888 | 1871.9997 | 57.9506
SYL-B.1.RR.249.1 | 24474749205298 | Sylhet, Beani Bazar, Matijura, Akram | 2019-09-26 | LU1001 | 10.6 | 457 | 10.6 | 458 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6888 | 1871.9997 | 111.6867
SYL-B.1.RR.250.1 | 24474749205298 | Sylhet, Beani Bazar, Matijura, Monogir Ali | 2019-09-26 | LU1001 | 8.4 | 459 | 7.8 | 460 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6888 | 1871.9997 | 82.1846
SYL-B.1.RR.250.2 | 24474749205298 | Sylhet, Beani Bazar, Matijura, Monogir Ali | 2022-04-17 | LU1001 | 21.4 | 163 | 21 | 164 | 2022-04-17 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 21 | 21 | 1.26 | 1.26 | 0.0007168 | 100% | 0% | 1.26 | 1.26 | 0.0011869 | 28 | 0.025259 | 0.025259 |  | 0 | 0 | 4344 | 1871.9997 | 157.008
SYL-B.1.RR.251.1 | 24531729206499 | Beanibazar, Khasha Gram, Shalay Ahammed Selim | 2019-09-16 | LU1001 | 10.5 | 239 | 10.5 | 240 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7176 | 1583.9997 | 110.6331
SYL-B.1.RR.252.1 | 24530789206543 | Beanibazar, Khasha Gram, Shahinur | 2019-09-16 | LU1001 | 10.3 | 241 | 10.3 | 242 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7176 | 1583.9997 | 108.5258
SYL-B.1.RR.253.1 | 24531049206566 | Beanibazar, Khasha Gram, Jomiruddin | 2019-09-16 | LU1001 | 6.9 | 243 | 6.9 | 244 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7176 | 1583.9997 | 72.7017
SYL-B.1.RR.254.1 | 24530589206458 | Beanibazar, Khasha Gram, Helaluddin | 2019-09-16 | LU1001 | 5.9 | 245 | 5.9 | 246 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7176 | 1583.9997 | 62.1652
SYL-B.1.RR.255.1 | 24530589206458 | Beanibazar, Khasha Gram, Pitu | 2019-09-16 | LU1001 | 5.7 | 247 | 5.7 | 248 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7176 | 1583.9997 | 60.0579
SYL-B.1.RR.256.1 | 24530589206458 | Beanibazar, Khasha Gram, Malekuddin | 2019-09-16 | LU1001 | 10.9 | 249 | 10.9 | 250 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7176 | 1583.9997 | 114.8476
SYL-B.1.RR.257.1 | 24505239209422 | Beanibazar, Khashir Shajipara (Abdullahpur), Chatol Road, Rashid Sarker Villa | 2019-09-17 | LU1001 | 7.6 | 263 | 7.6 | 264 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7008 | 1751.9997 | 80.0773
SYL-B.1.RR.258.1 | 24505049209433 | Beanibazar, Khashir Shajipara (Abdullahpur), Chatol Road, Abdul Motin | 2019-09-17 | LU1001 | 8.8 | 265 | 8.8 | 266 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7008 | 1751.9997 | 92.721
SYL-B.1.RR.259.1 | 24504889209459 | Beanibazar, Khashir Shajipara (Abdullahpur), Chatol Road, Elias Ali | 2019-09-17 | LU1001 | 11 | 267 | 11 | 268 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7008 | 1751.9997 | 115.9013
SYL-B.1.RR.260.1 | 24504939209468 | Beanibazar, Khashir Shajipara (Abdullahpur), Chatol Road, Nazmul Hoq | 2019-09-17 | LU1001 | 10.4 | 269 | 10.2 | 270 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7008 | 1751.9997 | 107.4721
SYL-B.1.RR.261.1 | 24495769209372 | Beanibazar, Khasha, Pondit Para Road, Farukur Islam | 2019-09-17 | LU1001 | 9.1 | 271 | 9.1 | 272 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6984 | 1775.9997 | 95.882
SYL-B.1.RR.261.2 | 24495769209372 | Beanibazar, Khasha, Pondit Para Road, Farukur Islam | 2022-04-25 | NQ1007 | 4.5 | 172 | 4.5 | 173 | 2022-04-25 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 4248 | 1775.9997 | 32.6054
SYL-B.1.RR.262.1 | 24495769209372 | Beanibazar, Khasha, Pondit Para Road, Sha-Jamal | 2019-09-17 | LU1001 | 3.8 | 273 | 3.8 | 274 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6984 | 1775.9997 | 40.0386
SYL-B.1.RR.263.1 | 24495639209331 | Beanibazar, Khasha, Pondit Para, Samsuddin | 2019-09-18 | LU1001 | 10.4 | 281 | 10.4 | 282 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6984 | 1775.9997 | 109.5794
SYL-B.1.RR.264.1 | 24500029209298 | Beanibazar, Khasha, Pondit Para, Babuluddin | 2019-09-18 | LU1001 | 11 | 283 | 10.6 | 284 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6984 | 1775.9997 | 111.6867
SYL-B.1.RR.265.1 | 24495019209359 | Beanibazar, Khasha, Pondit Para Road, Abdur Rahaman | 2019-09-18 | LU1001 | 8.6 | 285 | 8.6 | 286 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6984 | 1775.9997 | 90.6137
SYL-B.1.RR.266.1 | 24495019209359 | Beanibazar, Khasha, Pondit Para Road, Nurun Nesa | 2019-09-18 | LU1001 | 10.7 | 287 | 10.7 | 288 | 2022-01-01 | 2022-10-26 | NQ1007 | 1.3 | 82 | 1.3 | 83 | 2022-10-26 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7152 | 1607.9997
SYL-B.1.RR.267.1 | 24495019209359 | Beanibazar, Khasha, Pondit Para Road, Azaduddin | 2019-09-18 | LU1001 | 5.2 | 289 | 5.2 | 290 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6984 | 1775.9997 | 54.7897
SYL-B.1.RR.268.1 | 24484399210252 | Beanibazar, Chotodesh, Sharopar Road, Formuz Ali | 2019-09-19 | LU1001 | 9.6 | 291 | 9.6 | 292 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6936 | 1823.9997 | 101.1502
SYL-B.1.RR.269.1 | 24484399210252 | Beanibazar, Chotodesh, Sharopar Road, Abdul Malik | 2019-09-19 | LU1001 | 7.4 | 293 | 7.4 | 294 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6936 | 1823.9997 | 77.97
SYL-B.1.RR.270.1 | 24484979210285 | Beanibazar, Chotodesh, Mollatilakor, Moynul Hoq Villa | 2019-09-19 | LU1001 | 15.7 | 295 | 15.7 | 296 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 6936 | 1823.9997 | 165.4228
SYL-B.1.RR.271.1 | 24484979210285 | Beanibazar, Chotodesh, Mollatilakor, Abdul Hakim | 2019-09-19 | LU1001 | 8.2 | 297 | 8.2 | 298 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6936 | 1823.9997 | 86.3991
SYL-B.1.RR.272.1 | 24485289210282 | Beanibazar, Chotodesh, Sofritilla, Chanohor | 2019-09-21 | LU1001 | 5.9 | 317 | 5.5 | 318 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6936 | 1823.9997 | 57.9506
SYL-B.1.RR.273.1 | 24485369210305 | Beanibazar, Chotodesh, Sofritilla, Abdul Hekim | 2019-09-21 | LU1001 | 12.5 | 319 | 12.5 | 320 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6936 | 1823.9997 | 131.706
SYL-B.1.RR.274.1 | 24485409210310 | Beanibazar, Chotodesh, Sofritilla, Matabul | 2019-09-21 | LU1001 | 10 | 321 | 10 | 322 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6936 | 1823.9997 | 105.3648
SYL-B.1.RR.275.1 | 24485409210310 | Beanibazar, Chotodesh, Sofritilla, Toibur Rahaman | 2019-09-21 | LU1001 | 12.1 | 323 | 12.1 | 324 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6936 | 1823.9997 | 127.4914
SYL-B.1.RR.276.1 | 24485409210310 | Beanibazar, Chotodesh, Sofritilla, Fayjur Rahaman | 2019-09-21 | LU1001 | 12 | 325 | 12 | 326 | 2022-01-01 | [9 empty] | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0
SYL-B.1.RR.277.1 | 24485409210310 | Beanibazar, Chotodesh, Sofritilla, Abdul Sukkur | 2019-09-21 | LU1001 | 12.5 | 327 | 12.5 | 328 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6936 | 1823.9997 | 131.706
SYL-B.1.RR.278.1 | 24485889210298 | Beanibazar, Chotodesh, Sofritilla, Abdul Hannan | 2019-09-21 | LU1001 | 6.1 | 331 | 6.3 | 332 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6936 | 1823.9997 | 66.3798
SYL-B.1.RR.279.1 | 24490099210297 | Beanibazar, Chotodesh, Sofritilla, MD. Salauddin | 2019-09-21 | LU1001 | 4.6 | 333 | 4.6 | 334 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6936 | 1823.9997 | 48.4678
SYL-B.1.RR.280.1 | 24490209210306 | Beanibazar, Chotodesh, Malitikor, Abdul Latif | 2019-09-21 | LU1001 | 11.6 | 335 | 11.6 | 336 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6936 | 1823.9997 | 122.2232
SYL-B.1.RR.281.1 | 24490209210306 | Beanibazar, Chotodesh, Malitikor, Abdul Samad | 2019-09-21 | LU1001 | 5.4 | 337 | 5.4 | 338 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6936 | 1823.9997 | 56.897
SYL-B.1.RR.282.1 | 24490279210354 | Beanibazar, Chotodesh, Malitikor, Azir Uddin | 2019-09-21 | LU1001 | 13.8 | 341 | 13.8 | 342 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 6936 | 1823.9997 | 145.4034
SYL-B.1.RR.283.1 | 24490279210354 | Beanibazar, Chotodesh, Malitikor, Mashukur Rahaman | 2019-09-21 | LU1001 | 3.7 | 343 | 3.7 | 344 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6936 | 1823.9997 | 38.985
SYL-B.1.RR.284.1 | 24490529210378 | Beanibazar, Chotodesh, Hazitila, Sawkot Alam | 2019-09-21 | LU1001 | 10.9 | 345 | 10.9 | 346 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6936 | 1823.9997 | 114.8476
SYL-B.1.RR.285.1 | 24490529210378 | Beanibazar, Chotodesh, Hazitila, Hannan | 2019-09-21 | LU1001 | 10 | 347 | 9.5 | 348 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6936 | 1823.9997 | 100.0966
SYL-B.1.RR.286.1 | 24501189210174 | Beanibazar, Ghungadia, Kazir Bazar Road, Fazlul Hoq | 2019-09-22 | LU1001 | 17.2 | 365 | 16.9 | 366 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 6960 | 1799.9997 | 178.0665
SYL-B.1.RR.287.1 | 24502189210261 | Beanibazar, Ghungadia, Fulbari, Amir Uddin | 2019-09-22 | LU1001 | 9.1 | 367 | 9.1 | 368 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6960 | 1799.9997 | 95.882
SYL-B.1.RR.288.1 | 24502229210224 | Beanibazar, Ghungadia, Fulbari, Fokor Uddin | 2019-09-22 | LU1001 | 4.1 | 369 | 4.1 | 370 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6960 | 1799.9997 | 43.1996
SYL-B.1.RR.289.1 | 24502229210224 | Beanibazar, Ghungadia, Fulbari, Rafiq Uddin | 2019-09-22 | LU1001 | 6.4 | 371 | 6.4 | 372 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6960 | 1799.9997 | 67.4335
SYL-B.1.RR.290.1 | 24495099209485 | Beanibazar,Khasha, Sahidtila, Hazi Murtuz Ali | 2019-09-23 | LU1001 | 6.7 | 373 | 6.7 | 374 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6960 | 1799.9997 | 70.5944
SYL-B.1.RR.291.1 | 24495359209591 | Beanibazar,Khasha, Sahidtila, MD. Bodrul Islam | 2019-09-23 | LU1001 | 3.3 | 375 | 3.3 | 376 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 6960 | 1799.9997 | 34.7704
SYL-B.1.RR.292.1 | 24495149209589 | Beanibazar,Khasha, Sahidtila, Foyzul Hoq | 2019-09-23 | LU1001 | 11.4 | 377 | 11.4 | 378 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6960 | 1799.9997 | 120.1159
SYL-B.1.RR.293.1 | 24502349210290 | Beanibazar, Ghungadia, Fulbari, Abdul Motin | 2019-09-23 | LU1001 | 11.8 | 379 | 11.8 | 380 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6960 | 1799.9997 | 124.3305
SYL-B.1.RR.293.2 | 24502349210290 | Beanibazar, Ghungadia, Fulbari, Abdul Motin | 2021-01-26 | LX1011 | 7 | 71 | 7 | 72 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6960 | 1799.9997 | 73.7554
SYL-B.1.RR.294.1 | 24502349210290 | Beanibazar, Ghungadia, Fulbari, Kamrul | 2019-09-23 | LU1001 | 8.8 | 383 | 8.8 | 384 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6960 | 1799.9997 | 92.721
SYL-B.1.RR.295.1 | 24495449210442 | Beanibazar, Borodesh, Hazi Bari, Abdul Ahad | 2019-09-24 | LU1001 | 10.9 | 411 | 10.9 | 412 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6960 | 1799.9997 | 114.8476
SYL-B.1.RR.296.1 | 24495449210442 | Beanibazar, Borodesh, Hazi Bari, Helal Uddin | 2019-09-24 | LU1001 | 11.2 | 415 | 11.2 | 416 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6960 | 1799.9997 | 118.0086
SYL-B.1.RR.297.1 | 24495449210442 | Beanibazar, Borodesh, Hazi Bari, MD. Abdul Jabbar | 2019-09-24 | LU1001 | 10.9 | 417 | 10.9 | 418 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6960 | 1799.9997 | 114.8476
SYL-B.1.RR.298.1 | 24495439210460 | Beanibazar, Borodesh, Hazi Bari, Abdul Mannan | 2019-09-24 | LU1001 | 12.3 | 419 | 12.3 | 420 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6960 | 1799.9997 | 129.5987
SYL-B.1.RR.299.1 | 24495439210460 | Beanibazar, Borodesh, Hazi Bari, Motiur Rahaman | 2019-09-24 | LU1001 | 10.3 | 421 | 10.3 | 422 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6960 | 1799.9997 | 108.5258
SYL-B.1.RR.300.1 | 24475359207089 | Beanibazar, Nalbhor, Shodor Pur, Moin Mia | 2019-09-26 | LU1001 | 6 | 429 | 6 | 430 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6888 | 1871.9997 | 63.2189
SYL-B.1.RR.301.1 | 24533849204114 | Beanibazar, Alinogor, Khalagram, Mollapara, Kala Daroga Shaheber Bari | 2019-09-15 | NQ1000 | 6.7 | 204 | 6.7 | 205 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7176 | 1583.9997 | 70.5944
SYL-B.1.RR.302.1 | 24533849204114 | Beanibazar, Alinogor, Khalagram, Mollapara, Kala Daroga Shaheber Bari | 2019-09-15 | NQ1000 | 12.9 | 206 | 12.9 | 207 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7176 | 1583.9997 | 135.9206
SYL-B.1.RR.302.2 | 24533849204114 | Beanibazar, Alinogor, Khalagram, Mollapara, Kala Daroga Shaheber Bari | 2022-04-27 | NQ1007 | 12.7 | 178 | 12.7 | 179 | 2022-04-27 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 4392 | 1583.9997 | 91.2863
SYL-B.1.RR.303.1 | 24532529204055 | Beanibazar, Sherpur, Babul Khan | 2019-09-15 | NQ1000 | 5.1 | 208 | 5.1 | 209 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7176 | 1583.9997 | 53.7361
SYL-B.1.RR.304.1 | 24531829204056 | Beanibazar, Sherpur, Asnu Chowdhury | 2019-09-15 | NQ1000 | 10.3 | 210 | 10.3 | 211 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7176 | 1583.9997 | 108.5258
SYL-B.1.RR.305.1 | 24531829204056 | Beanibazar, Sherpur, Asfaq Chowdhury | 2019-09-15 | NQ1000 | 10.4 | 212 | 10 | 213 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7176 | 1583.9997 | 105.3648
SYL-B.1.RR.306.1 | 24531949204139 | Beanibazar, Sherpur, North Bhag, Muhibur Rahman | 2019-09-15 | NQ1000 | 11.3 | 214 | 11.3 | 215 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7176 | 1583.9997 | 119.0622
SYL-B.1.RR.307.1 | 24530649204232 | Beanibazar, Raut Bhag, Tikorpara, Alhaz Shamir Ali Bhabon | 2019-09-15 | NQ1000 | 11.8 | 216 | 11.8 | 217 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7176 | 1583.9997 | 124.3305
SYL-B.1.RR.308.1 | 24534449205003 | Beanibazar, Alinogor, Najmul | 2019-09-16 | MN1018 | 8.1 | 239 | 8.1 | 240 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7176 | 1583.9997 | 85.3455
SYL-B.1.RR.309.1 | 24534769204575 | Beanibazar, Alinogor, Jahid Ali | 2019-09-16 | MN1018 | 11.1 | 241 | 11.1 | 242 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7176 | 1583.9997 | 116.9549
SYL-B.1.RR.310.1 | 24532489205197 | Beanibazar, Chandanpur, Abdul Rawf | 2019-09-16 | MN1018 | 5.8 | 243 | 5.8 | 244 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7176 | 1583.9997 | 61.1116
SYL-B.1.RR.311.1 | 24532489205197 | Beanibazar, Chandanpur, Abdul Rawf | 2019-09-16 | MN1018 | 11.1 | 245 | 10.6 | 246 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7176 | 1583.9997 | 111.6867
SYL-B.1.RR.312.1 | 24533249205248 | Beanibazar, Chandanpur, Abdul Hamid | 2019-09-16 | MN1018 | 3.2 | 247 | 3.2 | 248 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7176 | 1583.9997 | 33.7167
SYL-B.1.RR.313.1 | 24533249205248 | Beanibazar, Chandanpur, Najrul Islam | 2019-09-16 | MN1018 | 7.9 | 249 | 7.9 | 250 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7176 | 1583.9997 | 83.2382
SYL-B.1.RR.313.2 | 24533249205248 | Beanibazar, Chandanpur, Najrul Islam | 2021-01-28 | MN1018 | 4.3 | 47 | 4.3 | 48 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7176 | 1583.9997 | 45.3069
SYL-B.1.RR.314.1 | 24525849206088 | Beanibazar, Ramda, Chandogram, Maruf Ahmad | 2019-09-16 | MN1018 | 9.5 | 251 | 9.5 | 252 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7176 | 1583.9997 | 100.0966
SYL-B.1.RR.315.1 | 24525759206087 | Beanibazar, Ramda, Chandogram, Abdul Kaium | 2019-09-16 | MN1018 | 4.6 | 253 | 4.6 | 254 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7176 | 1583.9997 | 48.4678
SYL-B.1.RR.316.1 | 24540389208378 | Beanibazar, Charkhai, Najmul Haque | 2019-09-16 | MN1018 | 8 | 255 | 8.6 | 256 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7056 | 1703.9997 | 90.6137
SYL-B.1.RR.317.1 | 24540389208378 | Beanibazar, Charkhai, Fazlul Haque | 2019-09-16 | MN1018 | 11 | 257 | 10.9 | 258 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7056 | 1703.9997 | 114.8476
SYL-B.1.RR.318.1 | 24525779212173 | Beanibazar, Mewa, East-North Moholla, Somir Khan | 2019-09-17 | NQ1000 | 8.1 | 248 | 8.1 | 249 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7056 | 1703.9997 | 85.3455
SYL-B.1.RR.319.1 | 24525779212173 | Beanibazar, Mewa, East-North Moholla, Khalilur Rahman | 2019-09-17 | NQ1000 | 11.6 | 250 | 11.6 | 251 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7056 | 1703.9997 | 122.2232
SYL-B.1.RR.320.1 | 24525779212173 | Beanibazar, Mewa, East-North Moholla, Israq Ali | 2019-09-17 | NQ1000 | 13.7 | 252 | 13.7 | 253 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7056 | 1703.9997 | 144.3498
SYL-B.1.RR.321.1 | 24524849212108 | Beanibazar, Mewa, South-West Moholla, Faizul | 2019-09-17 | NQ1000 | 10.7 | 254 | 10.7 | 255 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7056 | 1703.9997 | 112.7403
SYL-B.1.RR.322.1 | 24524849212108 | Beanibazar, Mewa, South-West Moholla, Nurul Islam | 2019-09-17 | NQ1000 | 2.5 | 256 | 2.5 | 257 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7056 | 1703.9997 | 26.3412
SYL-B.1.RR.322.2 | 24524849212108 | Beanibazar, Mewa, South-West Moholla, Nurul Islam | 2021-01-31 | LX1011 | 2.8 | 79 | 2.8 | 80 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7056 | 1703.9997 | 29.5021
SYL-B.1.RR.323.1 | 24501749209258 | Beanibazar, Kasba, Khasha, Khasha Khadim Bari | 2019-09-18 | NQ1000 | 13.2 | 266 | 13.2 | 267 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7008 | 1751.9997 | 139.0816
SYL-B.1.RR.324.1 | 24501749209258 | Beanibazar, Kasba, Khasha, Khasha Khadim Bari | 2019-09-18 | NQ1000 | 8.1 | 268 | 8.1 | 269 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7008 | 1751.9997 | 85.3455
SYL-B.1.RR.325.1 | 24501749209258 | Beanibazar, Kasba, Khasha, Khasha Khadim Bari | 2019-09-18 | NQ1000 | 18.3 | 270 | 18.3 | 271 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 18.3 | 18.3 | 1.098 | 1.098 | 0.0007168 | 100% | 0% | 1.098 | 1.098 | 0.0011869 | 28 | 0.022011 | 0.022011 |  | 0 | 0 | 7008 | 1751.9997 | 192.8176
SYL-B.1.RR.326.1 | 24501749209258 | Beanibazar, Kasba, Khasha, Khasha Khadim Bari | 2019-09-18 | NQ1000 | 10.8 | 272 | 10 | 273 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7008 | 1751.9997 | 105.3648
SYL-B.1.RR.327.1 | 24501749209258 | Beanibazar, Kasba, Khasha, Khasha Khadim Bari | 2019-09-18 | NQ1000 | 7.4 | 274 | 7.4 | 275 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7008 | 1751.9997 | 77.97
SYL-B.1.RR.328.1 | 24501749209258 | Beanibazar, Kasba, Khasha, Khasha Khadim Bari | 2019-09-18 | NQ1000 | 12.7 | 276 | 12.7 | 277 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7008 | 1751.9997 | 133.8133
SYL-B.1.RR.329.1 | 24501659209238 | Beanibazar, Kasba, Khasha, Rokon | 2019-09-18 | NQ1000 | 11.2 | 278 | 10.8 | 279 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7008 | 1751.9997 | 113.794
SYL-B.1.RR.330.1 | 24501639209224 | Beanibazar, Kasba, Khasha, Abdul Asib | 2019-09-18 | NQ1000 | 6.4 | 280 | 6.4 | 281 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7008 | 1751.9997 | 67.4335
SYL-B.1.RR.330.2 | 24501639209224 | Beanibazar, Kasba, Khasha, Abdul Asib | 2019-09-18 | NQ1000 | 48.3 | 282 | 46.5 | 283 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 46.5 | 46.5 | 2.79 | 2.79 | 0.0007168 | 100% | 0% | 2.79 | 2.79 | 0.0011869 | 28 | 0.05593 | 0.05593 |  | 0 | 0 | 7008 | 1751.9997 | 489.9464
SYL-B.1.RR.331.1 | 24501569209217 | Beanibazar, Kasba, Khasha, Ziauddin | 2019-09-18 | NQ1000 | 10 | 284 | 9.9 | 285 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7008 | 1751.9997 | 104.3112
SYL-B.1.RR.332.1 | 24501569209217 | Beanibazar, Kasba, Khasha, Ziauddin | 2019-09-18 | NQ1000 | 5.3 | 286 | 5.3 | 287 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7008 | 1751.9997 | 55.8434
SYL-B.1.RR.333.1 | 24501659209175 | Beanibazar, Kasba, Khasha, Emdadul Haque | 2019-09-19 | NQ1000 | 2.4 | 306 | 2.4 | 307 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7008 | 1751.9997 | 25.2876
SYL-B.1.RR.334.1 | 24502079209131 | Beanibazar, Kasba, Khasha, Nujrul Islam | 2019-09-19 | NQ1000 | 9.9 | 308 | 9.9 | 309 | 2022-01-01 | [9 empty] | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0
SYL-B.1.RR.334.2 | 24502079209131 | Beanibazar, Kasba, Khasha, Nujrul Islam | 2019-09-19 | NQ1000 | 8.8 | 310 | 8.9 | 311 | 2022-01-01 | [9 empty] | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0
SYL-B.1.RR.335.1 | 24501449209118 | Beanibazar, Kasba, Mulair Gusthi, Alauddin | 2019-09-19 | NQ1000 | 10.8 | 312 | 10.8 | 313 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6984 | 1775.9997 | 113.794
SYL-B.1.RR.336.1 | 24500939209188 | Beanibazar, Kasba, Mulair Gusthi, Faridul Alam | 2019-09-19 | NQ1000 | 8.7 | 314 | 8.7 | 315 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6984 | 1775.9997 | 91.6674
SYL-B.1.RR.337.1 | 24494299209585 | Beanibazar, North Nayagram, Alauddin | 2019-09-19 | NQ1000 | 8.6 | 316 | 8.6 | 317 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6960 | 1799.9997 | 90.6137
SYL-B.1.RR.338.1 | 24494159210102 | Beanibazar, North Nayagram, Faruk Ahmad | 2019-09-19 | NQ1000 | 3.6 | 318 | 3.6 | 319 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6960 | 1799.9997 | 37.9313
SYL-B.1.RR.339.1 | 24494159210102 | Beanibazar, North Nayagram, Hazi Tafazzol Ali | 2019-09-19 | NQ1000 | 4.3 | 320 | 4.3 | 321 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6960 | 1799.9997 | 45.3069
SYL-B.1.RR.340.1 | 24494159210102 | Beanibazar, North Nayagram, Asuddor Ali | 2019-09-19 | NQ1000 | 8.9 | 322 | 8.9 | 323 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6960 | 1799.9997 | 93.7747
SYL-B.1.RR.341.1 | 24493969210109 | Beanibazar, North Nayagram, Abdul Mannan | 2019-09-19 | NQ1000 | 5.8 | 324 | 5.8 | 325 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6960 | 1799.9997 | 61.1116
SYL-B.1.RR.341.2 | 24493969210109 | Beanibazar, North Nayagram, Abdul Mannan | 2019-09-19 | NQ1000 | 8.6 | 326 | 8.6 | 327 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6960 | 1799.9997 | 90.6137
SYL-B.1.RR.342.1 | 24484519210006 | Beanibazar, Khasaripara, Hazi Shamsuddin | 2019-09-21 | NQ1000 | 11.3 | 340 | 11.3 | 341 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6936 | 1823.9997 | 119.0622
SYL-B.1.RR.343.1 | 24484369209517 | Beanibazar, Khasaripara, Abdul Khaleq | 2019-09-21 | NQ1000 | 3.6 | 342 | 3.6 | 343 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6936 | 1823.9997 | 37.9313
SYL-B.1.RR.344.1 | 24484009209528 | Beanibazar, Khasaripara, Faruk Ahmad | 2019-09-21 | NQ1000 | 10 | 344 | 10 | 345 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6936 | 1823.9997 | 105.3648
SYL-B.1.RR.345.1 | 24482869209451 | Beanibazar, Khasaripara, Shamsul Islam | 2019-09-21 | NQ1000 | 7.9 | 346 | 7.9 | 347 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6936 | 1823.9997 | 83.2382
SYL-B.1.RR.346.1 | 24482869209451 | Beanibazar, Khasaripara, Shamsul Islam | 2019-09-21 | NQ1000 | 15.1 | 348 | 13.9 | 349 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6936 | 1823.9997 | 146.4571
SYL-B.1.RR.347.1 | 24482749209433 | Beanibazar, Nidonpur, Nasiruddin | 2019-09-21 | NQ1000 | 51.6 | 350 | 51.6 | 351 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 51.6 | 51.6 | 3.096 | 3.096 | 0.0007168 | 100% | 0% | 3.096 | 3.096 | 0.0011869 | 28 | 0.062064 | 0.062064 |  | 0 | 0 | 6936 | 1823.9997 | 543.6824
SYL-B.1.RR.348.1 | 24480589209227 | Beanibazar, South Nidonpur, Mainuddin | 2019-09-22 | NQ1000 | 12.4 | 372 | 12.4 | 373 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6840 | 1919.9997 | 130.6524
SYL-B.1.RR.349.1 | 24481169209160 | Beanibazar, South Nidonpur, Nijamul | 2019-09-22 | NQ1000 | 11.2 | 374 | 11.2 | 375 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6840 | 1919.9997 | 118.0086
SYL-B.1.RR.350.1 | 24481159209105 | Beanibazar, Nidonpur, Abdul Kader | 2019-09-22 | NQ1000 | 11.1 | 376 | 11.1 | 377 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6840 | 1919.9997 | 116.9549
SYL-B.1.RR.351.1 | 24534589204489 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Jainal | 2019-09-16 | NQ1000 | 9.2 | 218 | 9.2 | 219 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7176 | 1583.9997 | 96.9356
SYL-B.1.RR.352.1 | 24534509204489 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Dilu Mia | 2019-09-16 | NQ1000 | 4.2 | 224 | 4.2 | 225 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7176 | 1583.9997 | 44.2532
SYL-B.1.RR.353.1 | 24534509204489 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Jabul | 2019-09-16 | NQ1000 | 4.9 | 228 | 4.9 | 229 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7176 | 1583.9997 | 51.6288
SYL-B.1.RR.354.1 | 24533879204520 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Mojid Ali | 2019-09-16 | NQ1000 | 12.1 | 230 | 12.7 | 231 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7176 | 1583.9997 | 133.8133
SYL-B.1.RR.355.1 | 24533879204520 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Azid Ali | 2019-09-16 | NQ1000 | 13.5 | 232 | 13.5 | 233 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7176 | 1583.9997 | 142.2425
SYL-B.1.RR.356.1 | 24533589204504 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Abdul Motin | 2019-09-16 | NQ1000 | 4.8 | 234 | 4.7 | 235 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7176 | 1583.9997 | 49.5215
SYL-B.1.RR.357.1 | 24533589204504 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Rofiq Uddin | 2019-09-16 | NQ1000 | 9.3 | 236 | 9.4 | 237 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7176 | 1583.9997 | 99.0429
SYL-B.1.RR.358.1 | 24533589204504 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Salik Uddin | 2019-09-16 | NQ1000 | 4.7 | 238 | 4.7 | 239 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7176 | 1583.9997 | 49.5215
SYL-B.1.RR.359.1 | 24532329204500 | Bianibazar, Alinagor, Uttorvag, Nowagram Road, Rosub Ali | 2019-09-16 | NQ1000 | 4.2 | 240 | 4.2 | 241 | 2022-01-01 | 2022-10-27 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7176 | 1583.9997 | 44.2532
SYL-B.1.RR.360.1 | 24504229209440 | Bianibazar, Abdullah Pur, Kosir Nowa Bari, Fokrul Islam | 2019-09-17 | NQ1000 | 17.9 | 258 | 17.9 | 259 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 7008 | 1751.9997 | 188.603
SYL-B.1.RR.361.1 | 24504259209453 | Bianibazar, Abdullah Pur, Kosir Nowa Bari, Haris Ali | 2019-09-17 | NQ1000 | 8.7 | 260 | 8.7 | 261 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7008 | 1751.9997 | 91.6674
SYL-B.1.RR.362.1 | 24504099209382 | Bianibazar, Abdullah Pur, Near CNG Pump, Abul Kalam | 2019-09-17 | NQ1000 | 68.7 | 264 | 68.7 | 265 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 68.7 | 68.7 | 4.122 | 4.122 | 0.0007168 | 100% | 0% | 4.122 | 4.122 | 0.0011869 | 28 | 0.082632 | 0.082632 |  | 0 | 0 | 7008 | 1751.9997 | 723.8563
SYL-B.1.RR.363.1 | 24502079209232 | Bianibazar, Kosba, Kuar Par, Mostak | 2019-09-18 | NQ1000 | 13 | 288 | 13 | 289 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7008 | 1751.9997 | 136.9743
SYL-B.1.RR.363.2 | 24502079209232 | Bianibazar, Kosba, Kuar Par, Mostak | 2019-09-18 | NQ1000 | 11 | 290 | 11 | 291 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7008 | 1751.9997 | 115.9013
SYL-B.1.RR.364.1 | 24502169209249 | Bianibazar, Kosba, Kuar Par, Mohammad Shaiful Islam | 2019-09-18 | NQ1000 | 8.8 | 292 | 8.8 | 293 | 2022-01-01 | 2022-10-20 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7008 | 1751.9997 | 92.721
SYL-B.1.RR.365.1 | 24500969209151 | Bianibazar, South Kosba, Delower Hossain | 2019-09-18 | NQ1000 | 10.6 | 294 | 10.8 | 295 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6984 | 1775.9997 | 113.794
SYL-B.1.RR.366.1 | 24500759209168 | Bianibazar, South Kosba, Jomshed Ali | 2019-09-18 | NQ1000 | 10.8 | 296 | 10.8 | 297 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6984 | 1775.9997 | 113.794
SYL-B.1.RR.367.1 | 24500759209168 | Bianibazar, South Kosba, Faysal Ahmed | 2019-09-18 | NQ1000 | 18.9 | 298 | 18.9 | 299 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6984 | 1775.9997 | 199.1395
SYL-B.1.RR.368.1 | 24500529209174 | Bianibazar, South Kosba, Tota Mia | 2019-09-18 | NQ1000 | 3.8 | 300 | 3.8 | 301 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6984 | 1775.9997 | 40.0386
SYL-B.1.RR.369.1 | 24500509209186 | Bianibazar, South Kosba, Ataur Rahman | 2019-09-18 | NQ1000 | 10.3 | 304 | 10.3 | 305 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6984 | 1775.9997 | 108.5258
SYL-B.1.RR.370.1 | 24484889209486 | Bianibazar, Khasari Para, Hibju Rahman Gate, Abdur Roshid | 2019-09-19 | NQ1000 | 2.6 | 328 | 2.6 | 329 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6936 | 1823.9997 | 27.3949
SYL-B.1.RR.371.1 | 24484719209461 | Bianibazar, Khasari Para, Hibju Rahman Gate, Joynul Haque(Senaj) | 2019-09-19 | NQ1000 | 16 | 330 | 16 | 331 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6936 | 1823.9997 | 168.5837
SYL-B.1.RR.372.1 | 24490439209482 | Bianibazar, Khasari Para, Near Mosque, Elis Ali | 2019-09-19 | NQ1000 | 9.5 | 332 | 9.2 | 333 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6936 | 1823.9997 | 96.9356
SYL-B.1.RR.373.1 | 24490439209482 | Bianibazar, Khasari Para, Near Mosque, Eashak Ali | 2019-09-19 | NQ1000 | 10.9 | 334 | 11.2 | 335 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6936 | 1823.9997 | 118.0086
SYL-B.1.RR.374.1 | 24490899209553 | Bianibazar, Khasari Para, Hazi Surot Ali | 2019-09-19 | NQ1000 | 10.7 | 336 | 10.7 | 337 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6936 | 1823.9997 | 112.7403
SYL-B.1.RR.375.1 | 24490899209553 | Bianibazar, Khasari Para, Chand Ali | 2019-09-19 | NQ1000 | 3.7 | 338 | 3.7 | 339 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6936 | 1823.9997 | 38.985
SYL-B.1.RR.376.1 | 24481239209494 | Bianibazar, Chandrogram, Near Chandrogram Mosque, Sahed | 2019-09-21 | NQ1000 | 10.3 | 352 | 10.6 | 353 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6936 | 1823.9997 | 111.6867
SYL-B.1.RR.377.1 | 24481239209494 | Bianibazar, Chandrogram, Near Chandrogram Mosque, Soforul Islam | 2019-09-21 | NQ1000 | 5.7 | 354 | 5.7 | 355 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 6936 | 1823.9997 | 60.0579
SYL-B.1.RR.378.1 | 24481729209519 | Bianibazar, Chandrogram, Beside Chandrogram Mosque, Jakir Hossain | 2019-09-21 | NQ1000 | 11.2 | 356 | 11.2 | 357 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6936 | 1823.9997 | 118.0086
SYL-B.1.RR.379.1 | 24482329210001 | Bianibazar, Chandrogram, Abdul Khalek | 2019-09-21 | NQ1000 | 15.7 | 358 | 15.4 | 359 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6936 | 1823.9997 | 162.2618
SYL-B.1.RR.379.2 | 24482329210001 | Bianibazar, Chandrogram, Abdul Khalek | 2021-01-27 | MN1018 | 7.6 | 37 | 7.1 | 38 | 2022-01-01 | 2022-10-17 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6936 | 1823.9997 | 74.809
SYL-B.1.RR.380.1 | 24482139209187 | Bianibazar, Nidonpur, Hazi Para Road, Iqbal Hossain | 2019-09-21 | NQ1000 | 12.7 | 360 | 12.3 | 361 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6840 | 1919.9997 | 129.5987
SYL-B.1.RR.380.2 | 24482139209187 | Bianibazar, Nidonpur, Hazi Para Road, Iqbal Hossain | 2019-09-21 | NQ1000 | 4.5 | 362 | 4.5 | 363 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6840 | 1919.9997 | 47.4142
SYL-B.1.RR.381.1 | 24482259209155 | Bianibazar, Nidonpur, Hazi Para Road, Pollob Chairman | 2019-09-21 | NQ1000 | 18.2 | 366 | 18.2 | 367 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 6840 | 1919.9997 | 191.764
SYL-B.1.RR.381.2 | 24482259209155 | Bianibazar, Nidonpur, Hazi Para Road, Pollob Chairman | 2019-09-21 | NQ1000 | 7.7 | 368 | 7.7 | 369 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6840 | 1919.9997 | 81.1309
SYL-B.1.RR.382.1 | 24482229209145 | Bianibazar, Nidonpur, Hazi Para Road, Motin Molla | 2019-09-21 | NQ1000 | 4.6 | 370 | 4.6 | 371 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6840 | 1919.9997 | 48.4678
SYL-B.1.RR.383.1 | 24464179209344 | Bianibazar, Abdullahapur, Azim Uddin | 2019-09-22 | NQ1000 | 4.8 | 392 | 4.8 | 393 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6840 | 1919.9997 | 50.5751
SYL-B.1.RR.384.1 | 24463559209207 | Bianibazar, Abdullahapur, Habibur Rahman | 2019-09-22 | NQ1000 | 10 | 394 | 9.8 | 395 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6840 | 1919.9997 | 103.2575
SYL-B.1.RR.385.1 | 24463379209199 | Bianibazar, Abdullahapur, Captain Mostak Ahmed | 2019-09-22 | NQ1000 | 2.1 | 396 | 2.1 | 397 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 6840 | 1919.9997 | 22.1266
SYL-B.1.RR.386.1 | 24462969209197 | Bianibazar, Abdullahapur, Baroigram Bazar, Abdul Mannan | 2019-09-22 | NQ1000 | 9.8 | 398 | 9.4 | 399 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6840 | 1919.9997 | 99.0429
SYL-B.1.RR.387.1 | 24462909209244 | Bianibazar, Abdullahapur, Baroigram Bazar, Ahmed Hossain Shopon | 2019-09-22 | NQ1000 | 9.1 | 400 | 9.1 | 401 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6840 | 1919.9997 | 95.882
SYL-B.1.RR.387.2 | 24462909209244 | Bianibazar, Abdullahapur, Baroigram Bazar, Ahmed Hossain Shopon | 2021-01-27 | LX1011 | 3.6 | 76 | 3.6 | 77 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6840 | 1919.9997 | 37.9313
SYL-B.1.RR.388.1 | 24463449209257 | Bianibazar, Abdullahapur, Koyes Ahmed | 2019-09-22 | NQ1000 | 10.5 | 402 | 10.1 | 403 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6840 | 1919.9997 | 106.4185
SYL-B.1.RR.389.1 | 24492649209423 | Bianibazar, Noyagram, Noyagram Road, Hazi Abdul Awal | 2019-09-23 | NQ1000 | 2.2 | 406 | 2.2 | 407 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6984 | 1775.9997 | 23.1803
SYL-B.1.RR.390.1 | 24493229209434 | Bianibazar, Noyagram, Noyagram Road, Abdul Based khan | 2019-09-23 | NQ1000 | 5.8 | 410 | 5.8 | 411 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6984 | 1775.9997 | 61.1116
SYL-B.1.RR.391.1 | 24493309209449 | Bianibazar, Noyagram, Noyagram Road, Helal Ahmed | 2019-09-23 | NQ1000 | 11 | 412 | 10.8 | 413 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6984 | 1775.9997 | 113.794
SYL-B.1.RR.392.1 | 24493229209476 | Bianibazar, Noyagram, Noyagram Road, Moklasur Rahman | 2019-09-23 | NQ1000 | 11.7 | 414 | 11.6 | 415 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6984 | 1775.9997 | 122.2232
SYL-B.1.RR.392.2 | 24493229209476 | Bianibazar, Noyagram, Noyagram Road, Moklasur Rahman | 2019-09-23 | NQ1000 | 16.6 | 416 | 16.6 | 417 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 6984 | 1775.9997 | 174.9056
SYL-B.1.RR.393.1 | 24492119209442 | Bianibazar, Middle Noyagram, Nikil Chandro Deb | 2019-09-23 | NQ1000 | 11 | 420 | 11 | 421 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6984 | 1775.9997 | 115.9013
SYL-B.1.RR.394.1 | 24492119209442 | Bianibazar, Middle Noyagram, Pronoy Vuson Deb | 2019-09-23 | NQ1000 | 2.5 | 422 | 2.5 | 423 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6984 | 1775.9997 | 26.3412
SYL-B.1.RR.395.1 | 24492119209442 | Bianibazar, Middle Noyagram, Pijus Deb | 2019-09-23 | NQ1000 | 11.5 | 424 | 11.5 | 425 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6984 | 1775.9997 | 121.1695
SYL-B.1.RR.396.1 | 24492119209442 | Bianibazar, Middle Noyagram, Porimol Deb | 2019-09-23 | NQ1000 | 11.8 | 426 | 12 | 427 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6984 | 1775.9997 | 126.4378
SYL-B.1.RR.397.1 | 24485159207317 | Bianibazar, Mathiura Purbopar, Aminur Rahman | 2019-09-24 | NQ1000 | 14.1 | 440 | 13.7 | 441 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6912 | 1847.9997 | 144.3498
SYL-B.1.RR.398.1 | 24484959207282 | Bianibazar, Mathiura Minarai, Sahab Uddin | 2019-09-24 | NQ1000 | 5.8 | 442 | 5.8 | 443 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6912 | 1847.9997 | 61.1116
SYL-B.1.RR.399.1 | 24484269207241 | Bianibazar, Mathiura Minarai, Lokman Uddin | 2019-09-24 | NQ1000 | 11.8 | 444 | 11.4 | 445 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6912 | 1847.9997 | 120.1159
SYL-B.1.RR.400.1 | 24484089207060 | Bianibazar, Mathiura (Kolagram), Jamal uddin | 2019-09-24 | NQ1000 | 9.9 | 446 | 10.3 | 447 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6912 | 1847.9997 | 108.5258
SYL-B.1.RR.401.1 | 24474669209191 | Beanibazar, Mollapur, Mojom Kha, Oliur Rahman | 2019-09-22 | LP1002 | 12.5 | 398 | 12.5 | 399 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6840 | 1919.9997 | 131.706
SYL-B.1.RR.402.1 | 24474049209185 | Beanibazar, Mollapur, Paton, Dulal | 2019-09-22 | LP1002 | 4.9 | 400 | 4.9 | 401 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6840 | 1919.9997 | 51.6288
SYL-B.1.RR.402.2 | 24474049209185 | Beanibazar, Mollapur, Paton, Dulal | 2022-10-13 | NQ1007 | 14 | 69 | 14 | 70 | 2022-10-13 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 0 | 1919.9997 | 32.3311
SYL-B.1.RR.403.1 | 24474579209426 | Beanibazar, Mollapur, Nidhonpur, Rezaul Islam | 2019-09-22 | LP1002 | 12.5 | 402 | 12.2 | 403 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6840 | 1919.9997 | 128.5451
SYL-B.1.RR.403.2 | 24474579209426 | Beanibazar, Mollapur, Nidhonpur, Rezaul Islam | 2022-04-19 | LU1001 | 7.7 | 174 | 7.7 | 175 | 2022-04-19 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 4248 | 1919.9997 | 57.125
SYL-B.1.RR.404.1 | 24490779207395 | Beanibazar, Mathiura, East Par, Tota Ma | 2019-09-23 | LP1002 | 10.6 | 444 | 10.6 | 445 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6912 | 1847.9997 | 111.6867
SYL-B.1.RR.405.1 | 24491049207358 | Beanibazar, Mathiura, East Par, Sofiq Uddin Mastar | 2019-09-23 | LP1002 | 7.4 | 446 | 7.4 | 447 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6912 | 1847.9997 | 77.97
SYL-B.1.RR.406.1 | 24490999207228 | Beanibazar, Mathiura, East Par, A. Malek, (Near Mathiura Praimary School) | 2019-09-23 | LP1002 | 13.3 | 448 | 13.3 | 449 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6912 | 1847.9997 | 140.1352
SYL-B.1.RR.406.2 | 24490999207228 | Beanibazar, Mathiura, East Par, A. Malek, (Near Mathiura Praimary School) | 2022-04-18 | LU1001 | 6.4 | 168 | 6.4 | 169 | 2022-04-18 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 4344 | 1847.9997 | 47.6653
SYL-B.1.RR.407.1 | 24490999207228 | Beanibazar, Mathiura, East Par, Model School Road, A. Rahim | 2019-09-23 | LP1002 | 5.2 | 452 | 5.2 | 453 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 6912 | 1847.9997 | 54.7897
SYL-B.1.RR.408.1 | 24490789207192 | Beanibazar, Mathiura, East Par, Model School Road, Ashab uddin | 2019-09-23 | LP1002 | 10.6 | 454 | 10.6 | 455 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6912 | 1847.9997 | 111.6867
SYL-B.1.RR.409.1 | 24490789207192 | Beanibazar, Mathiura, East Par, Model School Road, Ayaz Ali | 2019-09-23 | LP1002 | 10.7 | 456 | 10.7 | 457 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6912 | 1847.9997 | 112.7403
SYL-B.1.RR.410.1 | 24490789207192 | Beanibazar, Mathiura, East Par, Model School Road, Foyaz Ali | 2019-09-23 | LP1002 | 8.2 | 458 | 8.3 | 459 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6912 | 1847.9997 | 87.4528
SYL-B.1.RR.411.1 | 24490629207183 | Beani Bazar, Mathiura, East Par, Model School Road, Ali Hosain | 2019-09-24 | LP1002 | 8.8 | 464 | 8.8 | 465 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6912 | 1847.9997 | 92.721
SYL-B.1.RR.412.1 | 24491099207108 | Beani Bazar, Mathiura, East Par, Anam Uddin | 2019-09-24 | LP1002 | 15.6 | 466 | 15.6 | 467 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6912 | 1847.9997 | 164.3691
SYL-B.1.RR.413.1 | 24491039207084 | Beani Bazar, Mathiura, East Par, Jasim Uddin | 2019-09-24 | LP1002 | 10.8 | 468 | 10.2 | 469 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6912 | 1847.9997 | 107.4721
SYL-B.1.RR.414.1 | 24493829206418 | Beani Baza, Mathiura, West Par, Abdul Wahid | 2019-09-24 | LP1002 | 10.2 | 470 | 10.2 | 471 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6912 | 1847.9997 | 107.4721
SYL-B.1.RR.415.1 | 24494089206412 | Beani Baza, Mathiura, West Par, Haji Nazrul Islam | 2019-09-24 | LP1002 | 2.5 | 472 | 2.5 | 473 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6912 | 1847.9997 | 26.3412
SYL-B.1.RR.416.1 | 24493749206214 | Beani Baza, Mathiura, West Par, Purush Pal Road, Abdul Ahad | 2019-09-24 | LP1002 | 4.1 | 474 | 4.1 | 475 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6912 | 1847.9997 | 43.1996
SYL-B.1.RR.417.1 | 24493519206135 | Beani Baza, Mathiura, Purush Pal, Moinuddin | 2019-09-24 | LP1002 | 15.4 | 476 | 15.4 | 477 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 6912 | 1847.9997 | 162.2618
SYL-B.1.RR.418.1 | 24493489206083 | Beani Bazar, Mathiura, Purush Pal, A. Hasib | 2019-09-26 | LP1002 | 18.5 | 504 | 18.6 | 505 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 6912 | 1847.9997 | 195.9786
SYL-B.1.RR.419.1 | 24494509206119 | Beani Bazar, Mathiura, Purush Pal, Sareng Bari, A. Rahim | 2019-09-26 | LP1002 | 4.6 | 506 | 4.6 | 507 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6912 | 1847.9997 | 48.4678
SYL-B.1.RR.420.1 | 24494509206119 | Beani Bazar, Mathiura, Purush Pal, Sareng Bari, Abbas Ali | 2019-09-26 | LP1002 | 42.2 | 508 | 42.2 | 509 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 42.2 | 42.2 | 2.532 | 2.532 | 0.0007168 | 100% | 0% | 2.532 | 2.532 | 0.0011869 | 28 | 0.050758 | 0.050758 |  | 0 | 0 | 6912 | 1847.9997 | 444.6395
SYL-B.1.RR.421.1 | 24493879206086 | Beani Bazar, Mathiura, Purush Pal, Samsuddin Membar Bari, A. Nur | 2019-09-26 | LP1002 | 8.7 | 510 | 8.7 | 511 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 1920 | 0 | 4992 | 1847.9997 | 71.5759
SYL-B.1.RR.422.1 | 24493879206086 | Beani Bazar, Mathiura, Purush Pal, Samsuddin Membar Bari, Harun | 2019-09-26 | LP1002 | 18 | 512 | 18 | 513 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 18 | 18 | 1.08 | 1.08 | 0.0007168 | 100% | 0% | 1.08 | 1.08 | 0.0011869 | 28 | 0.02165 | 0.02165 |  | 0 | 0 | 6912 | 1847.9997 | 189.6567
SYL-B.1.RR.423.1 | 24494339206053 | Beani Bazar, Mathiura, Purush Pal, Ataur Rahman | 2019-09-26 | LP1002 | 25.7 | 514 | 25.8 | 515 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 25.8 | 25.8 | 1.548 | 1.548 | 0.0007168 | 100% | 0% | 1.548 | 1.548 | 0.0011869 | 28 | 0.031032 | 0.031032 |  | 0 | 0 | 6912 | 1847.9997 | 271.8412
SYL-B.1.RR.424.1 | 24493959206043 | Beani Bazar, Mathiura, Purush Pal, Commandar Bari, A. Malek | 2019-09-26 | LP1002 | 10.2 | 516 | 10.2 | 517 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6912 | 1847.9997 | 107.4721
SYL-B.1.RR.425.1 | 24494319206038 | Beani Bazar, Mathiura, Purush Pal, A. Moqit | 2019-09-26 | LP1002 | 11 | 518 | 11 | 519 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6912 | 1847.9997 | 115.9013
SYL-B.1.RR.426.1 | 24482479206019 | Beanibazar, Til Para, Hazi Tera mia | 2019-09-28 | LP1002 | 6.6 | 520 | 6.6 | 521 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6888 | 1871.9997 | 69.5408
SYL-B.1.RR.427.1 | 24481989205596 | Beanibazar, Til Para, Nizam Uddin,( Opposite of Til Para Sub Health Center ) | 2019-09-28 | LP1002 | 13 | 522 | 12.5 | 523 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6888 | 1871.9997 | 131.706
SYL-B.1.RR.428.1 | 24482549206155 | Beanibazar, Mathiura, Soto Basegram, Late Azir Uddin | 2019-09-28 | LP1002 | 2.9 | 524 | 2.9 | 525 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6888 | 1871.9997 | 30.5558
SYL-B.1.RR.428.2 | 24482549206155 | Beanibazar, Mathiura, Soto Basegram, Late Azir Uddin | 2021-09-20 | LX1011 | 14.6 | 667 | 14.6 | 668 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6888 | 1871.9997 | 153.8326
SYL-B.1.RR.451.1 | 24475099209593 | Beani Bazar, Borthol, Jolldup, Attab Ali | 2019-09-23 | LP1002 | 7 | 426 | 7 | 427 | 2022-01-01 | [9 empty] | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0
SYL-B.1.RR.452.1 | 24491339208290 | Beani Bazar, Mathiura, Losuytola, Hazi Mohib Ali | 2019-09-23 | LP1002 | 4.9 | 428 | 4.9 | 429 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6912 | 1847.9997 | 51.6288
SYL-B.1.RR.453.1 | 24491329208270 | Beani Bazar, Mathiura, Losuytola, Tarak | 2019-09-23 | LP1002 | 12.3 | 430 | 12.3 | 431 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6912 | 1847.9997 | 129.5987
SYL-B.1.RR.454.1 | 24490269207553 | Beani Bazar, Mathiura, Mathiura Bazar, Jomila Khatun/Anamuuddin | 2019-09-23 | LP1002 | 6.6 | 432 | 6.6 | 433 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6912 | 1847.9997 | 69.5408
SYL-B.1.RR.455.1 | 24490469207566 | Beani Bazar, Mathiura, East Para, Hazi Md. Taurmuzali | 2019-09-23 | LP1002 | 4.3 | 434 | 4.3 | 435 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6912 | 1847.9997 | 45.3069
SYL-B.1.RR.456.1 | 24490999207427 | Beani Bazar, Mathiura, North Para, Dawlor | 2019-09-23 | LP1002 | 11.5 | 436 | 11.5 | 437 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6912 | 1847.9997 | 121.1695
SYL-B.1.RR.457.1 | 24490999207427 | Beani Bazar, Mathiura, North Para, Shohel | 2019-09-23 | LP1002 | 12.4 | 442 | 12.4 | 443 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6912 | 1847.9997 | 130.6524
SYL-B.1.RR.458.1 | 24491759207269 | Beani Bazar, Mathiura, North Para, Boro Bari, Fokor Uddin | 2019-09-24 | LP1002 | 9.9 | 460 | 9.9 | 461 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6912 | 1847.9997 | 104.3112
SYL-B.1.RR.459.1 | 24491899207280 | Beani Bazar, Mathiura, North Para, Boro Bari, Late Fayzul Rohaman | 2019-09-24 | LP1002 | 8.8 | 462 | 8.9 | 463 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6912 | 1847.9997 | 93.7747
SYL-B.1.RR.460.1 | 24492249207278 | Beani Bazar, Mathiura, North para, Shorifuddin | 2019-09-26 | LP1002 | 16.2 | 478 | 16.8 | 479 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6912 | 1847.9997 | 177.0129
SYL-B.1.RR.461.1 | 24492519207214 | Beani Bazar, Mathiura, North para, Royel | 2019-09-26 | LP1002 | 12.3 | 480 | 12.3 | 481 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6912 | 1847.9997 | 129.5987
SYL-B.1.RR.462.1 | 24492679207234 | Beani Bazar, Mathiura, North para, Gas uddin | 2019-09-26 | LP1002 | 6.6 | 482 | 6.6 | 483 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6912 | 1847.9997 | 69.5408
SYL-B.1.RR.463.1 | 24492229207213 | Beani Bazar, Mathiura, North para, Eidga Bazar, Shoul Ahamad Ludi | 2019-09-26 | LP1002 | 8.1 | 484 | 8.1 | 485 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6912 | 1847.9997 | 85.3455
SYL-B.1.RR.463.2 | 24492229207213 | Beani Bazar, Mathiura, North para, Eidga Bazar, Shoul Ahamad Ludi | 2019-09-26 | LP1002 | 4.5 | 486 | 4.5 | 487 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6912 | 1847.9997 | 47.4142
SYL-B.1.RR.464.1 | 24490919207013 | Beani Bazar, Mathiura, Dhowakha, Fozlur karim | 2019-09-26 | LP1002 | 4.3 | 488 | 4.3 | 489 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6912 | 1847.9997 | 45.3069
SYL-B.1.RR.465.1 | 24490279206582 | Beani Bazar, Mathiura, Dhowakha, Shoykot | 2019-09-26 | LP1002 | 4.5 | 490 | 4.5 | 491 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6912 | 1847.9997 | 47.4142
SYL-B.1.RR.466.1 | 24485809206568 | Beani Bazar, Mathiura, Dowakha, Mokter Ali | 2019-09-26 | LP1002 | 10.2 | 494 | 10.2 | 495 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6912 | 1847.9997 | 107.4721
SYL-B.1.RR.467.1 | 24490079207036 | Beani Bazar, Mathiura, Dowakha, Hazi Arob Ali | 2019-09-26 | LP1002 | 11 | 496 | 11 | 497 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 6912 | 1847.9997 | 115.9013
SYL-B.1.RR.468.1 | 24490049207038 | Beani Bazar, Mathiura, Dowakha, Late Nimer Ali | 2019-09-26 | LP1002 | 10.8 | 498 | 10.8 | 499 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6912 | 1847.9997 | 113.794
SYL-B.1.RR.469.1 | 24485489207071 | Beani Bazar, Mathiura, Minaray, Waliur Rohaman | 2019-09-26 | LP1002 | 3.9 | 502 | 3.9 | 503 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6912 | 1847.9997 | 41.0923
SYL-B.1.RR.470.1 | 24484879207076 | Beani Bazar, Mathura , Minaray, Rofique uddin | 2019-09-28 | LP1002 | 3.5 | 528 | 3.5 | 529 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 6912 | 1847.9997 | 36.8777
SYL-B.1.RR.471.1 | 24484879207076 | Beani Bazar, Mathura , Minaray, Anamuddin | 2019-09-28 | LP1002 | 10.1 | 530 | 10.1 | 531 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6912 | 1847.9997 | 106.4185
SYL-B.1.RR.472.1 | 24494839206357 | Beani Bazar, Mathura , West par, Shak Lal, Fokoruddin | 2019-09-28 | LP1002 | 11.3 | 532 | 11.3 | 533 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6912 | 1847.9997 | 119.0622
SYL-B.1.RR.501.1 | 24502119210525 | Biani Bazar, Gungadesha Boro Mosque, Moskoh Ali | 2019-09-23 | MN1018 | 1.8 | 447 | 1.8 | 448 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6960 | 1799.9997 | 18.9657
SYL-B.1.RR.501.2 | 24502119210525 | Biani Bazar, Gungadesha Boro Mosque, Moskoh Ali | 2022-04-24 | NQ1007 | 2.1 | 156 | 2.1 | 157 | 2022-04-24 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 4248 | 1799.9997 | 15.2765
SYL-B.1.RR.502.1 | 24481869206498 | Biani Bazar, Tilpara, Nalbahar, Md. Halaluddin | 2019-09-24 | MN1018 | 10.5 | 472 | 10.5 | 473 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6888 | 1871.9997 | 110.6331
SYL-B.1.RR.503.1 | 24481799206488 | Biani Bazar, Tilpara, Nalbahar, Boloy Mia | 2019-09-24 | MN1018 | 7.5 | 474 | 7.5 | 475 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6888 | 1871.9997 | 79.0236
SYL-B.1.RR.504.1 | 24481799206488 | Biani Bazar, Tilpara, Nalbahar, Pakhi Mia | 2019-09-24 | MN1018 | 4.4 | 476 | 4.4 | 477 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6888 | 1871.9997 | 46.3605
SYL-B.1.RR.505.1 | 24481799206488 | Biani Bazar, Tilpara, Nalbahar, Jaiur Rahman | 2019-09-24 | MN1018 | 3.9 | 482 | 3.9 | 483 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 6888 | 1871.9997 | 41.0923
SYL-B.1.RR.506.1 | 24520219210596 | Biani Bazar, Teradal, Ibrahim Ali | 2019-09-26 | MN1018 | 9 | 484 | 8.7 | 485 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7056 | 1703.9997 | 91.6674
SYL-B.1.RR.507.1 | 24520219210596 | Biani Bazar, Teradal, Shafiaul Islam | 2019-09-26 | MN1018 | 11.8 | 486 | 11.8 | 487 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7056 | 1703.9997 | 124.3305
SYL-B.1.RR.508.1 | 24520309210595 | Biani Bazar, Teradal, Kamaluddin | 2019-09-26 | MN1018 | 8.2 | 488 | 8.2 | 489 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7056 | 1703.9997 | 86.3991
SYL-B.1.RR.509.1 | 24520159210565 | Biani Bazar, Teradal, Samsuddin | 2019-09-26 | MN1018 | 3.1 | 490 | 3.1 | 491 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7056 | 1703.9997 | 32.6631
SYL-B.1.RR.510.1 | 24515859210560 | Biani Bazar, Teradal, Asaduddin | 2019-09-26 | MN1018 | 5 | 492 | 5 | 493 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7056 | 1703.9997 | 52.6824
SYL-B.1.RR.511.1 | 24514749210585 | Biani Bazar, Teradal, Abdus Salam | 2019-09-26 | MN1018 | 11.3 | 494 | 11.3 | 495 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7056 | 1703.9997 | 119.0622
SYL-B.1.RR.512.1 | 24514749210585 | Biani Bazar, Teradal, Tota Mia | 2019-09-26 | MN1018 | 5.1 | 496 | 5.1 | 497 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7056 | 1703.9997 | 53.7361
SYL-B.1.RR.513.1 | 24514829210581 | Biani Bazar, Teradal, Khalilur Rahman | 2019-09-26 | MN1018 | 2.4 | 498 | 2.4 | 499 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7056 | 1703.9997 | 25.2876
SYL-B.1.RR.514.1 | 24520879210527 | Biani Bazar, Teradal, Abdur Nur Master | 2019-09-26 | MN1018 | 10.6 | 502 | 10.7 | 503 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7056 | 1703.9997 | 112.7403
SYL-B.1.RR.515.1 | 24521009210555 | Biani Bazar, Teradal, Hosen Ahmed | 2019-09-26 | MN1018 | 4.7 | 506 | 4.3 | 507 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7056 | 1703.9997 | 45.3069
SYL-B.1.RR.551.1 | 24495669210374 | Biani Bazar, Borodesh, Block-A, Surab Ali | 2019-09-24 | MN1018 | 11.3 | 466 | 11.3 | 467 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6960 | 1799.9997 | 119.0622
SYL-B.1.RR.552.1 | 24495939210383 | Biani Bazar, Borodesh, Block-A, Abdul Haque | 2019-09-24 | MN1018 | 6.3 | 468 | 6.4 | 469 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6960 | 1799.9997 | 67.4335
SYL-B.1.RR.553.1 | 24495519210374 | Biani Bazar, Borodesh, Block-A, Road# 1/1, Giasuddin | 2019-09-24 | MN1018 | 4.9 | 470 | 4.9 | 471 | 2022-01-01 | 2022-10-18 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6960 | 1799.9997 | 51.6288
SYL-B.1.RR.554.1 | 24481479206553 | Biani Bazar, Nal Bohor, Mazor Bari, Abdul Monnan | 2019-09-26 | MN1018 | 26 | 508 | 26 | 509 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 26 | 26 | 1.56 | 1.56 | 0.0007168 | 100% | 0% | 1.56 | 1.56 | 0.0011869 | 28 | 0.031273 | 0.031273 |  | 0 | 0 | 6888 | 1871.9997 | 273.9485
SYL-B.1.RR.555.1 | 24481479206553 | Biani Bazar, Nal Bohor, Mazor Bari, Abdul Halim | 2019-09-26 | MN1018 | 40 | 510 | 40 | 511 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 40 | 40 | 2.4 | 2.4 | 0.0007168 | 100% | 0% | 2.4 | 2.4 | 0.0011869 | 28 | 0.048112 | 0.048112 |  | 0 | 0 | 6888 | 1871.9997 | 421.4593
SYL-B.1.RR.556.1 | 24481479206553 | Biani Bazar, Nal Bohor, Mazor Bari, Late-Abdul Kuddus | 2019-09-26 | MN1018 | 5.6 | 512 | 5.6 | 513 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6888 | 1871.9997 | 59.0043
SYL-B.1.RR.557.1 | 24481699206528 | Biani Bazar, Nal Bohor, Gias Uddin | 2019-09-26 | MN1018 | 1.5 | 514 | 1.5 | 515 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6888 | 1871.9997 | 15.8047
SYL-B.1.RR.558.1 | 24481829207073 | Biani Bazar, Nal Bohor, Motin Mia | 2019-09-26 | MN1018 | 11.7 | 516 | 11.7 | 517 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6888 | 1871.9997 | 123.2768
SYL-B.1.RR.559.1 | 24481829207073 | Biani Bazar, Nal Bohor, Azimuddin | 2019-09-26 | MN1018 | 6.8 | 518 | 6.2 | 519 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6888 | 1871.9997 | 65.3262
SYL-B.1.RR.560.1 | 24482179207098 | Biani Bazar, Agrengabad, South Mathura, Hazi Azmol Monzil | 2019-09-26 | MN1018 | 7.1 | 520 | 7.1 | 521 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 6888 | 1871.9997 | 74.809
SYL-B.1.RR.561.1 | 24494169209410 | Biani Bazar, Main Road, Hospital Gate, City Diagonstic, Abdul Basik | 2019-09-28 | MN1018 | 10.9 | 522 | 10.9 | 523 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6984 | 1775.9997 | 114.8476
SYL-B.1.RR.561.2 | 24494169209410 | Biani Bazar, Main Road, Hospital Gate, City Diagonstic, Abdul Basik | 2022-04-25 | NQ1007 | 14.6 | 168 | 14.1 | 169 | 2022-04-25 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 4248 | 1775.9997 | 102.1635
SYL-B.1.RR.562.1 | 24494329209410 | Biani Bazar, Opposite Hospital Gate, Rouful Islam(Arif Vila) | 2019-09-28 | MN1018 | 7.5 | 524 | 7.5 | 525 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6984 | 1775.9997 | 79.0236
SYL-B.1.RR.563.1 | 24494309209383 | Biani Bazar, West Noyagram, Aynul Huda Mojumdar | 2019-09-28 | MN1018 | 1.5 | 526 | 1.5 | 527 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6984 | 1775.9997 | 15.8047
SYL-B.1.RR.564.1 | 24495399209418 | Biani Bazar, Shohid tila, Doctor Motinuddin Ahmed | 2019-09-28 | MN1018 | 5.1 | 528 | 5.1 | 529 | 2022-01-01 | 2022-10-19 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6984 | 1775.9997 | 53.7361
SYL-B.1.RR.601.1 | 24474219205257 | Sylhet, Beani Bazar, Matijura, Alimoddin | 2019-09-26 | LU1001 | 1.8 | 461 | 1.8 | 462 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6888 | 1871.9997 | 18.9657
SYL-B.1.RR.602.1 | 24474219205257 | Sylhet, Beani Bazar, Matijura, Nurul Haque | 2019-09-26 | LU1001 | 11.3 | 463 | 11.3 | 464 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6888 | 1871.9997 | 119.0622
SYL-B.1.RR.603.1 | 24474219205257 | Sylhet, Beani Bazar, Matijura, Tomij Ali | 2019-09-26 | LU1001 | 5.6 | 465 | 5.6 | 466 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6888 | 1871.9997 | 59.0043
SYL-B.1.RR.604.1 | 24472599205184 | Sylhet, Beani Bazar, Matijura, Abdus Sattar | 2019-09-26 | LU1001 | 10.2 | 467 | 10.3 | 468 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6888 | 1871.9997 | 108.5258
SYL-B.1.RR.605.1 | 24492389208305 | Sylhet, Beani Bazar, 52 Battalian, BGB Officers Mess | 2019-09-28 | LU1001 | 10.5 | 485 | 10.5 | 486 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6912 | 1847.9997 | 110.6331
SYL-B.1.RR.606.1 | 24484769207247 | Sylhet, Beani Bazar, Mathiura, Abdul Manik | 2019-09-28 | LU1001 | 8 | 487 | 8 | 488 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6912 | 1847.9997 | 84.2919
SYL-B.1.RR.607.1 | 24500019206391 | Sylhet, Beani Bazar, Mathiura, Dodbox, Noyal, M A Latif | 2019-09-28 | LU1001 | 9.1 | 489 | 9.1 | 490 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6912 | 1847.9997 | 95.882
SYL-B.1.RR.651.1 | 24474129206587 | Beanibazar, Nalbhor, Shodor Pur, Seraj Uddin | 2019-09-26 | LU1001 | 10.6 | 431 | 10.6 | 432 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6888 | 1871.9997 | 111.6867
SYL-B.1.RR.652.1 | 24474129206587 | Beanibazar, Nalbhor, Shodor Pur, Kamor Uddin | 2019-09-26 | LU1001 | 7 | 433 | 7 | 434 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6888 | 1871.9997 | 73.7554
SYL-B.1.RR.653.1 | 24474129206587 | Beanibazar, Nalbhor, Shodor Pur, Mokles | 2019-09-26 | LU1001 | 10.8 | 435 | 10.7 | 436 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6888 | 1871.9997 | 112.7403
SYL-B.1.RR.654.1 | 24473969206587 | Beanibazar, Nalbhor, Shodor Pur, Sad Uddin | 2019-09-26 | LU1001 | 5.8 | 437 | 5.6 | 438 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 6888 | 1871.9997 | 59.0043
SYL-B.1.RR.655.1 | 24473909206593 | Beanibazar, Nalbhor, Shodor Pur, Hafiz Uddin | 2019-09-26 | LU1001 | 16.8 | 439 | 16.8 | 440 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 6888 | 1871.9997 | 177.0129
SYL-B.1.RR.656.1 | 24473809206593 | Beanibazar, Nalbhor, Shodor Pur, Azizur Rahaman | 2019-09-26 | LU1001 | 5.5 | 441 | 5.5 | 442 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6888 | 1871.9997 | 57.9506
SYL-B.1.RR.657.1 | 24473709207017 | Beanibazar, Nalbhor, Shodor Pur, Sonjit Ali | 2019-09-28 | LU1001 | 5.8 | 469 | 5.8 | 470 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6888 | 1871.9997 | 61.1116
SYL-B.1.RR.658.1 | 24473709207017 | Beanibazar, Nalbhor, Shodor Pur, Nuruj Ali | 2019-09-28 | LU1001 | 9.9 | 471 | 9.9 | 472 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6888 | 1871.9997 | 104.3112
SYL-B.1.RR.659.1 | 24473709207017 | Beanibazar, Nalbhor, Shodor Pur, Islam Uddin | 2019-09-28 | LU1001 | 9.5 | 473 | 9.1 | 474 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 6888 | 1871.9997 | 95.882
SYL-B.1.RR.660.1 | 24473749206578 | Beanibazar, Nalbhor, Shodor Pur, Billal Ahammed | 2019-09-28 | LU1001 | 10.6 | 475 | 10.6 | 476 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6888 | 1871.9997 | 111.6867
SYL-B.1.RR.661.1 | 24473749206578 | Beanibazar, Nalbhor, Shodor Pur, Toslima Begum | 2019-09-28 | LU1001 | 8.7 | 477 | 8.7 | 478 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6888 | 1871.9997 | 91.6674
SYL-B.1.RR.662.1 | 24473779206553 | Beanibazar, Nalbhor, Shodor Pur, Arman Ali | 2019-09-28 | LU1001 | 18.9 | 479 | 18.9 | 480 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 6888 | 1871.9997 | 199.1395
SYL-B.1.RR.663.1 | 24474749206557 | Beanibazar, Nalbhor, Shodor Pur, Abdus Salam | 2019-09-28 | LU1001 | 4.9 | 481 | 4.9 | 482 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6888 | 1871.9997 | 51.6288
SYL-B.1.RR.664.1 | 24475309207026 | Beanibazar, Nalbhor, Shodor Pur, Mahabubur Rahaman | 2019-09-28 | LU1001 | 9.3 | 483 | 9.3 | 484 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6888 | 1871.9997 | 97.9893
SYL-B.1.RR.701.1 | 24481159209105 | Beanibazar, Nidonpur, Rehan | 2019-09-22 | NQ1000 | 6.1 | 378 | 6.1 | 379 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6840 | 1919.9997 | 64.2725
SYL-B.1.RR.702.1 | 24481319209095 | Beanibazar, Nidonpur, Shamsuddin | 2019-09-22 | NQ1000 | 22.5 | 380 | 22.3 | 381 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 6840 | 1919.9997 | 234.9635
SYL-B.1.RR.703.1 | 24481319209095 | Beanibazar, Nidonpur, Jiyauddin | 2019-09-22 | NQ1000 | 10.3 | 382 | 10.3 | 383 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6840 | 1919.9997 | 108.5258
SYL-B.1.RR.703.2 | 24481319209095 | Beanibazar, Nidonpur, Jiyauddin | 2020-10-17 | MP1032 | 19.7 | 587 | 19.4 | 588 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 19.4 | 19.4 | 1.164 | 1.164 | 0.0007168 | 100% | 0% | 1.164 | 1.164 | 0.0011869 | 28 | 0.023334 | 0.023334 |  | 0 | 0 | 6840 | 1919.9997 | 204.4077
SYL-B.1.RR.704.1 | 24481349209084 | Beanibazar, Nidonpur, Atibur Rahman | 2019-09-22 | NQ1000 | 6.8 | 384 | 7.3 | 385 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6840 | 1919.9997 | 76.9163
SYL-B.1.RR.705.1 | 24481469209047 | Beanibazar, Nidonpur, Mostofa | 2019-09-22 | NQ1000 | 10.6 | 386 | 10.6 | 387 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6840 | 1919.9997 | 111.6867
SYL-B.1.RR.706.1 | 24481229209052 | Beanibazar, Nidonpur, Alom Hossain | 2019-09-22 | NQ1000 | 9 | 388 | 9 | 389 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6840 | 1919.9997 | 94.8283
SYL-B.1.RR.706.2 | 24481229209052 | Beanibazar, Nidonpur, Alom Hossain | 2022-04-19 | LU1001 | 8.2 | 176 | 8.2 | 177 | 2022-04-19 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 4248 | 1919.9997 | 60.8345
SYL-B.1.RR.707.1 | 24481229209052 | Beanibazar, Nidonpur, Shaidul Hossain | 2019-09-22 | NQ1000 | 4.3 | 390 | 4.3 | 391 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6840 | 1919.9997 | 45.3069
SYL-B.1.RR.708.1 | 24491309209124 | Beanibazar, Dasgram, Ruhul Amin | 2019-09-23 | NQ1000 | 8.5 | 428 | 8.5 | 429 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6840 | 1919.9997 | 89.5601
SYL-B.1.RR.709.1 | 24491309209124 | Beanibazar, Dasgram, Shamim | 2019-09-23 | NQ1000 | 9.7 | 430 | 9.7 | 431 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6840 | 1919.9997 | 102.2039
SYL-B.1.RR.710.1 | 24491249209105 | Beanibazar, Dasgram, Saleh Ahmad | 2019-09-23 | NQ1000 | 10.8 | 432 | 10.8 | 433 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6840 | 1919.9997 | 113.794
SYL-B.1.RR.711.1 | 24491499209031 | Beanibazar, Dasgram, Aniruddho | 2019-09-23 | NQ1000 | 9.6 | 434 | 9.6 | 435 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6840 | 1919.9997 | 101.1502
SYL-B.1.RR.711.2 | 24491499209031 | Beanibazar, Dasgram, Aniruddho | 2019-09-23 | NQ1000 | 9.9 | 436 | 9.9 | 437 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6840 | 1919.9997 | 104.3112
SYL-B.1.RR.712.1 | 24491899209044 | Beanibazar, Dasgram, Bodrul Haque | 2019-09-23 | NQ1000 | 9.7 | 438 | 9.7 | 439 | 2022-01-01 | 2022-10-13 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6840 | 1919.9997 | 102.2039
SYL-B.1.RR.713.1 | 24485659206590 | Beanibazar, Mathiura, Kholagram, Abdul Alim | 2019-09-24 | NQ1000 | 7.7 | 450 | 7.7 | 451 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 6912 | 1847.9997 | 81.1309
SYL-B.1.RR.714.1 | 24485379207009 | Beanibazar, Mathiura, Kholagram, Alauddin | 2019-09-24 | NQ1000 | 11.2 | 452 | 11.2 | 453 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6912 | 1847.9997 | 118.0086
SYL-B.1.RR.715.1 | 24482849206539 | Beanibazar, Mathiura, Arenggabad, Abdul Kader | 2019-09-24 | NQ1000 | 3.1 | 454 | 3.1 | 455 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6888 | 1871.9997 | 32.6631
SYL-B.1.RR.716.1 | 24472329206364 | Beanibazar, South Dasura, Abdul Sukkur | 2019-09-26 | NQ1000 | 5.8 | 476 | 5.3 | 477 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 6888 | 1871.9997 | 55.8434
SYL-B.1.RR.717.1 | 24472329206364 | Beanibazar, South Dasura, Abdul Muiz | 2019-09-26 | NQ1000 | 22.9 | 478 | 22.9 | 479 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 22.9 | 22.9 | 1.374 | 1.374 | 0.0007168 | 100% | 0% | 1.374 | 1.374 | 0.0011869 | 28 | 0.027544 | 0.027544 |  | 0 | 0 | 6888 | 1871.9997 | 241.2854
SYL-B.1.RR.718.1 | 24472049206386 | Beanibazar, South Dasura, Mamun Mia | 2019-09-26 | NQ1000 | 4.6 | 480 | 4.6 | 481 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6888 | 1871.9997 | 48.4678
SYL-B.1.RR.719.1 | 24471059206414 | Beanibazar, South Dasura, Abdul Ahad | 2019-09-26 | NQ1000 | 10.3 | 482 | 10.3 | 483 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 6888 | 1871.9997 | 108.5258
SYL-B.1.RR.719.2 | 24471059206414 | Beanibazar, South Dasura, Abdul Ahad | 2022-04-17 | LU1001 | 36.9 | 159 | 36.9 | 160 | 2022-04-17 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 36.9 | 36.9 | 2.214 | 2.214 | 0.0007168 | 100% | 0% | 2.214 | 2.214 | 0.0011869 | 28 | 0.044383 | 0.044383 |  | 0 | 0 | 4344 | 1871.9997 | 275.8855
SYL-B.1.RR.720.1 | 24471059206414 | Beanibazar, South Dasura, Abdul Sumed | 2019-09-26 | NQ1000 | 9.7 | 484 | 9.7 | 485 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6888 | 1871.9997 | 102.2039
SYL-B.1.RR.720.2 | 24471059206414 | Beanibazar, South Dasura, Abdul Sumed | 2021-01-23 | LX1011 | 11.6 | 47 | 11.6 | 48 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6888 | 1871.9997 | 122.2232
SYL-B.1.RR.721.1 | 24465679206370 | Beanibazar, Gangkul, Khairul Islam | 2019-09-26 | NQ1000 | 5.9 | 486 | 5.9 | 487 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 6888 | 1871.9997 | 62.1652
SYL-B.1.RR.722.1 | 24465679206370 | Beanibazar, Gangkul, Khairul Islam | 2019-09-26 | NQ1000 | 9.5 | 488 | 9.5 | 489 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6888 | 1871.9997 | 100.0966
SYL-B.1.RR.723.1 | 24474489206187 | Beanibazar, Dasura, Shoaib Ali | 2019-09-26 | NQ1000 | 4.4 | 490 | 4.4 | 491 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6888 | 1871.9997 | 46.3605
SYL-B.1.RR.724.1 | 24474169206057 | Beanibazar, Dasura, Muhib Ali | 2019-09-26 | NQ1000 | 2.6 | 494 | 2.6 | 495 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6888 | 1871.9997 | 27.3949
SYL-B.1.RR.725.1 | 24474169206057 | Beanibazar, Dasura, Muhib Ali | 2019-09-26 | NQ1000 | 1.9 | 496 | 1.9 | 497 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6888 | 1871.9997 | 20.0193
SYL-B.1.RR.726.1 | 24484979207203 | Beanibazar, Mathiura, Minarai, Jalil | 2019-09-28 | NQ1000 | 2.6 | 498 | 2.6 | 499 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 6912 | 1847.9997 | 27.3949
SYL-B.1.RR.726.2 | 24484979207203 | Beanibazar, Mathiura, Minarai, Jalil | 2021-01-23 | LX1011 | 9.6 | 51 | 9.6 | 52 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6912 | 1847.9997 | 101.1502
SYL-B.1.RR.727.1 | 24485779207135 | Beanibazar, Mathiura, Minarai, Kamaluddin | 2019-09-28 | NQ1000 | 3.8 | 500 | 3.8 | 501 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6912 | 1847.9997 | 40.0386
SYL-B.1.RR.727.2 | 24485779207135 | Beanibazar, Mathiura, Minarai, Kamaluddin | 2022-04-18 | LU1001 | 21.6 | 170 | 21.6 | 171 | 2022-04-18 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 4344 | 1847.9997 | 160.8704
SYL-B.1.RR.728.1 | 24511479210119 | Beanibazar, Angarjur South, Mayanuddin | 2019-09-28 | NQ1000 | 1.8 | 502 | 1.8 | 503 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7056 | 1703.9997 | 18.9657
SYL-B.1.RR.729.1 | 24511479210119 | Beanibazar, Angarjur South, Abdur Rahman | 2019-09-28 | NQ1000 | 2.8 | 506 | 2.8 | 507 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7056 | 1703.9997 | 29.5021
SYL-B.1.RR.730.1 | 24511969210028 | Beanibazar, Angarjur South, Nijamuddin | 2019-09-28 | NQ1000 | 3.9 | 508 | 3.9 | 509 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7056 | 1703.9997 | 41.0923
SYL-B.1.RR.731.1 | 24512099210132 | Beanibazar, Angarjur South, Shahed Ahmad | 2019-09-28 | NQ1000 | 2.2 | 511 | 2.2 | 512 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7056 | 1703.9997 | 23.1803
SYL-B.1.RR.732.1 | 24513959209582 | Beanibazar, Angarjur, Taherunnesa | 2019-09-28 | NQ1000 | 3.2 | 513 | 3.2 | 514 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7056 | 1703.9997 | 33.7167
SYL-B.1.RR.733.1 | 24512859210014 | Beanibazar, Angarjur, Akhlak Habib | 2019-09-28 | NQ1000 | 7 | 515 | 6.8 | 516 | 2022-01-01 | 2022-10-22 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7056 | 1703.9997 | 71.6481
SYL-B.1.RR.751.1 | 24484159207044 | Bianibazar, Mathiura (Kolagram), Abdul Hadi | 2019-09-24 | NQ1000 | 3.2 | 448 | 3.2 | 449 | 2022-01-01 | 2022-10-16 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6912 | 1847.9997 | 33.7167
SYL-B.1.RR.752.1 | 24474539206331 | Bianibazar, Dasura, Dasura Bazar, Bodrul Haque | 2019-09-26 | NQ1000 | 11.6 | 456 | 11.7 | 457 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6888 | 1871.9997 | 123.2768
SYL-B.1.RR.753.1 | 24473869206370 | Bianibazar, Dasura, Dasura Bazar, Mojiruddin | 2019-09-26 | NQ1000 | 5.1 | 458 | 5.1 | 459 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6888 | 1871.9997 | 53.7361
SYL-B.1.RR.754.1 | 24473869206370 | Bianibazar, Dasura, Dasura Bazar, Azimuddin | 2019-09-26 | NQ1000 | 8.6 | 460 | 8.5 | 461 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6888 | 1871.9997 | 89.5601
SYL-B.1.RR.755.1 | 24473869206370 | Bianibazar, Dasura, Dasura Bazar, Naziuddin | 2019-09-26 | NQ1000 | 11.2 | 462 | 11.2 | 463 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6888 | 1871.9997 | 118.0086
SYL-B.1.RR.756.1 | 24474069206412 | Bianibazar, Dasura, Dasura Bazar, Riaz Ali | 2019-09-26 | NQ1000 | 4.7 | 464 | 4.7 | 465 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6888 | 1871.9997 | 49.5215
SYL-B.1.RR.757.1 | 24474279206485 | Bianibazar, Dasura, Gowali bari, Hazi Mokarrom Ali | 2019-09-26 | NQ1000 | 10.8 | 468 | 10.8 | 469 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6888 | 1871.9997 | 113.794
SYL-B.1.RR.757.2 | 24474279206485 | Bianibazar, Dasura, Gowali bari, Hazi Mokarrom Ali | 2021-09-20 | NQ1007 | 10.5 | 37 | 10.9 | 38 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6888 | 1871.9997 | 114.8476
SYL-B.1.RR.758.1 | 24473789206312 | Bianibazar, Dasura, Near Dasura Bazar, Abdul Ali | 2019-09-26 | NQ1000 | 6.1 | 470 | 6.1 | 471 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6888 | 1871.9997 | 64.2725
SYL-B.1.RR.759.1 | 24473729206312 | Bianibazar, Dasura, Near Dasura Mosque, Abdul Hakim | 2019-09-26 | NQ1000 | 6 | 472 | 6 | 473 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 6888 | 1871.9997 | 63.2189
SYL-B.1.RR.760.1 | 24473729206312 | Bianibazar, Dasura, Near Dasura Mosque, Sohid Ahamed | 2019-09-26 | NQ1000 | 10.7 | 474 | 10.7 | 475 | 2022-01-01 | 2022-10-15 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6888 | 1871.9997 | 112.7403
SYL-E.1.CR.1.1 | 24550149156327 | Shahporan, Khadim Nagar, Rustampur, Dhaka Biriyani House | 2019-04-13 | LP1002 | 1.8 | 90 | 1.8 | 91 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7632 | 1127.9997 | 18.9657
SYL-E.1.CR.5.1 | 24535559154377 | Majortila, Islampur, Otithi Restaurent | 2019-08-29 | MP1006 | 3.3 | 363 | 3.3 | 364 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7608 | 1151.9997 | 34.7704
SYL-E.1.RR.1.1 | 24540059154553 | Sylhet Sadar, Islampur, Nurpur R/A, Rajia Begum | 2019-04-04 | LP1002 | 1 | 1 | 1 | 2 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7656 | 1103.9997 | 10.5365
SYL-E.1.RR.3.1 | 24535189154565 | Sylhet Sadar, Islampur, Nurpur Residential Area, Abdul Aziz | 2019-04-04 | LP1002 | 4.7 | 5 | 4.7 | 6 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7656 | 1103.9997 | 49.5215
SYL-E.1.RR.4.1 | 24535129154559 | Sylhet Sadar, Islampur, Mejor Tila, Tareb Ali Khan | 2019-04-04 | LP1002 | 5.3 | 7 | 5.3 | 8 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7656 | 1103.9997 | 55.8434
SYL-E.1.RR.5.1 | 24535139154513 | Sylhet Sadar, Mejor Tila, Islampur, Block D, Faruk Reza | 2019-04-04 | LP1002 | 3.4 | 9 | 3.4 | 10 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7608 | 1151.9997 | 35.824
SYL-E.1.RR.5.2 | 24535139154513 | Sylhet Sadar, Mejor Tila, Islampur, Block D, Faruk Reza | 2021-02-16 | MN1018 | 32.1 | 125 | 32.1 | 126 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 32.1 | 32.1 | 1.926 | 1.926 | 0.0007168 | 100% | 0% | 1.926 | 1.926 | 0.0011869 | 28 | 0.03861 | 0.03861 |  | 0 | 0 | 7608 | 1151.9997 | 338.221
SYL-E.1.RR.6.1 | 24535139154497 | Sylhet Sadar, Mejor Tila, Islampur, Block D, H # 112 | 2019-04-04 | LP1002 | 1 | 11 | 1 | 12 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7608 | 1151.9997 | 10.5365
SYL-E.1.RR.6.2 | 24535139154497 | Sylhet Sadar, Mejor Tila, Islampur, Block D, H # 112 | 2022-11-14 | NQ1007 | 4.8 | 155 | 4.8 | 156 | 2022-11-14 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 0 | 1151.9997 | 6.651
SYL-E.1.RR.7.1 | 24535019154480 | Sylhet Sadar, Mejor Tila, Islampur, Block D, H # 111 | 2019-04-04 | LP1002 | 1.5 | 13 | 1.5 | 14 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7608 | 1151.9997 | 15.8047
SYL-E.1.RR.9.1 | 24534969154479 | Sylhet Sadar, Mejor Tila, Islampur, Block D, H # 108 | 2019-04-04 | LP1002 | 11.7 | 17 | 11.8 | 18 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7608 | 1151.9997 | 124.3305
SYL-E.1.RR.9.2 | 24534969154479 | Sylhet Sadar, Mejor Tila, Islampur, Block D, H # 108 | 2019-04-04 | LP1002 | 24.7 | 19 | 24.7 | 20 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 24.7 | 24.7 | 1.482 | 1.482 | 0.0007168 | 100% | 0% | 1.482 | 1.482 | 0.0011869 | 28 | 0.029709 | 0.029709 |  | 0 | 0 | 7608 | 1151.9997 | 260.2511
SYL-E.1.RR.10.1 | 24534979154477 | Syhlet Sadar, Mejor Tila , Islampur, Block - D, H # 105/2 | 2019-04-04 | LP1002 | 2.7 | 21 | 2.7 | 22 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7608 | 1151.9997 | 28.4485
SYL-E.1.RR.11.1 | 24534959154481 | Sylhet Sadar, Mejor Tila, Islampur, Block-D, H#107 | 2019-04-04 | LP1002 | 4.4 | 23 | 4.4 | 24 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7608 | 1151.9997 | 46.3605
SYL-E.1.RR.12.1 | 24535049154461 | Syhlet Sadar, Mejor Tila , Islampur, Block - D, H # 109 | 2019-04-05 | LP1002 | 4.3 | 25 | 4.3 | 26 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7608 | 1151.9997 | 45.3069
SYL-E.1.RR.12.2 | 24535049154461 | Syhlet Sadar, Mejor Tila , Islampur, Block - D, H # 109 | 2019-04-05 | LP1002 | 1.3 | 27 | 1.3 | 28 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7608 | 1151.9997 | 13.6974
SYL-E.1.RR.13.1 | 24535239154407 | Syhlet Sadar, Islampur, Muslim Nagar , H # 1 | 2019-04-05 | LP1002 | 1.1 | 29 | 1.2 | 30 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7608 | 1151.9997 | 12.6438
SYL-E.1.RR.13.2 | 24535239154407 | Syhlet Sadar, Islampur, Muslim Nagar , H # 1 | 2021-11-21 | LU1001 | 12.8 | 147 | 12.8 | 148 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7608 | 1151.9997 | 134.867
SYL-E.1.RR.15.1 | 24535039154397 | Syhlet Sadar, Islampur, Muslim Nagar , Shen Mrket | 2019-04-05 | LP1002 | 1.6 | 35 | 1.6 | 36 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7608 | 1151.9997 | 16.8584
SYL-E.1.RR.16.1 | 24534929154407 | Syhlet Sadar, Islampur, Muslim Nagar , Shen Mrket | 2019-04-05 | LP1002 | 3.9 | 37 | 3.6 | 38 | 2022-01-01 | [9 empty] | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0
SYL-E.1.RR.21.1 | 24535059155010 | Sylhet, Mojortila, Islampur, Noorpur R/A, H# 55, Dilder Hosain | 2019-04-04 | MN1032 | 6 | 1 | 5.8 | 2 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7656 | 1103.9997 | 61.1116
SYL-E.1.RR.23.1 | 24534989155053 | Sylhet, Mojortila, Islampur, Noorpur R/A, H# 63, Sonu Mia | 2019-04-04 | MN1032 | 1 | 5 | 1 | 6 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7656 | 1103.9997 | 10.5365
SYL-E.1.RR.24.1 | 24535119155103 | Sylhet, Mojortila, Islampur, Noorpur R/A, Siddik Ali, H # 83 | 2019-04-04 | MN1032 | 2.9 | 7 | 2.9 | 8 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7656 | 1103.9997 | 30.5558
SYL-E.1.RR.26.1 | 24535229155116 | Sylhet, Mojortila, Islampur, Noorpur R/A, H # 86, Abul Kasham | 2019-04-04 | MN1032 | 2.3 | 11 | 2.3 | 12 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7656 | 1103.9997 | 24.2339
SYL-E.1.RR.27.1 | 24535229155116 | Sylhet, Mojortila, Islampur, Noorpur R/A, H # 88, Rokib Ali | 2019-04-04 | MN1032 | 11.6 | 13 | 11.4 | 14 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7656 | 1103.9997 | 120.1159
SYL-E.1.RR.31.1 | 24540199154477 | Sylhet Sadar, Islampur, Purabi R/A, Road # 1, H # 05, Sayed Bari | 2019-04-09 | MN1032 | 11.2 | 1 | 11.4 | 2 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7656 | 1103.9997 | 120.1159
SYL-E.1.RR.32.1 | 24540519154493 | Islampur, Tamabil, R# 02, H# 9, Sayada Hosna Banu | 2019-04-09 | MN1032 | 2.9 | 7 | 2.9 | 8 | 2022-01-01 | [9 empty] | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0
SYL-E.1.RR.33.1 | 24540899155053 | Islampur, Chamelibag, Chamelibag jamme Masjid | 2019-04-09 | MN1032 | 1.3 | 9 | 1.3 | 10 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 8088 | 671.9997 | 13.6974
SYL-E.1.RR.34.1 | 24541039155054 | Islampur, Chamelibag Road # 02, Jule Ahmmed | 2019-04-09 | MN1032 | 3 | 11 | 3 | 12 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 8088 | 671.9997 | 31.6094
SYL-E.1.RR.35.1 | 24541689155064 | Sylhet , Islampur, Chamelibag, Road # 02, H # 28/3, Nayan Das | 2019-04-09 | MN1032 | 2.3 | 14 | 2.3 | 15 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8088 | 671.9997 | 24.2339
SYL-E.1.RR.36.1 | 24541639155048 | Sylhet, Islampur,Chamelibag, Road # 02, H # 28, Kripesh Chandra Das (Inside the house) | 2019-04-09 | MN1032 | 12.9 | 17 | 12.1 | 18 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 8088 | 671.9997 | 127.4914
SYL-E.1.RR.37.1 | 24541319155045 | Sylhet Sadar, Chamelibag, Road # 02, Saleur Rahman | 2019-04-10 | MN1032 | 2.5 | 19 | 2.5 | 20 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 8088 | 671.9997 | 26.3412
SYL-E.1.RR.38.1 | 24540959154595 | Sylhet Sadar, Chamelibag, Road # 01, Rofiq | 2019-04-10 | MN1032 | 1.8 | 21 | 1.8 | 22 | 2022-01-01 | [9 empty] | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0
SYL-E.1.RR.39.1 | 24540929154576 | Sylhet Sadar, Chamelibag, Road # 01, H # 18, Mostofa Kamal | 2019-04-10 | MN1032 | 2.5 | 23 | 2.4 | 24 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 8088 | 671.9997 | 25.2876
SYL-E.1.RR.40.1 | 24540859155029 | Sylhet Sadar, Islampur, Chamelibag, Main Road, H # 7 | 2019-04-10 | MN1032 | 1.2 | 25 | 1.1 | 26 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 8088 | 671.9997 | 11.5901
SYL-E.1.RR.41.1 | 24543289154533 | Sylhet Sadar, Islampur, Mohammadpur R/A, Block # H Prottasha, H # 11/2, Dilip Comissionar | 2019-04-10 | MN1032 | 12.6 | 29 | 12.1 | 30 | 2022-01-01 | [9 empty] | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0
SYL-E.1.RR.42.1 | 24543089154543 | Sylhet Sadar, Islampur, Mohammadpur R/A, Block - H, H # 6 | 2019-04-10 | MN1032 | 3.8 | 31 | 3.8 | 32 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8088 | 671.9997 | 40.0386
SYL-E.1.RR.43.1 | 24542959155003 | Sylhet, Majortila, Islampur, Mohammadpur, H# Prottasha-109 | 2019-04-11 | MN1032 | 7.3 | 36 | 7.3 | 37 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8088 | 671.9997 | 76.9163
SYL-E.1.RR.44.1 | 24542889155006 | Sylhet, Majortila, Islampur, Mohammadpur, H# 484, Fakir Ahmed | 2019-04-11 | MN1032 | 6.7 | 38 | 6.4 | 39 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8088 | 671.9997 | 67.4335
SYL-E.1.RR.44.2 | 24542889155006 | Sylhet, Majortila, Islampur, Mohammadpur, H# 484, Fakir Ahmed | 2021-02-16 | LX1011 | 12.8 | 137 | 12.8 | 138 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8088 | 671.9997 | 134.867
SYL-E.1.RR.45.1 | 24542959154589 | Sylhet, Majortila, Islampur, Mohammadpur, H# Prottasha-75, Ashraf Hossen | 2019-04-11 | MN1032 | 2.7 | 40 | 2.7 | 41 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 8088 | 671.9997 | 28.4485
SYL-E.1.RR.46.1 | 24543019154591 | Sylhet, Majortila, Islampur, Mohammadpur, H# 105, Kutub Mia | 2019-04-11 | MN1032 | 1.8 | 42 | 1.8 | 43 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 8088 | 671.9997 | 18.9657
SYL-E.1.RR.46.2 | 24543019154591 | Sylhet, Majortila, Islampur, Mohammadpur, H# 105, Kutub Mia | 2021-02-16 | LX1011 | 2.1 | 133 | 2.1 | 134 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 8088 | 671.9997 | 22.1266
SYL-E.1.RR.46.3 | 24543019154591 | Sylhet, Majortila, Islampur, Mohammadpur, H# 105, Kutub Mia | 2021-02-16 | LX1011 | 4.8 | 135 | 4.8 | 136 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8088 | 671.9997 | 50.5751
SYL-E.1.RR.47.1 | 24543269155001 | Sylhet, Majortila, Islampur, Mohammadpur, H# 498, Himu Ahmed | 2019-04-11 | MN1032 | 1.6 | 45 | 1.6 | 46 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 8088 | 671.9997 | 16.8584
SYL-E.1.RR.48.1 | 24542969154495 | Sylhet, Majortila, Mohammadpur, Prottasha, R/A-6, Block- G, Alamgir | 2019-04-11 | MN1032 | 8.9 | 47 | 8.7 | 48 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8088 | 671.9997 | 91.6674
SYL-E.1.RR.49.1 | 24543299154512 | Sylhet, Majortila, Mohammadpur, Prottasha-15, Block-G, Mahadi Villa | 2019-04-11 | MN1032 | 11.1 | 49 | 11.1 | 50 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8088 | 671.9997 | 116.9549
SYL-E.1.RR.50.1 | 24551509156243 | Sylhet, Khadimnagar, Diganto R/A, Rd # 1, H # 1, Ataur Villa | 2019-04-13 | MN1032 | 5.5 | 54 | 5.5 | 55 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7632 | 1127.9997 | 57.9506
SYL-E.1.RR.51.1 | 24551539156324 | Sylhet, Khadimnagar, Diganto R/A, Rd # 6,H # 152, Anu Mia | 2019-04-13 | MN1032 | 3.1 | 56 | 3.1 | 57 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7632 | 1127.9997 | 32.6631
SYL-E.1.RR.52.1 | 24551539156319 | Sylhet, Khadimnagar, Diganto R/A, Aminur Rahman | 2019-04-13 | MN1032 | 11 | 58 | 11 | 59 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7632 | 1127.9997 | 115.9013
SYL-E.1.RR.53.1 | 24550279156469 | Sylhet, Khadimnagar, Dattorgrame, Khidirpur, Anser Mia, Eastern Side Of Khidirpur Mosque | 2019-04-13 | MN1032 | 102 | 60 | 102 | 61 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 102 | 102 | 6.12 | 6.12 | 0.0007168 | 100% | 0% | 6.12 | 6.12 | 0.0011869 | 28 | 0.12269 | 0.12269 |  | 0 | 0 | 7632 | 1127.9997 | 1074.7211
SYL-E.1.RR.54.1 | 24550419156497 | Sylhet, Khadimnagar, Dattorgrame, Khidirpur, Faruk Miah | 2019-04-13 | MN1032 | 5 | 62 | 5 | 63 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7632 | 1127.9997 | 52.6824
SYL-E.1.RR.55.1 | 24550999156492 | Sylhet, Khadimnagar, Dattorgrame, Khidirpur, Hossen Mia | 2019-04-13 | MN1032 | 3.2 | 64 | 3.1 | 65 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7632 | 1127.9997 | 32.6631
SYL-E.1.RR.56.1 | 24524369153314 | Sylhet, East Sadatikor R/A, Block-B, H# Asha-13, Moni Singha | 2019-04-15 | MN1032 | 2.3 | 80 | 2.3 | 81 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7464 | 1295.9997 | 24.2339
SYL-E.1.RR.57.1 | 24524389153309 | Sylhet, East Sadatikor R/A, Block-B, H# Asha-15, Abdul Hannan | 2019-04-15 | MN1032 | 2.1 | 82 | 2.1 | 83 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7464 | 1295.9997 | 22.1266
SYL-E.1.RR.58.1 | 24524269153335 | Sylhet, East Sadatikor R/A, Block-B, H# Asha-88, Sajjad | 2019-04-15 | MN1032 | 2.9 | 84 | 2.9 | 85 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7464 | 1295.9997 | 30.5558
SYL-E.1.RR.59.1 | 24524519153599 | Sylhet, East Kusighat Bazar, Gazi borhan Uddin Road, Nurul Islam | 2019-04-15 | MN1032 | 3.6 | 86 | 3.6 | 87 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7464 | 1295.9997 | 37.9313
SYL-E.1.RR.60.1 | 24525309153565 | Sylhet, Sahaporan, Tultugor, Chamelibag, H# 113, Saiful Alam | 2019-04-15 | MN1032 | 7 | 88 | 7 | 89 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7464 | 1295.9997 | 73.7554
SYL-E.1.RR.60.2 | 24525309153565 | Sylhet, Sahaporan, Tultugor, Chamelibag, H# 113, Saiful Alam | 2019-04-15 | MN1032 | 8.3 | 90 | 8.3 | 91 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7464 | 1295.9997 | 87.4528
SYL-E.1.RR.61.1 | 24525309153565 | Sylhet, Sahaporan, Tultugor, Chamelibag, H# 113, Saiful Alam | 2019-04-15 | MN1032 | 13.1 | 92 | 12.9 | 93 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7464 | 1295.9997 | 135.9206
SYL-E.1.RR.62.1 | 24530599153063 | Sylhet, Shahjalal Uposhor, Block- E, Rd # 5, H # 161, Sulaiman Hussain | 2019-04-16 | MN1032 | 4.2 | 104 | 4.2 | 105 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7488 | 1271.9997 | 44.2532
SYL-E.1.RR.63.1 | 24530719153081 | Sylhet, Shahjalal Uposhor, Block- E, Rd # 5, H # 157, Shanti Neer | 2019-04-16 | MN1032 | 3.2 | 106 | 3.2 | 107 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7488 | 1271.9997 | 33.7167
SYL-E.1.RR.64.1 | 24530749153091 | Sylhet, Shahjalal Uposhor, Block- E, Rd # 5, H # 189, Haque Mahol | 2019-04-16 | MN1032 | 2 | 108 | 2 | 109 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 8280 | 479.9997 | 21.073
SYL-E.1.RR.65.1 | 24530299153128 | Sylhet, Shahjalal Uposhor, Block- I, Mendibag Road, Mohibur Raja | 2019-04-16 | MN1032 | 10.6 | 110 | 10.6 | 111 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7488 | 1271.9997 | 111.6867
SYL-E.1.RR.66.1 | 24530479153202 | Sylhet, Shahjalal Uposhor, Block- H, Rd # 1, H # 9/3, Eaor Palace | 2019-04-16 | MN1032 | 4.7 | 114 | 4.7 | 115 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7488 | 1271.9997 | 49.5215
SYL-E.1.RR.67.1 | 24530389153237 | Sylhet, Shahjalal Uposhor, Block- H, Rd # 1, H # 235, Masuk | 2019-04-16 | MN1032 | 3.7 | 116 | 3.4 | 117 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7488 | 1271.9997 | 35.824
SYL-E.1.RR.68.1 | 24530479153271 | Sylhet, Shahjalal Uposhor, Block- H, Rd # 1, H # 242 | 2019-04-16 | MN1032 | 1.1 | 118 | 1.1 | 119 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7488 | 1271.9997 | 11.5901
SYL-E.1.RR.69.1 | 24530799153175 | Sylhet, Shahjalal Uposhor, Block- J, Rd # 3, H # 33 | 2019-04-16 | MN1032 | 9.7 | 120 | 9.7 | 121 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7488 | 1271.9997 | 102.2039
SYL-E.1.RR.70.1 | 24530749153186 | Sylhet, Shahjalal Uposhor, Block- J, Rd # 3, H # 37 | 2019-04-16 | MN1032 | 3.5 | 122 | 3.5 | 123 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7488 | 1271.9997 | 36.8777
SYL-E.1.RR.71.1 | 24532729154032 | Sylhet Sadar, Tilagor, Shaplabugh R/A, Rd#2, H#73, Abdul Jolil Munna | 2019-04-17 | MN1018 | 7.8 | 178 | 7.8 | 179 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7608 | 1151.9997 | 82.1846
SYL-E.1.RR.71.2 | 24532729154032 | Sylhet Sadar, Tilagor, Shaplabugh R/A, Rd#2, H#73, Abdul Jolil Munna | 2019-04-17 | MN1018 | 77.6 | 180 | 77.6 | 181 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 77.6 | 77.6 | 4.656 | 4.656 | 0.0007168 | 100% | 0% | 4.656 | 4.656 | 0.0011869 | 28 | 0.093337 | 0.093337 |  | 0 | 0 | 7608 | 1151.9997 | 817.6309
SYL-E.1.RR.72.1 | 24532919154001 | Sylhet Sadar, Tilagor, Shaplabugh R/A, Block-A, Rd#1, H#43, Rahman Presidence | 2019-04-17 | MN1018 | 11.3 | 183 | 11 | 184 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7608 | 1151.9997 | 115.9013
SYL-E.1.RR.73.1 | 24532789154002 | Sylhet Sadar, Tilagor, Shaplabugh R/A, Rd#1, H#52, Kutub Monjil, Md, Asaduzzaman | 2019-04-17 | MN1018 | 1.8 | 185 | 1.8 | 186 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7608 | 1151.9997 | 18.9657
SYL-E.1.RR.74.1 | 24532879153571 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#30, Md. Mizanur Rahman | 2019-04-17 | MN1018 | 5.1 | 187 | 5.1 | 188 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7608 | 1151.9997 | 53.7361
SYL-E.1.RR.75.1 | 24532719153575 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#33, Chowdhury Villa | 2019-04-17 | MN1018 | 26.6 | 191 | 26.6 | 192 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 26.6 | 26.6 | 1.596 | 1.596 | 0.0007168 | 100% | 0% | 1.596 | 1.596 | 0.0011869 | 28 | 0.031994 | 0.031994 |  | 0 | 0 | 7608 | 1151.9997 | 280.2704
SYL-E.1.RR.75.2 | 24532719153575 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#33, Chowdhury Villa | 2021-02-17 | MN1018 | 3.9 | 135 | 3.9 | 136 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7608 | 1151.9997 | 41.0923
SYL-E.1.RR.76.1 | 24532649153580 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#32/A, Abbus & Anas Villa | 2019-04-17 | MN1018 | 1.2 | 189 | 1.2 | 190 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7608 | 1151.9997 | 12.6438
SYL-E.1.RR.77.1 | 24532769153546 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#39, Malik Monjil | 2019-04-17 | MN1018 | 4.4 | 193 | 4.4 | 194 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7608 | 1151.9997 | 46.3605
SYL-E.1.RR.78.1 | 24532699153541 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#96, Junid Ahamad | 2019-04-17 | MN1018 | 43.1 | 198 | 43.1 | 199 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 43.1 | 43.1 | 2.586 | 2.586 | 0.0007168 | 100% | 0% | 2.586 | 2.586 | 0.0011869 | 28 | 0.05184 | 0.05184 |  | 0 | 0 | 7608 | 1151.9997 | 454.1223
SYL-E.1.RR.78.2 | 24532699153541 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#96, Junid Ahamad | 2019-04-17 | MN1018 | 24.2 | 200 | 24.2 | 201 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 24.2 | 24.2 | 1.452 | 1.452 | 0.0007168 | 100% | 0% | 1.452 | 1.452 | 0.0011869 | 28 | 0.029108 | 0.029108 |  | 0 | 0 | 7608 | 1151.9997 | 254.9828
SYL-E.1.RR.79.1 | 24532739153545 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#40, Hazi Watir Ali Villa | 2019-04-17 | MN1018 | 3.6 | 202 | 3.4 | 203 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7608 | 1151.9997 | 35.824
SYL-E.1.RR.80.1 | 24532579153528 | Sylhet Sadar, Sibgonj, Golapbugh R/A, H#85, Khan Monjil, Toyob Khan | 2019-04-17 | MN1018 | 5.9 | 204 | 5.7 | 205 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7608 | 1151.9997 | 60.0579
SYL-E.1.RR.81.1 | 24532469153529 | Sylhet, Sibgonj, Golapbag R/A, H # 76/5, Johur Mia | 2019-04-17 | MN1018 | 1.7 | 210 | 1.7 | 211 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7608 | 1151.9997 | 17.912
SYL-E.1.RR.82.1 | 24532199153545 | Sylhet, Sibgonj, Golapbag R/A, H # 72/3, Tahomid Monjil, Abdul Malek | 2019-04-17 | MN1018 | 1.5 | 212 | 1.4 | 213 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7608 | 1151.9997 | 14.7511
SYL-E.1.RR.82.2 | 24532199153545 | Sylhet, Sibgonj, Golapbag R/A, H # 72/3, Tahomid Monjil, Abdul Malek | 2021-02-17 | MN1018 | 5.6 | 133 | 5.6 | 134 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7608 | 1151.9997 | 59.0043
SYL-E.1.RR.83.1 | 24532569153560 | Sylhet, Sibgonj, Golapbag R/A, H # 54, Jalal Uddin | 2019-04-17 | MN1018 | 1.3 | 219 | 1.3 | 220 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7608 | 1151.9997 | 13.6974
SYL-E.1.RR.84.1 | 24532509153576 | Sylhet, Sibgonj, Golapbag R/A, H # 56, Abdul Mosabir, Esita Stor | 2019-04-17 | MN1018 | 1 | 221 | 1 | 222 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7608 | 1151.9997 | 10.5365
SYL-E.1.RR.85.1 | 24532539153586 | Sylhet, Sibgonj, Golapbag R/A, H # 60, Najma Begom | 2019-04-17 | MN1018 | 1.1 | 223 | 1.1 | 224 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7608 | 1151.9997 | 11.5901
SYL-E.1.RR.86.1 | 24532559153585 | Sylhet, Sibgonj, Golapbag R/A, H # 58/1, Shahan Monjil | 2019-04-17 | MN1018 | 1.3 | 225 | 1.3 | 226 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7608 | 1151.9997 | 13.6974
SYL-E.1.RR.87.1 | 24532779153468 | Sylhet, Sibgonj, Sobujbag R/A, H # 6, Abdul Kayem | 2019-04-17 | MN1018 | 3 | 227 | 3 | 228 | 2022-01-01 | 2022-11-14 | NQ1007 |  |  | 0 | 162 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7608 | 1151.9997
SYL-E.1.RR.88.1 | 24532609153489 | Sylhet, Sibgonj, Sobujbag R/A, H # 7/3, Khanom Villa | 2019-04-17 | MN1018 | 11.1 | 229 | 11.1 | 230 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7608 | 1151.9997 | 116.9549
SYL-E.1.RR.89.1 | 24532409153470 | Sylhet, Sibgonj, Sobujbag R/A, H # 9/10, Khan Monjil | 2019-04-17 | MN1018 | 6.1 | 231 | 6.1 | 232 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7608 | 1151.9997 | 64.2725
SYL-E.1.RR.90.1 | 24533539152568 | Sylhet, Jothorpur, Novopuspo, R/A, H # 91, Razia Villa | 2019-04-18 | MN1032 | 1.6 | 183 | 1.5 | 184 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7512 | 1247.9997 | 15.8047
SYL-E.1.RR.91.1 | 24533059152533 | Sylhet, Jothorpur, Novopuspo, R/A, H # 10, Sirajol Haque | 2019-04-18 | MN1032 | 2.4 | 185 | 2.4 | 186 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7488 | 1271.9997 | 25.2876
SYL-E.1.RR.92.1 | 24533149152519 | Sylhet Sadar, Jothorpur, Mowban-22, Sadeq Ahmed | 2019-04-18 | MN1032 | 1 | 188 | 1.1 | 189 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7488 | 1271.9997 | 11.5901
SYL-E.1.RR.93.1 | 24532759152524 | Sylhet Sadar, Shobhanighat, Mowban 30/3, ShahNewaj | 2019-04-18 | MN1032 | 2 | 192 | 1.9 | 193 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7488 | 1271.9997 | 20.0193
SYL-E.1.RR.94.1 | 24532499152507 | Sylhet Sadar, Shobhanighat, Mowban, H # 35 | 2019-04-18 | MN1032 | 1.8 | 194 | 1.8 | 195 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7488 | 1271.9997 | 18.9657
SYL-E.1.RR.101.1 | 24542049155205 | Sylhet Sadar, Shahporan, Khadim Para, Road No-2, Jewel | 2019-04-09 | LP1002 | 1.7 | 3 | 1.7 | 4 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 8088 | 671.9997 | 17.912
SYL-E.1.RR.102.1 | 24542489155193 | Sylhet Sadar, Shahporan, Khadim Para, Road No-2, H#14, Saira Vila | 2019-04-09 | LP1002 | 1.6 | 9 | 1.5 | 10 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 8088 | 671.9997 | 15.8047
SYL-E.1.RR.103.1 | 24542809155162 | Sylhet Sadar, Shahporan, Khadim Para, Road No-2, Akram Hossain | 2019-04-09 | LP1002 | 4.6 | 12 | 4.6 | 13 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 8088 | 671.9997 | 48.4678
SYL-E.1.RR.104.1 | 24543029155147 | Sylhet Sadar, Shahporan, Khadimpara, Road No-2, H # 80, Abu Bakkar | 2019-04-10 | LP1002 | 1.5 | 17 | 1.5 | 18 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 8088 | 671.9997 | 15.8047
SYL-E.1.RR.105.1 | 24543109155149 | Sylhet Sadar, Shahporan, Khadimpara, Rd # 2, Nannu Mia | 2019-04-10 | LP1002 | 1.2 | 19 | 1.2 | 20 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8088 | 671.9997 | 12.6438
SYL-E.1.RR.106.1 | 24543109155149 | Sylhet Sadar, Shahporan, Khadimpara, Rd # 2, A. Mannan | 2019-04-10 | LP1002 | 1.6 | 21 | 1.6 | 22 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 8088 | 671.9997 | 16.8584
SYL-E.1.RR.106.2 | 24543109155149 | Sylhet Sadar, Shahporan, Khadimpara, Rd # 2, A. Mannan | 2021-11-04 | LU1001 | 4.1 | 139 | 4.1 | 140 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 8088 | 671.9997 | 43.1996
SYL-E.1.RR.107.1 | 24542489155177 | Sylhet Sadar, Shahporan, Khadimpara, Rd # 2, Anwar Hossain | 2019-04-10 | LP1002 | 1.1 | 23 | 1.1 | 24 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 8088 | 671.9997 | 11.5901
SYL-E.1.RR.108.1 | 24543139155341 | Sylhet Sadar, Khadimpara, Rd # 8, Abdul Malik | 2019-04-10 | LP1002 | 10.5 | 25 | 10.5 | 26 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8088 | 671.9997 | 110.6331
SYL-E.1.RR.108.2 | 24543139155341 | Sylhet Sadar, Khadimpara, Rd # 8, Abdul Malik | 2022-12-04 | NQ1007 | 7.7 | 250 | 7.7 | 251 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 0 | 671.9997 | 6.2237
SYL-E.1.RR.109.1 | 24543149155296 | Sylhet Sadar, Khadimpara, Rd # 6, Hazi Abdullah | 2019-04-10 | LP1002 | 6.4 | 27 | 6.4 | 28 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8088 | 671.9997 | 67.4335
SYL-E.1.RR.110.1 | 24543359155300 | Sylhet Sadar, Khadimpara, Rd # 6, Alauddin | 2019-04-10 | LP1002 | 1.7 | 29 | 1.6 | 30 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 8088 | 671.9997 | 16.8584
SYL-E.1.RR.111.1 | 24543219155371 | Sylhet Sadar, Shahporan, Khadimpara, Bohor R/A, BIDC Road, Selim | 2019-04-11 | LP1002 | 1.4 | 33 | 1.4 | 34 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 8088 | 671.9997 | 14.7511
SYL-E.1.RR.112.1 | 24543299155376 | Khadimpara, BIDC, Rd # 8, H # 13, Mrs. Nargis Begum | 2019-04-11 | LP1002 | 1.1 | 36 | 1.1 | 37 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 8088 | 671.9997 | 11.5901
SYL-E.1.RR.113.1 | 24543789155318 | Sylhet Sadar, Shahporan, Al Baraka R/A, Rd # 1, Block-B, H # 2, Jahurul Haque | 2019-04-11 | LP1002 | 1.6 | 38 | 1.6 | 39 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 8088 | 671.9997 | 16.8584
SYL-E.1.RR.114.1 | 24544069155320 | Sylhet Sadar, Shahporan, Al Baraka R/A, Al Baraka Main Road, H # 5, Faruk Ahmed | 2019-04-11 | LP1002 | 10.5 | 42 | 10.5 | 43 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8088 | 671.9997 | 110.6331
SYL-E.1.RR.115.1 | 24543789155356 | Sylhet Sadar, Shahporan, BIDC R/A, Nuruddin | 2019-04-11 | LP1002 | 2.3 | 44 | 2.3 | 45 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8088 | 671.9997 | 24.2339
SYL-E.1.RR.116.1 | 24544089155357 | Sylhet Sadar, Shahporan, BIDC R/A, Alamgir Hossain | 2019-04-11 | LP1002 | 1.6 | 48 | 1.6 | 49 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 8088 | 671.9997 | 16.8584
SYL-E.1.RR.116.2 | 24544089155357 | Sylhet Sadar, Shahporan, BIDC R/A, Alamgir Hossain | 2019-04-11 | LP1002 | 1.9 | 50 | 1.9 | 51 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8088 | 671.9997 | 20.0193
SYL-E.1.RR.117.1 | 24544219155340 | Sylhet Sadar, Shahporan, BIDC R/A, Bohor Residential Area, Moslem Uddin | 2019-04-11 | LP1002 | 1 | 54 | 1 | 55 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 8088 | 671.9997 | 10.5365
SYL-E.1.RR.118.1 | 24544119155376 | Sylhet Sadar, Shahporan, BIDC , Bohor Residential Area, Abdul Motin | 2019-04-11 | LP1002 | 3.5 | 56 | 3.5 | 57 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 8088 | 671.9997 | 36.8777
SYL-E.1.RR.119.1 | 24544209155379 | Sylhet Sadar, Shahporan, BIDC , Bohor Residential Area, Md. Khorshed Alam | 2019-04-11 | LP1002 | 50.3 | 61 | 50.1 | 62 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 50.1 | 50.1 | 3.006 | 3.006 | 0.0007168 | 100% | 0% | 3.006 | 3.006 | 0.0011869 | 28 | 0.06026 | 0.06026 |  | 0 | 0 | 8088 | 671.9997 | 527.8777
SYL-E.1.RR.120.1 | 24544509155354 | Sylhet Sadar, Shahporan, Bahar R/A, Rd # 1, H # 83, Rumon Gazi | 2019-04-12 | LP1002 | 4.2 | 63 | 4.2 | 64 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 8088 | 671.9997 | 44.2532
SYL-E.1.RR.121.1 | 24544539155340 | Sylhet Sadar, Shahporan, Bahar R/A, Rd # 1, Razu Ahmed | 2019-04-12 | LP1002 | 3.8 | 66 | 3.8 | 67 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8088 | 671.9997 | 40.0386
SYL-E.1.RR.121.2 | 24544539155340 | Sylhet Sadar, Shahporan, Bahar R/A, Rd # 1, Razu Ahmed | 2021-11-04 | LU1001 | 4.8 | 141 | 4.8 | 142 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8088 | 671.9997 | 50.5751
SYL-E.1.RR.122.1 | 24544639155312 | Sylhet Sadar, Shahporan, Bahar R/A, Rd # 1, Aktaruzzaman | 2019-04-12 | LP1002 | 14.4 | 68 | 14.4 | 69 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 8088 | 671.9997 | 151.7253
SYL-E.1.RR.123.1 | 24544679155308 | Sylhet Sadar, Shahporan, Bahar R/A, Rd # 1, Romijuddin | 2019-04-12 | LP1002 | 1 | 70 | 1 | 71 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 8088 | 671.9997 | 10.5365
SYL-E.1.RR.124.1 | 24544589156027 | Sylhet Sadar, Khadimnagar, Bahubol R/A, Rd # 2, Md. Abdul Motin | 2019-04-12 | LP1002 | 3.1 | 72 | 3.1 | 73 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7632 | 1127.9997 | 32.6631
SYL-E.1.RR.125.1 | 24544959156038 | Sylhet Sadar, Shahporan, Khadimnagar, Bahubol R/A, Rd # 3, Ranjan Biswas | 2019-04-12 | LP1002 | 5.2 | 76 | 5.1 | 77 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7632 | 1127.9997 | 53.7361
SYL-E.1.RR.126.1 | 24545429156053 | Sylhet Sadar, Shahporan, Khadimnagar, Bahubol R/A, Rd # 4, Habbab Chowdhury | 2019-04-12 | LP1002 | 4.1 | 78 | 4.1 | 79 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7632 | 1127.9997 | 43.1996
SYL-E.1.RR.127.1 | 24550849156138 | Shahporan, Uposhohor R/A, Rd# 03, H# 03, Abdul Malek | 2019-04-13 | LP1002 | 4.9 | 80 | 4.9 | 81 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7632 | 1127.9997 | 51.6288
SYL-E.1.RR.128.1 | 24550739156123 | Shahporan, Uposhohor R/A, Rd# 03, Abdur Rohim Masuk | 2019-04-13 | LP1002 | 2.9 | 82 | 3 | 83 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7632 | 1127.9997 | 31.6094
SYL-E.1.RR.129.1 | 24550359156152 | Shahporan R/A, Cha Bagan Street,Rd# 02, H# 1, Rakib Ali | 2019-04-13 | LP1002 | 1.1 | 84 | 1.1 | 85 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7632 | 1127.9997 | 11.5901
SYL-E.1.RR.130.1 | 24550179156137 | Shahporan Uposhohor R/A, Rd#2, APU | 2019-04-13 | LP1002 | 1.3 | 88 | 1.3 | 89 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 8280 | 479.9997 | 13.6974
SYL-E.1.RR.131.1 | 24550499156305 | Shahporan, Khadim Nagar, Rustompur, Nilupa Begum | 2019-04-13 | LP1002 | 1.5 | 92 | 1.5 | 93 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7632 | 1127.9997 | 15.8047
SYL-E.1.RR.131.2 | 24550499156305 | Shahporan, Khadim Nagar, Rustompur, Nilupa Begum | 2021-02-25 | LX1011 | 1.9 | 162 | 1.9 | 163 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7632 | 1127.9997 | 20.0193
SYL-E.1.RR.132.1 | 24551639157061 | Shahporan, Khadim Nagar, Chakgram R/A, Abdus Salam | 2019-04-13 | LP1002 | 0.9 | 94 | 0.9 | 95 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 0.9 | 0.9 | 0.054 | 0.054 | 0.0007168 | 100% | 0% | 0.054 | 0.054 | 0.0011869 | 28 | 0.0010825 | 0.0010825 |  | 0 | 0 | 7632 | 1127.9997 | 9.4828
SYL-E.1.RR.133.1 | 24525659153066 | Sylhet, Shahjalal Uposohor, Block-F, Rd # 2, H # 58 | 2019-04-15 | LP1002 | 1 | 106 | 1 | 107 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7488 | 1271.9997 | 10.5365
SYL-E.1.RR.134.1 | 24530059153101 | Sylhet, Shahjalal Uposohor, Block-F, Rd # 1/A, Md. Liakot Hossain | 2019-04-15 | LP1002 | 1.3 | 108 | 1.3 | 109 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7488 | 1271.9997 | 13.6974
SYL-E.1.RR.134.2 | 24530059153101 | Sylhet, Shahjalal Uposohor, Block-F, Rd # 1/A, Md. Liakot Hossain | 2021-02-10 | MN1018 | 9.5 | 98 | 9.5 | 99 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7488 | 1271.9997 | 100.0966
SYL-E.1.RR.135.1 | 24530059153101 | Sylhet, Shahjalal Uposohor, Block-F, Rd # 1/A, Md. Liakot Hossain | 2019-04-15 | LP1002 | 1.4 | 110 | 1.4 | 111 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7488 | 1271.9997 | 14.7511
SYL-E.1.RR.136.1 | 24530489153039 | Sylhet, Shahjalal Uposohor, Block-E, Rd # 5, H # 180 | 2019-04-15 | LP1002 | 2.4 | 112 | 2.4 | 113 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7488 | 1271.9997 | 25.2876
SYL-E.1.RR.137.1 | 24530849153027 | Sylhet, Shahjalal Uposohor, Block-E, Rd # 3, H # 97, Mostofa Kamal | 2019-04-15 | LP1002 | 1.5 | 118 | 1.5 | 119 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7488 | 1271.9997 | 15.8047
SYL-E.1.RR.138.1 | 24530809153023 | Sylhet, Shahjalal Uposohor, Block-E, Rd # 3, H # 80, Shirajul Islam | 2019-04-15 | LP1002 | 1.7 | 120 | 1.7 | 121 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7488 | 1271.9997 | 17.912
SYL-E.1.RR.139.1 | 24530589152588 | Sylhet, Shahjalal Uposohor, Block-E, Rd # 3, H # 88/3E, Roshid Ahmed | 2019-04-15 | LP1002 | 2.2 | 122 | 2.2 | 123 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7488 | 1271.9997 | 23.1803
SYL-E.1.RR.140.1 | 24530749152573 | Sylhet, Shahjalal Uposohor, Block-E, Rd # 2, H # 40/2 | 2019-04-15 | LP1002 | 1.7 | 124 | 1.6 | 125 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7488 | 1271.9997 | 16.8584
SYL-E.1.RR.141.1 | 24531589153269 | Sylhet, Shahjalal Uposhohor, Block-c, Rd # 44, H # 71, Bagan Bilash | 2019-04-16 | LP1002 | 2.1 | 136 | 2.1 | 137 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7584 | 1175.9997 | 22.1266
SYL-E.1.RR.142.1 | 24531279153236 | Sylhet, Terroton, Uposhohor, Block-C, Rd # 43, H # 50, Salek Ahmed | 2019-04-16 | LP1002 | 12.4 | 141 | 12.4 | 142 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7584 | 1175.9997 | 130.6524
SYL-E.1.RR.143.1 | 24531089153296 | Sylhet, Terroton, Uposhohor, Block-C, H # 10, Kodor Ahmed | 2019-04-16 | LP1002 | 15.2 | 143 | 15.2 | 144 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7584 | 1175.9997 | 160.1545
SYL-E.1.RR.144.1 | 24531169153303 | Sylhet, Terroton, Uposhohor, Block-C, Rd # 43, H # 14, Atikur Rahman | 2019-04-16 | LP1002 | 2 | 145 | 2 | 146 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7584 | 1175.9997 | 21.073
SYL-E.1.RR.145.1 | 24531059153277 | Sylhet, Terroton, Uposhohor, Block-C, Rd # 43, Alkas Mia | 2019-04-16 | LP1002 | 4.6 | 147 | 4.6 | 148 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7584 | 1175.9997 | 48.4678
SYL-E.1.RR.146.1 | 24531019153277 | Sylhet, Terroton, Uposhohor, Block-C, Rd # 43, H # 52, Omar Shah | 2019-04-16 | LP1002 | 2.8 | 149 | 2.8 | 150 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7584 | 1175.9997 | 29.5021
SYL-E.1.RR.147.1 | 24531039153337 | Sylhet, Shahjalal Uposhohor, Terroton, Rd # 44, London Coloni, Faruk Mia | 2019-04-16 | LP1002 | 1.3 | 153 | 1.3 | 154 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7584 | 1175.9997 | 13.6974
SYL-E.1.RR.201.1 | 24535379154278 | Sylhet Sadar, Islampur Main Road, Shamoli R/A, R# 2, H# 8 | 2019-04-09 | MP1032 | 1.5 | 1 | 1.4 | 2 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7656 | 1103.9997 | 14.7511
SYL-E.1.RR.202.1 | 24535549154296 | Sylhet Sadar, Islampur Main Road, Shamoli R/A, R# 2, H#11 | 2019-04-09 | MP1032 | 5.1 | 4 | 4.9 | 5 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7656 | 1103.9997 | 51.6288
SYL-E.1.RR.202.2 | 24535549154296 | Sylhet Sadar, Islampur Main Road, Shamoli R/A, R# 2, H#11 | 2020-10-18 | MP1006 | 4.5 | 498 | 4.5 | 499 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7656 | 1103.9997 | 47.4142
SYL-E.1.RR.203.1 | 24535729154306 | Sylhet Sadar, Islampur, Shamoli R/A, Road#2, House#12/5 | 2019-04-09 | MP1032 | 2.6 | 6 | 2.5 | 7 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7656 | 1103.9997 | 26.3412
SYL-E.1.RR.204.1 | 24535689154278 | Sylhet Sadar, Islampur, Shamoli R/A, H# 17/2, Asrafuddin | 2019-04-09 | MP1032 | 3.5 | 8 | 3.4 | 9 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7656 | 1103.9997 | 35.824
SYL-E.1.RR.205.1 | 24535509154240 | Sylhet Sadar, Islampur, Shamoli R/A, Road#1, House#109 | 2019-04-09 | MP1032 | 4 | 10 | 4 | 11 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7656 | 1103.9997 | 42.1459
SYL-E.1.RR.206.1 | 24540159154223 | Sylhet Sadar, Majortila, Islampur, Shamoli R/A, Rd # 1/8, H # 72, Mohiuddin | 2019-04-10 | MP1032 | 6.2 | 14 | 6.2 | 15 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7656 | 1103.9997 | 65.3262
SYL-E.1.RR.207.1 | 24540199154218 | Sylhet Sadar, Majortila, Islampur, Shamoli R/A, Block - A, Rd # 8, H # 26 | 2019-04-10 | MP1032 | 2.4 | 16 | 2.4 | 17 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7656 | 1103.9997 | 25.2876
SYL-E.1.RR.208.1 | 24540749154204 | Sylhet Sadar, Majortila, Islampur, Shamoli R/A, Block - D, Rd # 11, H # 9 | 2019-04-10 | MP1032 | 3 | 18 | 3.1 | 19 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7656 | 1103.9997 | 32.6631
SYL-E.1.RR.209.1 | 24541049154208 | Sylhet Sadar, Majortila, Islampur, Shamoli R/A, Block - D, Rd # 13, H # 35 | 2019-04-10 | MP1032 | 10.9 | 20 | 10.6 | 21 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7656 | 1103.9997 | 111.6867
SYL-E.1.RR.210.1 | 24540339154239 | Sylhet Sadar, Majortila, Islampur, Shamoli R/A, Rd # 1, H # 904, Motin | 2019-04-10 | MP1032 | 3.5 | 22 | 3.3 | 23 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7656 | 1103.9997 | 34.7704
SYL-E.1.RR.211.1 | 24541249154244 | Sylhet Sadar, Majortila, Islampur, Block - E, Rd # 15, H # 10, Khonikaloy | 2019-04-10 | MP1032 | 4.4 | 24 | 4.2 | 25 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7656 | 1103.9997 | 44.2532
SYL-E.1.RR.212.1 | 24540419154267 | Sylhet Sadar, Majortila, Islampur, Block - C, Rd # 5, H # 30 | 2019-04-10 | MP1032 | 1.2 | 26 | 1.2 | 27 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7656 | 1103.9997 | 12.6438
SYL-E.1.RR.213.1 | 24540089154272 | Sylhet Sadar, Majortila, Islampur, Shamoli R/A, Rd # 3, H # 13 | 2019-04-10 | MP1032 | 5.1 | 30 | 4.9 | 31 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7656 | 1103.9997 | 51.6288
SYL-E.1.RR.214.1 | 24541409155110 | Sylhet Sadar, East Islampur, Chamilybagh R/A, Rd # 3, H # 2/1 | 2019-04-11 | MP1032 | 1.1 | 32 | 1.2 | 33 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8088 | 671.9997 | 12.6438
SYL-E.1.RR.215.1 | 24541619155126 | Sylhet Sadar, East Islampur, Chamilybagh R/A, Rd # 3, H # 12 | 2019-04-11 | MP1032 | 2.1 | 34 | 2.1 | 35 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 8088 | 671.9997 | 22.1266
SYL-E.1.RR.216.1 | 24543459155442 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 2 | 2019-04-11 | MP1032 | 4.5 | 36 | 4.5 | 37 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7776 | 983.9997 | 47.4142
SYL-E.1.RR.217.1 | 24543519155437 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 6/1 | 2019-04-11 | MP1032 | 4.2 | 38 | 4 | 39 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7776 | 983.9997 | 42.1459
SYL-E.1.RR.217.2 | 24543519155437 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 6/1 | 2019-04-11 | MP1032 | 8.2 | 40 | 8.2 | 41 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7776 | 983.9997 | 86.3991
SYL-E.1.RR.218.1 | 24543529155406 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 14 | 2019-04-11 | MP1032 | 1.1 | 42 | 1.1 | 43 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7776 | 983.9997 | 11.5901
SYL-E.1.RR.219.1 | 24543489155411 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 16 | 2019-04-11 | MP1032 | 7.7 | 44 | 7.8 | 45 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7776 | 983.9997 | 82.1846
SYL-E.1.RR.220.1 | 24543449155412 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 17 | 2019-04-11 | MP1032 | 5.2 | 46 | 5.2 | 47 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7776 | 983.9997 | 54.7897
SYL-E.1.RR.221.1 | 24544079155452 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 23, Narayan | 2019-04-11 | MP1032 | 1.7 | 50 | 1.7 | 51 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7776 | 983.9997 | 17.912
SYL-E.1.RR.222.1 | 24543909155440 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, Rd # 1, H # 23, Nirendra Kumar | 2019-04-11 | MP1032 | 11 | 52 | 10.6 | 53 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7776 | 983.9997 | 111.6867
SYL-E.1.RR.223.1 | 24544239155428 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H # 28, Md. Abu Taher | 2019-04-12 | MP1032 | 2.2 | 54 | 2.1 | 55 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7776 | 983.9997 | 22.1266
SYL-E.1.RR.223.2 | 24544239155428 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H # 28, Md. Abu Taher | 2022-11-21 | NQ1007 | 3.7 | 175 | 3.7 | 176 | 2022-11-21 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 0 | 983.9997 | 4.3791
SYL-E.1.RR.224.1 | 24544379155460 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H # 29/3, Rukon | 2019-04-12 | MP1032 | 1.5 | 56 | 1.5 | 57 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7776 | 983.9997 | 15.8047
SYL-E.1.RR.225.1 | 24544349155461 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H# 29/1, Babul | 2019-04-12 | MP1032 | 1.6 | 58 | 1.6 | 59 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7776 | 983.9997 | 16.8584
SYL-E.1.RR.225.2 | 24544349155461 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H# 29/1, Babul | 2019-04-12 | MP1032 | 2.5 | 60 | 2.7 | 61 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7776 | 983.9997 | 28.4485
SYL-E.1.RR.226.1 | 24544259155462 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H # 31 | 2019-04-12 | MP1032 | 4.3 | 64 | 4.3 | 65 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7776 | 983.9997 | 45.3069
SYL-E.1.RR.227.1 | 24544439155469 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H # 39/5 | 2019-04-12 | MP1032 | 1 | 66 | 1 | 67 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7776 | 983.9997 | 10.5365
SYL-E.1.RR.228.1 | 24544509155472 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H # 30/A | 2019-04-12 | MP1032 | 2.1 | 75 | 2.1 | 76 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7776 | 983.9997 | 22.1266
SYL-E.1.RR.228.2 | 24544509155472 | Sylhet Sadar, Khadimnagar, Shantibagh R/A, H # 30/A | 2019-04-12 | MP1032 | 1.7 | 77 | 1.7 | 78 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7776 | 983.9997 | 17.912
SYL-E.1.RR.230.1 | 24545329156105 | Sylhet, Khadimnagar, SahParan R/A, Block - A, Rd # 3, Shahinul Huq | 2019-04-13 | MP1032 | 2.3 | 81 | 2.3 | 82 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7632 | 1127.9997 | 24.2339
SYL-E.1.RR.231.1 | 24545599156091 | Sylhet, Khadimnagar, SahParan R/A, Block - A, Rd # 3, H # 18 | 2019-04-13 | MP1032 | 1.2 | 85 | 1.2 | 86 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7632 | 1127.9997 | 12.6438
SYL-E.1.RR.232.1 | 24545449156062 | Sylhet, Khadimnagar, SahParan R/A, Block - A, Rd # 3, H # 11 | 2019-04-13 | MP1032 | 6.8 | 87 | 6.8 | 88 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7632 | 1127.9997 | 71.6481
SYL-E.1.RR.233.1 | 24545989156147 | Sylhet, Khadimnagar, SahParan R/A, Block - A, Rd # 3, H # 5, Anwar Islam | 2019-04-13 | MP1032 | 1 | 89 | 1 | 90 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7632 | 1127.9997 | 10.5365
SYL-E.1.RR.234.1 | 24545979156135 | Sylhet, Khadimnagar, SahParan R/A, Block - A, Rd # 5, Loni Begum | 2019-04-13 | MP1032 | 1.2 | 91 | 1.2 | 92 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7632 | 1127.9997 | 12.6438
SYL-E.1.RR.235.1 | 24545989156131 | Sylhet, Khadimnagar, SahParan R/A, Block - A, Rd # 5, Mojnul Islam | 2019-04-13 | MP1032 | 5.3 | 93 | 5.1 | 94 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7632 | 1127.9997 | 53.7361
SYL-E.1.RR.235.2 | 24545989156131 | Sylhet, Khadimnagar, SahParan R/A, Block - A, Rd # 5, Mojnul Islam | 2022-11-15 | NQ1007 | 4 | 164 | 4 | 165 | 2022-11-15 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 0 | 1127.9997 | 5.427
SYL-E.1.RR.236.1 | 24550469157066 | Sylhet, Biyani Bazar, Siraj Uddin | 2019-04-13 | MP1032 | 3.4 | 95 | 3.3 | 96 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7632 | 1127.9997 | 34.7704
SYL-E.1.RR.237.1 | 24525559153255 | Sylhet Sadar, Shadipur-2, Shada Tikor, Md. Shahin Mia | 2019-04-15 | MP1032 | 3.4 | 124 | 3.3 | 125 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7488 | 1271.9997 | 34.7704
SYL-E.1.RR.238.1 | 24524169153489 | Sylhet Sadar, Borhan Uddin Road, Kushighat, Block-C, H#86, Tota Mia | 2019-04-15 | MP1032 | 4.5 | 126 | 4.5 | 127 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 2736 | 0 | 4728 | 1295.9997 | 32.6054
SYL-E.1.RR.239.1 | 24524349153494 | Sylhet Sadar, Borhan Uddin Road, Kushighat, Block-C, H#105 | 2019-04-15 | MP1032 | 1.2 | 128 | 1.1 | 129 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7464 | 1295.9997 | 11.5901
SYL-E.1.RR.240.1 | 24524339153490 | Sylhet Sadar, Borhan Uddin Road, Kushighat, Block-C, H#101 | 2019-04-15 | MP1032 | 3.4 | 130 | 3.5 | 131 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7464 | 1295.9997 | 36.8777
SYL-E.1.RR.241.1 | 24524369153525 | Sylhet Sadar, Borhan Uddin Road, Kushighat, Block-C, Nesar Ahmed | 2019-04-15 | MP1032 | 2.6 | 133 | 2.6 | 134 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7464 | 1295.9997 | 27.3949
SYL-E.1.RR.242.1 | 24524089153499 | Sylhet Sadar, Borhan Uddin Road, Kushighat, Block-C, Infrfont Of Kushighat Jame Mosque | 2019-04-15 | MP1032 | 35.6 | 135 | 35.6 | 136 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 35.6 | 35.6 | 2.136 | 2.136 | 0.0007168 | 100% | 0% | 2.136 | 2.136 | 0.0011869 | 28 | 0.042819 | 0.042819 |  | 0 | 0 | 7464 | 1295.9997 | 375.0987
SYL-E.1.RR.243.1 | 24530549154012 | Sylhet Sadar, Shahaporan, Block- A, Rd # 7, Mirpara, H # 182 | 2019-04-16 | MP1032 | 11.6 | 153 | 11.5 | 154 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7464 | 1295.9997 | 121.1695
SYL-E.1.RR.244.1 | 24530549154012 | Sylhet Sadar, Shahaporan, Block- A, Rd # 7, Mirpara, H # 183 | 2019-04-16 | MP1032 | 1.3 | 155 | 1.3 | 156 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7464 | 1295.9997 | 13.6974
SYL-E.1.RR.245.1 | 24530539154025 | Sylhet Sadar, Shahaporan, Block- A, Rd # 7, Mirpara, H # 184 | 2019-04-16 | MP1032 | 1.1 | 157 | 1.1 | 158 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7464 | 1295.9997 | 11.5901
SYL-E.1.RR.246.1 | 24530489154058 | Sylhet Sadar, Shahaporan, Block- A, Mirpara, Tilagor, Rd # 7, H # 189 | 2019-04-16 | MP1032 | 3.6 | 159 | 3.6 | 160 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7464 | 1295.9997 | 37.9313
SYL-E.1.RR.247.1 | 24530439154074 | Sylhet Sadar, Shahaporan, Block- A, Mirpara, Tilagor, Rd # 7, Md. Jahangir | 2019-04-16 | MP1032 | 18.5 | 165 | 18.5 | 166 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 7464 | 1295.9997 | 194.9249
SYL-E.1.RR.248.1 | 24530809154037 | Sylhet, Shahaporan, Tulikor, Mirapara, Burhanuddin Road, Block- B, H # 159 | 2019-04-16 | MP1032 | 1.3 | 169 | 1.3 | 170 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7464 | 1295.9997 | 13.6974
SYL-E.1.RR.248.2 | 24530809154037 | Sylhet, Shahaporan, Tulikor, Mirapara, Burhanuddin Road, Block- B, H # 159 | 2021-02-09 | LX1011 | 4 | 103 | 4 | 104 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7464 | 1295.9997 | 42.1459
SYL-E.1.RR.249.1 | 24530799154033 | Sylhet, Shahaporan, Mirapara, Burhanuddin Road, Block- A, H # 175 | 2019-04-16 | MP1032 | 2.5 | 171 | 2.5 | 172 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7464 | 1295.9997 | 26.3412
SYL-E.1.RR.250.1 | 24530859154034 | Sylhet, Shahaporan, Block- A, Mirapara, Burhanuddin Road, Ajmol Ali | 2019-04-16 | MP1032 | 1.5 | 173 | 1.5 | 174 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7464 | 1295.9997 | 15.8047
SYL-E.1.RR.250.2 | 24530859154034 | Sylhet, Shahaporan, Block- A, Mirapara, Burhanuddin Road, Ajmol Ali | 2020-10-18 | MP1006 | 4.7 | 565 | 4.7 | 566 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7464 | 1295.9997 | 49.5215
SYL-E.1.RR.251.1 | 24530859154041 | Sylhet, Shahaporan, Block- A, Mirapara, Burhanuddin Road, Giashuddin | 2019-04-16 | MP1032 | 3.8 | 175 | 3.8 | 176 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-E.1.RR.252.1 | 24530909154045 | Sylhet, Shahaporan, Mirapara, Burhanuddin Road, H # 170 | 2019-04-16 | MP1032 | 3.8 | 177 | 3.8 | 178 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-E.1.RR.253.1 | 24533009154054 | Sylhet, Tilagor, Shaplabag R/A, Rd # 3, Morshed Ali | 2019-04-16 | MP1032 | 2.5 | 181 | 2.5 | 182 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7608 | 1151.9997 | 26.3412
SYL-E.1.RR.254.1 | 24533299154068 | Sylhet, Tilagor, Shaplabag R/A, Rd # 3, H # 29, Moklhies Khan | 2019-04-16 | MP1032 | 3.5 | 183 | 3.5 | 184 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7680 | 1079.9997 | 36.8777
SYL-E.1.RR.255.1 | 24533849153588 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 32 | 2019-04-17 | MP1032 | 1.1 | 211 | 1.1 | 212 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7680 | 1079.9997 | 11.5901
SYL-E.1.RR.256.1 | 24533479153593 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 27 | 2019-04-17 | MP1032 | 6.4 | 213 | 6.4 | 214 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7680 | 1079.9997 | 67.4335
SYL-E.1.RR.257.1 | 24533249153593 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 46 | 2019-04-17 | MP1032 | 1.6 | 215 | 1.6 | 216 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7680 | 1079.9997 | 16.8584
SYL-E.1.RR.258.1 | 24533009154009 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 72 | 2019-04-17 | MP1032 | 1 | 217 | 1 | 218 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7608 | 1151.9997 | 10.5365
SYL-E.1.RR.259.1 | 24533219154028 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 37 | 2019-04-17 | MP1032 | 4.1 | 219 | 4 | 220 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7680 | 1079.9997 | 42.1459
SYL-E.1.RR.259.2 | 24533219154028 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 37 | 2019-04-17 | MP1032 | 4.7 | 221 | 4.5 | 222 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7680 | 1079.9997 | 47.4142
SYL-E.1.RR.260.1 | 24533379154009 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 58 | 2019-04-17 | MP1032 | 1.3 | 223 | 1.3 | 224 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7680 | 1079.9997 | 13.6974
SYL-E.1.RR.261.1 | 24533549154015 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 21 | 2019-04-17 | MP1032 | 2 | 227 | 2 | 228 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7680 | 1079.9997 | 21.073
SYL-E.1.RR.262.1 | 24533579154013 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 50/KA | 2019-04-17 | MP1032 | 1.2 | 229 | 1.2 | 230 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7680 | 1079.9997 | 12.6438
SYL-E.1.RR.263.1 | 24532949154025 | Sylhet, Tilagor, Shaplabag R/A, Block- A, Rd # 1, H # 53 | 2019-04-17 | MP1032 | 5 | 231 | 5 | 232 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7608 | 1151.9997 | 52.6824
SYL-E.1.RR.264.1 | 24534459154052 | Sylhet, Tilagor, Shaplabag, Kalashil Road, H # 10, Ferdous Mia | 2019-04-17 | MP1032 | 10.3 | 234 | 10.3 | 235 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7680 | 1079.9997 | 108.5258
SYL-E.1.RR.265.1 | 24534629154046 | Sylhet, Tilagor, Kalashil, Kalashil Road, H # 9/B, Chairmen Bari | 2019-04-17 | MP1032 | 4.8 | 237 | 4.8 | 238 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8280 | 479.9997 | 50.5751
SYL-E.1.RR.265.2 | 24534629154046 | Sylhet, Tilagor, Kalashil, Kalashil Road, H # 9/B, Chairmen Bari | 2019-04-17 | MP1032 | 1.4 | 239 | 1.4 | 240 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 8280 | 479.9997 | 14.7511
SYL-E.1.RR.266.1 | 24544699155481 | Sylhet Sadar, Khadim Nagor, Bahuboli R/A, Rd # 1, H # 4 | 2019-04-17 | MP1032 | 2.4 | 241 | 2.4 | 242 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7776 | 983.9997 | 25.2876
SYL-E.1.RR.274.1 | 24533199153121 | Sylhet Sadar, Shonarpara, Novoron R/A, H # 165, Raja Mia | 2019-04-20 | MN1032 | 1.7 | 224 | 1.8 | 225 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7512 | 1247.9997 | 18.9657
SYL-E.1.RR.275.1 | 24533229153112 | Sylhet Sadar, Shonarpara, Novoron R/A, H # 317 | 2019-04-20 | MN1032 | 1 | 226 | 1 | 227 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7512 | 1247.9997 | 10.5365
SYL-E.1.RR.276.1 | 24533289153093 | Sylhet Sadar, Shonarpara, Novoron R/A, Ansar Mia | 2019-04-20 | MN1032 | 1.1 | 228 | 1.1 | 229 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7512 | 1247.9997 | 11.5901
SYL-E.1.RR.277.1 | 24533599153089 | Sylhet Sadar, Shonarpara, Novoron R/A, Sayed Taher Ali | 2019-04-20 | MN1032 | 1.1 | 230 | 1.1 | 231 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7512 | 1247.9997 | 11.5901
SYL-E.1.RR.278.1 | 24533579153069 | Sylhet Sadar, Shonarpara, Novoron R/A, Musfique Villa, H # 368 | 2019-04-20 | MN1032 | 1.6 | 232 | 1.6 | 233 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7512 | 1247.9997 | 16.8584
SYL-E.1.RR.279.1 | 24533529153142 | Sylhet Sadar, Shonarpara, Novoron R/A, H # 386 | 2019-04-20 | MN1032 | 1.9 | 234 | 1.9 | 235 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7512 | 1247.9997 | 20.0193
SYL-E.1.RR.280.1 | 24533469153185 | Sylhet Sadar, Shonarpara, Novoron R/A, Nazmul Haque | 2019-04-20 | MN1032 | 1.2 | 236 | 1.2 | 237 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7512 | 1247.9997 | 12.6438
SYL-E.1.RR.281.1 | 24533759153151 | Sylhet Sadar, Shonarpara, Novoron R/A, Zubair | 2019-04-20 | MN1032 | 1 | 238 | 1 | 239 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7512 | 1247.9997 | 10.5365
SYL-E.1.RR.301.1 | 24540509154458 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 1, H # 14/1, Younus | 2019-04-09 | MN1018 | 3.3 | 1 | 3.2 | 2 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7656 | 1103.9997 | 33.7167
SYL-E.1.RR.302.1 | 24540649154461 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 1, H # 18, Lotif | 2019-04-09 | MN1018 | 1.7 | 3 | 1.6 | 4 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7656 | 1103.9997 | 16.8584
SYL-E.1.RR.303.1 | 24540719154456 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 1, Naim Monjil | 2019-04-09 | MN1018 | 12.7 | 7 | 12.5 | 8 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7656 | 1103.9997 | 131.706
SYL-E.1.RR.304.1 | 24540899154430 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 4, Beside H # 14 | 2019-04-09 | MN1018 | 4 | 11 | 3.7 | 12 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7656 | 1103.9997 | 38.985
SYL-E.1.RR.305.1 | 24541079154427 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 4, H # 18 | 2019-04-09 | MN1018 | 3.7 | 13 | 3.9 | 14 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7656 | 1103.9997 | 41.0923
SYL-E.1.RR.306.1 | 24541139154430 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 4, H # 20 | 2019-04-09 | MN1018 | 1.9 | 15 | 1.9 | 16 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7656 | 1103.9997 | 20.0193
SYL-E.1.RR.307.1 | 24541329154426 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 4, H # 24 | 2019-04-09 | MN1018 | 4.4 | 17 | 4.3 | 18 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7656 | 1103.9997 | 45.3069
SYL-E.1.RR.308.1 | 24540339154469 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 1, Advocate M.A Muktadir | 2019-04-10 | MN1018 | 2.4 | 19 | 2.4 | 20 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7656 | 1103.9997 | 25.2876
SYL-E.1.RR.309.1 | 24540299154439 | Sylhet Sadar, Mejortila, Islampur, Purobi R/A, Rd # 1, Rokiya Villah, Fozlur Rahman | 2019-04-10 | MN1018 | 1.5 | 21 | 1.5 | 22 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7656 | 1103.9997 | 15.8047
SYL-E.1.RR.310.1 | 24540789154508 | Sylhet Sadar, Mejortila, Islampur, Mohammadpur R/A, Prottasha 18/B, Apon Nibash | 2019-04-10 | MN1018 | 1.5 | 23 | 1.5 | 24 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7656 | 1103.9997 | 15.8047
SYL-E.1.RR.311.1 | 24540919154515 | Sylhet Sadar, Mejortila, Islampur, Mohammadpur, H # 2, Janani Villa | 2019-04-10 | MN1018 | 1 | 27 | 1 | 28 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7656 | 1103.9997 | 10.5365
SYL-E.1.RR.312.1 | 24541119154497 | Sylhet Sadar, Mejortila, Islampur, Mohammodpur R/A, Prottasha-11, Rasel | 2019-04-10 | MN1018 | 1.3 | 31 | 1.3 | 32 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7656 | 1103.9997 | 13.6974
SYL-E.1.RR.313.1 | 24542379154493 | Sylhet Sadar, Mejortila, Islampur, Mohammadpu R/A, Prottasha, Block # E, H # 2 | 2019-04-10 | MN1018 | 1.8 | 35 | 1.8 | 36 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 8088 | 671.9997 | 18.9657
SYL-E.1.RR.314.1 | 24542379154488 | Sylhet Sadar, Mejortila, Islampur, Mohammadpur R/A, Prottasha, Block # E, H # 3 | 2019-04-10 | MN1018 | 12.2 | 33 | 12.2 | 34 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 8088 | 671.9997 | 128.5451
SYL-E.1.RR.314.2 | 24542379154488 | Sylhet Sadar, Mejortila, Islampur, Mohammadpur R/A, Prottasha, Block # E, H # 3 | 2022-12-04 | NQ1007 | 12.8 | 252 | 12.8 | 253 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 0 | 671.9997 | 10.346
SYL-E.1.RR.315.1 | 24542459154473 | Sylhet Sadar, Mejortila, Islampur, Mohammadpur, Ali Hossen Road, Block # E, Sadek Khan | 2019-04-10 | MN1018 | 1.2 | 37 | 1.2 | 38 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8088 | 671.9997 | 12.6438
SYL-E.1.RR.316.1 | 24542429154438 | Sylhet Sadar, Mejortila, Sayedpur, Udoin-21, Goni Miah | 2019-04-11 | MN1018 | 1.2 | 41 | 1.2 | 42 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8088 | 671.9997 | 12.6438
SYL-E.1.RR.317.1 | 24542649154474 | Sylhet Sadar, Mejortila, Islampur, Mohammadpur R/A, Proythasa, Abdul Hannan | 2019-04-11 | MN1018 | 2 | 45 | 1.9 | 46 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8088 | 671.9997 | 20.0193
SYL-E.1.RR.319.1 | 24542939154434 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Md. Ebadur Rahman | 2019-04-11 | MN1018 | 1.9 | 49 | 1.9 | 50 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8088 | 671.9997 | 20.0193
SYL-E.1.RR.320.1 | 24542919154427 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Udoin-32, Block-B, Robban Monjil | 2019-04-11 | MN1018 | 5.5 | 51 | 5.3 | 52 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 8088 | 671.9997 | 55.8434
SYL-E.1.RR.320.2 | 24542919154427 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Udoin-32, Block-B, Robban Monjil | 2021-02-16 | LX1011 | 5.8 | 140 | 5.8 | 141 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8088 | 671.9997 | 61.1116
SYL-E.1.RR.321.1 | 24542929154424 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Jabbar | 2019-04-11 | MN1018 | 5.7 | 53 | 5.6 | 54 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 8088 | 671.9997 | 59.0043
SYL-E.1.RR.322.1 | 24543049154460 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Udoin, Block-B, H # 37 | 2019-04-11 | MN1018 | 1.4 | 55 | 1.4 | 56 | 2022-01-01 | 2022-12-04 | NQ1007 |  |  | 0 | 243 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8088 | 671.9997
SYL-E.1.RR.323.1 | 24543439154481 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Block-B, H # 61, Ashraf Vila | 2019-04-11 | MN1018 | 2.8 | 59 | 2.8 | 60 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 8088 | 671.9997 | 29.5021
SYL-E.1.RR.324.1 | 24543129154388 | Sylhet Sadar, Mejortila, Islampur, Syedpur, Abdul Bari | 2019-04-12 | MN1018 | 3.6 | 61 | 3.6 | 62 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 8088 | 671.9997 | 37.9313
SYL-E.1.RR.325.1 | 24543299154438 | Sylhet Sadar, Mejortila, Islampur, Syedpur, M.A. Mohit Chowdory | 2019-04-12 | MN1018 | 2.2 | 63 | 2.2 | 64 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 8088 | 671.9997 | 23.1803
SYL-E.1.RR.326.1 | 24543339154435 | Sylhet Sadar, Mejortila, Islampur, Jahanpur, Textile Road, Abdul Malik | 2019-04-12 | MN1018 | 1.8 | 65 | 1.8 | 66 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 8088 | 671.9997 | 18.9657
SYL-E.1.RR.327.1 | 24543529154437 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Odayon, Block-B, Saleha Villa, H # 68 | 2019-04-12 | MN1018 | 1 | 67 | 1 | 68 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 8088 | 671.9997 | 10.5365
SYL-E.1.RR.327.2 | 24543529154437 | Sylhet Sadar, Mejortila, Islampur, Syedpur R/A, Odayon, Block-B, Saleha Villa, H # 68 | 2022-12-04 | NQ1007 | 3.4 | 248 | 3.4 | 249 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 0 | 671.9997 | 2.7481
SYL-E.1.RR.328.1 | 24543549154517 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Moniul Islam | 2019-04-12 | MN1018 | 2.4 | 69 | 2.3 | 70 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8088 | 671.9997 | 24.2339
SYL-E.1.RR.329.1 | 24543759154476 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Renesa - 24, Rasel Ahmed | 2019-04-12 | MN1018 | 1.3 | 71 | 1.2 | 72 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8088 | 671.9997 | 12.6438
SYL-E.1.RR.330.1 | 24543849154487 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Renesa - 27, Md. Joshim Uddin | 2019-04-12 | MN1018 | 1 | 73 | 1 | 74 | 2022-01-01 | 2022-12-04 | NQ1007 | 0.2 | 240 | 0.2 | 241 | 2022-12-04 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8088 | 671.9997
SYL-E.1.RR.331.1 | 24543579154531 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Shorif Mia | 2019-04-12 | MN1018 | 2.9 | 75 | 2.9 | 76 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 8088 | 671.9997 | 30.5558
SYL-E.1.RR.331.2 | 24543579154531 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Shorif Mia | 2022-12-04 | NQ1007 | 5.1 | 246 | 5.4 | 247 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 0 | 671.9997 | 4.3647
SYL-E.1.RR.332.1 | 24543829154544 | Sylhet Sadar, Mejortila, Islampur, Jahanpur, Plot # 27, Haji Komor Uddin | 2019-04-12 | MN1018 | 10.1 | 77 | 10.1 | 78 | 2022-01-01 | 2022-12-04 | NQ1007 |  |  | 0 | 242 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8088 | 671.9997
SYL-E.1.RR.333.1 | 24544039154445 | Sylhet Sadar, Mejortila, Islampur, Jahanpur, Nurul Haque | 2019-04-12 | MN1018 | 4.6 | 80 | 4.7 | 81 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 8088 | 671.9997 | 49.5215
SYL-E.1.RR.334.1 | 24544089154459 | Sylhet Sadar, Mejortila, Islampur, Jahanpur, Sonavan Villa | 2019-04-12 | MN1018 | 1.7 | 82 | 1.7 | 83 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 8088 | 671.9997 | 17.912
SYL-E.1.RR.334.2 | 24544089154459 | Sylhet Sadar, Mejortila, Islampur, Jahanpur, Sonavan Villa | 2020-10-21 | MP1006 | 3.7 | 694 | 3.7 | 695 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 8088 | 671.9997 | 38.985
SYL-E.1.RR.335.1 | 24544019154451 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Block-B, Renesa-5, Shamsul Hossen | 2019-04-13 | MN1018 | 5.2 | 84 | 5.1 | 85 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 8088 | 671.9997 | 53.7361
SYL-E.1.RR.336.1 | 24544129154478 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Block-B, Renesa-293, Md Bulbul | 2019-04-13 | MN1018 | 5 | 86 | 4.9 | 87 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 8088 | 671.9997 | 51.6288
SYL-E.1.RR.336.2 | 24544129154478 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Block-B, Renesa-293, Md Bulbul | 2020-10-21 | MP1006 | 13.6 | 686 | 13.7 | 687 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 8088 | 671.9997 | 144.3498
SYL-E.1.RR.337.1 | 24544089154494 | Sylhet Sadar, Mejortila, Islampur, Jahanpur, Abdul Karim | 2019-04-13 | MN1018 | 1.3 | 88 | 1.3 | 89 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 8088 | 671.9997 | 13.6974
SYL-E.1.RR.338.1 | 24544569154577 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Jodge Rd, Hazi Abu Bakkar | 2019-04-13 | MN1018 | 7.5 | 90 | 7.5 | 91 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 8088 | 671.9997 | 79.0236
SYL-E.1.RR.338.2 | 24544569154577 | Sylhet Sadar, Mejortila, Islampur, Jahanpur R/A, Jodge Rd, Hazi Abu Bakkar | 2022-12-04 | NQ1007 | 6.6 | 236 | 6.7 | 237 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 0 | 671.9997 | 5.4155
SYL-E.1.RR.340.1 | 24544879154496 | Sylhet Sadar, Mejortila, Islampur, North Jahanpur R/A, Ziaur | 2019-04-13 | MN1018 | 1 | 94 | 1 | 95 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 8088 | 671.9997 | 10.5365
SYL-E.1.RR.341.1 | 24544859154509 | Sylhet Sadar, Mejortila, Islampur, North Jahanpur R/A, Mamunur Rashid | 2019-04-13 | MN1018 | 1.8 | 96 | 1.8 | 97 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 8088 | 671.9997 | 18.9657
SYL-E.1.RR.342.1 | 24545289154538 | Sylhet Sadar, Mejortila, Islampur, North Jahanpur R/A, Abul Kashem | 2019-04-13 | MN1018 | 7.5 | 98 | 7.6 | 99 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8088 | 671.9997 | 80.0773
SYL-E.1.RR.343.1 | 24545239154548 | Sylhet Sadar, Mejortila, Islampur, North Jahanpur, Abdul Khalek | 2019-04-13 | MN1018 | 1.1 | 100 | 1.1 | 101 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 8088 | 671.9997 | 11.5901
SYL-E.1.RR.344.1 | 24545459154547 | Sylhet Sadar, Mejortila, Islampur, North Jahanpur, Bornali R/A, Koyes Ahmed | 2019-04-13 | MN1018 | 1.3 | 102 | 1.3 | 103 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 8088 | 671.9997 | 13.6974
SYL-E.1.RR.345.1 | 24525209153455 | Sylhet Sadar, Burhanbad, Kushighat, Raza Mia | 2019-04-15 | MN1018 | 4.4 | 126 | 4.4 | 127 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7464 | 1295.9997 | 46.3605
SYL-E.1.RR.345.2 | 24525209153455 | Sylhet Sadar, Burhanbad, Kushighat, Raza Mia | 2019-04-15 | MN1018 | 11.2 | 130 | 10.8 | 131 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7464 | 1295.9997 | 113.794
SYL-E.1.RR.345.3 | 24525209153455 | Sylhet Sadar, Burhanbad, Kushighat, Raza Mia | 2021-02-09 | MN1018 | 10.8 | 96 | 10.8 | 97 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7464 | 1295.9997 | 113.794
SYL-E.1.RR.346.1 | 24525449153498 | Sylhet Sadar, Tultikor, Fulbagh R/A, Gius Ali | 2019-04-15 | MN1018 | 11.3 | 132 | 11.2 | 133 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7464 | 1295.9997 | 118.0086
SYL-E.1.RR.347.1 | 24525559153495 | Sylhet Sadar, Tultikor, Fulbagh R/A, H # 60/1, Sawkot Ahmed | 2019-04-15 | MN1018 | 3.8 | 134 | 3.8 | 135 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-E.1.RR.347.2 | 24525559153495 | Sylhet Sadar, Tultikor, Fulbagh R/A, H # 60/1, Sawkot Ahmed | 2019-04-15 | MN1018 | 2.6 | 136 | 2.6 | 137 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7464 | 1295.9997 | 27.3949
SYL-E.1.RR.348.1 | 24525589153496 | Sylhet Sadar, Tultikor, Fulbagh R/A, Rafiq Mia | 2019-04-15 | MN1018 | 12.7 | 138 | 12.7 | 139 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7464 | 1295.9997 | 133.8133
SYL-E.1.RR.349.1 | 24525679153493 | Sylhet Sadar, Tultikor, Fulbagh R/A, Sahbuddin | 2019-04-15 | MN1018 | 1.8 | 140 | 1.8 | 141 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7464 | 1295.9997 | 18.9657
SYL-E.1.RR.350.1 | 24525699153503 | Sylhet Sadar, Tultikor, Fulbagh R/A, Sondhi-37, Alauddin | 2019-04-15 | MN1018 | 3.3 | 142 | 3.4 | 143 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7464 | 1295.9997 | 35.824
SYL-E.1.RR.351.1 | 24525809153506 | Sylhet Sadar, Tultikor, Fulbagh R/A, Hazi Abdus Salam Bulbul | 2019-04-15 | MN1018 | 1.5 | 144 | 1.5 | 145 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7464 | 1295.9997 | 15.8047
SYL-E.1.RR.352.1 | 24530059153497 | Sylhet Sadar, Tultikor, Fulbagh R/A, Ataur Rahman | 2019-04-15 | MN1018 | 2.5 | 146 | 2.5 | 147 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7464 | 1295.9997 | 26.3412
SYL-E.1.RR.353.1 | 24525989153455 | Sylhet Sadar, Tultikor, Fulbagh R/A, Amina Begum | 2019-04-15 | MN1018 | 1.3 | 148 | 1.3 | 149 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7464 | 1295.9997 | 13.6974
SYL-E.1.RR.354.1 | 24532929154100 | Sylhet Sadar, Tilagor, Gazi Burhan Uddin Road, Shaplabagh R/A, Burhan Uddin Loskor | 2019-04-16 | MN1018 | 1.6 | 158 | 1.6 | 159 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 8280 | 479.9997 | 16.8584
SYL-E.1.RR.354.2 | 24532929154100 | Sylhet Sadar, Tilagor, Gazi Burhan Uddin Road, Shaplabagh R/A, Burhan Uddin Loskor | 2021-02-17 | MN1018 | 13 | 140 | 13 | 141 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8280 | 479.9997 | 136.9743
SYL-E.1.RR.355.1 | 24532939154089 | Sylhet Sadar, Tilagor, Gazi Burhan Uddin Road, Shaplabagh R/A, Rono Sorkar | 2019-04-16 | MN1018 | 3.1 | 160 | 3 | 161 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7608 | 1151.9997 | 31.6094
SYL-E.1.RR.356.1 | 24532799154082 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Rd # 3, Block-D, H # 84, Azizul Nesa Khanom | 2019-04-16 | MN1018 | 1.6 | 162 | 1.6 | 163 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7608 | 1151.9997 | 16.8584
SYL-E.1.RR.357.1 | 24533179154078 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Rd # 3, Block-D, H # 55, Abul Leiz | 2019-04-16 | MN1018 | 3.3 | 164 | 3.3 | 165 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7608 | 1151.9997 | 34.7704
SYL-E.1.RR.358.1 | 24533179154078 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Rd # 3, Block-D, H # 55, Abul Leiz | 2019-04-16 | MN1018 | 3.8 | 166 | 3.8 | 167 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7608 | 1151.9997 | 40.0386
SYL-E.1.RR.359.1 | 24533179154078 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Rd # 3, Block-D, H # 55, Abul Leiz | 2019-04-16 | MN1018 | 4.4 | 168 | 4.5 | 169 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7608 | 1151.9997 | 47.4142
SYL-E.1.RR.359.2 | 24533179154078 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Rd # 3, Block-D, H # 55, Abul Leiz | 2021-02-17 | MN1018 | 13.5 | 137 | 13.5 | 138 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7608 | 1151.9997 | 142.2425
SYL-E.1.RR.360.1 | 24532889154063 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Rd # 3, Block-D, H # 66, Bilash Bhavan | 2019-04-16 | MN1018 | 1.3 | 170 | 1.3 | 171 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7608 | 1151.9997 | 13.6974
SYL-E.1.RR.361.1 | 24532999154045 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Block-D, Rd # 3, H # 32, Mojid Monjil | 2019-04-16 | MN1018 | 1.9 | 172 | 1.9 | 173 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7608 | 1151.9997 | 20.0193
SYL-E.1.RR.362.1 | 24532999154045 | Sylhet Sadar, Tilagor, Shaplabagh R/A, Block-C, Rd # 2, H # 37, Chandu Mia | 2019-04-16 | MN1018 | 4.6 | 174 | 4.6 | 175 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7608 | 1151.9997 | 48.4678
SYL-E.1.RR.363.1 | 24533359153533 | Sylhet Sadar, East Shibgonj, Burhanbag R/A, Ahommod Ali | 2019-04-17 | MN1032 | 1.2 | 150 | 1.2 | 151 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7584 | 1175.9997 | 12.6438
SYL-E.1.RR.364.1 | 24534059153528 | Sylhet Sadar, Shibgonj, Borhan Bag R/A, H # 5 | 2019-04-17 | MN1032 | 12.2 | 152 | 12.2 | 153 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7584 | 1175.9997 | 128.5451
SYL-E.1.RR.365.1 | 24534169153488 | Sylhet Sadar, Shibgonj, Hatimbag R/A, Rd # 2, H # 2 | 2019-04-17 | MN1032 | 1.6 | 154 | 1.6 | 155 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7584 | 1175.9997 | 16.8584
SYL-E.1.RR.366.1 | 24534059153487 | Sylhet Sadar, Shibgonj, Hatimbag R/A, Rd # 2, H # 6 | 2019-04-17 | MN1032 | 1.3 | 156 | 1.3 | 157 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7584 | 1175.9997 | 13.6974
SYL-E.1.RR.367.1 | 24533839153461 | Sylhet Sadar, Shibgonj, Hatimbag R/A, Rd # 1, West Side of Hatimbag Jame Masjid, H # B/57 | 2019-04-17 | MN1032 | 1.2 | 158 | 1.2 | 159 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7584 | 1175.9997 | 12.6438
SYL-E.1.RR.368.1 | 24533669153485 | Sylhet Sadar, Shibgonj, Hatimbag R/A, Rd # 1, H # 86/B, Junaid vila | 2019-04-17 | MN1032 | 14.1 | 160 | 14.1 | 161 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7584 | 1175.9997 | 148.5644
SYL-E.1.RR.369.1 | 24534399154045 | Sylhet, Tilagor, Kalashil, Kalashil Road, H # 13 | 2019-04-18 | MP1032 | 3.6 | 245 | 3.6 | 246 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7680 | 1079.9997 | 37.9313
SYL-E.1.RR.370.1 | 24534309154054 | Sylhet, Tilagor, Kalashil, Kalashil Road, H # 16/KA | 2019-04-18 | MP1032 | 4.2 | 249 | 4.1 | 250 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7680 | 1079.9997 | 43.1996
SYL-E.1.RR.371.1 | 24534069154129 | Sylhet, Tilagor, Rajpara R/A, Rd # 3, H # 76 | 2019-04-18 | MP1032 | 2.7 | 251 | 2.8 | 252 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7680 | 1079.9997 | 29.5021
SYL-E.1.RR.372.1 | 24534349154139 | Sylhet, Tilagor, Rajpara R/A, Rd # 2, H # 50, Abdul Kadir | 2019-04-18 | MP1032 | 2.5 | 255 | 2.6 | 256 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7680 | 1079.9997 | 27.3949
SYL-E.1.RR.373.1 | 24534429154138 | Sylhet, Tilagor, Rajpara R/A, Rd # 2, H # 46/B, Minar | 2019-04-18 | MP1032 | 11.3 | 259 | 11.3 | 260 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7680 | 1079.9997 | 119.0622
SYL-E.1.RR.374.1 | 24534459154095 | Sylhet, Tilagor, Rajpara R/A, Rd # 1, H # 34, Rafiquzzaman | 2019-04-18 | MP1032 | 10.1 | 261 | 9.8 | 262 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7680 | 1079.9997 | 103.2575
SYL-E.1.RR.375.1 | 24534619154095 | Sylhet, Tilagor, Rajpara R/A, Rd # 1, H # 28, Lilu Mia | 2019-04-18 | MP1032 | 1.1 | 263 | 1.1 | 264 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7680 | 1079.9997 | 11.5901
SYL-E.1.RR.375.2 | 24534619154095 | Sylhet, Tilagor, Rajpara R/A, Rd # 1, H # 28, Lilu Mia | 2021-11-01 | LU1001 | 11.5 | 121 | 11.5 | 122 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7680 | 1079.9997 | 121.1695
SYL-E.1.RR.376.1 | 24534039153290 | Sylhet, Uposohor Road, Shibganj point, Nobarun-5, Samim | 2019-04-18 | MP1032 | 3.7 | 267 | 3.5 | 268 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7584 | 1175.9997 | 36.8777
SYL-E.1.RR.377.1 | 24533919153280 | Sylhet, Uposohor Road, Shibganj point, Nobarun-12, Sujon Mia | 2019-04-18 | MP1032 | 1.4 | 269 | 1.4 | 270 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7584 | 1175.9997 | 14.7511
SYL-E.1.RR.378.1 | 24532789153283 | Sylhet, Uposohor, Shibganj, Main Road, Block #A, H #59, Mofejul Islam | 2019-04-18 | MP1032 | 13.7 | 271 | 13.7 | 272 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7584 | 1175.9997 | 144.3498
SYL-E.1.RR.379.1 | 24532589153309 | Sylhet, Uposohor, Shibganj, Main Road, Block #A, Road #8, H #6, Fockrul Islam | 2019-04-18 | MP1032 | 1.5 | 273 | 1.4 | 274 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7584 | 1175.9997 | 14.7511
SYL-E.1.RR.380.1 | 24532609153314 | Sylhet, Uposohor, Shibganj, Block #A, Road #8, H #7, Kawsar Vaban | 2019-04-18 | MP1032 | 2.3 | 275 | 2.3 | 276 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7584 | 1175.9997 | 24.2339
SYL-E.1.RR.381.1 | 24532569153333 | Sylhet, Uposohor, Shibganj, Block #A, Road #8, H #15, Dowan Abdur Rokib | 2019-04-18 | MP1032 | 2.4 | 277 | 2.4 | 278 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7584 | 1175.9997 | 25.2876
SYL-E.1.RR.381.2 | 24532569153333 | Sylhet, Uposohor, Shibganj, Block #A, Road #8, H #15, Dowan Abdur Rokib | 2021-10-31 | LU1001 | 9.4 | 110 | 9.4 | 111 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7584 | 1175.9997 | 99.0429
SYL-E.1.RR.382.1 | 24533619153448 | Sylhet Sadar, Hatimbag Residential Area, Rd # 1, H # 37, Hazi Chaista Mia | 2019-04-18 | MN1018 | 3.2 | 240 | 3.2 | 241 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7584 | 1175.9997 | 33.7167
SYL-E.1.RR.383.1 | 24533499153439 | Sylhet Sadar, Hatimbag, Rd # 1, H # 44/C, Nozir Ahmmed | 2019-04-18 | MN1018 | 1.1 | 242 | 1.1 | 243 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7584 | 1175.9997 | 11.5901
SYL-E.1.RR.384.1 | 24533489153437 | Sylhet Sadar, Hatimbag, Rd # 1, H # 47/C, Shofiq Mia | 2019-04-18 | MN1018 | 4.9 | 244 | 4.9 | 245 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7584 | 1175.9997 | 51.6288
SYL-E.1.RR.385.1 | 24533489153411 | Sylhet Sadar, Lamapara, Rd # 1, H # 160, Lokman Ahmed, Bekary House | 2019-04-18 | MN1018 | 1.1 | 246 | 1.1 | 247 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7584 | 1175.9997 | 11.5901
SYL-E.1.RR.385.2 | 24533489153411 | Sylhet Sadar, Lamapara, Rd # 1, H # 160, Lokman Ahmed, Bekary House | 2021-02-14 | LX1011 | 2.9 | 124 | 2.9 | 125 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7584 | 1175.9997 | 30.5558
SYL-E.1.RR.386.1 | 24532809153455 | Sylhet Sadar, Hatimbag, Rd # 1, H # 121/B, Lokman Chowdhury | 2019-04-18 | MN1018 | 3.7 | 248 | 3.6 | 249 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7608 | 1151.9997 | 37.9313
SYL-E.1.RR.387.1 | 24533279153443 | Sylhet Sadar, Hatimbag, Rd # 1, H # 69, Babul Mia | 2019-04-18 | MN1018 | 9.6 | 250 | 9.3 | 251 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7584 | 1175.9997 | 97.9893
SYL-E.1.RR.388.1 | 24533359153462 | Sylhet Sadar, Hatimbag, Rd # 1, H # 63, Mohsin Habib | 2019-04-18 | MN1018 | 2.5 | 252 | 2.4 | 253 | 2022-01-01 | [9 empty] | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0
SYL-E.1.RR.401.1 | 24540749154533 | Sylhet Sadar, Major Tila, Mohammadpur R/A, Prottasha, H # 16, Abdul Musabbir | 2019-04-09 | MP1006 | 43.1 | 1 | 43.1 | 2 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 43.1 | 43.1 | 2.586 | 2.586 | 0.0007168 | 100% | 0% | 2.586 | 2.586 | 0.0011869 | 28 | 0.05184 | 0.05184 |  | 0 | 0 | 7656 | 1103.9997 | 454.1223
SYL-E.1.RR.401.2 | 24540749154533 | Sylhet Sadar, Major Tila, Mohammadpur R/A, Prottasha, H # 16, Abdul Musabbir | 2021-11-03 | LU1001 | 12.6 | 137 | 12.6 | 138 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7656 | 1103.9997 | 132.7597
SYL-E.1.RR.402.1 | 24541079154528 | Sylhet Sadar, Major Tila, Mohammadpur R/A, Prottasha, H # 32, Anwar | 2019-04-09 | MP1006 | 3.2 | 3 | 3.2 | 4 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7656 | 1103.9997 | 33.7167
SYL-E.1.RR.403.1 | 24541149154531 | Sylhet Sadar, Major Tila, Mohammadpur R/A, Prottasha, H # 36, Abdul Motin | 2019-04-09 | MP1006 | 3.8 | 5 | 3.8 | 6 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7656 | 1103.9997 | 40.0386
SYL-E.1.RR.404.1 | 24541679154552 | Sylhet Sadar, Islampur, Major Tila, Mohammadpur 3A, Block - C, Chishti Monjil | 2019-04-09 | MP1006 | 2.8 | 7 | 2.8 | 8 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 8088 | 671.9997 | 29.5021
SYL-E.1.RR.405.1 | 24541809154573 | Sylhet Sadar, Major Tila, Mohammadpur, Block - C, Prottasha - 9, Sikandar Vila | 2019-04-09 | MP1006 | 3.4 | 9 | 3.4 | 10 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 8088 | 671.9997 | 35.824
SYL-E.1.RR.406.1 | 24541219155029 | Sylhet Sadar, Islampur, Chamelibag, Rd # 2, H # 17, Rozob Ali | 2019-04-10 | MP1006 | 1.1 | 12 | 1.1 | 13 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 8088 | 671.9997 | 11.5901
SYL-E.1.RR.407.1 | 24541239154514 | Sylhet Sadar, Mohammadpur, Prottasha - 2, Block - B, H # 449, Khaledur Rahman | 2019-04-10 | MP1006 | 1.4 | 17 | 1.4 | 18 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7656 | 1103.9997 | 14.7511
SYL-E.1.RR.407.2 | 24541239154514 | Sylhet Sadar, Mohammadpur, Prottasha - 2, Block - B, H # 449, Khaledur Rahman | 2021-11-03 | LU1001 | 7.7 | 135 | 7.7 | 136 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7656 | 1103.9997 | 81.1309
SYL-E.1.RR.408.1 | 24541419154470 | Sylhet Sadar, Mejortilla, Islampur, Mohammadpur, Prottasha - 14, Hannan Mia | 2019-04-10 | MP1006 | 10.2 | 21 | 10.2 | 22 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7656 | 1103.9997 | 107.4721
SYL-E.1.RR.409.1 | 24541409154453 | Sylhet Sadar, Mohammadpur R/A, Block - B - 16, Abdul Khalid | 2019-04-10 | MP1006 | 4.2 | 23 | 4.2 | 24 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7656 | 1103.9997 | 44.2532
SYL-E.1.RR.410.1 | 24541549154443 | Sylhet Sadar, Mohammadpur, Block - B, Prottasha - 36, Mahbub Ahmed | 2019-04-10 | MP1006 | 1.2 | 32 | 1.2 | 33 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7656 | 1103.9997 | 12.6438
SYL-E.1.RR.411.1 | 24541599154442 | Sylhet Sadar, Mohammadpur, Block - B, Prottasha - 35, Md. Nurul Islam | 2019-04-10 | MP1006 | 1.7 | 34 | 1.7 | 35 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7656 | 1103.9997 | 17.912
SYL-E.1.RR.412.1 | 24541719154462 | Sylhet Sadar, Mohammadpur, Block - B, Prottasha, H # 26 | 2019-04-10 | MP1006 | 2.9 | 36 | 2.8 | 37 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7656 | 1103.9997 | 29.5021
SYL-E.1.RR.413.1 | 24541689154458 | Sylhet Sadar, Islampur, Mohammadpur R/A, Block - B, Prottasha - 30, Ahmedul Kawsar | 2019-04-10 | MP1006 | 2.2 | 38 | 2.2 | 39 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7656 | 1103.9997 | 23.1803
SYL-E.1.RR.414.1 | 24541799154452 | Sylhet Sadar, Mohammadpur, Block - B, Prottasha - 22, Mohammad Abu Khayer | 2019-04-10 | MP1006 | 1.2 | 40 | 1.2 | 41 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7656 | 1103.9997 | 12.6438
SYL-E.1.RR.415.1 | 24541799154446 | Sylhet Sadar, Mohammadpur, Block - B, Prottasha - 23, Mojumder Mia | 2019-04-10 | MP1006 | 2.8 | 42 | 2.8 | 43 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7656 | 1103.9997 | 29.5021
SYL-E.1.RR.416.1 | 24541789154454 | Sylhet Sadar, Mohammadpur, Block - B, Prottasha - 24, Salim Ahmed Khan | 2019-04-10 | MP1006 | 2.7 | 46 | 2.7 | 47 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7656 | 1103.9997 | 28.4485
SYL-E.1.RR.417.1 | 24542299154543 | Sylhet Sadar, Mohammadpur, Prottasha, Block - C, H # 20, Sabia Begum | 2019-04-11 | MP1006 | 1.8 | 50 | 1.8 | 51 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 8088 | 671.9997 | 18.9657
SYL-E.1.RR.418.1 | 24542169154551 | Sylhet Sadar, Mohammadpur, Prottasha, Block - C, H # 18 | 2019-04-11 | MP1006 | 2.1 | 52 | 2.1 | 53 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 8088 | 671.9997 | 22.1266
SYL-E.1.RR.419.1 | 24542329154556 | Sylhet Sadar, Mohammadpur, Block - C, H # 20, Ismail | 2019-04-11 | MP1006 | 2.7 | 54 | 2.7 | 55 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 8088 | 671.9997 | 28.4485
SYL-E.1.RR.420.1 | 24542089154568 | Sylhet Sadar, Islampur, Mohammadpur, Block - C, Prottasha - 14, Makhtab Ahmed | 2019-04-11 | MP1006 | 1.5 | 56 | 1.5 | 57 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 8088 | 671.9997 | 15.8047
SYL-E.1.RR.421.1 | 24542399154513 | Sylhet Sadar, Mohammadpur, Block - A, R # 1, H # 65, Sharan | 2019-04-11 | MP1006 | 12 | 58 | 11.5 | 59 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8088 | 671.9997 | 121.1695
SYL-E.1.RR.422.1 | 24542389154526 | Sylhet Sadar, Mohammadpur, Block - A, Prottasha - 66, Anfur Ali | 2019-04-11 | MP1006 | 3.6 | 60 | 3.6 | 61 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 8088 | 671.9997 | 37.9313
SYL-E.1.RR.423.1 | 24544329155593 | Sylhet Sadar, Khadim Nagar, Bahuboli R/A, R # 1, H # 3 | 2019-04-11 | MP1006 | 1.1 | 62 | 1 | 63 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7776 | 983.9997 | 10.5365
SYL-E.1.RR.424.1 | 24544329155593 | Sylhet Sadar, Khadim Nagar, Bahuboli R/A, R # 1, H # 4 | 2019-04-11 | MP1006 | 2.4 | 64 | 2.3 | 65 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7776 | 983.9997 | 24.2339
SYL-E.1.RR.425.1 | 24544619155593 | Sylhet Sadar, Bahubol R/A, Block - A, Rd # 1, H # 5, Lutfor Rahaman | 2019-04-12 | MP1006 | 3 | 69 | 3 | 70 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7776 | 983.9997 | 31.6094
SYL-E.1.RR.425.2 | 24544619155593 | Sylhet Sadar, Bahubol R/A, Block - A, Rd # 1, H # 5, Lutfor Rahaman | 2019-04-12 | MP1006 | 1.1 | 71 | 1.1 | 72 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7776 | 983.9997 | 11.5901
SYL-E.1.RR.426.1 | 24544769155535 | Sylhet Sadar, Bahubol R/A, Block - A, Rd # 1, H # 12, Podonno Chandranath | 2019-04-12 | MP1006 | 12.2 | 75 | 12.2 | 76 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7776 | 983.9997 | 128.5451
SYL-E.1.RR.427.1 | 24544309155542 | Sylhet Sadar, Bahubol R/A, Block - A, Rd # 1, H # 8/1, Sajid Mia | 2019-04-12 | MP1006 | 1.2 | 79 | 1.2 | 80 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7776 | 983.9997 | 12.6438
SYL-E.1.RR.428.1 | 24544309155542 | Sylhet Sadar, Khadim Nagar, Bahubol R/A, Block - B, Rd # 1, H # 8/3, Abdul Jolil | 2019-04-12 | MP1006 | 1.5 | 81 | 1.5 | 82 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7776 | 983.9997 | 15.8047
SYL-E.1.RR.429.1 | 24544179155544 | Sylhet Sadar, Khadim Nagar, Bahubol R/A, Block - B, Rd # 1, H # 8/7, Omor Faruk | 2019-04-12 | MP1006 | 1.5 | 83 | 1.5 | 84 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7776 | 983.9997 | 15.8047
SYL-E.1.RR.430.1 | 24544699155531 | Sylhet Sadar, Khadim Nagar, Bahubol R/A, Block - B, Rd # 1, H # 18, Bono Kutir | 2019-04-12 | MP1006 | 2.5 | 85 | 2.5 | 86 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7776 | 983.9997 | 26.3412
SYL-E.1.RR.431.1 | 24544999155533 | Sylhet Sadar, Khadim Nagar, Bahubol R/A, Block - B, Rd # 1, H # 13, Mamun Al Hadi | 2019-04-12 | MP1006 | 11.8 | 87 | 11.8 | 88 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7776 | 983.9997 | 124.3305
SYL-E.1.RR.432.1 | 24545049155532 | Sylhet Sadar, Khadim Nagar, Bahubol R/A, Block - B, Rd # 1, H # 25, Babul Natth | 2019-04-12 | MP1006 | 1.2 | 89 | 1.2 | 90 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7776 | 983.9997 | 12.6438
SYL-E.1.RR.433.1 | 24545369155488 | Sylhet Sadar, Khadim Nagar, Bahubol R/A, Block - C, Rd # 1, Samsuddin | 2019-04-12 | MP1006 | 2.1 | 93 | 2.1 | 94 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7776 | 983.9997 | 22.1266
SYL-E.1.RR.434.1 | 24545749156195 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, Parek Ahmed, Zindabazar House | 2019-04-13 | MP1006 | 1.3 | 95 | 1.3 | 96 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7632 | 1127.9997 | 13.6974
SYL-E.1.RR.434.2 | 24545749156195 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, Parek Ahmed, Zindabazar House | 2021-02-25 | LX1011 | 4 | 159 | 4 | 160 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7632 | 1127.9997 | 42.1459
SYL-E.1.RR.435.1 | 24550249156222 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Lal Mia | 2019-04-13 | MP1006 | 1.5 | 99 | 1.5 | 100 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7632 | 1127.9997 | 15.8047
SYL-E.1.RR.435.2 | 24550249156222 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Lal Mia | 2019-04-13 | MP1006 | 12.3 | 103 | 12.3 | 104 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7632 | 1127.9997 | 129.5987
SYL-E.1.RR.436.1 | 24550209156229 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Faruk Manjil | 2019-04-13 | MP1006 | 1 | 105 | 1 | 106 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7632 | 1127.9997 | 10.5365
SYL-E.1.RR.437.1 | 24550129156223 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Abdur Rashid | 2019-04-13 | MP1006 | 2.4 | 109 | 2.5 | 110 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7632 | 1127.9997 | 26.3412
SYL-E.1.RR.438.1 | 24550229156250 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Sazzad Ali | 2019-04-13 | MP1006 | 7 | 115 | 7 | 116 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7632 | 1127.9997 | 73.7554
SYL-E.1.RR.438.2 | 24550229156250 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Sazzad Ali | 2019-04-13 | MP1006 | 1.4 | 117 | 1.4 | 118 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7632 | 1127.9997 | 14.7511
SYL-E.1.RR.439.1 | 24550229156250 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Badsha Mia | 2019-04-13 | MP1006 | 1.7 | 119 | 1.7 | 120 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7632 | 1127.9997 | 17.912
SYL-E.1.RR.440.1 | 24550249156248 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Sobor Ali | 2019-04-13 | MP1006 | 1.5 | 122 | 1.5 | 123 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7632 | 1127.9997 | 15.8047
SYL-E.1.RR.441.1 | 24550409156238 | Sylhet Sadar, Khadim Nagar, Rostompur R/A, R # 1, H # 769, Rokib Mia | 2019-04-13 | MP1006 | 1.4 | 124 | 1.4 | 125 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7632 | 1127.9997 | 14.7511
SYL-E.1.RR.442.1 | 24525519153090 | Sylhet Sadar, Shahajalal Uposhahar, Block - F, Rd # 3, H # 92, Hammad Billah | 2019-04-15 | MP1006 | 4.6 | 144 | 4.6 | 145 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7488 | 1271.9997 | 48.4678
SYL-E.1.RR.443.1 | 24525539153073 | Sylhet Sadar, Shahajalal Uposhahar, Block - F, Rd # 3, H # 96, Haydar Ali | 2019-04-15 | MP1006 | 12.2 | 146 | 12.2 | 147 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7488 | 1271.9997 | 128.5451
SYL-E.1.RR.444.1 | 24525599153214 | Sylhet Sadar, Shahajalal Uposhahar, Block - H, Rd # 6, Sayek Ahmed | 2019-04-15 | MP1006 | 4 | 148 | 4 | 149 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7488 | 1271.9997 | 42.1459
SYL-E.1.RR.445.1 | 24525859153242 | Sylhet Sadar, Shahajalal Uposhahar, Block - H, Rd # 5, H # 52, Haji Ana Mia | 2019-04-15 | MP1006 | 3.3 | 150 | 3.3 | 151 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7488 | 1271.9997 | 34.7704
SYL-E.1.RR.446.1 | 24525799153242 | Sylhet Sadar, Shahajalal Uposhahar, Block - H, Rd # 5, H # 51, Monu Mia | 2019-04-15 | MP1006 | 1.5 | 152 | 1.5 | 153 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7488 | 1271.9997 | 15.8047
SYL-E.1.RR.447.1 | 24530019153302 | Sylhet Sadar, Shahajalal Uposhahar, Block - H, Rd # 8, Simul | 2019-04-15 | MP1006 | 5.2 | 154 | 5.2 | 155 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7488 | 1271.9997 | 54.7897
SYL-E.1.RR.448.1 | 24525979153309 | Sylhet Sadar, Borhanuddin R/A, Block - H, Rd # 8, Jahurul Islam | 2019-04-15 | MP1006 | 3.7 | 156 | 3.7 | 157 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7488 | 1271.9997 | 38.985
SYL-E.1.RR.449.1 | 24531999153343 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 4, H # 14, Chandrima | 2019-04-16 | MP1006 | 5.7 | 189 | 5.8 | 190 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7584 | 1175.9997 | 61.1116
SYL-E.1.RR.450.1 | 24531969153375 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 4, H # 25, Razia Begum Chowdhury | 2019-04-16 | MP1006 | 3.5 | 191 | 3.6 | 192 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7584 | 1175.9997 | 37.9313
SYL-E.1.RR.451.1 | 24531969153382 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 4, H # 31, Haji S.M Khan | 2019-04-16 | MP1006 | 2.2 | 193 | 2.2 | 194 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7584 | 1175.9997 | 23.1803
SYL-E.1.RR.452.1 | 24532039153327 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 4, H # 10, Chan Mia | 2019-04-16 | MP1006 | 3.1 | 195 | 3.1 | 196 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7584 | 1175.9997 | 32.6631
SYL-E.1.RR.453.1 | 24531939153292 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 5, H # 4, Samsuddin Ahammed | 2019-04-16 | MP1006 | 2.2 | 197 | 2.2 | 198 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7584 | 1175.9997 | 23.1803
SYL-E.1.RR.453.2 | 24531939153292 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 5, H # 4, Samsuddin Ahammed | 2019-04-16 | MP1006 | 3 | 199 | 3 | 200 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7584 | 1175.9997 | 31.6094
SYL-E.1.RR.454.1 | 24531979153287 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 5, H # 2, Rahman Nibash | 2019-04-16 | MP1006 | 2.8 | 201 | 2.8 | 202 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7584 | 1175.9997 | 29.5021
SYL-E.1.RR.455.1 | 24532099153301 | Sylhet Sadar, Shahajalal Upashahar, Block - A, Rd # 4, H # 7, | 2019-04-16 | MP1006 | 2 | 203 | 2 | 204 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7584 | 1175.9997 | 21.073
SYL-E.1.RR.456.1 | 24532249153250 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 14, H # 36/A, | 2019-04-16 | MP1006 | 12.9 | 205 | 12.9 | 206 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7512 | 1247.9997 | 135.9206
SYL-E.1.RR.456.2 | 24532249153250 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 14, H # 36/A, | 2019-04-16 | MP1006 | 18.8 | 207 | 18.8 | 208 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 7512 | 1247.9997 | 198.0858
SYL-E.1.RR.457.1 | 24532279153203 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 14, H # 40, Islam Villa | 2019-04-16 | MP1006 | 12.5 | 209 | 12.5 | 210 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7512 | 1247.9997 | 131.706
SYL-E.1.RR.457.2 | 24532279153203 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 14, H # 40, Islam Villa | 2019-04-16 | MP1006 | 25.3 | 211 | 25.1 | 212 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 25.1 | 25.1 | 1.506 | 1.506 | 0.0007168 | 100% | 0% | 1.506 | 1.506 | 0.0011869 | 28 | 0.03019 | 0.03019 |  | 0 | 0 | 7512 | 1247.9997 | 264.4657
SYL-E.1.RR.458.1 | 24532259153168 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 14, H # 31, Rashed Palace | 2019-04-16 | MP1006 | 1.8 | 213 | 1.8 | 214 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7512 | 1247.9997 | 18.9657
SYL-E.1.RR.459.1 | 24532209153167 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 14, H # 30, Moynul Islam | 2019-04-16 | MP1006 | 10.6 | 215 | 10.6 | 216 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7512 | 1247.9997 | 111.6867
SYL-E.1.RR.460.1 | 24532559153186 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 19, H # 7, Abdul Hi | 2019-04-17 | MP1006 | 10 | 236 | 10 | 237 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7512 | 1247.9997 | 105.3648
SYL-E.1.RR.460.2 | 24532559153186 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 19, H # 7, Abdul Hi | 2019-04-17 | MP1006 | 1.5 | 238 | 1.5 | 239 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7512 | 1247.9997 | 15.8047
SYL-E.1.RR.461.1 | 24532699153188 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 18, H # 1, Akhtaruzzaman | 2019-04-17 | MP1006 | 3.4 | 240 | 3.4 | 241 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7512 | 1247.9997 | 35.824
SYL-E.1.RR.461.2 | 24532699153188 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 18, H # 1, Akhtaruzzaman | 2021-02-11 | MN1018 | 3.3 | 105 | 3.3 | 106 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7512 | 1247.9997 | 34.7704
SYL-E.1.RR.462.1 | 24532599153215 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 16, H # 6/A, SZ Kamal | 2019-04-17 | MP1006 | 3.9 | 242 | 3.9 | 243 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7512 | 1247.9997 | 41.0923
SYL-E.1.RR.463.1 | 24532589153223 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 16, H # 7-B, | 2019-04-17 | MP1006 | 6.6 | 244 | 6.3 | 245 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7512 | 1247.9997 | 66.3798
SYL-E.1.RR.464.1 | 24532629153245 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 16, H # 11/A, | 2019-04-17 | MP1006 | 1.2 | 246 | 1.2 | 247 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7512 | 1247.9997 | 12.6438
SYL-E.1.RR.465.1 | 24532599153241 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 16, H # 10/A, | 2019-04-17 | MP1006 | 8.5 | 248 | 8.5 | 249 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7512 | 1247.9997 | 89.5601
SYL-E.1.RR.466.1 | 24532389153200 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 15, H # 6, | 2019-04-17 | MP1006 | 3.4 | 252 | 3.4 | 253 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7512 | 1247.9997 | 35.824
SYL-E.1.RR.467.1 | 24532399153203 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 15, H # 5, Hosen Villa | 2019-04-17 | MP1006 | 2.8 | 254 | 2.6 | 255 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7512 | 1247.9997 | 27.3949
SYL-E.1.RR.468.1 | 24532429153212 | Sylhet Sadar, Shahajalal Upashahar, Block - B, Rd # 15, H # 9, | 2019-04-17 | MP1006 | 2.9 | 256 | 2.8 | 257 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7512 | 1247.9997 | 29.5021
SYL-E.1.RR.469.1 | 24533629153467 | Sylhet, Shibghanj, Hatimbag R/A, H #37 | 2019-04-18 | MN1018 | 4.7 | 254 | 4.7 | 255 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7584 | 1175.9997 | 49.5215
SYL-E.1.RR.470.1 | 24533409153330 | Sylhet, Shibghanj, Lamapara, Mohini-109 | 2019-04-18 | MN1018 | 4.3 | 258 | 4.3 | 259 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7584 | 1175.9997 | 45.3069
SYL-E.1.RR.471.1 | 24533529153358 | Sylhet, Shibghanj, Lamapara, Mohini-46 | 2019-04-18 | MN1018 | 2.2 | 260 | 2.2 | 261 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7584 | 1175.9997 | 23.1803
SYL-E.1.RR.472.1 | 24533909153368 | Sylhet, Shibghanj, Lamapara, Mohini-15/c | 2019-04-18 | MN1018 | 4.1 | 262 | 4.1 | 263 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7584 | 1175.9997 | 43.1996
SYL-E.1.RR.473.1 | 24532239153053 | Sylhet Sadar, Uposhohor, Block - D, R# 14, H # 7 | 2019-04-19 | MN1032 | 2.9 | 198 | 2.9 | 199 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7488 | 1271.9997 | 30.5558
SYL-E.1.RR.474.1 | 24532259153054 | Sylhet Sadar, Shahajalal Uposhohor, Block - D, R# 27, H # 1, Aangur Villa | 2019-04-19 | MN1032 | 0.7 | 200 | 0.7 | 201 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 0.7 | 0.7 | 0.042 | 0.042 | 0.0007168 | 100% | 0% | 0.042 | 0.042 | 0.0011869 | 28 | 0.00084196 | 0.00084196 |  | 0 | 0 | 7488 | 1271.9997 | 7.3755
SYL-E.1.RR.474.2 | 24532259153054 | Sylhet Sadar, Shahajalal Uposhohor, Block - D, R# 27, H # 1, Aangur Villa | 2019-04-19 | MN1032 | 0.7 | 202 | 0.7 | 203 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 0.7 | 0.7 | 0.042 | 0.042 | 0.0007168 | 100% | 0% | 0.042 | 0.042 | 0.0011869 | 28 | 0.00084196 | 0.00084196 |  | 0 | 0 | 7488 | 1271.9997 | 7.3755
SYL-E.1.RR.475.1 | 24532199153068 | Sylhet Sadar, Shahajalal Uposhohor, Block - D, R# 14, H # 9, C.S Monjil | 2019-04-19 | MN1032 | 1.3 | 204 | 1.3 | 205 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7488 | 1271.9997 | 13.6974
SYL-E.1.RR.476.1 | 24532689153093 | Sylhet Sadar, Uposhohor, Block - D, R# 25, Nobarun - 412 | 2019-04-19 | MN1032 | 2.7 | 206 | 2.6 | 207 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7512 | 1247.9997 | 27.3949
SYL-E.1.RR.476.2 | 24532689153093 | Sylhet Sadar, Uposhohor, Block - D, R# 25, Nobarun - 412 | 2022-11-10 | NQ1007 | 9.3 | 151 | 9.3 | 152 | 2022-11-10 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 0 | 1247.9997 | 13.9601
SYL-E.1.RR.477.1 | 24532799153095 | Sylhet Sadar, Uposhohor, Block - D, R# 25, Nobarun - 428, Shohed Mia | 2019-04-19 | MN1032 | 2.3 | 208 | 2.3 | 209 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7512 | 1247.9997 | 24.2339
SYL-E.1.RR.478.1 | 24532959153120 | Sylhet Sadar, Uposhohor, R # 25, Shibgonj, Sonapara, Nobarun - 149 | 2019-04-19 | MN1032 | 5.2 | 210 | 5.2 | 211 | 2022-01-01 | [9 empty] | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0
SYL-E.1.RR.479.1 | 24532959153120 | Sylhet Sadar, Uposhohor, R # 25, Shibgonj, Sonapara, Nobarun - 150/A | 2019-04-19 | MN1032 | 1.2 | 212 | 1.2 | 213 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7512 | 1247.9997 | 12.6438
SYL-E.1.RR.479.2 | 24532959153120 | Sylhet Sadar, Uposhohor, R # 25, Shibgonj, Sonapara, Nobarun - 150/A | 2021-08-18 | LX1011 | 12.1 | 26 | 12.1 | 27 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7512 | 1247.9997 | 127.4914
SYL-E.1.RR.480.1 | 24533009153119 | Sylhet Sadar, Uposhohor, Shibgonj, Sonapara, Nobarun - 164, Muktar Mia | 2019-04-19 | MN1032 | 5.3 | 214 | 5.3 | 215 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7512 | 1247.9997 | 55.8434
SYL-E.1.RR.481.1 | 24532919153135 | Sylhet Sadar, Uposhohor, Shibgonj, Sonapara, Nobarun - 140/5 | 2019-04-19 | MN1032 | 1.3 | 216 | 1.3 | 217 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7512 | 1247.9997 | 13.6974
SYL-E.1.RR.482.1 | 24532899153137 | Sylhet Sadar, Uposhohor, Shibgonj, Sonapara, Nobarun - 148 | 2019-04-19 | MN1032 | 5.1 | 218 | 5 | 219 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7512 | 1247.9997 | 52.6824
SYL-E.1.RR.483.1 | 24532699153139 | Sylhet Sadar, Uposhohor, Shibgonj, Sonapara, Nobarun - 143 | 2019-04-19 | MN1032 | 4.7 | 220 | 4.7 | 221 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7512 | 1247.9997 | 49.5215
SYL-E.1.RR.483.2 | 24532699153139 | Sylhet Sadar, Uposhohor, Shibgonj, Sonapara, Nobarun - 144 | 2019-04-19 | MN1032 | 1 | 222 | 1 | 223 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7512 | 1247.9997 | 10.5365
SYL-E.1.RR.501.1 | 24525699153022 | Syhet Sadar, Mendibag R/A, Mosjid Rd, Hasan | 2019-04-15 | LP1002 | 10.1 | 96 | 10.1 | 97 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7488 | 1271.9997 | 106.4185
SYL-E.1.RR.502.1 | 24525739153027 | Syhet Sadar, Mendibag R/A, Mosjid Rd, Hazi Kalam Rashid | 2019-04-15 | LP1002 | 6.6 | 98 | 6.6 | 99 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7488 | 1271.9997 | 69.5408
SYL-E.1.RR.503.1 | 24525699153166 | Syhet Sadar, Sahajalal Uposahor, Block-G, Rd# 4, H # 94 | 2019-04-15 | LP1002 | 1.2 | 100 | 1.2 | 101 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7488 | 1271.9997 | 12.6438
SYL-E.1.RR.503.2 | 24525699153166 | Syhet Sadar, Sahajalal Uposahor, Block-G, Rd# 4, H # 94 | 2021-02-10 | MN1018 | 6.6 | 100 | 6.6 | 101 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7488 | 1271.9997 | 69.5408
SYL-E.1.RR.504.1 | 24525619153206 | Syhet Sadar, Sahajalal Uposahor, Block-G, Rd# 4, H # 102 | 2019-04-15 | LP1002 | 2.3 | 102 | 2.3 | 103 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7488 | 1271.9997 | 24.2339
SYL-E.1.RR.505.1 | 24525779153157 | Syhet Sadar, Sahajalal Uposahor, Block-G, Rd# 3, H # 64 | 2019-04-15 | LP1002 | 1.5 | 104 | 1.5 | 105 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7488 | 1271.9997 | 15.8047
SYL-E.1.RR.506.1 | 24532299153291 | Shajalal, Uposhohor, Rd# 12, H#8, Shamim | 2019-04-16 | MP1006 | 1 | 158 | 1 | 159 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7584 | 1175.9997 | 10.5365
SYL-E.1.RR.507.1 | 24532299153337 | Sylhet,Shajalal, Uposohor,Block #A, Rd# 7, H #9 | 2019-04-16 | MP1006 | 2 | 162 | 2 | 163 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7584 | 1175.9997 | 21.073
SYL-E.1.RR.508.1 | 24532219153344 | Sylhet,Shajalal, Uposohor,Block #A, Rd# 3, H #1 | 2019-04-16 | MP1006 | 2.6 | 164 | 2.6 | 165 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7584 | 1175.9997 | 27.3949
SYL-E.1.RR.509.1 | 24532139153364 | Sylhet,Shajalal, Uposohor,Block #A, Rd# 3, H #7 | 2019-04-16 | MP1006 | 3.5 | 166 | 3.5 | 167 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7584 | 1175.9997 | 36.8777
SYL-E.1.RR.510.1 | 24532109153397 | Sylhet,Shajalal, Uposohor,Block #A, Rd# 3, H #18, Shirin Villa | 2019-04-16 | MP1006 | 1.3 | 170 | 1.3 | 171 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7584 | 1175.9997 | 13.6974
SYL-E.1.RR.511.1 | 24532129153409 | Sylhet, Shajalal uposhohor,Block #A, Rd# 3, H #21 | 2019-04-16 | MP1006 | 4.5 | 173 | 4.3 | 174 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7584 | 1175.9997 | 45.3069
SYL-E.1.RR.512.1 | 24532159153420 | Sylhet, Shador Para, Alamin-49, md Salak Mia | 2019-04-16 | MP1006 | 1 | 175 | 1 | 176 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7584 | 1175.9997 | 10.5365
SYL-E.1.RR.513.1 | 24532229153405 | Sylhet, Shajalal uposhohor,Block #A, Rd# 2, H #8 | 2019-04-16 | MP1006 | 1.2 | 177 | 1.1 | 178 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7584 | 1175.9997 | 11.5901
SYL-E.1.RR.514.1 | 24532249153394 | Sylhet, Shajalal uposhohor,Block #A, Rd# 2, H #4 | 2019-04-16 | MP1006 | 4.4 | 181 | 4.4 | 182 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7584 | 1175.9997 | 46.3605
SYL-E.1.RR.515.1 | 24532379153401 | Sylhet, Shajalal uposhohor,Block #A, Rd# 2, H #2 | 2019-04-16 | MP1006 | 1.3 | 183 | 1.3 | 184 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7584 | 1175.9997 | 13.6974
SYL-E.1.RR.516.1 | 24532389153402 | Sylhet, Shajalal uposhohor,Block #A, Rd# 1, H #8 | 2019-04-16 | MP1006 | 2.3 | 185 | 2.3 | 186 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7584 | 1175.9997 | 24.2339
SYL-E.1.RR.517.1 | 24532509153389 | Sylhet, Shibganz, Lampara, Mohoni-83, Chowdhuri Bari | 2019-04-16 | MP1006 | 1.1 | 187 | 1.1 | 188 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7584 | 1175.9997 | 11.5901
SYL-E.1.RR.551.1 | 24524399153207 | Sylhet Sadar, Shadipur - 2, Noagaon, Golam Rabbani | 2019-04-15 | MP1032 | 4.1 | 97 | 4.1 | 98 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7488 | 1271.9997 | 43.1996
SYL-E.1.RR.552.1 | 24524919153222 | Sylhet Sadar, Shadipur - 2, Noagaon, Saeed Alam | 2019-04-15 | MP1032 | 1.9 | 99 | 1.9 | 100 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 3216 | 0 | 4272 | 1271.9997 | 12.6698
SYL-E.1.RR.553.1 | 24525299153244 | Sylhet Sadar, Shadipur - 2, Shadatikor, Matri Chaya, Faruk Ahmed | 2019-04-15 | MP1032 | 2.9 | 101 | 2.9 | 102 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7488 | 1271.9997 | 30.5558
SYL-E.1.RR.554.1 | 24525409153245 | Sylhet Sadar, Shadipur - 2, Shadatikor, Abdur Razzak | 2019-04-15 | MP1032 | 5.9 | 103 | 5.9 | 104 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7488 | 1271.9997 | 62.1652
SYL-E.1.RR.554.2 | 24525409153245 | Sylhet Sadar, Shadipur - 2, Shadatikor, Abdur Razzak | 2019-04-15 | MP1032 | 105.5 | 106 | 105.5 | 107 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 105.5 | 105.5 | 6.33 | 6.33 | 0.0007168 | 100% | 0% | 6.33 | 6.33 | 0.0011869 | 28 | 0.12689 | 0.12689 |  | 0 | 0 | 7488 | 1271.9997 | 1111.5988
SYL-E.1.RR.554.3 | 24525409153245 | Sylhet Sadar, Shadipur - 2, Shadatikor, Abdur Razzak | 2019-04-15 | MP1032 | 1.5 | 108 | 1.5 | 109 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7488 | 1271.9997 | 15.8047
SYL-E.1.RR.555.1 | 24525439153233 | Sylhet Sadar, Shadipur - 2, Shadatikor, Fayez Ahmed | 2019-04-15 | MP1032 | 1.1 | 110 | 1.1 | 111 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7488 | 1271.9997 | 11.5901
SYL-E.1.RR.556.1 | 24525529153246 | Sylhet Sadar, Shadipur - 2, Shadatikor, Mokbul Hossain | 2019-04-15 | MP1032 | 2.7 | 112 | 2.7 | 113 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7488 | 1271.9997 | 28.4485
SYL-E.1.RR.557.1 | 24525559153248 | Sylhet Sadar, Shadipur - 2, Shadatikor, Sharifuddin | 2019-04-15 | MP1032 | 1.5 | 117 | 1.5 | 118 | 2022-01-01 | [9 empty] | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0
SYL-E.1.RR.558.1 | 24525629153251 | Sylhet Sadar, Shadipur - 2, Shadatikor, Abdur Rahim | 2019-04-15 | MP1032 | 1.7 | 119 | 1.7 | 120 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7488 | 1271.9997 | 17.912
SYL-E.1.RR.559.1 | 24525629153251 | Sylhet Sadar, Shadipur - 2, Shadatikor, Ratan Mia | 2019-04-15 | MP1032 | 1.4 | 122 | 1.4 | 123 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7488 | 1271.9997 | 14.7511
SYL-E.1.RR.560.1 | 24531069152599 | Shahjalal Uposhohor, Block - E, Rd #1, H # 6, Shafiqul Haque | 2019-04-16 | MN1032 | 1.8 | 94 | 1.8 | 95 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7488 | 1271.9997 | 18.9657
SYL-E.1.RR.561.1 | 24531369153026 | Shahjalal Uposhohor, Block - C, Rd #33/A, H # 1/B, Abdur Rahim | 2019-04-16 | MN1032 | 10.9 | 96 | 10.6 | 97 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7488 | 1271.9997 | 111.6867
SYL-E.1.RR.562.1 | 24531229153095 | Shahjalal Uposhohor, Block - E, Rd #3, H # 65 | 2019-04-16 | MN1032 | 1.2 | 98 | 1.2 | 99 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7488 | 1271.9997 | 12.6438
SYL-E.1.RR.563.1 | 24530879153068 | Shahjalal Uposhohor, Block - E, Rd #4, H # 146 | 2019-04-16 | MN1032 | 1.6 | 100 | 1.5 | 101 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7488 | 1271.9997 | 15.8047
SYL-E.1.RR.564.1 | 24530649153048 | Shahjalal Uposhohor, Block - E, Rd #4, H # 144, Pioneer School & College | 2019-04-16 | MN1032 | 4.1 | 102 | 4 | 103 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 6984 | 0 | 504 | 1271.9997 | 8.5447
SYL-E.1.RR.565.1 | 24531019153182 | Sylhet, Shahjalal Uposhohor, Block-J, Rd # 4, H # 18, Junaid Ahmed | 2019-04-17 | LP1002 | 1.1 | 155 | 1.1 | 156 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7488 | 1271.9997 | 11.5901
SYL-E.1.RR.565.2 | 24531019153182 | Sylhet, Shahjalal Uposhohor, Block-J, Rd # 4, H # 18, Junaid Ahmed | 2021-02-10 | MN1018 | 14.3 | 102 | 13.9 | 103 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7488 | 1271.9997 | 146.4571
SYL-E.1.RR.566.1 | 24531449152579 | Sylhet, Shahjalal Uposhohor, Block-D, Rd # 36, H # 9, Rafid Ahmed | 2019-04-17 | LP1002 | 1.2 | 157 | 1.2 | 158 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7488 | 1271.9997 | 12.6438
SYL-E.1.RR.567.1 | 24531389153011 | Sylhet, Shahjalal Uposhohor, Block-D, Rd # 34, Khalilur Rahman | 2019-04-17 | LP1002 | 2.7 | 159 | 2.6 | 160 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7488 | 1271.9997 | 27.3949
SYL-E.1.RR.568.1 | 24531879153013 | Sylhet, Shahjalal Uposhohor, Block-D, Rd # 31, H # 1, Kamal Ahmed | 2019-04-17 | LP1002 | 5.7 | 161 | 5.7 | 162 | 2022-01-01 | [9 empty] | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0
SYL-E.1.RR.569.1 | 24532019153047 | Sylhet, Shahjalal Housing state, Block - D, Rd # 30, H # 11 | 2019-04-17 | LP1002 | 17.5 | 163 | 17.5 | 164 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 7488 | 1271.9997 | 184.3884
SYL-E.1.RR.570.1 | 24532029153042 | Sylhet, Shahjalal Housing state, Block - D, Rd # 30, H # 9 | 2019-04-17 | LP1002 | 1.5 | 165 | 1.5 | 166 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7488 | 1271.9997 | 15.8047
SYL-E.1.RR.571.1 | 24532019153022 | Sylhet, Shahjalal Housing state, Block - D, Rd # 30, H # 3 | 2019-04-17 | LP1002 | 2.5 | 167 | 2.5 | 168 | 2022-01-01 | [9 empty] | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0
SYL-E.1.RR.572.1 | 24531999153021 | Sylhet, Shahjalal Housing state, Block - D, Rd # 30, H # 2 | 2019-04-17 | LP1002 | 13.9 | 169 | 13.2 | 170 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7488 | 1271.9997 | 139.0816
SYL-E.1.RR.573.1 | 24531729152582 | Sylhet, Shahjalal Housing state, Block - D, Rd # 29/1, H # 21 | 2019-04-17 | LP1002 | 1.3 | 173 | 1.3 | 174 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7488 | 1271.9997 | 13.6974
SYL-E.1.RR.574.1 | 24532139153004 | Sylhet, Shahjalal Housing state, Block - D, Rd # 29/1, H # 4/A | 2019-04-17 | LP1002 | 1 | 175 | 1 | 176 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7488 | 1271.9997 | 10.5365
SYL-E.1.RR.575.1 | 24532199153036 | Sylhet, Shahjalal Housing state, Block - D, Rd # 29, H # 3 | 2019-04-17 | LP1002 | 13.9 | 179 | 13.9 | 180 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7488 | 1271.9997 | 146.4571
SYL-E.1.RR.576.1 | 24532559153036 | Sylhet, Jotorpur, Nobopushpo, Abdur Razzak | 2019-04-17 | LP1002 | 1 | 181 | 1 | 182 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7488 | 1271.9997 | 10.5365
SYL-E.1.RR.577.1 | 24532689152598 | Sylhet, Jotorpur, Nobopushpo, Plot # 399, Anowara Begum | 2019-04-17 | LP1002 | 15 | 183 | 14.3 | 184 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7488 | 1271.9997 | 150.6717
SYL-E.1.RR.578.1 | 24532659152591 | Sylhet, Jotorpur, Nobopushpo, H # 55/1, Aklaquzzaman | 2019-04-17 | LP1002 | 1 | 185 | 1 | 186 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7488 | 1271.9997 | 10.5365
SYL-E.1.RR.579.1 | 24532449153474 | Sylhet,Sabujbagh R/A, Rd # 3, H #10, Habiba begum | 2019-04-18 | LP1002 | 4.5 | 187 | 4.4 | 188 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7608 | 1151.9997 | 46.3605
SYL-E.1.RR.579.2 | 24532449153474 | Sylhet,Sabujbagh R/A, Rd # 3, H #10, Habiba begum | 2022-11-14 | NQ1007 | 7.1 | 157 | 7.1 | 158 | 2022-11-14 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 0 | 1151.9997 | 9.8379
SYL-E.1.RR.580.1 | 24532409153500 | Sylhet,Sabujbagh R/A, Rd # 2, H #10/5, Bagan Bilas, Azad Laskar | 2019-04-18 | LP1002 | 1.6 | 189 | 1.6 | 190 | 2022-01-01 | 2022-11-14 | NQ1007 |  |  | 0 | 161 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7608 | 1151.9997
SYL-E.1.RR.581.1 | 24531779153561 | Sylhet,Shibjong, Sabujbagh, R/A, H # 5 syful Islam | 2019-04-18 | LP1002 | 2.1 | 191 | 2.1 | 192 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7608 | 1151.9997 | 22.1266
SYL-E.1.RR.582.1 | 24531849153567 | Sylhet,Shibjong, Sabujbagh, R/A, Rd # 8,H # 1, The Arian Tower, Ekbal Hossen | 2019-04-18 | LP1002 | 4 | 193 | 4 | 194 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7608 | 1151.9997 | 42.1459
SYL-E.1.RR.583.1 | 24532229153469 | Sylhet,Shibjong, Sabujbagh, H # 24, Limon Mia | 2019-04-18 | LP1002 | 3.4 | 195 | 3.4 | 196 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7608 | 1151.9997 | 35.824
SYL-E.1.RR.585.1 | 24533189153379 | Sylhet,Shibjong, Lamapara, Mohini, H # 64, Azizur Rahman | 2019-04-18 | LP1002 | 4.7 | 201 | 4.7 | 202 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7584 | 1175.9997 | 49.5215
SYL-E.1.RR.586.1 | 24532909153400 | Sylhet,Shibjong, Lamapara, Mohini, H # 511, Nuruz Ali | 2019-04-18 | LP1002 | 0.6 | 207 | 0.6 | 208 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 0.6 | 0.6 | 0.036 | 0.036 | 0.0007168 | 100% | 0% | 0.036 | 0.036 | 0.0011869 | 28 | 0.00072168 | 0.00072168 |  | 0 | 0 | 7584 | 1175.9997 | 6.3219
SYL-E.1.RR.586.2 | 24532909153400 | Sylhet,Shibjong, Lamapara, Mohini, H # 511, Nuruz Ali | 2019-04-18 | LP1002 | 0.6 | 209 | 0.6 | 210 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 0.6 | 0.6 | 0.036 | 0.036 | 0.0007168 | 100% | 0% | 0.036 | 0.036 | 0.0011869 | 28 | 0.00072168 | 0.00072168 |  | 0 | 0 | 7584 | 1175.9997 | 6.3219
SYL-E.1.RR.587.1 | 24534489153462 | Sylhet, Shibganj, Shadipur R/A, H # 1, Habibunnesa | 2019-04-19 | LP1002 | 1.4 | 228 | 1.4 | 229 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7752 | 1007.9997 | 14.7511
SYL-E.1.RR.587.2 | 24534489153462 | Sylhet, Shibganj, Shadipur R/A, H # 1, Habibunnesa | 2022-11-20 | NQ1007 | 7.5 | 171 | 7.5 | 172 | 2022-11-20 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 0 | 1007.9997 | 9.0931
SYL-E.1.RR.588.1 | 24534719153463 | Sylhet, Shibganj, Shadipur R/A, Hatem Ali Road, Noya Jame Mosjid | 2019-04-19 | LP1002 | 1.4 | 230 | 1.4 | 231 | 2022-01-01 | 2022-11-20 | NQ1007 |  |  | 0 | 174 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7752 | 1007.9997
SYL-E.1.RR.589.1 | 24534699153476 | Sylhet, Shibganj, Shadipur R/A, Hatem Ali Road, Enam | 2019-04-19 | LP1002 | 13.2 | 232 | 13.2 | 233 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7752 | 1007.9997 | 139.0816
SYL-E.1.RR.590.1 | 24534829153482 | Sylhet, Shibganj, Shadipur R/A, Hatem Ali Road, Jamal | 2019-04-19 | LP1002 | 1.9 | 234 | 1.8 | 235 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7752 | 1007.9997 | 18.9657
SYL-E.1.RR.591.1 | 24535279153480 | Sylhet, Shibganj, Shadipur R/A, H # 18, Orup Chakroborty | 2019-04-19 | LP1002 | 1.2 | 236 | 1.2 | 237 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7752 | 1007.9997 | 12.6438
SYL-E.1.RR.592.1 | 24535259153485 | Sylhet, Shibganj, Shadipur R/A, H # 19, Biresh Chakroborty | 2019-04-19 | LP1002 | 2.5 | 238 | 2.5 | 239 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7752 | 1007.9997 | 26.3412
SYL-E.1.RR.593.1 | 24535359153506 | Sylhet, Shibganj, Shadipur R/A, H # 28, Shekhor Chowdhury | 2019-04-19 | LP1002 | 1.1 | 240 | 1 | 241 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7752 | 1007.9997 | 10.5365
SYL-E.1.RR.594.1 | 24535559153502 | Sylhet, Shibganj, Shadipur R/A, H # 32, Wahidujjaman | 2019-04-19 | LP1002 | 1.1 | 242 | 1.1 | 243 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7752 | 1007.9997 | 11.5901
SYL-E.1.RR.595.1 | 24535679153507 | Sylhet, Shibganj, Shadipur R/A, H # 36, Nurul Haq Khan | 2019-04-19 | LP1002 | 2.1 | 244 | 2.1 | 245 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7752 | 1007.9997 | 22.1266
SYL-E.1.RR.596.1 | 24535589153511 | Sylhet, Shibganj, Shadipur R/A, H # 40/1, Nurul Islam | 2019-04-19 | LP1002 | 2 | 246 | 2 | 247 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7752 | 1007.9997 | 21.073
SYL-E.1.RR.601.1 | 24525069153201 | Sylhet Sadar, Shadatikor, Shahjalal Housing R/A, H # 23, Aysha Khatun | 2019-04-15 | MP1006 | 2.1 | 126 | 1.9 | 127 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7488 | 1271.9997 | 20.0193
SYL-E.1.RR.602.1 | 24525449153207 | Sylhet Sadar, Shadatikor, Shahjalal Housing R/A, H # 38, Foyez Manjil | 2019-04-15 | MP1006 | 1.2 | 128 | 1.2 | 129 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8280 | 479.9997 | 12.6438
SYL-E.1.RR.603.1 | 24525509153200 | Sylhet Sadar, Shadatikor, Shahjalal Housing R/A, H # 103/1, Akbar Manjil | 2019-04-15 | MP1006 | 1.8 | 130 | 1.8 | 131 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7488 | 1271.9997 | 18.9657
SYL-E.1.RR.603.2 | 24525509153200 | Sylhet Sadar, Shadatikor, Shahjalal Housing R/A, H # 103/1, Akbar Manjil | 2019-04-15 | MP1006 | 1.2 | 134 | 1.2 | 135 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7488 | 1271.9997 | 12.6438
SYL-E.1.RR.604.1 | 24525209153149 | Sylhet, Shahjalal Uposhohor, Block-F, Rd # 4, H # 123 | 2019-04-15 | MP1006 | 29.6 | 136 | 29.8 | 137 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 29.8 | 29.8 | 1.788 | 1.788 | 0.0007168 | 100% | 0% | 1.788 | 1.788 | 0.0011869 | 28 | 0.035843 | 0.035843 |  | 0 | 0 | 7488 | 1271.9997 | 313.9871
SYL-E.1.RR.604.2 | 24525209153149 | Sylhet, Shahjalal Uposhohor, Block-F, Rd # 4, H # 123 | 2019-04-15 | MP1006 | 1.3 | 138 | 1.3 | 139 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7488 | 1271.9997 | 13.6974
SYL-E.1.RR.605.1 | 24525369153140 | Sylhet, Shahjalal Uposhohor, Block-F, Rd # 4, H # 121 | 2019-04-15 | MP1006 | 1.5 | 140 | 1.4 | 141 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7488 | 1271.9997 | 14.7511
SYL-E.1.RR.606.1 | 24525339153056 | Sylhet, Shahjalal Uposhohor, Block-F, Rd # 4, H # 104, Hussain Villa | 2019-04-15 | MP1006 | 2.1 | 142 | 2.1 | 143 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7488 | 1271.9997 | 22.1266
SYL-E.1.RR.607.1 | 24530899154068 | Sylhet, Mirapara, Borhanuddin Road, H#140, Block-A, R/D#05, Mahabub | 2019-04-16 | MN1018 | 1.1 | 150 | 1.1 | 151 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7464 | 1295.9997 | 11.5901
SYL-E.1.RR.608.1 | 24530899154068 | Sylhet, Mirapara, Borhanuddin Road, H#141, Block-A, R/D#05, Abdus Salam | 2019-04-16 | MN1018 | 1.9 | 152 | 1.9 | 153 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7464 | 1295.9997 | 20.0193
SYL-E.1.RR.608.2 | 24530899154068 | Sylhet, Mirapara, Borhanuddin Road, H#141, Block-A, R/D#05, Abdus Salam | 2021-02-17 | MN1018 | 18.4 | 142 | 18.4 | 143 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 7464 | 1295.9997 | 193.8713
SYL-E.1.RR.609.1 | 24532129154074 | Sylhet, Mirapara, Block-D, H#02, Guljar Ahmed | 2019-04-16 | MN1018 | 5.7 | 154 | 5.4 | 155 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7608 | 1151.9997 | 56.897
SYL-E.1.RR.610.1 | 24532099154065 | Sylhet, Mirapara, Block-D, H#03, Abdul Kalam | 2019-04-16 | MN1018 | 3 | 156 | 3 | 157 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7608 | 1151.9997 | 31.6094
SYL-E.1.RR.611.1 | 24533099154033 | Sylhet, Tilagor, Shaplabag, Block-C, Rd # 3, Tofazzel Hosen Chowdhury | 2019-04-17 | MP1032 | 1 | 185 | 1 | 186 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7608 | 1151.9997 | 10.5365
SYL-E.1.RR.612.1 | 24533229154022 | Sylhet, Tilagor, Shaplabag, Block-B, Rd # 2, H # 40, Murad | 2019-04-17 | MP1032 | 5.2 | 187 | 4.9 | 188 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7608 | 1151.9997 | 51.6288
SYL-E.1.RR.613.1 | 24533269154034 | Sylhet, Tilagor, Shaplabag, Block-C, Rd # 2, H # 12, Rumi Villa | 2019-04-17 | MP1032 | 1.6 | 189 | 1.6 | 190 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7680 | 1079.9997 | 16.8584
SYL-E.1.RR.613.2 | 24533269154034 | Sylhet, Tilagor, Shaplabag, Block-C, Rd # 2, H # 12, Rumi Villa | 2021-02-14 | MN1018 | 20.6 | 110 | 20.6 | 111 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 20.6 | 20.6 | 1.236 | 1.236 | 0.0007168 | 100% | 0% | 1.236 | 1.236 | 0.0011869 | 28 | 0.024778 | 0.024778 |  | 0 | 0 | 7680 | 1079.9997 | 217.0515
SYL-E.1.RR.614.1 | 24533959154016 | Sylhet, Tilagor, Shaplabag, Block-B, Rd # 2, H # 26, Hormuj Mia | 2019-04-17 | MP1032 | 10.9 | 191 | 10.9 | 192 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7680 | 1079.9997 | 114.8476
SYL-E.1.RR.615.1 | 24534079154005 | Sylhet, Tilagor, Shaplabag, Block-B, Rd # 2 , Najimuddin | 2019-04-17 | MP1032 | 6.3 | 193 | 6.3 | 194 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7680 | 1079.9997 | 66.3798
SYL-E.1.RR.616.1 | 24534119154011 | Sylhet, Tilagor, Shaplabag, Block-B, Rd # 2, H # 8, Hazi Akil Uddin | 2019-04-17 | MP1032 | 1.8 | 195 | 1.8 | 196 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7680 | 1079.9997 | 18.9657
SYL-E.1.RR.617.1 | 24534359154008 | Sylhet, Tilagor, Shaplabag, Rd # 1, H # 1, Anfor Ali | 2019-04-17 | MP1032 | 1.8 | 197 | 1.8 | 198 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7680 | 1079.9997 | 18.9657
SYL-E.1.RR.617.2 | 24534359154008 | Sylhet, Tilagor, Shaplabag, Rd # 1, H # 1, Anfor Ali | 2021-02-14 | MN1018 | 12.1 | 108 | 12.1 | 109 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7680 | 1079.9997 | 127.4914
SYL-E.1.RR.618.1 | 24534259153583 | Sylhet, Tilagor, Shajo Road, Rd # 1, Forkan Miah | 2019-04-17 | MP1032 | 4.6 | 199 | 4.6 | 200 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7680 | 1079.9997 | 48.4678
SYL-E.1.RR.619.1 | 24534159153594 | Sylhet, Tilagor, Shaplabag, Rd # 1, H # 20, Khalilullah | 2019-04-17 | MP1032 | 1.8 | 201 | 1.8 | 202 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7680 | 1079.9997 | 18.9657
SYL-E.1.RR.619.2 | 24534159153594 | Sylhet, Tilagor, Shaplabag, Rd # 1, H # 20, Khalilullah | 2019-04-17 | MP1032 | 1 | 205 | 1 | 206 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7680 | 1079.9997 | 10.5365
SYL-E.1.RR.620.1 | 24534139153596 | Sylhet, Tilagor, Shaplabag, Rd # 1, H # 15, Anam Ahmed | 2019-04-17 | MP1032 | 1.2 | 207 | 1.2 | 208 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7680 | 1079.9997 | 12.6438
SYL-E.1.RR.621.1 | 24533889153592 | Sylhet, Tilagor, Shaplabag R/A, Rd # 1, H # 21/A | 2019-04-17 | MP1032 | 9.6 | 209 | 9.6 | 210 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7680 | 1079.9997 | 101.1502
SYL-E.1.RR.622.1 | 24532729153377 | Sylhet Sadar, Shibgonj, Lamapara, H # 82, Fokharuddin | 2019-04-18 | LP1002 | 36.1 | 211 | 36 | 212 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 36 | 36 | 2.16 | 2.16 | 0.0007168 | 100% | 0% | 2.16 | 2.16 | 0.0011869 | 28 | 0.043301 | 0.043301 |  | 0 | 0 | 7584 | 1175.9997 | 379.3133
SYL-E.1.RR.623.1 | 24532569153383 | Sylhet Sadar, Shibgonj, Lamapara, H # 83, Jonota Cottege, Shamsul Alom | 2019-04-18 | LP1002 | 1.5 | 213 | 1.5 | 214 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7584 | 1175.9997 | 15.8047
SYL-E.1.RR.626.1 | 24533279152446 | Sylhet Sadar, Sobani Ghat, Mowbon-5, Abdur Razzak | 2019-04-18 | LP1002 | 1 | 224 | 1 | 225 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7512 | 1247.9997 | 10.5365
SYL-E.1.RR.627.1 | 24533049152456 | Sylhet Sadar, Sobani Ghat, Mowbon, Bagha Villa | 2019-04-18 | LP1002 | 2.8 | 226 | 2.9 | 227 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7512 | 1247.9997 | 30.5558
SYL-E.1.RR.627.2 | 24533049152456 | Sylhet Sadar, Sobani Ghat, Mowbon, Bagha Villa | 2021-02-11 | LX1011 | 5.2 | 108 | 5.2 | 109 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7512 | 1247.9997 | 54.7897
SYL-E.1.RR.628.1 | 24533789154120 | Sylhet Sador, Tilagor, Kallanpur, Road #2, Emaran Hossain | 2019-04-19 | MP1032 | 1.3 | 279 | 1.3 | 280 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7680 | 1079.9997 | 13.6974
SYL-E.1.RR.628.2 | 24533789154120 | Sylhet Sador, Tilagor, Kallanpur, Road #2, Emaran Hossain | 2022-06-08 | LU1001 | 5.2 | 198 | 5.2 | 199 | 2022-06-08 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 3888 | 1079.9997 | 31.0725
SYL-E.1.RR.628.3 | 24533789154120 | Sylhet Sador, Tilagor, Kallanpur, Road #2, Emaran Hossain | 2022-06-08 | LU1001 | 2.3 | 200 | 2.3 | 201 | 2022-06-08 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 3888 | 1079.9997 | 13.7436
SYL-E.1.RR.629.1 | 24533619154115 | Sylhet Sador, Tilagor, Kallanpur, Road #2, H #50, Mahmud | 2019-04-19 | MP1032 | 1.6 | 281 | 1.6 | 282 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7680 | 1079.9997 | 16.8584
SYL-E.1.RR.631.1 | 24533349154168 | Sylhet Sador, Tilagor, Kallanpur, East Shaplabag, Block #A, Road #2, H #16, Motiour Rahman | 2019-04-19 | MP1032 | 14.1 | 284 | 14.1 | 285 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7680 | 1079.9997 | 148.5644
SYL-E.1.RR.631.2 | 24533349154168 | Sylhet Sador, Tilagor, Kallanpur, East Shaplabag, Block #A, Road #2, H #16, Motiour Rahman | 2021-02-14 | MN1018 | 11.8 | 115 | 11.8 | 116 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7680 | 1079.9997 | 124.3305
SYL-E.1.RR.632.1 | 24533489154169 | Sylhet Sador, Tilagor, Kallanpur, East Shaplabag, Block #A, Road #2, Ahmed | 2019-04-19 | MP1032 | 1.8 | 286 | 1.8 | 287 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7680 | 1079.9997 | 18.9657
SYL-E.1.RR.633.1 | 24534589153550 | Sylhet Sadar, Tilagor, Vathatikor, Md. Abdul Malek | 2019-04-19 | MP1006 | 1.2 | 258 | 1.2 | 259 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8280 | 479.9997 | 12.6438
SYL-E.1.RR.634.1 | 24535009153532 | Sylhet Sadar, Tilagor, Vathatikor, H # 33, Bablul Haque | 2019-04-19 | MP1006 | 1.7 | 260 | 1.7 | 261 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7752 | 1007.9997 | 17.912
SYL-E.1.RR.635.1 | 24535319153571 | Sylhet Sadar, Tilagor, Vatatikor, Amanullah Khan Road, H # 2/21, ATM Sofiqul Islam | 2019-04-19 | MP1006 | 1.5 | 262 | 1.5 | 263 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7752 | 1007.9997 | 15.8047
SYL-E.1.RR.636.1 | 24534579153576 | Sylhet Sadar, Tilagor, Vatatikor, Amanullah Khan Road, H # 6/1 | 2019-04-19 | MP1006 | 2 | 264 | 2 | 265 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7752 | 1007.9997 | 21.073
SYL-E.1.RR.637.1 | 24534539153551 | Sylhet Sadar, Tilagor, Vatatikor, Rd # 1, H # 8, MA Sahid | 2019-04-19 | MP1006 | 3.3 | 266 | 3.3 | 267 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7752 | 1007.9997 | 34.7704
SYL-E.1.RR.638.1 | 24534579153552 | Sylhet Sadar, Tilagor, Vatatikor, Rd # 1, H # 8, Abdul Rofique Mukul | 2019-04-19 | MP1006 | 3 | 268 | 2.9 | 269 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7752 | 1007.9997 | 30.5558
SYL-E.1.RR.651.1 | 24524009153356 | Sylhet Sadar, Shahporan, Nayabazar, Khusi Ghat, H #95, Abdus Samad | 2019-04-15 | MN1032 | 1.2 | 66 | 1.2 | 67 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7464 | 1295.9997 | 12.6438
SYL-E.1.RR.652.1 | 24523889153369 | Sylhet Sadar, Shahporan, Nayabazar, Khusi Ghat, A/1 Babul Ahmed | 2019-04-15 | MN1032 | 15.3 | 68 | 15 | 69 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 7464 | 1295.9997 | 158.0472
SYL-E.1.RR.653.1 | 24524199153388 | Sylhet Sadar, Shahporan, Nayabazar, Khusi Ghat, Monipuri Para, A/14, Mintu | 2019-04-15 | MN1032 | 49.3 | 70 | 49.7 | 71 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 49.7 | 49.7 | 2.982 | 2.982 | 0.0007168 | 100% | 0% | 2.982 | 2.982 | 0.0011869 | 28 | 0.059779 | 0.059779 |  | 0 | 0 | 7464 | 1295.9997 | 523.6631
SYL-E.1.RR.654.1 | 24524049153377 | Sylhet Sadar, Shahporan, Nayabazar, Khusi Ghat, Monipuri Para, A/14, H #07, Orunkormokar | 2019-04-15 | MN1032 | 11.2 | 72 | 11.3 | 73 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7464 | 1295.9997 | 119.0622
SYL-E.1.RR.655.1 | 24524229153347 | Sylhet Sadar, Shahporan, East Sadatikor, H #89, Gano mia | 2019-04-15 | MN1032 | 3.2 | 74 | 3.2 | 75 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7464 | 1295.9997 | 33.7167
SYL-E.1.RR.656.1 | 24524229153347 | Sylhet Sadar, Shahporan, East Sadatikor, H #85, Sajjad Khan | 2019-04-15 | MN1032 | 1.3 | 76 | 1.2 | 77 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7464 | 1295.9997 | 12.6438
SYL-E.1.RR.657.1 | 24524159153332 | Sylhet Sadar, Shahporan, East Sadatikor, H #92, Bappy | 2019-04-15 | MN1032 | 5.2 | 78 | 5.1 | 79 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7464 | 1295.9997 | 53.7361
SYL-E.1.RR.658.1 | 24531679153106 | Shahjalal Uposohor, Block-C, Rd# 38, H# 8, Jalil Chy. | 2019-04-16 | LP1002 | 1.5 | 126 | 1.5 | 127 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7512 | 1247.9997 | 15.8047
SYL-E.1.RR.659.1 | 24531689153114 | Shahjalal Uposohor, Block-C, Rd# 38, H# 12, Shafiq Mia | 2019-04-16 | LP1002 | 11.3 | 128 | 11.5 | 129 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7512 | 1247.9997 | 121.1695
SYL-E.1.RR.659.2 | 24531689153114 | Shahjalal Uposohor, Block-C, Rd# 38, H# 12, Shafiq Mia | 2019-04-16 | LP1002 | 2.1 | 130 | 2.1 | 131 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7512 | 1247.9997 | 22.1266
SYL-E.1.RR.660.1 | 24531679153118 | Shahjalal Uposohor, Block-C, Rd# 38, H# 15, Ashraf | 2019-04-16 | LP1002 | 2.5 | 132 | 2.5 | 133 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7512 | 1247.9997 | 26.3412
SYL-E.1.RR.661.1 | 24531729153159 | Shahjalal Uposohor, Block-C, Rd# 38, H# 30, Dr. Mahmud | 2019-04-16 | LP1002 | 1 | 134 | 1 | 135 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7512 | 1247.9997 | 10.5365
SYL-E.1.RR.662.1 | 24530929153345 | Sylhet Upososhor, Taroroton Para, Haji Belal Mia | 2019-04-17 | MN1032 | 16.7 | 124 | 16.7 | 125 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 7584 | 1175.9997 | 175.9592
SYL-E.1.RR.663.1 | 24531489153402 | Sylhet Upososhor, Sadar Para, Al-Amin | 2019-04-17 | MN1032 | 8.4 | 126 | 7.9 | 127 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7584 | 1175.9997 | 83.2382
SYL-E.1.RR.664.1 | 24531659153412 | Sylhet Upososhor, Sadar Para, H # 13, Al-Amin | 2019-04-17 | MN1032 | 6.3 | 128 | 6.3 | 129 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7584 | 1175.9997 | 66.3798
SYL-E.1.RR.665.1 | 24531659153412 | Sylhet, Sadar Para, H # 10, Al-Amin | 2019-04-17 | MN1032 | 7.4 | 130 | 7.4 | 131 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7584 | 1175.9997 | 77.97
SYL-E.1.RR.666.1 | 24531799153394 | Sylhet, Sadar Para, H # 26/A, Abdul Mannan | 2019-04-17 | MN1032 | 3 | 132 | 3 | 133 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7584 | 1175.9997 | 31.6094
SYL-E.1.RR.666.2 | 24531799153394 | Sylhet, Sadar Para, H # 26/A, Abdul Mannan | 2021-02-14 | LX1011 | 4.2 | 116 | 4.2 | 117 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7584 | 1175.9997 | 44.2532
SYL-E.1.RR.667.1 | 24531629153385 | Sylhet, Sadar Para, Shahajal Uposohr, H # 35,Haji Mostak Hossen | 2019-04-17 | MN1032 | 3.5 | 134 | 3.6 | 135 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7584 | 1175.9997 | 37.9313
SYL-E.1.RR.668.1 | 24531509153385 | Sylhet, Sadar Para, Shahajal Uposohr, Block - A, Rd # 4, Al Amin-34 | 2019-04-17 | MN1032 | 1 | 136 | 1.1 | 137 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7584 | 1175.9997 | 11.5901
SYL-E.1.RR.668.2 | 24531509153385 | Sylhet, Sadar Para, Shahajal Uposohr, Block - A, Rd # 4, Al Amin-34 | 2021-02-14 | LX1011 | 2.9 | 113 | 2.9 | 114 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7584 | 1175.9997 | 30.5558
SYL-E.1.RR.669.1 | 24531219153378 | Sylhet, West Sadar Para, Shahajal Uposohr, Al Amin R/A, Selim Ahmed | 2019-04-17 | MN1032 | 1.4 | 138 | 1.3 | 139 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7584 | 1175.9997 | 13.6974
SYL-E.1.RR.670.1 | 24531149153373 | Sylhet, Amborkhana, Borobazar, H # 51/2, Piyara Begum | 2019-04-17 | MN1032 | 2.8 | 140 | 2.8 | 141 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7584 | 1175.9997 | 29.5021
SYL-E.1.RR.671.1 | 24531779153379 | Sylhet, Sadarpara, Al Amin-39, Abdul Khalek | 2019-04-17 | MN1032 | 2.9 | 142 | 2.9 | 143 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7584 | 1175.9997 | 30.5558
SYL-E.1.RR.672.1 | 24530829153268 | Sylhet, Shajalal Uposhor, Teroroton, H # 30, Chunnu Mia Manjil | 2019-04-17 | MN1032 | 1.3 | 144 | 1.3 | 145 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7584 | 1175.9997 | 13.6974
SYL-E.1.RR.673.1 | 24530719153262 | Sylhet, Shajalal Uposhor, Teroroton, Rokon Miar'r Boundary | 2019-04-17 | MN1032 | 1.4 | 146 | 1.3 | 147 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7584 | 1175.9997 | 13.6974
SYL-E.1.RR.673.2 | 24530719153262 | Sylhet, Shajalal Uposhor, Teroroton, Rokon Miar'r Boundary | 2019-04-17 | MN1032 | 1.6 | 148 | 1.6 | 149 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7584 | 1175.9997 | 16.8584
SYL-E.1.RR.674.1 | 24551869157095 | Shah Paran, Khadimnagar, Choke Grame Road, Choke Grame R/A, Masud | 2019-07-14 | NQ1009 | 14.1 | 385 | 14.1 | 386 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7632 | 1127.9997 | 148.5644
SYL-E.1.RR.675.1 | 24551879157100 | Shah Paran, Khadimnagar, Choke Grame Road, Choke Grame R/A, Md. Sayesta Mia | 2019-07-14 | NQ1009 | 11.7 | 387 | 11.7 | 388 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7632 | 1127.9997 | 123.2768
SYL-E.1.RR.676.1 | 24551529157109 | Shah Paran, Khadimnagar, Choke Grame Road, Choke Grame R/A, Humayon | 2019-07-14 | NQ1009 | 11.3 | 389 | 11 | 390 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7632 | 1127.9997 | 115.9013
SYL-E.1.RR.677.1 | 24534329153398 | Shibgonj, Lakhri Para, Sayesta Mia | 2019-07-16 | NQ1009 | 13.9 | 391 | 13.9 | 392 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7752 | 1007.9997 | 146.4571
SYL-E.1.RR.678.1 | 24534999153396 | Shibgonj, Lakhri Para, Redwan Monjil, Bozlur Rahman, H# 18 | 2019-07-16 | NQ1009 | 30.6 | 393 | 30.6 | 394 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 30.6 | 30.6 | 1.836 | 1.836 | 0.0007168 | 100% | 0% | 1.836 | 1.836 | 0.0011869 | 28 | 0.036806 | 0.036806 |  | 0 | 0 | 7752 | 1007.9997 | 322.4163
SYL-E.1.RR.679.1 | 24535259153394 | Shibgonj, Lakhri Para, Md. Anus Villa | 2019-07-16 | NQ1009 | 13 | 395 | 13 | 396 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7752 | 1007.9997 | 136.9743
SYL-E.1.RR.680.1 | 24535339153391 | Shibgonj, Lakhri Para, Rokeya Bhaban | 2019-07-16 | NQ1009 | 10.9 | 397 | 10.9 | 398 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7752 | 1007.9997 | 114.8476
SYL-E.1.RR.681.1 | 24552169157076 | Harpara, Khadim Nagor, Chokhgram, Chokhgram Road, Ismail | 2019-07-14 | MP1006 | 10.9 | 313 | 10.9 | 314 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7632 | 1127.9997 | 114.8476
SYL-E.1.RR.682.1 | 24551609157126 | Harpara, Khadim Nagor, Chokhgram, Chokhgram Road, Joynal Abedin | 2019-07-14 | MP1006 | 19.3 | 315 | 19.3 | 316 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 7632 | 1127.9997 | 203.3541
SYL-E.1.RR.683.1 | 24551609157126 | Harpara, Khadim Nagor, Chokhgram, Chokhgram Road, Md. Rubel | 2019-07-14 | MP1006 | 9 | 317 | 9 | 318 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7632 | 1127.9997 | 94.8283
SYL-E.1.RR.684.1 | 24535429153385 | Sylhet, Shibgonj, Senpara, Rahat Nibash | 2019-07-16 | MP1006 | 9.3 | 319 | 9.3 | 320 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7752 | 1007.9997 | 97.9893
SYL-E.1.RR.685.1 | 24535429153385 | Sylhet, Shibgonj, Senpara, Rahat Nibash | 2019-07-16 | MP1006 | 13.6 | 321 | 13.6 | 322 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7752 | 1007.9997 | 143.2961
SYL-E.1.RR.686.1 | 24535429153385 | Sylhet, Shibgonj, Senpara, Dhirendro Kuthir | 2019-07-16 | MP1006 | 7.3 | 323 | 7.3 | 324 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7752 | 1007.9997 | 76.9163
SYL-E.1.RR.686.2 | 24535429153385 | Sylhet, Shibgonj, Senpara, Dhirendro Kuthir | 2021-11-21 | LU1001 | 12.3 | 149 | 12.2 | 150 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7752 | 1007.9997 | 128.5451
SYL-E.1.RR.687.1 | 24535289153364 | Sylhet, Shibgonj, Senpara, Mongol Bahadur | 2019-07-16 | MP1006 | 23.1 | 325 | 23.1 | 326 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 23.1 | 23.1 | 1.386 | 1.386 | 0.0007168 | 100% | 0% | 1.386 | 1.386 | 0.0011869 | 28 | 0.027785 | 0.027785 |  | 0 | 0 | 7752 | 1007.9997 | 243.3927
SYL-E.1.RR.688.1 | 24535289153364 | Sylhet, Shibgonj, Senpara, Juthisthir Chaudhuri | 2019-07-16 | MP1006 | 11.8 | 327 | 11.8 | 328 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7752 | 1007.9997 | 124.3305
SYL-E.1.RR.689.1 | 24535289153364 | Sylhet, Shibgonj, Senpara, Shokti Podo Dash | 2019-07-16 | MP1006 | 13.5 | 329 | 13.7 | 330 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7752 | 1007.9997 | 144.3498
SYL-E.1.RR.690.1 | 24535319153345 | Sylhet, Shibgonj, Senpara, Omio Ronjon Pal | 2019-07-16 | MP1006 | 19.3 | 331 | 19.3 | 332 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 7752 | 1007.9997 | 203.3541
SYL-E.1.RR.691.1 | 24551369157166 | Khadimnagar, Harpara R/A, Bangla Bari | 2019-07-14 | NQ1003 | 11.1 | 304 | 11.1 | 305 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7632 | 1127.9997 | 116.9549
SYL-E.1.RR.692.1 | 24535549153402 | Sibgong, Shenpara, Puspayon R/A, H # 58, Mizan | 2019-07-16 | NQ1003 | 11.3 | 306 | 11.3 | 307 | 2022-01-01 | [9 empty] | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0
SYL-E.1.RR.693.1 | 24535319153399 | Sibgong, Shenpara, Puspayon R/A, H # 62, Khan Bari | 2019-07-16 | NQ1003 | 7.4 | 308 | 7.4 | 309 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7752 | 1007.9997 | 77.97
SYL-E.1.RR.694.1 | 24535669153440 | Sibgong, Shenpara, Chand Monzil Road, Pushpayon R/A, H # 56, Chand Monzil | 2019-07-16 | NQ1003 | 10.2 | 310 | 9.6 | 311 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7752 | 1007.9997 | 101.1502
SYL-E.1.RR.695.1 | 24534629153250 | Shibgong, Mojumdar Para, Bayrobkunjo, Khaled | 2019-07-17 | NQ1003 | 8.6 | 1 | 8.6 | 2 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7824 | 935.9997 | 90.6137
SYL-E.1.RR.696.1 | 24535729153223 | Shibgong, Mojumdar Para, Abdul Nur | 2019-07-17 | NQ1003 | 11.6 | 3 | 11.6 | 4 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7824 | 935.9997 | 122.2232
SYL-E.1.RR.697.1 | 24535729153223 | Shibgong, Mojumdar Para, Sonali-29, Badrul Haque | 2019-07-17 | NQ1003 | 5.9 | 5 | 5.9 | 6 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7824 | 935.9997 | 62.1652
SYL-E.1.RR.698.1 | 24535729153223 | Shibgong, Mojumdar Para, Abdul Motin | 2019-07-17 | NQ1003 | 7 | 7 | 7 | 8 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7824 | 935.9997 | 73.7554
SYL-E.1.RR.699.1 | 24535769153226 | Shibgong, Mojumdar Para, Sonali-28, Manik Mia | 2019-07-17 | NQ1003 | 8.1 | 9 | 8.1 | 10 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7824 | 935.9997 | 85.3455
SYL-E.1.RR.700.1 | 24535769153226 | Shibgong, Mojumdar Para, Sonali-26, Md. Abdul Hafiz | 2019-07-17 | NQ1003 | 9.6 | 11 | 9.6 | 12 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7824 | 935.9997 | 101.1502
SYL-E.1.RR.702.1 | 24524549153441 | Sylhet, Burhanbad, Kushighat, Block - B, H # 38 | 2019-04-15 | MN1018 | 11.5 | 106 | 11.5 | 107 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7464 | 1295.9997 | 121.1695
SYL-E.1.RR.703.1 | 24524559153437 | Sylhet, Burhanbad, Kushighat, Block - B, Ana Mia | 2019-04-15 | MN1018 | 3 | 108 | 3 | 109 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7464 | 1295.9997 | 31.6094
SYL-E.1.RR.704.1 | 24524559153437 | Sylhet, Burhanbad, Kushighat, Block - B, Monu Mia | 2019-04-15 | MN1018 | 2.9 | 110 | 2.9 | 111 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7464 | 1295.9997 | 30.5558
SYL-E.1.RR.705.1 | 24524619153439 | Sylhet, Burhanbad, Kushighat, Block - B, Donu Mia | 2019-04-15 | MN1018 | 5.1 | 112 | 5.1 | 113 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7464 | 1295.9997 | 53.7361
SYL-E.1.RR.706.1 | 24524819153475 | Sylhet, Burhanbad, Kushighat, Block - B, Ruhul Amin | 2019-04-15 | MN1018 | 1.1 | 114 | 1.1 | 115 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7464 | 1295.9997 | 11.5901
SYL-E.1.RR.707.1 | 24524849153446 | Sylhet, Burhanbad, Kushighat, Block - B, Alauddin Mia | 2019-04-15 | MN1018 | 1 | 116 | 1 | 117 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7464 | 1295.9997 | 10.5365
SYL-E.1.RR.708.1 | 24525089153416 | Sylhet, Burhanbad, Kushighat, Block - B, Anwar Ahmed | 2019-04-15 | MN1018 | 10.7 | 118 | 10.8 | 119 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7464 | 1295.9997 | 113.794
SYL-E.1.RR.709.1 | 24525069153447 | Sylhet, Burhanbad, Kushighat, Block - B, H # 67, Manik Mia | 2019-04-15 | MN1018 | 5.5 | 120 | 5.5 | 121 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7464 | 1295.9997 | 57.9506
SYL-E.1.RR.709.2 | 24525069153447 | Sylhet, Burhanbad, Kushighat, Block - B, Donu Mia | 2019-04-15 | MN1018 | 5.5 | 122 | 5.5 | 123 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7464 | 1295.9997 | 57.9506
SYL-E.1.RR.710.1 | 24525219153451 | Sylhet, Burhanbad, Kushighat, Block - B, H # 69, Haji Altafur Rahman | 2019-04-15 | MN1018 | 4.7 | 124 | 4.7 | 125 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7464 | 1295.9997 | 49.5215
SYL-E.1.RR.711.1 | 24525679153573 | Sylhet, Tultikor, Chamelibagh, Block - C, H # 95 | 2019-04-16 | MP1032 | 4.9 | 137 | 4.7 | 138 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7464 | 1295.9997 | 49.5215
SYL-E.1.RR.712.1 | 24525779153598 | Sylhet, Tultikor, Miarbagh, Block - B, H # 45, Sahjan Mia | 2019-04-16 | MP1032 | 1.8 | 139 | 1.8 | 140 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7464 | 1295.9997 | 18.9657
SYL-E.1.RR.713.1 | 24530139154029 | Sylhet, Tultikor, Miarbagh, Block - B, H # 58 | 2019-04-16 | MP1032 | 1.7 | 143 | 1.7 | 144 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7464 | 1295.9997 | 17.912
SYL-E.1.RR.714.1 | 24525579154009 | Sylhet, Tultikor, Miarbagh, Moulotkhana, Block - B, H # 80 | 2019-04-16 | MP1032 | 2.3 | 145 | 2.1 | 146 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7464 | 1295.9997 | 22.1266
SYL-E.1.RR.715.1 | 24530329153575 | Sylhet, Tultikor, Modhubagh, Block - A, H # 13 | 2019-04-16 | MP1032 | 2 | 147 | 1.9 | 148 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7464 | 1295.9997 | 20.0193
SYL-E.1.RR.716.1 | 24530349153586 | Sylhet, Tultikor, Miarbagh, Main Road, Joynal Rahman | 2019-04-16 | MP1032 | 3.2 | 149 | 3.2 | 150 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7464 | 1295.9997 | 33.7167
SYL-E.1.RR.717.1 | 24530499153577 | Sylhet, Tultikor, Miarbagh, Main Road, H # 9 | 2019-04-16 | MP1032 | 1 | 151 | 1 | 152 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7464 | 1295.9997 | 10.5365
SYL-E.1.RR.718.1 | 24532059153182 | Sylhet Sadar, Shahjalal Uposhahar, Block-B, Road # 22, H # 32 | 2019-04-17 | MP1006 | 2 | 217 | 2 | 218 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7512 | 1247.9997 | 21.073
SYL-E.1.RR.719.1 | 24531999153188 | Sylet, Sadar, Shahjalal Upashahar, Block- B, Rd# 22, H#34 | 2019-04-17 | MP1006 | 2.4 | 219 | 2.5 | 220 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7512 | 1247.9997 | 26.3412
SYL-E.1.RR.720.1 | 24532479153153 | Sylet, Sadar, Shahjalal Upashahar, Block- B, Rd# 21, H# 6 | 2019-04-17 | MP1006 | 1.2 | 223 | 1.2 | 224 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7512 | 1247.9997 | 12.6438
SYL-E.1.RR.721.1 | 24532849153149 | Sylet, Sadar, Shahjalal Upashahar, Block- B, Rd# 21, H# 24 | 2019-04-17 | MP1006 | 4.7 | 225 | 4.7 | 226 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7512 | 1247.9997 | 49.5215
SYL-E.1.RR.722.1 | 24532849153149 | Sylet, Sadar, Shahjalal Upashahar, Block- B, Rd# 21, H# 26 | 2019-04-17 | MP1006 | 2.2 | 227 | 2.1 | 228 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7512 | 1247.9997 | 22.1266
SYL-E.1.RR.723.1 | 24532909153149 | Sylet, Sadar, Shahjalal Upashahar, Block- B, Rd# 21, H# 27 | 2019-04-17 | MP1006 | 9.6 | 229 | 9.6 | 230 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7512 | 1247.9997 | 101.1502
SYL-E.1.RR.724.1 | 24532359153170 | Sylet, Sadar, Shahjalal Upashahar, Block- B, Rd# 20, H# 4 | 2019-04-17 | MP1006 | 2.4 | 232 | 2.3 | 233 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8280 | 479.9997 | 24.2339
SYL-E.1.RR.725.1 | 24532599153169 | Sylet, Sadar, Shahjalal Upashahar, Block- B, Rd# 20, H# 15 | 2019-04-17 | MP1006 | 1.2 | 234 | 1.2 | 235 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7512 | 1247.9997 | 12.6438
SYL-E.1.RR.726.1 | 24533069153007 | Sylhet, Jotorpur,Nobopushpo R/A, H#97, Barik Miah | 2019-04-18 | MN1032 | 1 | 162 | 1 | 163 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7488 | 1271.9997 | 10.5365
SYL-E.1.RR.727.1 | 24533079153003 | Sylhet, Jotorpur,Nobopushpo R/A, H#134/A | 2019-04-18 | MN1032 | 2.6 | 166 | 2.6 | 167 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7488 | 1271.9997 | 27.3949
SYL-E.1.RR.728.1 | 24533099153004 | Sylhet, Jotorpur,Nobopushpo R/A, H#133/A | 2019-04-18 | MN1032 | 3.2 | 168 | 3.3 | 169 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7488 | 1271.9997 | 34.7704
SYL-E.1.RR.729.1 | 24532789153052 | Sylhet, Jotorpur,Nobopushpo R/A, H#122 | 2019-04-18 | MN1032 | 2 | 170 | 2 | 171 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7488 | 1271.9997 | 21.073
SYL-E.1.RR.730.1 | 24532759153038 | Sylhet, Jotorpur,Nobopushpo R/A, H#116 | 2019-04-18 | MN1032 | 1.1 | 173 | 1.1 | 174 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7488 | 1271.9997 | 11.5901
SYL-E.1.RR.731.1 | 24532829152589 | Sylhet, Jotorpur,Nobopushpo R/A, H#49, Raja Mia | 2019-04-18 | MN1032 | 1.9 | 175 | 1.9 | 176 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7488 | 1271.9997 | 20.0193
SYL-E.1.RR.732.1 | 24532719152579 | Sylhet, Jotorpur,Nobopushpo R/A, H#50/A, Ahmad Vuia | 2019-04-18 | MN1032 | 2.7 | 177 | 2.7 | 178 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7488 | 1271.9997 | 28.4485
SYL-E.1.RR.733.1 | 24533279152575 | Sylhet, Jotorpur,Nobopushpo R/A, H#40 | 2019-04-18 | MN1032 | 1.1 | 179 | 1.1 | 180 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7488 | 1271.9997 | 11.5901
SYL-E.1.RR.734.1 | 24535719153525 | Sylhet, Shibgonj, Shadipur R/A, H # 44 | 2019-04-20 | MN1018 | 12.9 | 264 | 12.3 | 265 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7752 | 1007.9997 | 129.5987
SYL-E.1.RR.735.1 | 24535529153526 | Sylhet, Shibgonj, Shadipur R/A, H # 50, Abdul Banik | 2019-04-20 | MN1018 | 1.3 | 266 | 1.3 | 267 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7752 | 1007.9997 | 13.6974
SYL-E.1.RR.736.1 | 24535649153540 | Sylhet, Shibgonj, Shadipur R/A, H # 51, Nikhil Debnath | 2019-04-20 | MN1018 | 1.4 | 268 | 1.4 | 269 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7752 | 1007.9997 | 14.7511
SYL-E.1.RR.738.1 | 24535369153446 | Sylhet, Shibgonj, Shadipur, Mouchak R/A, H # 19 | 2019-04-20 | MN1018 | 5.6 | 272 | 5.6 | 273 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7752 | 1007.9997 | 59.0043
SYL-E.1.RR.738.2 | 24535369153446 | Sylhet, Shibgonj, Shadipur, Mouchak R/A, H # 19 | 2021-02-28 | MN1018 | 13.4 | 176 | 13.4 | 177 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7752 | 1007.9997 | 141.1888
SYL-E.1.RR.739.1 | 24535459153417 | Sylhet, Shibgonj, Shadipur, Mouchak R/A, H # 19/6 | 2019-04-20 | MN1018 | 3.8 | 274 | 3.8 | 275 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7752 | 1007.9997 | 40.0386
SYL-E.1.RR.740.1 | 24542849156098 | Shahporan, Majar Road, Al- Modina R/A, Block # A, Rd # 01, Sonamala Begum | 2019-07-16 | NQ1008 | 12.6 | 279 | 12.4 | 280 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7680 | 1079.9997 | 130.6524
SYL-E.1.RR.741.1 | 24543179156113 | Shahporan, Majar Road, Al- Modina R/A, Block # A, Rd # 02, Ziaul Islam | 2019-07-16 | NQ1008 | 12.5 | 281 | 12.5 | 282 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7680 | 1079.9997 | 131.706
SYL-E.1.RR.742.1 | 24543379156130 | Shahporan, Majar Road, Al- Modina R/A, Block # A, Rd # 03, Porimol Chondro | 2019-07-16 | NQ1008 | 6.8 | 283 | 6.8 | 284 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7680 | 1079.9997 | 71.6481
SYL-E.1.RR.743.1 | 24543499156137 | Shahporan, Majar Road, Al- Modina R/A, Block # A, Rd # 03, Biresh Debnath | 2019-07-16 | NQ1008 | 12.1 | 285 | 12.1 | 286 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7680 | 1079.9997 | 127.4914
SYL-E.1.RR.743.2 | 24543499156137 | Shahporan, Majar Road, Al- Modina R/A, Block # A, Rd # 03, Biresh Debnath | 2020-10-20 | MP1006 | 0.3 | 651 | 0.3 | 652 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 0.3 | 0.3 | 0.018 | 0.018 | 0.0007168 | 100% | 0% | 0.018 | 0.018 | 0.0011869 | 28 | 0.00036084 | 0.00036084 |  | 0 | 0 | 7680 | 1079.9997 | 3.1609
SYL-E.1.RR.744.1 | 24543639156136 | Shahporan, Majar Road, Al- Modina R/A, Block # A, Rd # 03, Ronjon Das, Rash Villa | 2019-07-16 | NQ1008 | 9.1 | 288 | 9.1 | 289 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7680 | 1079.9997 | 95.882
SYL-E.1.RR.745.1 | 24543609156149 | Shahporan, Majar Road, Al- Modina R/A, Block # A, Rd # 3/1, Mostofa Shohel, Bitul Mubarok | 2019-07-16 | NQ1008 | 4.9 | 290 | 4.9 | 291 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7680 | 1079.9997 | 51.6288
SYL-E.1.RR.751.1 | 24540569155338 | Khadimpara, Bohor Das Para, Road # 7, Mohim Roy | 2019-07-16 | NQ1008 | 13.3 | 292 | 13.3 | 293 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7680 | 1079.9997 | 140.1352
SYL-E.1.RR.752.1 | 24540949155308 | Khadimpara, Bohor Das Para, Mitali R/A, Road # 7, Jobrul Islam | 2019-07-16 | NQ1008 | 11.9 | 294 | 11.8 | 295 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7680 | 1079.9997 | 124.3305
SYL-E.1.RR.753.1 | 24540949155308 | Khadimpara, Bohor Das Para, Mitali R/A, Road # 7, Md.Rofik Alli | 2019-07-16 | NQ1008 | 25.3 | 296 | 25.3 | 297 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 25.3 | 25.3 | 1.518 | 1.518 | 0.0007168 | 100% | 0% | 1.518 | 1.518 | 0.0011869 | 28 | 0.030431 | 0.030431 |  | 0 | 0 | 7680 | 1079.9997 | 266.573
SYL-E.1.RR.754.1 | 24540749155315 | Khadimpara, Bohor Das Para, Road # 7, H # 4, Sri Somoresh Pal, Jononi Nibas | 2019-07-16 | NQ1008 | 9.2 | 300 | 9.2 | 301 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7680 | 1079.9997 | 96.9356
SYL-E.1.RR.755.1 | 24540749155315 | Khadimpara, Bohor Das Para, Road # 7, H # 4, Sri Somoresh Pal, Jononi Nibas | 2019-07-16 | NQ1008 | 7.6 | 304 | 7.6 | 305 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7680 | 1079.9997 | 80.0773
SYL-E.1.RR.756.1 | 24542349155345 | Khadimpara, Bohor Das Para, Road #7, Shahjalal City Technical College, H # 3, Abul Hannan | 2019-07-16 | NQ1008 | 4.5 | 306 | 4.5 | 307 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7680 | 1079.9997 | 47.4142
SYL-E.1.RR.761.1 | 24542609156089 | Shah Paran, Block -C, Rd # 2, H # 4, Khalilur Rahman | 2019-07-16 | MN1032 | 2.8 | 269 | 2.8 | 270 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7680 | 1079.9997 | 29.5021
SYL-E.1.RR.762.1 | 24542629156095 | Shah Paran, Block -C, Rd # 2, H # 5, Abdulr Ahad | 2019-07-16 | MN1032 | 11.7 | 271 | 11.8 | 272 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7680 | 1079.9997 | 124.3305
SYL-E.1.RR.763.1 | 24542469156114 | Shah Paran, Khadim Nagar, Rd # 4, Hazi Karim Mia, Tamim Idel School | 2019-07-16 | MN1032 | 2.9 | 273 | 2.9 | 274 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7680 | 1079.9997 | 30.5558
SYL-E.1.RR.771.1 | 24540909156247 | Khadimnagor, Islamabad, Rd # 1, Faruk Ahamed | 2019-07-16 | MN1032 | 9.4 | 275 | 9.4 | 276 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7632 | 1127.9997 | 99.0429
SYL-E.1.RR.772.1 | 24540909156247 | Khadimnagor, Islamabad, Rd # 1, Faruk Ahamed | 2019-07-16 | MN1032 | 7.5 | 277 | 7.5 | 278 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7632 | 1127.9997 | 79.0236
SYL-E.1.RR.773.1 | 24540969156247 | Khadimnagor, Islamabad, Rd # 1, Montaj Vila | 2019-07-16 | MN1032 | 4.6 | 279 | 4.6 | 280 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7632 | 1127.9997 | 48.4678
SYL-E.1.RR.774.1 | 24541089156252 | Khadimnagor, Islamabad, Rd # 1, Dr. Royel | 2019-07-16 | MN1032 | 17.7 | 281 | 17.7 | 282 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 7632 | 1127.9997 | 186.4957
SYL-E.1.RR.775.1 | 24542229156346 | Khadimnagor, Kollogram, Md. Nur Alam | 2019-07-16 | MN1032 | 7.4 | 283 | 7.4 | 284 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7632 | 1127.9997 | 77.97
SYL-E.1.RR.776.1 | 24542229156346 | Khadimnagor, Kollogram, Md. Nur Alam | 2019-07-16 | MN1032 | 22.7 | 288 | 22.7 | 289 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 22.7 | 22.7 | 1.362 | 1.362 | 0.0007168 | 100% | 0% | 1.362 | 1.362 | 0.0011869 | 28 | 0.027303 | 0.027303 |  | 0 | 0 | 7632 | 1127.9997 | 239.1781
SYL-E.1.RR.777.1 | 24541359156359 | Khadimnagor, Kollogram, Alim | 2019-07-16 | MN1032 | 12.1 | 290 | 12.1 | 291 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7632 | 1127.9997 | 127.4914
SYL-E.1.RR.778.1 | 24541359156359 | Khadimnagor, Kollogram, Alim | 2019-07-16 | MN1032 | 3.6 | 292 | 3.6 | 293 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7632 | 1127.9997 | 37.9313
SYL-E.1.RR.781.1 | 24543119155447 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 01, Hafiz Monjil | 2019-07-16 | NQ1011 | 24.6 | 277 | 24.2 | 278 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 24.2 | 24.2 | 1.452 | 1.452 | 0.0007168 | 100% | 0% | 1.452 | 1.452 | 0.0011869 | 28 | 0.029108 | 0.029108 |  | 0 | 0 | 8280 | 479.9997 | 254.9828
SYL-E.1.RR.782.1 | 24542229155517 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 03, Mobassir Ali Munsi | 2019-07-16 | NQ1011 | 8.9 | 279 | 8.9 | 280 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7680 | 1079.9997 | 93.7747
SYL-E.1.RR.783.1 | 24542159155522 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 03, Abdul Hannan | 2019-07-16 | NQ1011 | 6.7 | 281 | 6.7 | 282 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7680 | 1079.9997 | 70.5944
SYL-E.1.RR.783.2 | 24542159155522 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 03, Abdul Hannan | 2021-02-15 | LX1011 | 3.3 | 127 | 3.3 | 128 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7680 | 1079.9997 | 34.7704
SYL-E.1.RR.784.1 | 24542159155522 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 03, Mohammad Ali (H # 11) | 2019-07-16 | NQ1011 | 3.5 | 283 | 3.5 | 284 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7680 | 1079.9997 | 36.8777
SYL-E.1.RR.785.1 | 24542009155546 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 03, Abdus Sattar | 2019-07-16 | NQ1011 | 5.7 | 285 | 5.7 | 286 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7680 | 1079.9997 | 60.0579
SYL-E.1.RR.786.1 | 24541789155504 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 02, Ponkhi Mia | 2019-07-16 | NQ1011 | 4.6 | 287 | 4.6 | 288 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7680 | 1079.9997 | 48.4678
SYL-E.1.RR.786.2 | 24541789155504 | Sylhet Sadar, Khadim, Nipovon R/A, Rd # 02, Ponkhi Mia | 2020-10-21 | NQ1000 | 9.8 | 148 | 9.8 | 149 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7680 | 1079.9997 | 103.2575
SYL-E.1.RR.791.1 | 24542199155594 | Khadim Nagar, Lal Khatongi Road, Shahporan ( R ) Majar, Hafiz Maolana Abdul Malik | 2019-07-16 | NQ1011 | 6.6 | 273 | 6.6 | 274 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7680 | 1079.9997 | 69.5408
SYL-E.1.RR.792.1 | 24543729155595 | Shahporan, Shahporan Gate, Shahporan R/A, Rd # 1, Labu Mia | 2019-07-16 | NQ1011 | 9.3 | 275 | 9.3 | 276 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 8280 | 479.9997 | 97.9893
SYL-E.1.RR.801.1 | 24540259153286 | Shibgonj, Khoraddipara, Boishakhi R/A , H # 64/1 | 2019-07-17 | MP1006 | 12.7 | 1 | 12.7 | 2 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7824 | 935.9997 | 133.8133
SYL-E.1.RR.802.1 | 24540259153277 | Shibgonj, Khoraddipara, Boishakhi R/A , H # 116/1 | 2019-07-17 | MP1006 | 24.8 | 3 | 24.8 | 4 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 24.8 | 24.8 | 1.488 | 1.488 | 0.0007168 | 100% | 0% | 1.488 | 1.488 | 0.0011869 | 28 | 0.029829 | 0.029829 |  | 0 | 0 | 7824 | 935.9997 | 261.3047
SYL-E.1.RR.803.1 | 24540259153277 | Shibgonj, Khoraddipara, Boishakhi R/A , H # 116/A | 2019-07-17 | MP1006 | 12.1 | 5 | 12.1 | 6 | 2022-01-01 | 2022-11-23 | NQ1007 | 1.5 | 193 | 1.5 | 194 | 2022-11-23 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7824 | 935.9997
SYL-E.1.RR.804.1 | 24540389153280 | Shibgonj, Khoraddipara, Boishakhi R/A , Askonder Ali | 2019-07-17 | MP1006 | 6.1 | 7 | 6.1 | 8 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7824 | 935.9997 | 64.2725
SYL-E.1.RR.805.1 | 24540349153294 | Shibgonj, Khoraddipara, Boishakhi R/A , H # 73/3 | 2019-07-17 | MP1006 | 5.7 | 9 | 5.7 | 10 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7824 | 935.9997 | 60.0579
SYL-E.1.RR.806.1 | 24540719153270 | Shibgonj, Khoraddipara, Boishakhi R/A , H # 101/1 | 2019-07-17 | MP1006 | 8.5 | 13 | 8.5 | 14 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7824 | 935.9997 | 89.5601
SYL-E.1.RR.807.1 | 24540789153280 | Shibgonj, Khoraddipara, Boishakhi R/A , Anayetullah | 2019-07-17 | MP1006 | 10.8 | 15 | 10.8 | 16 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7824 | 935.9997 | 113.794
SYL-E.1.RR.808.1 | 24540789153280 | Shibgonj, Khoraddipara, Boishakhi R/A , Anayetullah | 2019-07-17 | MP1006 | 29.8 | 17 | 30 | 18 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 30 | 30 | 1.8 | 1.8 | 0.0007168 | 100% | 0% | 1.8 | 1.8 | 0.0011869 | 28 | 0.036084 | 0.036084 |  | 0 | 0 | 7824 | 935.9997 | 316.0944
SYL-E.1.RR.809.1 | 24540969153282 | Shibgonj, Khoraddipara, Boishakhi R/A , H # 96 | 2019-07-17 | MP1006 | 4.5 | 19 | 4.5 | 20 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7824 | 935.9997 | 47.4142
SYL-E.1.RR.810.1 | 24541279153278 | Shibgonj, Khoraddipara, Boishakhi R/A , H # 92/2 | 2019-07-17 | MP1006 | 21.1 | 21 | 21.1 | 22 | 2022-01-01 | 2022-11-23 | NQ1007 |  |  | 0 | 190 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7824 | 935.9997
SYL-E.1.RR.811.1 | 24541419153297 | Shibgonj, Khoraddipara, Boishakhi R/A , Kanchan Pal | 2019-07-17 | MP1006 | 8 | 23 | 8 | 24 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7824 | 935.9997 | 84.2919
SYL-E.1.RR.812.1 | 24541219153245 | Dorjibond, Nrayangor, Bashundhara R/A , Habibur Rashid | 2019-07-17 | MP1006 | 1.6 | 25 | 1.6 | 26 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7824 | 935.9997 | 16.8584
SYL-E.1.RR.813.1 | 24541219153245 | Dorjibond, Nrayangor, Bashundhara R/A , Habibur Rashid | 2019-07-17 | MP1006 | 8.2 | 27 | 8.2 | 28 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7824 | 935.9997 | 86.3991
SYL-E.1.RR.814.1 | 24541039153266 | Dorjibond, Nrayangor, Bashundhara R/A , 137/A | 2019-07-17 | MP1006 | 12 | 29 | 12 | 30 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7824 | 935.9997 | 126.4378
SYL-E.1.RR.815.1 | 24540419153164 | Dorjibond, Raynagar, Basundhara R/A, H # 79/2 | 2019-07-18 | MP1006 | 14.1 | 55 | 14.1 | 56 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7824 | 935.9997 | 148.5644
SYL-E.1.RR.815.2 | 24540419153164 | Dorjibond, Raynagar, Basundhara R/A, H # 79/2 | 2022-11-23 | NQ1007 | 8.7 | 198 | 8.8 | 199 | 2022-11-23 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 0 | 935.9997 | 9.9072
SYL-E.1.RR.816.1 | 24540739153151 | Dorjibond, Raynagar, Basundhara R/A, H # 73 | 2019-07-18 | MP1006 | 10.9 | 57 | 10.2 | 58 | 2022-01-01 | 2022-11-23 | NQ1007 |  |  | 0 | 200 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7824 | 935.9997
SYL-E.1.RR.817.1 | 24540739153151 | Dorjibond, Raynagar, Basundhara R/A, H # 73 | 2019-07-18 | MP1006 | 7.2 | 59 | 7.2 | 60 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7824 | 935.9997 | 75.8627
SYL-E.1.RR.818.1 | 24540739153151 | Dorjibond, Raynagar, Basundhara R/A, H # 75 | 2019-07-18 | MP1006 | 14.5 | 61 | 14.5 | 62 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7824 | 935.9997 | 152.779
SYL-E.1.RR.819.1 | 24540739153151 | Dorjibond, Raynagar, Basundhara R/A, H # 78 | 2019-07-18 | MP1006 | 6.5 | 63 | 6.5 | 64 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7824 | 935.9997 | 68.4871
SYL-E.1.RR.820.1 | 24541009153117 | Dorjibond, Raynagar, Basundhara R/A, Abdul Hannan Choudhuri | 2019-07-18 | MP1006 | 11.9 | 65 | 11.9 | 66 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7848 | 911.9997 | 125.3841
SYL-E.1.RR.821.1 | 24541259153130 | Razbari, Raynagar, Mitaly R/A, H # 42/2 | 2019-07-18 | MP1006 | 6.9 | 67 | 7 | 68 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7848 | 911.9997 | 73.7554
SYL-E.1.RR.822.1 | 24541299153158 | Razbari, Raynagar, Mitaly R/A, H # 4 | 2019-07-18 | MP1006 | 11.7 | 69 | 11.7 | 70 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7848 | 911.9997 | 123.2768
SYL-E.1.RR.823.1 | 24541839153186 | Razbari, Raynagar, Mitaly R/A, Lane # 5, H # 86 | 2019-07-18 | MP1006 | 4.8 | 71 | 4.8 | 72 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7848 | 911.9997 | 50.5751
SYL-E.1.RR.824.1 | 24541749153200 | Razbari, Raynagar, Mitaly R/A, Lane # 3, H # 131 | 2019-07-18 | MP1006 | 9 | 73 | 9 | 74 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7848 | 911.9997 | 94.8283
SYL-E.1.RR.825.1 | 24541609153171 | Razbari, Raynagar, Mitaly R/A, Lane # 3, H # 107 | 2019-07-18 | MP1006 | 11.4 | 75 | 11.4 | 76 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7848 | 911.9997 | 120.1159
SYL-E.1.RR.826.1 | 24535599152583 | Mirabazar, Ag Para, Moushumi R/A, H# 96/E | 2019-07-22 | MP1006 | 10.9 | 122 | 10.1 | 123 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8136 | 623.9997 | 106.4185
SYL-E.1.RR.827.1 | 24535539153007 | Mirabazar, Ag Para, Moushumi R/A, H# 111 | 2019-07-22 | MP1006 | 14.4 | 124 | 14.5 | 125 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 8136 | 623.9997 | 152.779
SYL-E.1.RR.828.1 | 24535829152599 | Mirabazar, Ag Para, Moushumi R/A, H# 107/A | 2019-07-22 | MP1006 | 3.9 | 126 | 3.9 | 127 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 8136 | 623.9997 | 41.0923
SYL-E.1.RR.829.1 | 24541489152533 | Shahi Eidgha, Dhanshri, Abdul Malek | 2019-07-22 | MP1006 | 10.1 | 128 | 10.3 | 129 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7848 | 911.9997 | 108.5258
SYL-E.1.RR.830.1 | 24541889152539 | Shahi Eidgha, Dhanshri, Chowdhury Cotage | 2019-07-22 | MP1006 | 4.7 | 130 | 4.7 | 131 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7848 | 911.9997 | 49.5215
SYL-E.1.RR.831.1 | 24541889152539 | Shahi Eidgha, Dhanshri, H# 41 | 2019-07-22 | MP1006 | 6.5 | 132 | 6.5 | 133 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7848 | 911.9997 | 68.4871
SYL-E.1.RR.832.1 | 24541579152584 | Shahi Eidgha, Dhanshri, Salem Mia | 2019-07-22 | MP1006 | 16.1 | 134 | 16.1 | 135 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 7848 | 911.9997 | 169.6373
SYL-E.1.RR.832.2 | 24541579152584 | Shahi Eidgha, Dhanshri, Salem Mia | 2021-11-18 | LU1001 | 6.8 | 145 | 6.8 | 146 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7848 | 911.9997 | 71.6481
SYL-E.1.RR.833.1 | 24541519152574 | Shahi Eidgha, Dhanshri, H# 35/E | 2019-07-22 | MP1006 | 16.1 | 136 | 16.1 | 137 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 7848 | 911.9997 | 169.6373
SYL-E.1.RR.834.1 | 24541519152574 | Shahi Eidgha, Dhanshri, Anu Mia | 2019-07-22 | MP1006 | 13.7 | 138 | 13.7 | 139 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7848 | 911.9997 | 144.3498
SYL-E.1.RR.835.1 | 24533359153205 | Sonapara, Nobarun, H# 207 | 2019-07-23 | MP1006 | 14.9 | 162 | 14.6 | 163 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7512 | 1247.9997 | 153.8326
SYL-E.1.RR.836.1 | 24533199153204 | Sonapara, Nobarun, H# 111 | 2019-07-23 | MP1006 | 13.2 | 164 | 13.3 | 165 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7512 | 1247.9997 | 140.1352
SYL-E.1.RR.837.1 | 24533179153206 | Sonapara, Nobarun, H# 112 | 2019-07-23 | MP1006 | 12.3 | 168 | 12.3 | 169 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7512 | 1247.9997 | 129.5987
SYL-E.1.RR.838.1 | 24533179153206 | Sonapara, Nobarun, H# 131/1 | 2019-07-23 | MP1006 | 6.6 | 170 | 6.6 | 171 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7512 | 1247.9997 | 69.5408
SYL-E.1.RR.839.1 | 24533099153209 | Sonapara, Nobarun, H# 113/1 | 2019-07-23 | MP1006 | 14.6 | 172 | 14.6 | 173 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7512 | 1247.9997 | 153.8326
SYL-E.1.RR.840.1 | 24533099153209 | Sonapara, Nobarun, H# 114 | 2019-07-23 | MP1006 | 11.8 | 174 | 11.8 | 175 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7512 | 1247.9997 | 124.3305
SYL-E.1.RR.841.1 | 24532949153202 | Sonapara, Nobarun, H# 123 | 2019-07-23 | MP1006 | 13.1 | 176 | 13.1 | 177 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7512 | 1247.9997 | 138.0279
SYL-E.1.RR.842.1 | 24532949153202 | Sonapara, Nobarun, H# 121 | 2019-07-23 | MP1006 | 11.4 | 180 | 11.4 | 181 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7512 | 1247.9997 | 120.1159
SYL-E.1.RR.843.1 | 24533019153184 | Sonapara, Nobarun, H# 129 | 2019-07-23 | MP1006 | 15.1 | 185 | 15.1 | 186 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7512 | 1247.9997 | 159.1009
SYL-E.1.RR.844.1 | 24533019153184 | Sonapara, Nobarun, H# 128/1 | 2019-07-23 | MP1006 | 15.2 | 187 | 15.2 | 188 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7512 | 1247.9997 | 160.1545
SYL-E.1.RR.845.1 | 24533019153184 | Sonapara, Nobarun, H# 126/1 | 2019-07-23 | MP1006 | 6.5 | 189 | 6.5 | 190 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7512 | 1247.9997 | 68.4871
SYL-E.1.RR.846.1 | 24533349153221 | Sonapara, Nobarun, H# 105 | 2019-07-23 | MP1006 | 18.3 | 191 | 18.3 | 192 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 18.3 | 18.3 | 1.098 | 1.098 | 0.0007168 | 100% | 0% | 1.098 | 1.098 | 0.0011869 | 28 | 0.022011 | 0.022011 |  | 0 | 0 | 7512 | 1247.9997 | 192.8176
SYL-E.1.RR.847.1 | 24560849158599 | Boteshhor Bazar, Ronkali Housing H # 4 | 2019-07-25 | MP1006 | 20 | 219 | 20 | 220 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 7800 | 959.9997 | 210.7296
SYL-E.1.RR.848.1 | 24560849158599 | Boteshhor Bazar, Ronkali Housing H # 5 | 2019-07-25 | MP1006 | 7.9 | 221 | 7.9 | 222 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7800 | 959.9997 | 83.2382
SYL-E.1.RR.849.1 | 24555519158570 | Boteshhor, Chuwabohor, Sabbir Ahmed | 2019-07-25 | MP1006 | 3.9 | 223 | 3.9 | 224 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7800 | 959.9997 | 41.0923
SYL-E.1.RR.850.1 | 24555559158563 | Boteshhor, Chuwabohor, Bimol Krishna | 2019-07-25 | MP1006 | 7.1 | 225 | 7.1 | 226 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7800 | 959.9997 | 74.809
SYL-E.1.RR.851.1 | 24535419153329 | Shibgonj, Shenpara, Alpona R/a, H # 102, Iqbal Hosen | 2019-07-16 | MP1006 | 9.8 | 333 | 9.8 | 334 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7752 | 1007.9997 | 103.2575
SYL-E.1.RR.852.1 | 24535419153329 | Shibgonj, Shenpara, Alpona R/a, H # 103, Mortuza Chowdhory | 2019-07-16 | MP1006 | 7.3 | 335 | 7.3 | 336 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7752 | 1007.9997 | 76.9163
SYL-E.1.RR.853.1 | 24535599153299 | Shibgonj, Devpara, Alpona R/a, H # 50,Biddut Vuson Dev | 2019-07-16 | MP1006 | 22.8 | 337 | 22.3 | 338 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 7824 | 935.9997 | 234.9635
SYL-E.1.RR.854.1 | 24535599153299 | Shibgonj, Devpara, Alpona R/a, H # 51,Bijoy Kumar Dotto | 2019-07-16 | MP1006 | 23.1 | 339 | 23.1 | 340 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 23.1 | 23.1 | 1.386 | 1.386 | 0.0007168 | 100% | 0% | 1.386 | 1.386 | 0.0011869 | 28 | 0.027785 | 0.027785 |  | 0 | 0 | 7824 | 935.9997 | 243.3927
SYL-E.1.RR.855.1 | 24535489153298 | Shibgonj, Devpara, Alpona R/a, H # 145,Manuk Lal Chokhroboty | 2019-07-16 | MP1006 | 10.8 | 341 | 10.8 | 342 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7824 | 935.9997 | 113.794
SYL-E.1.RR.856.1 | 24535999153303 | Shibgonj, Devpara, Alpona R/a, Sumon | 2019-07-16 | MP1006 | 14.4 | 343 | 14.4 | 344 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7824 | 935.9997 | 151.7253
SYL-E.1.RR.856.2 | 24535999153303 | Shibgonj, Devpara, Alpona R/a, Sumon | 2022-11-23 | NQ1007 | 3.5 | 186 | 3.6 | 187 | 2022-11-23 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 0 | 935.9997 | 4.0529
SYL-E.1.RR.857.1 | 24535919153274 | Shibgonj, Mozumder Para, Boyshaki R/a,Abdullah Siddiki | 2019-07-16 | MP1006 | 23.3 | 345 | 23.2 | 346 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 23.2 | 23.2 | 1.392 | 1.392 | 0.0007168 | 100% | 0% | 1.392 | 1.392 | 0.0011869 | 28 | 0.027905 | 0.027905 |  | 0 | 0 | 7824 | 935.9997 | 244.4464
SYL-E.1.RR.858.1 | 24535899153276 | Shibgonj, Mozumder Para, Boyshaki R/a, H # 19/B, Sikder Villa | 2019-07-16 | MP1006 | 17.3 | 347 | 17.3 | 348 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 7824 | 935.9997 | 182.2811
SYL-E.1.RR.859.1 | 24535799153275 | Shibgonj, Mozumder Para, Boyshaki R/a, H # 14, Poli House | 2019-07-16 | MP1006 | 5.3 | 349 | 5.3 | 350 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7824 | 935.9997 | 55.8434
SYL-E.1.RR.860.1 | 24540149153255 | Shibgonj, Mozumder Para, Boyshaki R/a, H # 121, Abdulla Siddiki | 2019-07-16 | MP1006 | 13.1 | 351 | 13.1 | 352 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7824 | 935.9997 | 138.0279
SYL-E.1.RR.861.1 | 24555419158520 | Shibgonj, Mozumder Para, Boyshaki R/a, H # 139, Motabbor Hosen Alam | 2019-07-16 | MP1006 | 9.9 | 353 | 9.9 | 354 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7824 | 935.9997 | 104.3112
SYL-E.1.RR.862.1 | 24541079153262 | Ray Nagor, Dorjibon, Bosundhora, Raja Mia | 2019-07-17 | MP1006 | 18.7 | 31 | 18.7 | 32 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 7824 | 935.9997 | 197.0322
SYL-E.1.RR.863.1 | 24541219153259 | Ray Nagor, Dorjibon, Bosundhora, H # 142, Soiyod Monjil | 2019-07-17 | MP1006 | 17.4 | 33 | 17.4 | 34 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 7824 | 935.9997 | 183.3348
SYL-E.1.RR.864.1 | 24541219153259 | Ray Nagor, Dorjibon, Bosundhora, H # 142, Soiyod Monjil | 2019-07-17 | MP1006 | 9.9 | 35 | 9.3 | 36 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7824 | 935.9997 | 97.9893
SYL-E.1.RR.865.1 | 24541019153223 | Ray Nagor, Dorjibon, Bosundhora, Samsun Nahar | 2019-07-17 | MP1006 | 17.1 | 37 | 17.2 | 38 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 7824 | 935.9997 | 181.2275
SYL-E.1.RR.866.1 | 24541089153229 | Ray Nagor, Dorjibon, Bosundhora, H # 127, Sanowar Ali | 2019-07-17 | MP1006 | 19.4 | 39 | 19.3 | 40 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 7824 | 935.9997 | 203.3541
SYL-E.1.RR.867.1 | 24541209153212 | Ray Nagor, Dorjibon, Bosundhora, H # 123/6, Chowdhory Plecse | 2019-07-17 | MP1006 | 2.6 | 41 | 2.6 | 42 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7824 | 935.9997 | 27.3949
SYL-E.1.RR.868.1 | 24540669153196 | Ray Nagor, Dorjibon, Bosundhora, H # 90, Hazi Mohammad Roshid Monjil | 2019-07-17 | MP1006 | 11.1 | 43 | 11.1 | 44 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7824 | 935.9997 | 116.9549
SYL-E.1.RR.869.1 | 24540669153196 | Ray Nagor, Dorjibon, Bosundhora, H # 90, Hazi Mohammad Roshid Monjil | 2019-07-17 | MP1006 | 9 | 45 | 9 | 46 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7824 | 935.9997 | 94.8283
SYL-E.1.RR.870.1 | 24540509153200 | Ray Nagor, Dorjibon, Bosundhora,Anowar Vila ( Be side of al chobor house) | 2019-07-17 | MP1006 | 27.5 | 47 | 27.5 | 48 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 27.5 | 27.5 | 1.65 | 1.65 | 0.0007168 | 100% | 0% | 1.65 | 1.65 | 0.0011869 | 28 | 0.033077 | 0.033077 |  | 0 | 0 | 7824 | 935.9997 | 289.7532
SYL-E.1.RR.871.1 | 24540509153200 | Ray Nagor, Dorjibon, Bosundhora, Mohim Mia | 2019-07-17 | MP1006 | 2.7 | 49 | 2.7 | 50 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7824 | 935.9997 | 28.4485
SYL-E.1.RR.872.1 | 24540609153167 | Ray Nagor, Dorjibon, Bosundhora, H # 83, Mona, Suruchi vhabon | 2019-07-17 | MP1006 | 23.4 | 51 | 23 | 52 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 23 | 23 | 1.38 | 1.38 | 0.0007168 | 100% | 0% | 1.38 | 1.38 | 0.0011869 | 28 | 0.027664 | 0.027664 |  | 0 | 0 | 7824 | 935.9997 | 242.3391
SYL-E.1.RR.873.1 | 24540609153167 | Ray Nagor, Dorjibon, Bosundhora, H # 83/A, Hoque Monjil | 2019-07-17 | MP1006 | 19.1 | 53 | 19.1 | 54 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 7824 | 935.9997 | 201.2468
SYL-E.1.RR.874.1 | 24541359153240 | Ray Nagor, Rajbari, Mitali R/A, Lane # 10, H # 31, Nasir Uddin | 2019-07-18 | MP1006 | 14.3 | 77 | 14.3 | 78 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7824 | 935.9997 | 150.6717
SYL-E.1.RR.875.1 | 24541359153258 | Ray Nagor, Rajbari, Mitali R/A, Lane # 10, H # 33/c, Abul Mia | 2019-07-18 | MP1006 | 4.4 | 79 | 4.4 | 80 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7824 | 935.9997 | 46.3605
SYL-E.1.RR.876.1 | 24541459153249 | Ray Nagor, Rajbari, Mitali R/A, Lane # 9, H # 149/1, Ahmod Monjil | 2019-07-18 | MP1006 | 6.9 | 81 | 6.3 | 82 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7824 | 935.9997 | 66.3798
SYL-E.1.RR.877.1 | 24541589153215 | Ray Nagor, Rajbari, Mitali R/A, Lane # 4, H # 116, Habibur Rashid Chowdhory | 2019-07-18 | MP1006 | 7.3 | 83 | 7.3 | 84 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7824 | 935.9997 | 76.9163
SYL-E.1.RR.878.1 | 24541589153215 | Ray Nagor, Rajbari, Mitali R/A, Lane # 4, H # 117, Hasan Reza Chowdhory | 2019-07-18 | MP1006 | 9.6 | 85 | 9.6 | 86 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7824 | 935.9997 | 101.1502
SYL-E.1.RR.879.1 | 24540599152533 | Kumarpara, Jhornarpar, H # 18, Anowar Hosen | 2019-07-18 | MP1006 | 3.6 | 87 | 3.6 | 88 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7848 | 911.9997 | 37.9313
SYL-E.1.RR.880.1 | 24540499152532 | Kumarpara, Jhornarpar, H # 05, Hazi Nur Mia | 2019-07-18 | MP1006 | 11.1 | 89 | 11.1 | 90 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7848 | 911.9997 | 116.9549
SYL-E.1.RR.881.1 | 24540569152541 | Kumarpara, Jhornarpar, H # 17/A, Md. Riaj Uddin | 2019-07-18 | MP1006 | 17.6 | 91 | 17.6 | 92 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 7848 | 911.9997 | 185.4421
SYL-E.1.RR.882.1 | 24540569152541 | Kumarpara, Jhornarpar, H # 16, Md. Aftabuzzaman Khan | 2019-07-18 | MP1006 | 14.4 | 93 | 14.4 | 94 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7848 | 911.9997 | 151.7253
SYL-E.1.RR.883.1 | 24540719152518 | Kumarpara, Jhornarpar, H # 03, Adv: Batir | 2019-07-20 | MP1006 | 10.4 | 95 | 10.4 | 96 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7848 | 911.9997 | 109.5794
SYL-E.1.RR.884.1 | 24540649152515 | Kumarpara, Jhornarpar, H # 02, Abdur Sattar | 2019-07-20 | MP1006 | 9.1 | 97 | 9.1 | 98 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7848 | 911.9997 | 95.882
SYL-E.1.RR.885.1 | 24540649152515 | Kumarpara, Jhornarpar, H # 02, Mahamuda Khatun | 2019-07-20 | MP1006 | 6.6 | 99 | 6.6 | 100 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7848 | 911.9997 | 69.5408
SYL-E.1.RR.886.1 | 24540879152518 | Kumarpara, Jhornarpar, H # 82, Nasim Ahamod | 2019-07-20 | MP1006 | 13.7 | 101 | 13.7 | 102 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7848 | 911.9997 | 144.3498
SYL-E.1.RR.887.1 | 24540879152527 | Kumarpara, Jhornarpar, H # 84, Lutfor Rahman | 2019-07-20 | MP1006 | 17.1 | 104 | 17.1 | 105 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 7848 | 911.9997 | 180.1738
SYL-E.1.RR.888.1 | 24540999152525 | Kumarpara, Jhornarpar, Jhorna-86, Moon Light House | 2019-07-20 | MP1006 | 10.4 | 106 | 10.4 | 107 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7848 | 911.9997 | 109.5794
SYL-E.1.RR.889.1 | 24540999152525 | Kumarpara, Jhornarpar, Jhorna-86, Nurul Amin | 2019-07-20 | MP1006 | 12.2 | 108 | 12.2 | 109 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7848 | 911.9997 | 128.5451
SYL-E.1.RR.890.1 | 24540639152501 | Kumarpara, Jhornarpar, Jhorna-1, Abdul Motin | 2019-07-20 | MP1006 | 10.7 | 110 | 10 | 111 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7848 | 911.9997 | 105.3648
SYL-E.1.RR.891.1 | 24540869152587 | Kumarpara, Jhornarpar, H # 33, Gazi Bari | 2019-07-21 | MP1006 | 3.2 | 112 | 3.2 | 113 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7848 | 911.9997 | 33.7167
SYL-E.1.RR.892.1 | 24540819152579 | Kumarpara, Jhornarpar, H # 32/A, Abdul Malik | 2019-07-21 | MP1006 | 4.9 | 114 | 4.9 | 115 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7848 | 911.9997 | 51.6288
SYL-E.1.RR.893.1 | 24541089152582 | Kumarpara, Jhornarpar, Sree Sree Bura Shib Bari, Jhornarpar Shib Mondir | 2019-07-21 | MP1006 | 12.9 | 116 | 12.9 | 117 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7848 | 911.9997 | 135.9206
SYL-E.1.RR.894.1 | 24541089152582 | Kumarpara, Jhornarpar, Sree Sree Bura Shib Bari, Jhornarpar Shib Mondir | 2019-07-21 | MP1006 | 6.4 | 120 | 6.4 | 121 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7848 | 911.9997 | 67.4335
SYL-E.1.RR.895.1 | 24542269152581 | Shahi Eidgah, Anamika R/A, Jaman Vila, H # 89 | 2019-07-23 | MP1006 | 4.9 | 140 | 4.9 | 141 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7848 | 911.9997 | 51.6288
SYL-E.1.RR.896.1 | 24542199152595 | Shahi Eidgah, Anamika R/A, H # 70/A, Ruman Ahamed | 2019-07-23 | MP1006 | 13.5 | 142 | 13.5 | 143 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 8280 | 479.9997 | 142.2425
SYL-E.1.RR.896.2 | 24542199152595 | Shahi Eidgah, Anamika R/A, H # 70/A, Ruman Ahamed | 2021-02-22 | LX1011 | 1.8 | 149 | 1.8 | 150 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 8280 | 479.9997 | 18.9657
SYL-E.1.RR.897.1 | 24541859152588 | Shahi Eidgah, Anamika R/A, H # 81/A, Mohibur Rahman | 2019-07-23 | MP1006 | 3.4 | 144 | 3.4 | 145 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7848 | 911.9997 | 35.824
SYL-E.1.RR.898.1 | 24541859152588 | Shahi Eidgah, Anamika R/A, H # 80/A, Abdur Rouf | 2019-07-23 | MP1006 | 19.1 | 148 | 19.1 | 149 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 7848 | 911.9997 | 201.2468
SYL-E.1.RR.899.1 | 24541739152596 | Shahi Eidgah, Anamika R/A, H # 74/A, Abdul Mohit Mogni | 2019-07-23 | MP1006 | 15.4 | 150 | 15.2 | 151 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7848 | 911.9997 | 160.1545
SYL-E.1.RR.900.1 | 24541699152592 | Shahi Eidgah, Anamika R/A, H # 73/5, Chaya Nir | 2019-07-23 | MP1006 | 9.3 | 152 | 9.3 | 153 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7848 | 911.9997 | 97.9893
SYL-E.1.RR.901.1 | 24535859153217 | Shibgong, Mojumdar Para, Monju mia | 2019-07-17 | NQ1003 | 8.3 | 14 | 8.3 | 15 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7824 | 935.9997 | 87.4528
SYL-E.1.RR.902.1 | 24542009153150 | Anamika, East Shahi Eidgah, Sorifa Khatun | 2019-07-18 | NQ1003 | 10.9 | 54 | 10.9 | 55 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7848 | 911.9997 | 114.8476
SYL-E.1.RR.903.1 | 24541969153150 | Anamika, East Shahi Eidgah, Akbar Hossain Baschu | 2019-07-18 | NQ1003 | 8.2 | 56 | 8.2 | 57 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7848 | 911.9997 | 86.3991
SYL-E.1.RR.903.2 | 24541969153150 | Anamika, East Shahi Eidgah, Akbar Hossain Baschu | 2019-07-18 | NQ1003 | 11.4 | 58 | 11.4 | 59 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7848 | 911.9997 | 120.1159
SYL-E.1.RR.904.1 | 24542039153148 | Anamika, East Shahi Eidgah, Abida Monjil | 2019-07-18 | NQ1003 | 10.8 | 60 | 10.8 | 61 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7848 | 911.9997 | 113.794
SYL-E.1.RR.905.1 | 24542069153155 | Anamika, East Shahi Eidgah, Mohammad Rahomot Ali | 2019-07-18 | NQ1003 | 3.6 | 62 | 3.6 | 63 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7848 | 911.9997 | 37.9313
SYL-E.1.RR.906.1 | 24542279153163 | Anamika, East Shahi Eidgah, Foyjun Villa | 2019-07-18 | NQ1003 | 8.5 | 67 | 8.5 | 68 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7848 | 911.9997 | 89.5601
SYL-E.1.RR.907.1 | 24542349153169 | Anamika, East Shahi Eidgah, Wahid Khan | 2019-07-18 | NQ1003 | 4.2 | 69 | 4.2 | 70 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7848 | 911.9997 | 44.2532
SYL-E.1.RR.908.1 | 24542409153166 | Anamika, East Shahi Eidgah, Joytun Villa | 2019-07-18 | NQ1003 | 7 | 71 | 7 | 72 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7848 | 911.9997 | 73.7554
SYL-E.1.RR.909.1 | 24542459153158 | Anamika, East Shahi Eidgah, TV Gate, Hosen Monjil | 2019-07-18 | NQ1003 | 3.9 | 73 | 3.9 | 74 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7848 | 911.9997 | 41.0923
SYL-E.1.RR.910.1 | 24542469153145 | Anamika, East Shahi Eidgah, TV Gate, Alhaz Kabir Ahmed | 2019-07-18 | NQ1003 | 4 | 75 | 4 | 76 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7848 | 911.9997 | 42.1459
SYL-E.1.RR.911.1 | 24542379153136 | Anamika, East Shahi Eidgah, TV Gate, Shahabuddin | 2019-07-18 | NQ1003 | 6.4 | 77 | 6.4 | 78 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7848 | 911.9997 | 67.4335
SYL-E.1.RR.912.1 | 24542409153124 | Anamika, East Shahi Eidgah, Taz Vabon | 2019-07-18 | NQ1003 | 9.9 | 79 | 9.9 | 80 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7848 | 911.9997 | 104.3112
SYL-E.1.RR.913.1 | 24542329153125 | Anamika, East Shahi Eidgah, M.F.H. Chowdhury, H # 25/1A | 2019-07-18 | NQ1003 | 8.8 | 81 | 8.8 | 82 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7848 | 911.9997 | 92.721
SYL-E.1.RR.914.1 | 24542329153125 | Anamika, East Shahi Eidgah, Anamika R/A, Ambience | 2019-07-18 | NQ1003 | 11.1 | 83 | 11.1 | 84 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7848 | 911.9997 | 116.9549
SYL-E.1.RR.915.1 | 24542329153125 | Anamika, East Shahi Eidgah, Anamika R/A, Hosain Ahmed | 2019-07-18 | NQ1003 | 2.9 | 85 | 2.9 | 86 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7848 | 911.9997 | 30.5558
SYL-E.1.RR.916.1 | 24534819152510 | Mira Bazar, Moushumi Residential Area, H # 29 | 2019-07-22 | NQ1003 | 13.4 | 137 | 13.4 | 138 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 8136 | 623.9997 | 141.1888
SYL-E.1.RR.917.1 | 24534819152519 | Mira Bazar, Moushumi Residential Area, H # 28 | 2019-07-22 | NQ1003 | 5.2 | 139 | 5.2 | 140 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 8136 | 623.9997 | 54.7897
SYL-E.1.RR.918.1 | 24534539152523 | Mira Bazar, Moushumi Residential Area, H # 19 | 2019-07-22 | NQ1003 | 4.3 | 141 | 4.3 | 142 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 8136 | 623.9997 | 45.3069
SYL-E.1.RR.919.1 | 24535199152458 | Kumarpara, Block - B, H # 43 | 2019-07-22 | NQ1003 | 11.7 | 143 | 11.7 | 144 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8136 | 623.9997 | 123.2768
SYL-E.1.RR.920.1 | 24535179152445 | Kumarpara, Block - B, H # 46 | 2019-07-22 | NQ1003 | 16.7 | 145 | 16.7 | 146 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 8136 | 623.9997 | 175.9592
SYL-E.1.RR.921.1 | 24535569152455 | Kumarpara, Block - A, Barobari, H # 55/A | 2019-07-22 | NQ1003 | 9.2 | 147 | 9.2 | 148 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8136 | 623.9997 | 96.9356
SYL-E.1.RR.922.1 | 24535569152455 | Kumarpara, Block - A, Barobari, H # 55/A | 2019-07-22 | NQ1003 | 10.7 | 150 | 10.7 | 151 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8136 | 623.9997 | 112.7403
SYL-E.1.RR.923.1 | 24540039152486 | Kumarpara, Block - C, Banyan British School, H # 66/1 | 2019-07-22 | NQ1003 | 4.9 | 152 | 4.9 | 153 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 8136 | 623.9997 | 51.6288
SYL-E.1.RR.924.1 | 24540039152486 | Kumarpara, Block - C, Banyan British School, H # 67 | 2019-07-22 | NQ1003 | 6.2 | 154 | 6.2 | 155 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8136 | 623.9997 | 65.3262
SYL-E.1.RR.926.1 | 24534139153039 | Kharpara, East Mira Bazar, H # 76, Masud Mia | 2019-07-23 | NQ1003 | 12.2 | 173 | 12.2 | 174 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7512 | 1247.9997 | 128.5451
SYL-E.1.RR.927.1 | 24534129153066 | Kharpara, East Mira Bazar, Rasos Residential Area, H # 3 | 2019-07-23 | NQ1003 | 7.4 | 175 | 7.4 | 176 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7512 | 1247.9997 | 77.97
SYL-E.1.RR.928.1 | 24534309153069 | Kharpara, East Mira Bazar, Tamabil Road, Tahera Bakkor | 2019-07-23 | NQ1003 | 2.3 | 177 | 2.3 | 178 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7512 | 1247.9997 | 24.2339
SYL-E.1.RR.929.1 | 24533959153069 | Raynagar, Sonarpara, East Mira Bazar, Al-Mamun Villa, H # 7 | 2019-07-23 | NQ1003 | 3.2 | 179 | 3.2 | 180 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7512 | 1247.9997 | 33.7167
SYL-E.1.RR.930.1 | 24533749153081 | Raynagar, Sonarpara, Hazi Ekram Monjil, H # 15 | 2019-07-23 | NQ1003 | 7.8 | 181 | 7.8 | 182 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7512 | 1247.9997 | 82.1846
SYL-E.1.RR.931.1 | 24534089153191 | Raynagar, Sonarpara, H # Urmi-20 | 2019-07-23 | NQ1003 | 21.1 | 183 | 20.3 | 184 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 20.3 | 20.3 | 1.218 | 1.218 | 0.0007168 | 100% | 0% | 1.218 | 1.218 | 0.0011869 | 28 | 0.024417 | 0.024417 |  | 0 | 0 | 7584 | 1175.9997 | 213.8906
SYL-E.1.RR.932.1 | 24533949153218 | Shibgonj, Sonarpara, Siramshi Villa, H # Urmi-35 | 2019-07-23 | NQ1003 | 4.4 | 185 | 4.4 | 186 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7584 | 1175.9997 | 46.3605
SYL-E.1.RR.933.1 | 24533889153226 | Shibgonj, Sonarpara, Ahad Villa, H # Urmi-36 | 2019-07-23 | NQ1003 | 11.8 | 187 | 11.8 | 188 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7584 | 1175.9997 | 124.3305
SYL-E.1.RR.934.1 | 24533939153204 | Shibgonj, Sonarpara, Mobarak Villa, H # Urmi-31/A | 2019-07-23 | NQ1003 | 6.6 | 189 | 6.6 | 190 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 3360 | 0 | 4224 | 1175.9997 | 42.8676
SYL-E.1.RR.935.1 | 24533439153262 | Shibgonj, Sonarpara, Nabarun, H # 74 | 2019-07-23 | NQ1003 | 11 | 191 | 11 | 192 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7584 | 1175.9997 | 115.9013
SYL-E.1.RR.936.1 | 24533119153263 | Shibgonj, Sonarpara, Nabarun, H # 54/3 | 2019-07-23 | NQ1003 | 10.4 | 193 | 10.4 | 194 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7584 | 1175.9997 | 109.5794
SYL-E.1.RR.937.1 | 24533039153269 | Shibgonj, Sonarpara, Nabarun, H # 53 | 2019-07-23 | NQ1003 | 5.1 | 195 | 5 | 196 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7584 | 1175.9997 | 52.6824
SYL-E.1.RR.938.1 | 24560249158354 | Boteshwar, Jalalabad Cantonment, Goilapara, Jahangir | 2019-07-25 | NQ1009 | 10.9 | 224 | 10.4 | 225 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7800 | 959.9997 | 109.5794
SYL-E.1.RR.939.1 | 24560399158358 | Boteshwar, Jalalabad Cantonment, Goilapara, Hazi Abdur Monsur | 2019-07-25 | NQ1009 | 4.3 | 226 | 4.3 | 227 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7800 | 959.9997 | 45.3069
SYL-E.1.RR.940.1 | 24560499158381 | Boteshwar, Jalalabad Cantonment, Goilapara, Nurul Amin | 2019-07-25 | NQ1009 | 11 | 228 | 11 | 229 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7800 | 959.9997 | 115.9013
SYL-E.1.RR.941.1 | 24560479158390 | Boteshwar, Jalalabad Cantonment, Goilapara, Jahangir Alam | 2019-07-25 | NQ1009 | 13.9 | 230 | 13.9 | 231 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7800 | 959.9997 | 146.4571
SYL-E.1.RR.942.1 | 24560709158354 | Boteshwar, Jalalabad Cantonment, Molaitila, Ataur Rahman | 2019-07-25 | NQ1009 | 8.5 | 232 | 8.5 | 233 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7800 | 959.9997 | 89.5601
SYL-E.1.RR.943.1 | 24561099158359 | Boteshwar, Jalalabad Cantonment, Molaitila, Shahin Mia | 2019-07-25 | NQ1009 | 13.2 | 234 | 12.8 | 235 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7800 | 959.9997 | 134.867
SYL-E.1.RR.944.1 | 24561319158304 | Boteshwar, Jalalabad Cantonment, Molaitila, Md. Sadullah | 2019-07-25 | NQ1009 | 11.1 | 236 | 11.2 | 237 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7800 | 959.9997 | 118.0086
SYL-E.1.RR.945.1 | 24561479158304 | Boteshwar, Jalalabad Cantonment, Molaitila, Tayeb Ali | 2019-07-25 | NQ1009 | 6.5 | 238 | 6.5 | 239 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7800 | 959.9997 | 68.4871
SYL-E.1.RR.946.1 | 24561639158321 | Boteshwar, Jalalabad Cantonment, Molaitila, Nazrul Islam | 2019-07-25 | NQ1009 | 32.2 | 240 | 32.2 | 241 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 32.2 | 32.2 | 1.932 | 1.932 | 0.0007168 | 100% | 0% | 1.932 | 1.932 | 0.0011869 | 28 | 0.03873 | 0.03873 |  | 0 | 0 | 7800 | 959.9997 | 339.2747
SYL-E.1.RR.947.1 | 24561479158266 | Boteshwar, Jalalabad Cantonment, Molaitila, Rob Dulal | 2019-07-25 | NQ1009 | 10.8 | 242 | 10.5 | 243 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7800 | 959.9997 | 110.6331
SYL-E.1.RR.947.2 | 24561479158266 | Boteshwar, Jalalabad Cantonment, Molaitila, Rob Dulal | 2021-02-25 | MN1018 | 11.8 | 173 | 11.8 | 174 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7800 | 959.9997 | 124.3305
SYL-E.1.RR.948.1 | 24561709158266 | Boteshwar, Jalalabad Cantonment, Molaitila, Bosir Ali | 2019-07-25 | NQ1009 | 15.6 | 244 | 15.6 | 245 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7800 | 959.9997 | 164.3691
SYL-E.1.RR.949.1 | 24561579158221 | Boteshwar, Jalalabad Cantonment, Molaitila, Gauch | 2019-07-25 | NQ1009 | 4.7 | 246 | 4.7 | 247 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7800 | 959.9997 | 49.5215
SYL-E.1.RR.950.1 | 24561569158183 | Boteshwar, Jalalabad Cantonment, Molaitila, Tofajjal Hosen | 2019-07-25 | NQ1009 | 5.1 | 248 | 5.1 | 249 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7800 | 959.9997 | 53.7361
SYL-E.1.RR.951.1 | 24535799153380 | Shibgonj, Senpara, Pushpayan, H # 98, Raj Mahal | 2019-07-16 | NQ1003 | 11 | 312 | 11 | 313 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7752 | 1007.9997 | 115.9013
SYL-E.1.RR.952.1 | 24535839153367 | Shibgonj, Senpara, Alpona, H # 94/A, Orun Shingho | 2019-07-16 | NQ1003 | 17.5 | 314 | 17.5 | 315 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 7752 | 1007.9997 | 184.3884
SYL-E.1.RR.953.1 | 24535849153360 | Shibgonj, Senpara, Alpona, H # 91, Khonica | 2019-07-16 | NQ1003 | 6.6 | 316 | 6.6 | 317 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7752 | 1007.9997 | 69.5408
SYL-E.1.RR.954.1 | 24535849153360 | Shibgonj, Senpara, Alpona, H # 90, Rothindra Kumar Das | 2019-07-16 | NQ1003 | 10.5 | 318 | 10.5 | 319 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7752 | 1007.9997 | 110.6331
SYL-E.1.RR.955.1 | 24535849153360 | Shibgonj, Senpara, Alpona, H # 97/2, Promod Kunja | 2019-07-16 | NQ1003 | 10.1 | 320 | 10.1 | 321 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7752 | 1007.9997 | 106.4185
SYL-E.1.RR.956.1 | 24535639153345 | Shibgonj, Senpara, Alpona, H # 98, Dilip Kumar Shingho | 2019-07-16 | NQ1003 | 11 | 322 | 11 | 323 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7752 | 1007.9997 | 115.9013
SYL-E.1.RR.957.1 | 24535879153423 | Shibgonj, Senpara, Alpona, H # 34, Regar Sultan | 2019-07-16 | NQ1003 | 10 | 324 | 10 | 325 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7752 | 1007.9997 | 105.3648
SYL-E.1.RR.958.1 | 24540089153442 | Shibgonj, Senpara, Alpona, H # 37, Hazi Monjil | 2019-07-16 | NQ1003 | 3.5 | 330 | 3.5 | 331 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7752 | 1007.9997 | 36.8777
SYL-E.1.RR.959.1 | 24540809153395 | Shibgonj, South Baluchar, Pushpayan, H # 127, Syeda Khatun | 2019-07-16 | NQ1003 | 8.2 | 332 | 8.2 | 333 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7752 | 1007.9997 | 86.3991
SYL-E.1.RR.960.1 | 24535039153042 | Raynagar, Aagpara, Shebok R/A, H # 44, Shamoyik | 2019-07-17 | NQ1003 | 21 | 16 | 21 | 17 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 21 | 21 | 1.26 | 1.26 | 0.0007168 | 100% | 0% | 1.26 | 1.26 | 0.0011869 | 28 | 0.025259 | 0.025259 |  | 0 | 0 | 8136 | 623.9997 | 221.2661
SYL-E.1.RR.961.1 | 24535039153042 | Raynagar, Aagpara, Shebok R/A, H # 46, Mohammad Mohibuddin | 2019-07-17 | NQ1003 | 10.7 | 18 | 10.7 | 19 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8136 | 623.9997 | 112.7403
SYL-E.1.RR.962.1 | 24535199153047 | Raynagar, Aagpara, Shebok R/A, H # 51, Aditto Villa | 2019-07-17 | NQ1003 | 6 | 20 | 6 | 21 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 8136 | 623.9997 | 63.2189
SYL-E.1.RR.963.1 | 24535339153049 | Raynagar, Aagpara, Shebok R/A, H # 53, Md. Ataur Rahman | 2019-07-17 | NQ1003 | 4.5 | 22 | 4.5 | 23 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 8136 | 623.9997 | 47.4142
SYL-E.1.RR.964.1 | 24535239153062 | Raynagar, Aagpara, Shebok R/A, H # 58, Belal Ahmed | 2019-07-17 | NQ1003 | 10.7 | 24 | 10.4 | 25 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8136 | 623.9997 | 109.5794
SYL-E.1.RR.965.1 | 24535239153062 | Raynagar, Aagpara, Shebok R/A, H # 58/A, Engineer Cottage | 2019-07-17 | NQ1003 | 9.8 | 26 | 9.8 | 27 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8136 | 623.9997 | 103.2575
SYL-E.1.RR.966.1 | 24534859153106 | Raynagar, Dorgipara, Sourav, H # 2/D, Jamal Uddin | 2019-07-17 | NQ1003 | 9.5 | 28 | 9.7 | 29 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7824 | 935.9997 | 102.2039
SYL-E.1.RR.967.1 | 24534859153106 | Raynagar, Dorgipara, Sourav, H # 2/D, Jamal Uddin | 2019-07-17 | NQ1003 | 4.5 | 30 | 4.5 | 31 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7824 | 935.9997 | 47.4142
SYL-E.1.RR.968.1 | 24535139153089 | Raynagar, Dadapir Road, Shebok R/A, H # 91 | 2019-07-17 | NQ1003 | 3.8 | 32 | 3.8 | 33 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7824 | 935.9997 | 40.0386
SYL-E.1.RR.969.1 | 24540189153082 | Raynagar,Prottoy R/A, H # 60, Suprova Das | 2019-07-18 | NQ1003 | 8 | 34 | 7.9 | 35 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7824 | 935.9997 | 83.2382
SYL-E.1.RR.970.1 | 24540339153129 | Raynagar, Bashundhara, H # 5, Nurun Nesa Begum | 2019-07-18 | NQ1003 | 10.3 | 36 | 10.3 | 37 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7824 | 935.9997 | 108.5258
SYL-E.1.RR.971.1 | 24540329153141 | Raynagar, Bashundhara, H # 5, Nuru Mia | 2019-07-18 | NQ1003 | 4.3 | 38 | 4.3 | 39 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7824 | 935.9997 | 45.3069
SYL-E.1.RR.972.1 | 24541009153117 | Raynagar, Raj Bari, Bashundhara, H # 62, Dipa Villa | 2019-07-18 | NQ1003 | 2.1 | 40 | 2.1 | 41 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7848 | 911.9997 | 22.1266
SYL-E.1.RR.973.1 | 24541479153148 | Raynagar, Raj Bari, Mitali R/A, Lane-1, H # 37, Sultana Begum | 2019-07-18 | NQ1003 | 11.8 | 42 | 11.5 | 43 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7848 | 911.9997 | 121.1695
SYL-E.1.RR.974.1 | 24541699153146 | Raynagar, Raj Bari, Mitali R/A, Lane-1, H # 41, Alhaj Furkan Ali | 2019-07-18 | NQ1003 | 9.5 | 44 | 9.6 | 45 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7848 | 911.9997 | 101.1502
SYL-E.1.RR.975.1 | 24541579153147 | Raynagar, Raj Bari, Mitali R/A, Lane-1, H # 44, Mayer Kol | 2019-07-18 | NQ1003 | 6.5 | 46 | 6.5 | 47 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7848 | 911.9997 | 68.4871
SYL-E.1.RR.976.1 | 24541759153146 | Raynagar, Raj Bari, Mitali R/A, Lane-1, H # 45 | 2019-07-18 | NQ1003 | 10.8 | 48 | 10.8 | 49 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7848 | 911.9997 | 113.794
SYL-E.1.RR.977.1 | 24541779153138 | Raynagar, Raj Bari, Mitali R/A, Lane-1, H # 45/B, Shahjahan Ahmed | 2019-07-18 | NQ1003 | 10.5 | 50 | 10.5 | 51 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7848 | 911.9997 | 110.6331
SYL-E.1.RR.978.1 | 24541829153146 | Raynagar, Raj Bari, Mitali R/A, Lane-1, H # 49, Hajera Monjil | 2019-07-18 | NQ1003 | 12.9 | 52 | 12.9 | 53 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7848 | 911.9997 | 135.9206
SYL-E.1.RR.979.1 | 24541229153070 | Raynagar, Raj Bari, Bashundhara, H # 36/2 | 2019-07-20 | NQ1003 | 7.3 | 87 | 7.3 | 88 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7848 | 911.9997 | 76.9163
SYL-E.1.RR.980.1 | 24541229153070 | Raynagar, Raj Bari, Bashundhara, H # 36/6 | 2019-07-20 | NQ1003 | 16.5 | 89 | 16.5 | 90 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 7848 | 911.9997 | 173.8519
SYL-E.1.RR.981.1 | 24541229153070 | Raynagar, Raj Bari, Bashundhara, H # 36/7, Md. Abdul Motin | 2019-07-20 | NQ1003 | 3.4 | 91 | 3.4 | 92 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7848 | 911.9997 | 35.824
SYL-E.1.RR.982.1 | 24541319153054 | Raynagar, Brojnath Tila, Cosba House, Shobuj, H # 16, Shofiku Nesa Tower-1 | 2019-07-20 | NQ1003 | 8.7 | 93 | 8.7 | 94 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7848 | 911.9997 | 91.6674
SYL-E.1.RR.983.1 | 24541319153054 | Raynagar, Brojnath Tila, Bashundhara, H # 37/8, Mizanur Rahman Chowdhury | 2019-07-20 | NQ1003 | 12.6 | 95 | 12.6 | 96 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7848 | 911.9997 | 132.7597
SYL-E.1.RR.984.1 | 24541319153054 | Raynagar, Brojnath Tila, Bashundhara, H # 37/7, Shorafot House | 2019-07-20 | NQ1003 | 5.2 | 97 | 5.2 | 98 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7848 | 911.9997 | 54.7897
SYL-E.1.RR.985.1 | 24541519153075 | Raynagar, Raj Bari, Shobuj, H # 19/A, Kakordia | 2019-07-20 | NQ1003 | 7.5 | 99 | 7.5 | 100 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7848 | 911.9997 | 79.0236
SYL-E.1.RR.986.1 | 24541609153065 | Raynagar, Raj Bari, Raj Bari Road, Beside Aabhawa Office, Cristal High Tower | 2019-07-20 | NQ1003 | 6.4 | 101 | 6.4 | 102 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7848 | 911.9997 | 67.4335
SYL-E.1.RR.987.1 | 24541609153065 | Raynagar, Raj Bari, Raj Bari Road, Beside Aabhawa Office, Cristal High Tower | 2019-07-20 | NQ1003 | 12.3 | 103 | 12.3 | 104 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7848 | 911.9997 | 129.5987
SYL-E.1.RR.988.1 | 24541609153065 | Raynagar, Raj Bari, Shobuj, H # 17 | 2019-07-20 | NQ1003 | 4.3 | 105 | 4.3 | 106 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7848 | 911.9997 | 45.3069
SYL-E.1.RR.989.1 | 24541299153031 | Raynagar, Sunatula Jhornarpar, Shobuj, H # 24/1, Towhid Ali Kotage | 2019-07-20 | NQ1003 | 26.7 | 107 | 26.7 | 108 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 26.7 | 26.7 | 1.602 | 1.602 | 0.0007168 | 100% | 0% | 1.602 | 1.602 | 0.0011869 | 28 | 0.032115 | 0.032115 |  | 0 | 0 | 7848 | 911.9997 | 281.324
SYL-E.1.RR.990.1 | 24541319153013 | Raynagar, Sunatula Jhornarpar, Shobuj, H # 22, Kaiub Mia | 2019-07-20 | NQ1003 | 3.8 | 111 | 3.8 | 112 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7848 | 911.9997 | 40.0386
SYL-E.1.RR.990.2 | 24541319153013 | Raynagar, Sunatula Jhornarpar, Shobuj, H # 22, Kaiub Mia | 2022-11-24 | NQ1007 | 7.1 | 206 | 7.1 | 207 | 2022-11-24 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 0 | 911.9997 | 7.7883
SYL-E.1.RR.991.1 | 24541319153016 | Raynagar, Sunatula Jhornarpar, Shobuj, H # 42 | 2019-07-20 | NQ1003 | 11.3 | 113 | 11.3 | 114 | 2022-01-01 | 2022-11-24 | NQ1007 | 1.2 | 203 | 1.2 | 204 | 2022-11-24 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7848 | 911.9997
SYL-E.1.RR.992.1 | 24541419153019 | Raynagar, Sunatula, Shobuj, H # 12 | 2019-07-20 | NQ1003 | 5.2 | 115 | 5.2 | 116 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7848 | 911.9997 | 54.7897
SYL-E.1.RR.993.1 | 24541419153019 | Raynagar, Sunatula, Shobuj, H # 10 | 2019-07-20 | NQ1003 | 2.4 | 117 | 2.5 | 118 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7848 | 911.9997 | 26.3412
SYL-E.1.RR.994.1 | 24541379153009 | Raynagar, Sunatula, Shobuj, H # 10/1 | 2019-07-20 | NQ1003 | 8.5 | 119 | 8.5 | 120 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7848 | 911.9997 | 89.5601
SYL-E.1.RR.995.1 | 24541439153021 | Raynagar, Sunatula, Shobuj, H # 13 | 2019-07-20 | NQ1003 | 7.1 | 121 | 7.1 | 122 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7848 | 911.9997 | 74.809
SYL-E.1.RR.996.1 | 24535389152515 | Jherjheripara, Evergreen R/A, H # 1 | 2019-07-21 | NQ1003 | 14.8 | 123 | 14.8 | 124 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 8136 | 623.9997 | 155.9399
SYL-E.1.RR.997.1 | 24535219152515 | Bhaiarpara, Mousumi R/A, H # 38 | 2019-07-21 | NQ1003 | 11.2 | 125 | 11.2 | 126 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8136 | 623.9997 | 118.0086
SYL-E.1.RR.998.1 | 24534749152503 | Bhaiarpara, Mousumi R/A, H # 58/A, Iqbal Hossen | 2019-07-21 | NQ1003 | 8.4 | 127 | 8.4 | 128 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8136 | 623.9997 | 88.5064
SYL-E.1.RR.999.1 | 24534639152506 | Bhaiarpara, Mousumi R/A, H # 57/A, Shopon Kumar Dey | 2019-07-21 | NQ1003 | 14.2 | 129 | 14.2 | 130 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 8136 | 623.9997 | 149.618
SYL-E.1.RR.1000.1 | 24534889152484 | Bhaiarpara, Mousumi R/A, H # 41/1 | 2019-07-21 | NQ1003 | 6.5 | 131 | 6.9 | 132 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 8136 | 623.9997 | 72.7017
SYL-E.1.RR.1001.1 | 24535339153391 | Shibgonj, Lakhri Para, Rezaul Karim | 2019-07-16 | NQ1009 | 6.4 | 399 | 6.4 | 400 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7752 | 1007.9997 | 67.4335
SYL-E.1.RR.1002.1 | 24535179153322 | Shibgonj, Monipuripara, Lokkhi Debi | 2019-07-17 | NQ1009 | 11.5 | 1 | 11.5 | 2 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7752 | 1007.9997 | 121.1695
SYL-E.1.RR.1003.1 | 24534989153299 | Shibgonj, Monipuripara, Nilmoni Singha | 2019-07-17 | NQ1009 | 5.1 | 3 | 5.1 | 4 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7752 | 1007.9997 | 53.7361
SYL-E.1.RR.1004.1 | 24534989153299 | Shibgonj, Monipuripara, Kamesshor Singha | 2019-07-17 | NQ1009 | 10.6 | 5 | 10.6 | 6 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7752 | 1007.9997 | 111.6867
SYL-E.1.RR.1005.1 | 24534929153309 | Shibgonj, Monipuripara, Nazrul Islam, H# 13/1/A | 2019-07-17 | NQ1009 | 9.1 | 7 | 9.1 | 8 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7752 | 1007.9997 | 95.882
SYL-E.1.RR.1006.1 | 24534909153312 | Shibgonj, Adittapara, Rafiq Uddin, H# 13/10 | 2019-07-17 | NQ1009 | 11.7 | 9 | 11.7 | 10 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7752 | 1007.9997 | 123.2768
SYL-E.1.RR.1007.1 | 24534949153295 | Shibgonj, Adittapara, Nagar Villa, Masuk Mia, H# 13/1-B | 2019-07-17 | NQ1009 | 18.5 | 11 | 18.6 | 12 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 7752 | 1007.9997 | 195.9786
SYL-E.1.RR.1008.1 | 24534909153282 | Shibgonj, Adittapara, Rose Wood Villa, Mogfur Hossain, H# 13/5 | 2019-07-17 | NQ1009 | 9 | 13 | 8.5 | 14 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7752 | 1007.9997 | 89.5601
SYL-E.1.RR.1009.1 | 24534809153304 | Shibgonj, Adittapara, Sonchita Niketon, Dr. Pankaj Pal, H# 12/2 | 2019-07-17 | NQ1009 | 8.5 | 15 | 8.8 | 16 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7752 | 1007.9997 | 92.721
SYL-E.1.RR.1010.1 | 24534689153329 | Shibgonj, Lakripara, beside of Shakil Community Centre, Foyez Ahmed | 2019-07-17 | NQ1009 | 10.3 | 17 | 10.3 | 18 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7752 | 1007.9997 | 108.5258
SYL-E.1.RR.1010.2 | 24534689153329 | Shibgonj, Lakripara, beside of Shakil Community Centre, Foyez Ahmed | 2021-02-18 | MN1018 | 10.4 | 144 | 10.4 | 145 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7752 | 1007.9997 | 109.5794
SYL-E.1.RR.1011.1 | 24535009153348 | Shibgonj, Lakripara, Ali Dowlat Dahar, H# 46 | 2019-07-17 | NQ1009 | 3.9 | 19 | 3.9 | 20 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7752 | 1007.9997 | 41.0923
SYL-E.1.RR.1012.1 | 24534619153361 | Shibgonj, Lakripara, Advocate Mohammad Ali | 2019-07-17 | NQ1009 | 9.1 | 21 | 9.1 | 22 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7752 | 1007.9997 | 95.882
SYL-E.1.RR.1013.1 | 24535339153178 | Raynagar, Dorjipara, Masjid Road, Milkis Rehana | 2019-07-18 | NQ1009 | 16.2 | 51 | 16.2 | 52 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 7824 | 935.9997 | 170.691
SYL-E.1.RR.1014.1 | 24535389153161 | Raynagar, Dorjipara, Masjid Road, Mamunur Rashid | 2019-07-18 | NQ1009 | 11.4 | 53 | 11.5 | 54 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7824 | 935.9997 | 121.1695
SYL-E.1.RR.1015.1 | 24535439153165 | Raynagar, Dorjipara, Masjid Road, H# 67/B | 2019-07-18 | NQ1009 | 11.9 | 55 | 11.9 | 56 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7824 | 935.9997 | 125.3841
SYL-E.1.RR.1016.1 | 24535439153165 | Raynagar, Dorjipara, Masjid Road, H# 68 | 2019-07-18 | NQ1009 | 8.7 | 57 | 8.7 | 58 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7824 | 935.9997 | 91.6674
SYL-E.1.RR.1017.1 | 24535599153158 | Raynagor, Dorjipara R/A, Rafiq, H# 112 | 2019-07-18 | NQ1009 | 16.9 | 59 | 16.9 | 60 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 7824 | 935.9997 | 178.0665
SYL-E.1.RR.1018.1 | 24540039153158 | Raynagar, Daptoripara R/A, Maa Bhaban, Prottoy 89/A | 2019-07-18 | NQ1009 | 24.5 | 61 | 24.5 | 62 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 7824 | 935.9997 | 258.1438
SYL-E.1.RR.1019.1 | 24540019153160 | Raynagar, Daptoripara R/A, Ruhani Villa, H# 93 | 2019-07-18 | NQ1009 | 8.7 | 63 | 9.1 | 64 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7824 | 935.9997 | 95.882
SYL-E.1.RR.1020.1 | 24535839153204 | Raynagar, Daptoripara R/A, Sayesta Khan, H# 102/E | 2019-07-18 | NQ1009 | 16 | 65 | 16 | 66 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 7824 | 935.9997 | 168.5837
SYL-E.1.RR.1021.1 | 24535879153104 | Raynagar, Daptoripara R/A, Alamtula, Forhad, Prottoy 44/B | 2019-07-18 | NQ1009 | 8.1 | 67 | 8.1 | 68 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7824 | 935.9997 | 85.3455
SYL-E.1.RR.1021.2 | 24535879153104 | Raynagar, Daptoripara R/A, Alamtula, Forhad, Prottoy 44/B | 2022-11-23 | NQ1007 | 9.6 | 191 | 9.6 | 192 | 2022-11-23 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 0 | 935.9997 | 10.8078
SYL-E.1.RR.1022.1 | 24541149153100 | Raynagar, Rajbari, Bashundhara, Shamim mia | 2019-07-18 | NQ1009 | 24.8 | 69 | 24.9 | 70 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 24.9 | 24.9 | 1.494 | 1.494 | 0.0007168 | 100% | 0% | 1.494 | 1.494 | 0.0011869 | 28 | 0.02995 | 0.02995 |  | 0 | 0 | 7848 | 911.9997 | 262.3584
SYL-E.1.RR.1023.1 | 24540829153046 | Raynagar, Rajbari, Bashundhara, Renu Begum, H# 25/1 | 2019-07-18 | NQ1009 | 15.5 | 71 | 15.5 | 72 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 7848 | 911.9997 | 163.3155
SYL-E.1.RR.1024.1 | 24540829153046 | Raynagar, Rajbari, Bashundhara 24, Sujon Mia | 2019-07-18 | NQ1009 | 18.8 | 73 | 18.8 | 74 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 7848 | 911.9997 | 198.0858
SYL-E.1.RR.1025.1 | 24540079153036 | Jherjheripara, Evergreen-78-D, Mahmuda Khanom | 2019-07-18 | NQ1009 | 10.2 | 75 | 10.2 | 76 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7848 | 911.9997 | 107.4721
SYL-E.1.RR.1026.1 | 24540419152594 | Jherjheripara, Evergreen-68/B | 2019-07-18 | NQ1009 | 15.8 | 77 | 15.8 | 78 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7848 | 911.9997 | 166.4764
SYL-E.1.RR.1027.1 | 24540549152587 | Jherjheripara, Evergreen-65/a, Shahed | 2019-07-18 | NQ1009 | 11.1 | 79 | 10.4 | 80 | 2022-01-01 | [9 empty] | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0
SYL-E.1.RR.1028.1 | 24534639152563 | Moushumi R/A, Bilal, H# 77/C | 2019-07-22 | NQ1009 | 19.2 | 119 | 19.2 | 120 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 19.2 | 19.2 | 1.152 | 1.152 | 0.0007168 | 100% | 0% | 1.152 | 1.152 | 0.0011869 | 28 | 0.023094 | 0.023094 |  | 0 | 0 | 8136 | 623.9997 | 202.3004
SYL-E.1.RR.1029.1 | 24534619152564 | Moushumi R/A, Nur Monjil, H# 76 | 2019-07-22 | NQ1009 | 10.5 | 121 | 10.6 | 122 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8136 | 623.9997 | 111.6867
SYL-E.1.RR.1030.1 | 24534599152578 | Moushumi R/A, Shahin Ahmed, H# 77 | 2019-07-22 | NQ1009 | 11.1 | 124 | 11.2 | 125 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8136 | 623.9997 | 118.0086
SYL-E.1.RR.1030.2 | 24534599152578 | Moushumi R/A, Shahin Ahmed, H# 77 | 2022-06-14 | LU1001 | 2.4 | 203 | 2.4 | 204 | 2022-06-14 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 4200 | 623.9997 | 13.9255
SYL-E.1.RR.1031.1 | 24534989152585 | Mirabazar, Agpara, Moushumi R/A, Rashid Villa, H# 82 | 2019-07-22 | NQ1009 | 12.8 | 128 | 12.8 | 129 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8136 | 623.9997 | 134.867
SYL-E.1.RR.1032.1 | 24535049152593 | Mirabazar, Agpara, Moushumi R/A, Munir Hossain, H# 84 | 2019-07-22 | NQ1009 | 11.1 | 130 | 11.1 | 131 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8136 | 623.9997 | 116.9549
SYL-E.1.RR.1033.1 | 24535169152597 | Mirabazar, Agpara, Moushumi R/A, Hazera Monjil, H# 89 | 2019-07-22 | NQ1009 | 10.8 | 132 | 10.5 | 133 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8136 | 623.9997 | 110.6331
SYL-E.1.RR.1034.1 | 24535359153020 | Mirabazar, Agpara, Moushumi R/A, H# 117 | 2019-07-22 | NQ1009 | 10.2 | 134 | 9.6 | 135 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8136 | 623.9997 | 101.1502
SYL-E.1.RR.1035.1 | 24535359153020 | Mirabazar, Agpara, Moushumi R/A,Sitara Monjil, H# 118 | 2019-07-22 | NQ1009 | 11.5 | 136 | 11.5 | 137 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8136 | 623.9997 | 121.1695
SYL-E.1.RR.1036.1 | 24535359153030 | Mirabazar, Agpara, Moushumi R/A, Mujibur Rahman, H# 94/A | 2019-07-22 | NQ1009 | 14.9 | 138 | 14.9 | 139 | 2022-01-01 | 2022-12-06 | NQ1007 | 4 | 266 | 4 | 267 | 2022-12-06 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8136 | 623.9997
SYL-E.1.RR.1037.1 | 24541609152509 | South Shahi Eidgha, Kumarpara Road, Dhanshiri-5, Lipi Begum | 2019-07-22 | NQ1009 | 12.9 | 140 | 12.9 | 141 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7848 | 911.9997 | 135.9206
SYL-E.1.RR.1038.1 | 24541609152509 | South Shahi Eidgha, Kumarpara Road, Abdur Rahman | 2019-07-22 | NQ1009 | 13.7 | 142 | 13.7 | 143 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7848 | 911.9997 | 144.3498
SYL-E.1.RR.1039.1 | 24541529152516 | South Shahi Eidgha, Kumarpara Road, Zahanara Begum | 2019-07-22 | NQ1009 | 13.6 | 144 | 13.6 | 145 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7848 | 911.9997 | 143.2961
SYL-E.1.RR.1040.1 | 24541529152516 | South Shahi Eidgha, Kumarpara Road, Dilbahar | 2019-07-22 | NQ1009 | 12 | 146 | 11.9 | 147 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7848 | 911.9997 | 125.3841
SYL-E.1.RR.1041.1 | 24533739152528 | Mirabazar, Uddipon, H# 44 | 2019-07-23 | NQ1009 | 10.9 | 173 | 10.9 | 174 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7512 | 1247.9997 | 114.8476
SYL-E.1.RR.1042.1 | 24533639152535 | Mirabazar, Uddipon, Istaq Monjil, H# 31 | 2019-07-23 | NQ1009 | 9.4 | 175 | 9.4 | 176 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7512 | 1247.9997 | 99.0429
SYL-E.1.RR.1043.1 | 24533639152535 | Mirabazar, Uddipon, Istaq Monjil, H# 31 | 2019-07-23 | NQ1009 | 9.8 | 177 | 9.8 | 178 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7512 | 1247.9997 | 103.2575
SYL-E.1.RR.1044.1 | 24534189153124 | Raynagar, Sonarpara, Rasos, H# 31/A | 2019-07-23 | NQ1009 | 10.4 | 179 | 10.4 | 180 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7824 | 935.9997 | 109.5794
SYL-E.1.RR.1045.1 | 24534049153130 | Raynagar, Sonarpara, Rasos, H# 31, Abdur Rahman | 2019-07-23 | NQ1009 | 12.4 | 182 | 12.6 | 183 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7824 | 935.9997 | 132.7597
SYL-E.1.RR.1046.1 | 24534049153130 | Raynagar, Sonarpara, Rasos, H# 31/C, Fatema Begum | 2019-07-23 | NQ1009 | 11 | 184 | 10.6 | 185 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7824 | 935.9997 | 111.6867
SYL-E.1.RR.1047.1 | 24534299153140 | Raynagar, Sonarpara, Tamabil Road, Rafal, Bike Shop | 2019-07-23 | NQ1009 | 12 | 186 | 11.9 | 187 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7824 | 935.9997 | 125.3841
SYL-E.1.RR.1048.1 | 24534339153294 | Shibgonj, Tamabil Road, Islam Plaza, H# 101 | 2019-07-23 | NQ1009 | 9.7 | 188 | 9.7 | 189 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7752 | 1007.9997 | 102.2039
SYL-E.1.RR.1049.1 | 24534279153320 | Shibgonj, Tamabil Road, Beside Of Agrani Bank, Taher Ali | 2019-07-23 | NQ1009 | 9.7 | 190 | 9.7 | 191 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7752 | 1007.9997 | 102.2039
SYL-E.1.RR.1050.1 | 24534279153320 | Shibgonj, Tamabil Road, Beside Of Agrani Bank, Taher Ali | 2019-07-23 | NQ1009 | 7.9 | 192 | 7.9 | 193 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7752 | 1007.9997 | 83.2382
SYL-E.1.RR.1051.1 | 24540939153400 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Parijat | 2019-07-16 | NQ1009 | 21.5 | 401 | 21.5 | 402 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 21.5 | 21.5 | 1.29 | 1.29 | 0.0007168 | 100% | 0% | 1.29 | 1.29 | 0.0011869 | 28 | 0.02586 | 0.02586 |  | 0 | 0 | 7752 | 1007.9997 | 226.5343
SYL-E.1.RR.1052.1 | 24540949153388 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Haji Asudor Monzil | 2019-07-16 | NQ1009 | 13 | 403 | 13 | 404 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7752 | 1007.9997 | 136.9743
SYL-E.1.RR.1053.1 | 24540919153375 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Amir House | 2019-07-16 | NQ1009 | 10.1 | 405 | 10.1 | 406 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7752 | 1007.9997 | 106.4185
SYL-E.1.RR.1054.1 | 24541029153375 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Anando # 4 | 2019-07-16 | NQ1009 | 3.8 | 407 | 3.8 | 408 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7752 | 1007.9997 | 40.0386
SYL-E.1.RR.1055.1 | 24541019153369 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Ali Monjil | 2019-07-16 | NQ1009 | 20 | 409 | 20 | 410 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 7752 | 1007.9997 | 210.7296
SYL-E.1.RR.1056.1 | 24541009153369 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Hazi Abdul Jolil | 2019-07-16 | NQ1009 | 23.7 | 411 | 23.9 | 412 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 23.9 | 23.9 | 1.434 | 1.434 | 0.0007168 | 100% | 0% | 1.434 | 1.434 | 0.0011869 | 28 | 0.028747 | 0.028747 |  | 0 | 0 | 7752 | 1007.9997 | 251.8219
SYL-E.1.RR.1057.1 | 24540759153324 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Luthfullah | 2019-07-16 | NQ1009 | 15.6 | 413 | 15.6 | 414 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7752 | 1007.9997 | 164.3691
SYL-E.1.RR.1058.1 | 24541039153319 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, H # 39 | 2019-07-16 | NQ1009 | 15.5 | 415 | 15.5 | 416 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 7752 | 1007.9997 | 163.3155
SYL-E.1.RR.1059.1 | 24541069153328 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, H # 45 | 2019-07-16 | NQ1009 | 3.7 | 417 | 3.7 | 418 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7752 | 1007.9997 | 38.985
SYL-E.1.RR.1060.1 | 24535939153370 | Shah Paran, South Baluchar, Khoradipara, Khoradipara Road, Anando Block, Jasmin Begum | 2019-07-16 | NQ1009 | 4.7 | 419 | 4.7 | 420 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7752 | 1007.9997 | 49.5215
SYL-E.1.RR.1061.1 | 24534349153287 | Shahparan, Tamabil Road, Shibganj Bazar, House # 116 | 2019-07-17 | NQ1009 | 10 | 23 | 10 | 24 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7752 | 1007.9997 | 105.3648
SYL-E.1.RR.1062.1 | 24534419153203 | Shahparan, Tamabil Road, Shibganj, Sonapara, Madrashatul Hiqmah | 2019-07-17 | NQ1009 | 28.9 | 25 | 28.9 | 26 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 28.9 | 28.9 | 1.734 | 1.734 | 0.0007168 | 100% | 0% | 1.734 | 1.734 | 0.0011869 | 28 | 0.034761 | 0.034761 |  | 0 | 0 | 7824 | 935.9997 | 304.5043
SYL-E.1.RR.1063.1 | 24534439153196 | Shahparan, Tamabil Road, Shibganj, Sonapara, Ali House | 2019-07-17 | NQ1009 | 9.2 | 27 | 9.2 | 28 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7824 | 935.9997 | 96.9356
SYL-E.1.RR.1064.1 | 24534279153205 | Shahparan, Tamabil Road, Shibganj, Sonapara, Urmi 55 | 2019-07-17 | NQ1009 | 7.2 | 29 | 7.2 | 30 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7824 | 935.9997 | 75.8627
SYL-E.1.RR.1065.1 | 24534629153123 | Shahparan, Tamabil Road, Shibganj, Darjipara, Rasos/55 | 2019-07-17 | NQ1009 | 13.6 | 31 | 13.6 | 32 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7824 | 935.9997 | 143.2961
SYL-E.1.RR.1066.1 | 24534699153106 | Shahparan, Tamabil Road, Shibganj, Darjipara, Surov, A/03 | 2019-07-17 | NQ1009 | 19.5 | 33 | 19.5 | 34 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 19.5 | 19.5 | 1.17 | 1.17 | 0.0007168 | 100% | 0% | 1.17 | 1.17 | 0.0011869 | 28 | 0.023454 | 0.023454 |  | 0 | 0 | 7824 | 935.9997 | 205.4614
SYL-E.1.RR.1067.1 | 24534699153106 | Shahparan, Tamabil Road, Shibganj, Darjipara, Surov, A/4 | 2019-07-17 | NQ1009 | 16.4 | 35 | 16.4 | 36 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 7824 | 935.9997 | 172.7983
SYL-E.1.RR.1068.1 | 24534659153090 | Shahparan, Tamabil Road, Shibganj, Darjipara, Surov, A/6 | 2019-07-17 | NQ1009 | 9.5 | 37 | 9.5 | 38 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7824 | 935.9997 | 100.0966
SYL-E.1.RR.1069.1 | 24534769153090 | Shahparan, Tamabil, Darjipara Road, Surov, A/8 | 2019-07-17 | NQ1009 | 8.7 | 39 | 8.7 | 40 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7824 | 935.9997 | 91.6674
SYL-E.1.RR.1070.1 | 24534879153122 | Shahparan, Tamabil, Darjipara Road, Surov, 03 | 2019-07-17 | NQ1009 | 5.1 | 41 | 5.1 | 42 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7824 | 935.9997 | 53.7361
SYL-E.1.RR.1072.1 | 24534739153163 | Shahparan, Tamabil, Darjipara Road, Surov, 19/3 | 2019-07-17 | NQ1009 | 13.5 | 45 | 14.1 | 46 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7824 | 935.9997 | 148.5644
SYL-E.1.RR.1073.1 | 24534879153181 | Shahparan, Tamabil, Darjipara Road, Surov, 29 | 2019-07-17 | NQ1009 | 10.2 | 47 | 10.2 | 48 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7824 | 935.9997 | 107.4721
SYL-E.1.RR.1074.1 | 24534879153181 | Shahparan, Tamabil, Darjipara Road, Surov/30 | 2019-07-17 | NQ1009 | 4.3 | 49 | 4.3 | 50 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7824 | 935.9997 | 45.3069
SYL-E.1.RR.1075.1 | 24540129152570 | Shahparan ,Jerjara Para ,Jerjara Para Road ,Samsur Nahar | 2019-07-20 | NQ1009 | 14.6 | 81 | 14.6 | 82 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 8136 | 623.9997 | 153.8326
SYL-E.1.RR.1076.1 | 24540159152563 | Shahparan ,Jerjara Para ,Jerjara Para Road ,House#38/A | 2019-07-20 | NQ1009 | 8.6 | 83 | 8.6 | 84 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7848 | 911.9997 | 90.6137
SYL-E.1.RR.1077.1 | 24540149152559 | Shahparan ,Jerjara Para ,Jerjara Para Road ,House#39 | 2019-07-20 | NQ1009 | 9.2 | 85 | 9.2 | 86 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7848 | 911.9997 | 96.9356
SYL-E.1.RR.1078.1 | 24540269152549 | Shahparan ,Jerjara Para ,Jerjara Para Road ,Nadim Hosan | 2019-07-20 | NQ1009 | 7 | 87 | 7.1 | 88 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7848 | 911.9997 | 74.809
SYL-E.1.RR.1079.1 | 24540209152543 | Shahparan ,Kummer Para Road ,Kummer Para ,House#38/A | 2019-07-20 | NQ1009 | 10.8 | 89 | 10.8 | 90 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7848 | 911.9997 | 113.794
SYL-E.1.RR.1080.1 | 24540299152532 | Shahparan ,Kummer Para Road ,Kummer Para ,House#56/5 | 2019-07-20 | NQ1009 | 9.1 | 91 | 9.1 | 92 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7848 | 911.9997 | 95.882
SYL-E.1.RR.1081.1 | 24540209152528 | Shahparan ,Kummer Para Road ,Kummer Para ,House#57/A | 2019-07-20 | NQ1009 | 11.5 | 93 | 11.5 | 94 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7848 | 911.9997 | 121.1695
SYL-E.1.RR.1082.1 | 24540399152514 | Shahparan ,Kummer Para Road ,Kumer Para ,House#54/C | 2019-07-20 | NQ1009 | 7.5 | 95 | 7.5 | 96 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7848 | 911.9997 | 79.0236
SYL-E.1.RR.1083.1 | 24540199152511 | Shahparan ,Kummer Para Road ,Kumer Para ,House#58/2-C | 2019-07-20 | NQ1009 | 10.5 | 97 | 10.5 | 98 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7848 | 911.9997 | 110.6331
SYL-E.1.RR.1084.1 | 24540199152511 | Shahparan ,Kummer Para Road ,Kummer Para ,House#58/1 | 2019-07-20 | NQ1009 | 11.4 | 99 | 11.4 | 100 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7848 | 911.9997 | 120.1159
SYL-E.1.RR.1085.1 | 24540019152582 | Shahparan ,Jerjara Para ,Jerjara Para Road ,House# 30 | 2019-07-20 | NQ1009 | 11 | 101 | 11 | 102 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8136 | 623.9997 | 115.9013
SYL-E.1.RR.1086.1 | 24535809152568 | Shahparan ,Jerjara Para ,Jerjara Para Road ,House# 22/B | 2019-07-20 | NQ1009 | 14.1 | 103 | 14.1 | 104 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 8136 | 623.9997 | 148.5644
SYL-E.1.RR.1087.1 | 24535809152518 | Shahparan ,Jerjara Para ,Jerjara Para Road ,House# 22/B | 2019-07-20 | NQ1009 | 8.2 | 105 | 8.2 | 106 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8136 | 623.9997 | 86.3991
SYL-E.1.RR.1088.1 | 24535519152522 | Sylhet Sodor, Kumarpara, Block-B, Kumarpara Road, H # 24 | 2019-07-21 | NQ1009 | 27.2 | 107 | 27.2 | 108 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 27.2 | 27.2 | 1.632 | 1.632 | 0.0007168 | 100% | 0% | 1.632 | 1.632 | 0.0011869 | 28 | 0.032716 | 0.032716 |  | 0 | 0 | 8136 | 623.9997 | 286.5923
SYL-E.1.RR.1089.1 | 24535739152497 | Sylhet Sodor, Kumarpara, Block-B, Kumarpara Road, H # 12 | 2019-07-21 | NQ1009 | 13.6 | 109 | 13.6 | 110 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 8136 | 623.9997 | 143.2961
SYL-E.1.RR.1090.1 | 24535679152500 | Sylhet Sodor, Kumarpara, Block-B, Kumarpara Road, H # 12/5 | 2019-07-21 | NQ1009 | 11.3 | 111 | 11.3 | 112 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8136 | 623.9997 | 119.0622
SYL-E.1.RR.1091.1 | 24534769152545 | Sylhet Sodor, Kumarpara, Block-B, Kumarpara Road, H # 61/A | 2019-07-21 | NQ1009 | 35.1 | 113 | 35.1 | 114 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 35.1 | 35.1 | 2.106 | 2.106 | 0.0007168 | 100% | 0% | 2.106 | 2.106 | 0.0011869 | 28 | 0.042218 | 0.042218 |  | 0 | 0 | 8136 | 623.9997 | 369.8305
SYL-E.1.RR.1092.1 | 24534909152563 | Sylhet Sodor, Mira Bazer, Agpara, Musomi, Block-G, H # 71/1 | 2019-07-21 | NQ1009 | 5.6 | 115 | 5.6 | 116 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 8136 | 623.9997 | 59.0043
SYL-E.1.RR.1093.1 | 24535089152552 | Sylhet Sodor, Mira Bazer, Agpara, Musomi, Block-G, H # 70/1 | 2019-07-21 | NQ1009 | 10.5 | 117 | 10.5 | 118 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8136 | 623.9997 | 110.6331
SYL-E.1.RR.1094.1 | 24533809152468 | Sylhet Sodor, Miara bazar Road, Uddipon R/A, Rd # 3, H # 85/15 | 2019-07-23 | NQ1009 | 5.9 | 148 | 5.9 | 149 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7512 | 1247.9997 | 62.1652
SYL-E.1.RR.1094.2 | 24533809152468 | Sylhet Sodor, Miara bazar Road, Uddipon R/A, Rd # 3, H # 85/15 | 2021-10-28 | LU1001 | 11.5 | 106 | 11.5 | 107 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7512 | 1247.9997 | 121.1695
SYL-E.1.RR.1095.1 | 24534029152489 | Sylhet Sodor, Miara bazar Road, Uddipon R/A, Rd # 3, H # 85/8 | 2019-07-23 | NQ1009 | 8.8 | 150 | 8.8 | 151 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7512 | 1247.9997 | 92.721
SYL-E.1.RR.1096.1 | 24534199152549 | Sylhet Sodor, Miara bazar Road, Uddipon R/A, Uddipon-1 | 2019-07-23 | NQ1009 | 12 | 152 | 12 | 153 | 2022-01-01 | [9 empty] | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0
SYL-E.1.RR.1097.1 | 24534149152566 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-17 | 2019-07-23 | NQ1009 | 6.5 | 154 | 6.5 | 155 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7512 | 1247.9997 | 68.4871
SYL-E.1.RR.1098.1 | 24534139152576 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-13 | 2019-07-23 | NQ1009 | 10.3 | 159 | 10.3 | 160 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7512 | 1247.9997 | 108.5258
SYL-E.1.RR.1098.2 | 24534139152576 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-13 | 2021-10-28 | LU1001 | 4.8 | 100 | 4.8 | 101 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7512 | 1247.9997 | 50.5751
SYL-E.1.RR.1099.1 | 24534889152484 | Bhaiarpara, Mousumi R/A, H # 39/B | 2019-07-21 | NQ1003 | 8.2 | 133 | 8.2 | 134 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8136 | 623.9997 | 86.3991
SYL-E.1.RR.1100.1 | 24534889152484 | Bhaiarpara, Mousumi R/A, H # 42 | 2019-07-21 | NQ1003 | 3.8 | 135 | 3.8 | 136 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8136 | 623.9997 | 40.0386
SYL-E.1.RR.1101.1 | 24555299158533 | Boteshhor, Chuwabohor, Md.Salim | 2019-07-25 | MP1006 | 17.5 | 227 | 17.5 | 228 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 17.5 | 17.5 | 1.05 | 1.05 | 0.0007168 | 100% | 0% | 1.05 | 1.05 | 0.0011869 | 28 | 0.021049 | 0.021049 |  | 0 | 0 | 7800 | 959.9997 | 184.3884
SYL-E.1.RR.1102.1 | 24555299158533 | Boteshhor, Chuwabohor, Abu Tahir | 2019-07-25 | MP1006 | 5.1 | 229 | 5.1 | 230 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7800 | 959.9997 | 53.7361
SYL-E.1.RR.1103.1 | 24555299158533 | Boteshhor, Chuwabohor, Ali Ahmed | 2019-07-25 | MP1006 | 7.5 | 231 | 7.5 | 232 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7800 | 959.9997 | 79.0236
SYL-E.1.RR.1104.1 | 24555299158533 | Boteshhor, Chuwabohor, Ali Ahmed | 2019-07-25 | MP1006 | 19.8 | 235 | 19.8 | 236 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 19.8 | 19.8 | 1.188 | 1.188 | 0.0007168 | 100% | 0% | 1.188 | 1.188 | 0.0011869 | 28 | 0.023815 | 0.023815 |  | 0 | 0 | 7800 | 959.9997 | 208.6223
SYL-E.1.RR.1105.1 | 24555299158533 | Boteshhor, Chuwabohor, Nurul Islam | 2019-07-25 | MP1006 | 20.4 | 241 | 20.4 | 242 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 20.4 | 20.4 | 1.224 | 1.224 | 0.0007168 | 100% | 0% | 1.224 | 1.224 | 0.0011869 | 28 | 0.024537 | 0.024537 |  | 0 | 0 | 7800 | 959.9997 | 214.9442
SYL-E.1.RR.1106.1 | 24555059158512 | Boteshhor, Chuwabohor, Amanuddin | 2019-07-25 | MP1006 | 2.3 | 243 | 2.3 | 244 | 2022-01-01 | [9 empty] | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0
SYL-E.1.RR.1107.1 | 24555079158499 | Boteshhor, Chuwabohor, Lais Ahmed | 2019-07-25 | MP1006 | 18.3 | 245 | 18.3 | 246 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 18.3 | 18.3 | 1.098 | 1.098 | 0.0007168 | 100% | 0% | 1.098 | 1.098 | 0.0011869 | 28 | 0.022011 | 0.022011 |  | 0 | 0 | 7800 | 959.9997 | 192.8176
SYL-E.1.RR.1108.1 | 24555079158499 | Boteshhor, Chuwabohor, Kamal | 2019-07-25 | MP1006 | 19.6 | 247 | 19.6 | 248 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 19.6 | 19.6 | 1.176 | 1.176 | 0.0007168 | 100% | 0% | 1.176 | 1.176 | 0.0011869 | 28 | 0.023575 | 0.023575 |  | 0 | 0 | 7800 | 959.9997 | 206.515
SYL-E.1.RR.1109.1 | 24592139202393 | Jointapur, West Bali para, Md.Muktar Ahmed | 2019-07-27 | MP1006 | 17.3 | 257 | 16.7 | 258 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 7776 | 983.9997 | 175.9592
SYL-E.1.RR.1109.2 | 24592139202393 | Jointapur, West Bali para, Md.Muktar Ahmed | 2019-07-27 | MP1006 | 6.5 | 261 | 6 | 262 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7776 | 983.9997 | 63.2189
SYL-E.1.RR.1110.1 | 24591569202386 | Jointapur, West Bali para, Md. Nurul Alom | 2019-07-27 | MP1006 | 3.7 | 263 | 3.7 | 264 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7776 | 983.9997 | 38.985
SYL-E.1.RR.1111.1 | 24591489202391 | Jointapur, West Bali para, Md. Mohibul Haq | 2019-07-27 | MP1006 | 17.2 | 265 | 16.6 | 266 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 7776 | 983.9997 | 174.9056
SYL-E.1.RR.1111.2 | 24591489202391 | Jointapur, West Bali para, Md. Mohibul Haq | 2021-11-11 | LU1001 | 7.7 | 143 | 7.7 | 144 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7776 | 983.9997 | 81.1309
SYL-E.1.RR.1112.1 | 24592019202484 | Jointapur, West Bali para, Md. Siddkur Rahman | 2019-07-27 | MP1006 | 14.6 | 267 | 14.6 | 268 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7776 | 983.9997 | 153.8326
SYL-E.1.RR.1113.1 | 24591679202524 | Jointapur, West Bali para, Tohid Ali | 2019-07-27 | MP1006 | 10.7 | 273 | 10.6 | 274 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7776 | 983.9997 | 111.6867
SYL-E.1.RR.1114.1 | 24543459156327 | Khadim Nagar, Kallagram, Md. Kutub Uddin | 2019-08-20 | NQ1003 | 10.9 | 98 | 10.9 | 99 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7632 | 1127.9997 | 114.8476
SYL-E.1.RR.1115.1 | 24543649156265 | Khadim Nagar, Kallagram, Lily Bagum | 2019-08-20 | NQ1003 | 12.3 | 100 | 11.9 | 101 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7632 | 1127.9997 | 125.3841
SYL-E.1.RR.1116.1 | 24543059156312 | Khadim Nagar, Kallagram, Bosir Uddin | 2019-08-20 | NQ1003 | 8.3 | 103 | 8.3 | 104 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 8280 | 479.9997 | 87.4528
SYL-E.1.RR.1117.1 | 24543059156312 | Khadim Nagar, Kallagram, Somir Uddin | 2019-08-20 | NQ1003 | 12.6 | 105 | 12.6 | 106 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 8280 | 479.9997 | 132.7597
SYL-E.1.RR.1118.1 | 24542839156343 | Khadim Nagar, Kallagram, Kodu Mia | 2019-08-20 | NQ1003 | 11.4 | 107 | 11.4 | 108 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7632 | 1127.9997 | 120.1159
SYL-E.1.RR.1119.1 | 24542619156354 | Khadim Nagar, Kallagram, Ali Ahamed | 2019-08-20 | NQ1003 | 17.2 | 109 | 17.2 | 110 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 7632 | 1127.9997 | 181.2275
SYL-E.1.RR.1120.1 | 24542619156354 | Khadim Nagar, Kallagram, Ali Ahamed | 2019-08-20 | NQ1003 | 12.5 | 111 | 12.5 | 112 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7632 | 1127.9997 | 131.706
SYL-E.1.RR.1121.1 | 24542309156343 | Khadim Nagar, Kallagram, Kodu Mia | 2019-08-20 | NQ1003 | 18.7 | 113 | 18.7 | 114 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 7632 | 1127.9997 | 197.0322
SYL-E.1.RR.1122.1 | 24541929156388 | Khadim Nagar, Kallagram, Kala mia | 2019-08-20 | NQ1003 | 14.5 | 115 | 14 | 116 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 7632 | 1127.9997 | 147.5107
SYL-E.1.RR.1123.1 | 24541599156464 | Khadim Nagar, Kallagram, Abdul Mannan | 2019-08-20 | NQ1003 | 2.6 | 117 | 2.6 | 118 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7632 | 1127.9997 | 27.3949
SYL-E.1.RR.1124.1 | 24542429156420 | Khadim Nagar, Kallagram, Mohiuddin | 2019-08-20 | NQ1003 | 23.4 | 119 | 23.4 | 120 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 23.4 | 23.4 | 1.404 | 1.404 | 0.0007168 | 100% | 0% | 1.404 | 1.404 | 0.0011869 | 28 | 0.028145 | 0.028145 |  | 0 | 0 | 7632 | 1127.9997 | 246.5537
SYL-E.1.RR.1125.1 | 24535159154419 | Islampur, Muslim Nagar, H # 2 | 2019-08-28 | MP1006 | 2.5 | 317 | 2.5 | 318 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7608 | 1151.9997 | 26.3412
SYL-E.1.RR.1126.1 | 24535159154419 | Islampur, Muslim Nagar, H # 2 | 2019-08-28 | MP1006 | 18.2 | 319 | 18.2 | 320 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 7608 | 1151.9997 | 191.764
SYL-E.1.RR.1127.1 | 24535159154419 | Islampur, Muslim Nagar, H # 2 | 2019-08-28 | MP1006 | 13.2 | 321 | 13 | 322 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7608 | 1151.9997 | 136.9743
SYL-E.1.RR.1128.1 | 24535069154395 | Islampur, Muslim Nagar, H # 26 | 2019-08-28 | MP1006 | 3.4 | 323 | 3.4 | 324 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7608 | 1151.9997 | 35.824
SYL-E.1.RR.1129.1 | 24535169154389 | Islampur, Muslim Nagar, Gofur Monjil | 2019-08-28 | MP1006 | 4 | 325 | 3.9 | 326 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7608 | 1151.9997 | 41.0923
SYL-E.1.RR.1130.1 | 24535129154379 | Islampur, Muslim Nagar, H # 23/A | 2019-08-28 | MP1006 | 17.6 | 329 | 17.6 | 330 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 7608 | 1151.9997 | 185.4421
SYL-E.1.RR.1131.1 | 24535209154374 | Islampur, Block-A, Salima Khatun | 2019-08-28 | MP1006 | 13.9 | 331 | 13.9 | 332 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7608 | 1151.9997 | 146.4571
SYL-E.1.RR.1132.1 | 24535209154374 | Islampur, Block-A, Nurul Islam | 2019-08-28 | MP1006 | 14.5 | 333 | 14.5 | 334 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7608 | 1151.9997 | 152.779
SYL-E.1.RR.1133.1 | 24535229154386 | Islampur, Block-A, H # 20/1 | 2019-08-28 | MP1006 | 4.7 | 335 | 4.5 | 336 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7608 | 1151.9997 | 47.4142
SYL-E.1.RR.1134.1 | 24535269154419 | Islampur, Islampur Colony, Sona Mia | 2019-08-28 | MP1006 | 7.4 | 337 | 7.4 | 338 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7608 | 1151.9997 | 77.97
SYL-E.1.RR.1135.1 | 24535269154419 | Islampur, Islampur Colony, Sona Mia | 2019-08-28 | MP1006 | 7.3 | 339 | 7.3 | 340 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7608 | 1151.9997 | 76.9163
SYL-E.1.RR.1136.1 | 24535299154445 | Islampur, Islampur Colony, Deloer Hossen | 2019-08-28 | MP1006 | 13 | 341 | 13 | 342 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7608 | 1151.9997 | 136.9743
SYL-E.1.RR.1137.1 | 24535459154437 | Islampur, Islampur Colony, Moharam Ali | 2019-08-28 | MP1006 | 3.1 | 343 | 3.1 | 344 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7608 | 1151.9997 | 32.6631
SYL-E.1.RR.1138.1 | 24545439157146 | Khadim Nagar, Daspara, Sanu Chandra | 2019-08-29 | MP1006 | 17.8 | 373 | 17.9 | 374 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 7632 | 1127.9997 | 188.603
SYL-E.1.RR.1138.2 | 24545439157146 | Khadim Nagar, Daspara, Sanu Chandra | 2021-02-15 | MN1018 | 27 | 123 | 27 | 124 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 27 | 27 | 1.62 | 1.62 | 0.0007168 | 100% | 0% | 1.62 | 1.62 | 0.0011869 | 28 | 0.032475 | 0.032475 |  | 0 | 0 | 7632 | 1127.9997 | 284.485
SYL-E.1.RR.1139.1 | 24545519157146 | Khadim Nagar, Daspara, Ranjit Chandra | 2019-08-29 | MP1006 | 7 | 375 | 7 | 376 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7632 | 1127.9997 | 73.7554
SYL-E.1.RR.1140.1 | 24550069157154 | Khadim Nagar, Daspara, Mofiz Mia | 2019-08-29 | MP1006 | 5 | 377 | 4.7 | 378 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7632 | 1127.9997 | 49.5215
SYL-E.1.RR.1151.1 | 24541759152583 | Shahi Eidgah, Anamika R/A, H # 76/A, Akbul Villa | 2019-07-23 | MP1006 | 14.7 | 154 | 14.7 | 155 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7848 | 911.9997 | 154.8863
SYL-E.1.RR.1152.1 | 24541759152583 | Shahi Eidgah, Anamika R/A, H # 76/A, Akbul Villa | 2019-07-23 | MP1006 | 13.6 | 158 | 13.6 | 159 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7848 | 911.9997 | 143.2961
SYL-E.1.RR.1153.1 | 24541759152583 | Shahi Eidgah, Anamika R/A, H # 76/A, Akbul Villa | 2019-07-23 | MP1006 | 3.3 | 160 | 3.3 | 161 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7848 | 911.9997 | 34.7704
SYL-E.1.RR.1154.1 | 24551869158051 | Shahporan, Ward # 7, Talepara, Harun Rashid | 2019-07-24 | MP1006 | 7.5 | 193 | 7.5 | 194 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7800 | 959.9997 | 79.0236
SYL-E.1.RR.1155.1 | 24551689158043 | Shahporan, Ward # 7, Talepara, Ismail, Sofat Monjil | 2019-07-24 | MP1006 | 21.4 | 195 | 21.4 | 196 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 7800 | 959.9997 | 225.4807
SYL-E.1.RR.1156.1 | 24551579158047 | Shahporan, Ward # 7, Talepara, Ishak Ali | 2019-07-24 | MP1006 | 2.1 | 197 | 2.1 | 198 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7800 | 959.9997 | 22.1266
SYL-E.1.RR.1157.1 | 24551539158058 | Shahporan, Ward # 7, Talepara, Nozmul Hossain | 2019-07-24 | MP1006 | 3.4 | 199 | 3.4 | 200 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7800 | 959.9997 | 35.824
SYL-E.1.RR.1158.1 | 24551439158044 | Shahporan, Ward # 7, Talepara, Jamal Uddin | 2019-07-24 | MP1006 | 2.8 | 201 | 2.8 | 202 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7800 | 959.9997 | 29.5021
SYL-E.1.RR.1159.1 | 24551439158044 | Shahporan, Ward # 7, Talepara, Mostiquim Ali | 2019-07-24 | MP1006 | 10.5 | 203 | 10.5 | 204 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7800 | 959.9997 | 110.6331
SYL-E.1.RR.1161.1 | 24555959158394 | Boteshor, Ghotle Para, Tamabil Road, Kaoser | 2019-07-25 | MP1006 | 12.3 | 207 | 12.3 | 208 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7800 | 959.9997 | 129.5987
SYL-E.1.RR.1162.1 | 24560069158402 | Boteshor, Ghotle Para, Tamabil Road, Ittadi Furniture Gallary, Habibur Rahman | 2019-07-25 | MP1006 | 22.5 | 209 | 22.2 | 210 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 22.2 | 22.2 | 1.332 | 1.332 | 0.0007168 | 100% | 0% | 1.332 | 1.332 | 0.0011869 | 28 | 0.026702 | 0.026702 |  | 0 | 0 | 7800 | 959.9997 | 233.9099
SYL-E.1.RR.1163.1 | 24555629158416 | Boteshor,Chua Bohor, Tamabil Road, Sonargone R/A, Rd # 3, Aftab | 2019-07-25 | MP1006 | 11.4 | 211 | 11.4 | 212 | 2022-01-01 | 2022-11-22 | NQ1007 |  |  | 0 | 183 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7800 | 959.9997
SYL-E.1.RR.1164.1 | 24555879158439 | Boteshor,Chua Bohor, Tamabil Road, Sonargone R/A, Dr. Ahona Nutaq | 2019-07-25 | MP1006 | 19.3 | 213 | 19.3 | 214 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 7800 | 959.9997 | 203.3541
SYL-E.1.RR.1165.1 | 24555939158454 | Boteshor,Chua Bohor, Tamabil Road, Sonargone R/A, Khalilur Rahman | 2019-07-25 | MP1006 | 4.1 | 215 | 4.1 | 216 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7800 | 959.9997 | 43.1996
SYL-E.1.RR.1166.1 | 24555889158457 | Boteshor,Chua Bohor, Tamabil Road, Sonargone R/A, Kazi Abdur Rahman | 2019-07-25 | MP1006 | 9.2 | 217 | 9.2 | 218 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7800 | 959.9997 | 96.9356
SYL-E.1.RR.1167.1 | 24591599202144 | Jointapur, Horipur, Poshchimtul, Abul Kalam | 2019-07-27 | NQ1003 | 11.6 | 255 | 11.6 | 256 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7776 | 983.9997 | 122.2232
SYL-E.1.RR.1167.2 | 24591599202144 | Jointapur, Horipur, Poshchimtul, Abul Kalam | 2019-07-27 | NQ1003 | 12.4 | 257 | 12.4 | 258 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7776 | 983.9997 | 130.6524
SYL-E.1.RR.1168.1 | 24590839202377 | Jointapur, Horipur, Poshchim Balipara, Abdul Hannan | 2019-07-27 | NQ1003 | 12.3 | 259 | 12.3 | 260 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7776 | 983.9997 | 129.5987
SYL-E.1.RR.1169.1 | 24590789202374 | Jointapur, Horipur, Poshchim Balipara, Toyoubur Rahman | 2019-07-27 | NQ1003 | 9.8 | 261 | 9.8 | 262 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7776 | 983.9997 | 103.2575
SYL-E.1.RR.1170.1 | 24590859202375 | Jointapur, Horipur, Poshchim Balipara, Abdul Motin | 2019-07-27 | NQ1003 | 12.9 | 263 | 12.9 | 264 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7776 | 983.9997 | 135.9206
SYL-E.1.RR.1170.2 | 24590859202375 | Jointapur, Horipur, Poshchim Balipara, Abdul Motin | 2022-11-21 | NQ1007 | 11.3 | 179 | 11.3 | 180 | 2022-11-21 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 0 | 983.9997 | 13.3741
SYL-E.1.RR.1171.1 | 24534609154426 | Majortila, Islampur R/A, Block-C, H 75/A, Garden View | 2019-08-28 | MP1006 | 23 | 300 | 23 | 301 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 23 | 23 | 1.38 | 1.38 | 0.0007168 | 100% | 0% | 1.38 | 1.38 | 0.0011869 | 28 | 0.027664 | 0.027664 |  | 0 | 0 | 7608 | 1151.9997 | 242.3391
SYL-E.1.RR.1171.2 | 24534609154426 | Majortila, Islampur R/A, Block-C, H 75/A, Garden View | 2021-02-16 | MN1018 | 3.8 | 129 | 3.8 | 130 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7608 | 1151.9997 | 40.0386
SYL-E.1.RR.1172.1 | 24534769154425 | Majortila, Islampur R/A, H # 92/1, Md. Azmil Mia | 2019-08-28 | MP1006 | 10.6 | 302 | 10.6 | 303 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7608 | 1151.9997 | 111.6867
SYL-E.1.RR.1173.1 | 24534849154436 | Majortila, Islampur R/A, H # 20, Lalu Mia | 2019-08-28 | MP1006 | 12.3 | 304 | 12.3 | 305 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7608 | 1151.9997 | 129.5987
SYL-E.1.RR.1174.1 | 24534729154366 | Majortila, Islampur R/A, Block # A, H # 35 | 2019-08-28 | MP1006 | 11.5 | 307 | 11.5 | 308 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7608 | 1151.9997 | 121.1695
SYL-E.1.RR.1175.1 | 24534549154341 | Majortila, Islampur R/A, Block # A, H # 46, Monjurunnesa | 2019-08-28 | MP1006 | 15.1 | 309 | 15.1 | 310 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7608 | 1151.9997 | 159.1009
SYL-E.1.RR.1176.1 | 24534489154340 | Majortila, Islampur R/A, Block # A, H # 47, Islam Monjil | 2019-08-28 | MP1006 | 11 | 311 | 11.3 | 312 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7608 | 1151.9997 | 119.0622
SYL-E.1.RR.1177.1 | 24535429154399 | Majortila, Islampur, Habibur Rahman | 2019-08-29 | MP1006 | 13.6 | 345 | 13.5 | 346 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7608 | 1151.9997 | 142.2425
SYL-E.1.RR.1178.1 | 24535459154421 | Majortila, Islampur, Rojina Begum | 2019-08-29 | MP1006 | 8.4 | 347 | 7.8 | 348 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7608 | 1151.9997 | 82.1846
SYL-E.1.RR.1179.1 | 24535389154425 | Majortila, Islampur, Momtaz Ali | 2019-08-29 | MP1006 | 6.7 | 349 | 6.7 | 350 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7608 | 1151.9997 | 70.5944
SYL-E.1.RR.1180.1 | 24535509154418 | Majortila, Islampur, H # 939 | 2019-08-29 | MP1006 | 10.1 | 351 | 10.1 | 352 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7608 | 1151.9997 | 106.4185
SYL-E.1.RR.1181.1 | 24535549154407 | Majortila, Islampur, Anhar Villa | 2019-08-29 | MP1006 | 8 | 353 | 8 | 354 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7608 | 1151.9997 | 84.2919
SYL-E.1.RR.1182.1 | 24535509154428 | Majortila, Islampur, Fuljan Bibi | 2019-08-29 | MP1006 | 5.5 | 355 | 5.5 | 356 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7608 | 1151.9997 | 57.9506
SYL-E.1.RR.1183.1 | 24535619154427 | Majortila, Islampur, Akmot Mia | 2019-08-29 | MP1006 | 7.2 | 357 | 7.2 | 358 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7608 | 1151.9997 | 75.8627
SYL-E.1.RR.1184.1 | 24535619154427 | Majortila, Islampur, Md. Sanaullah | 2019-08-29 | MP1006 | 4.7 | 359 | 4.7 | 360 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7608 | 1151.9997 | 49.5215
SYL-E.1.RR.1185.1 | 24535529154452 | Majortila, Islampur, Arzu Mia | 2019-08-29 | MP1006 | 6.1 | 361 | 6.1 | 362 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7608 | 1151.9997 | 64.2725
SYL-E.1.RR.1186.1 | 24540209154419 | Majortila, Islampur, Kushumbag R/A, Hazi Abdul Goni | 2019-08-29 | MP1006 | 5 | 365 | 5 | 366 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7656 | 1103.9997 | 52.6824
SYL-E.1.RR.1187.1 | 24540209154416 | Majortila, Islampur, Kushumbag R/A, Abdur Rahman | 2019-08-29 | MP1006 | 3.9 | 367 | 3.9 | 368 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7656 | 1103.9997 | 41.0923
SYL-E.1.RR.1188.1 | 24535679154453 | Majortila, Islampur, Kushumbag R/A, Abdur Rahman | 2019-08-29 | MP1006 | 11.7 | 369 | 11.7 | 370 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7608 | 1151.9997 | 123.2768
SYL-E.1.RR.1189.1 | 24535679154453 | Majortila, Islampur, Poragon Property Ltd, Bhobon-D | 2019-08-29 | MP1006 | 9.7 | 371 | 9.7 | 372 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7608 | 1151.9997 | 102.2039
SYL-E.1.RR.1190.1 | 24545369157494 | Shahporan, Noagaon R/A, Koyes Mia,Near Moi Rahman | 2019-08-31 | MP1006 | 14.2 | 378 | 14.2 | 379 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7632 | 1127.9997 | 149.618
SYL-E.1.RR.1191.1 | 24543499157546 | Shahporan, Noagaon R/A, Jahangir Alam | 2019-08-31 | MP1006 | 7.1 | 381 | 7.1 | 382 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7632 | 1127.9997 | 74.809
SYL-E.1.RR.1192.1 | 24543499157546 | Shahporan, Noagaon R/A, Foezuddin | 2019-08-31 | MP1006 | 4 | 383 | 3.8 | 384 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7632 | 1127.9997 | 40.0386
SYL-E.1.RR.1193.1 | 24543069158002 | Shahporan, Noagaon R/A, Hazi Anwar Hossain | 2019-08-31 | MP1006 | 11.7 | 385 | 11.7 | 386 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7632 | 1127.9997 | 123.2768
SYL-E.1.RR.1194.1 | 24535279154025 | Tillagarh, MC College Road, Roton Dev | 2019-09-04 | NQ1008 | 70.8 | 25 | 70.8 | 26 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 70.8 | 70.8 | 4.248 | 4.248 | 0.0007168 | 100% | 0% | 4.248 | 4.248 | 0.0011869 | 28 | 0.085158 | 0.085158 |  | 0 | 0 | 7752 | 1007.9997 | 745.9829
SYL-E.1.RR.1195.1 | 24535279154025 | Tillagarh, MC College Road, Moni Kormokar | 2019-09-04 | NQ1008 | 15.7 | 27 | 15.7 | 28 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 7752 | 1007.9997 | 165.4228
SYL-E.1.RR.1196.1 | 24535279154025 | Tillagarh, MC College Road, Laxmikanta Dey | 2019-09-04 | NQ1008 | 12.9 | 29 | 12.9 | 30 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7752 | 1007.9997 | 135.9206
SYL-E.1.RR.1197.1 | 24535479154033 | Tillagarh, MC College Road, Somon Dotto | 2019-09-04 | NQ1008 | 15.7 | 31 | 15.7 | 32 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 7752 | 1007.9997 | 165.4228
SYL-E.1.RR.1198.1 | 24535479154033 | Tillagarh, MC College Road, Kartik | 2019-09-04 | NQ1008 | 24.6 | 33 | 24.6 | 34 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 24.6 | 24.6 | 1.476 | 1.476 | 0.0007168 | 100% | 0% | 1.476 | 1.476 | 0.0011869 | 28 | 0.029589 | 0.029589 |  | 0 | 0 | 7752 | 1007.9997 | 259.1974
SYL-E.1.RR.1199.1 | 24535929154028 | Gopaltila, Tillagarh, MC College Road, H # 92 | 2019-09-04 | NQ1008 | 3.5 | 35 | 3.5 | 36 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7752 | 1007.9997 | 36.8777
SYL-E.1.RR.1200.1 | 24540309153591 | M.C College Road, Madanibag R/A, H # 81/A / Mostak Ahammed | 2019-09-04 | NQ1008 | 10.3 | 37 | 10.3 | 38 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7752 | 1007.9997 | 108.5258
SYL-E.1.RR.1201.1 | 24561659158179 | Boteshwar, Jalalabad Cantonment, Pirer Chak, Dudu mia | 2019-07-25 | NQ1009 | 8.2 | 250 | 8.2 | 251 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7800 | 959.9997 | 86.3991
SYL-E.1.RR.1202.1 | 24561699158178 | Boteshwar, Jalalabad Cantonment, Pirer Chak, Soriful Islam | 2019-07-25 | NQ1009 | 13.9 | 254 | 13.9 | 255 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7800 | 959.9997 | 146.4571
SYL-E.1.RR.1203.1 | 24561629158343 | Boteshwar, Jalalabad Cantonment, Molaitila, Hazrat Ali | 2019-07-25 | NQ1003 | 10.5 | 237 | 10.5 | 238 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7800 | 959.9997 | 110.6331
SYL-E.1.RR.1204.1 | 24560089158407 | Boteshwar, Chuhabahar, Jalalabad Cantonment, Abdul Momin | 2019-07-25 | NQ1003 | 9.4 | 239 | 9.1 | 240 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7800 | 959.9997 | 95.882
SYL-E.1.RR.1205.1 | 24572609200407 | Jaintapur, Chiknagul, College Gate, College Road, Ali Ahmed | 2019-07-27 | NQ1003 | 6.6 | 241 | 6.8 | 242 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7776 | 983.9997 | 71.6481
SYL-E.1.RR.1206.1 | 24572839200363 | Jaintapur, Chiknagul, College Gate, College Road, Madoris Ali | 2019-07-27 | NQ1003 | 9.6 | 243 | 9.6 | 244 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7776 | 983.9997 | 101.1502
SYL-E.1.RR.1208.1 | 24572979200328 | Jaintapur, Chiknagul, College Gate, College Road, Estama Bari, Azad Mia | 2019-07-27 | NQ1003 | 4.3 | 247 | 4.3 | 248 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7776 | 983.9997 | 45.3069
SYL-E.1.RR.1209.1 | 24572889200323 | Jaintapur, Chiknagul, College Gate, College Road, Anamul Kabir Liton | 2019-07-27 | NQ1003 | 6.5 | 249 | 6.5 | 250 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7776 | 983.9997 | 68.4871
SYL-E.1.RR.1210.1 | 24572869200283 | Jaintapur, Chiknagul, College Gate, College Road, Tila Bari, Abdul Mosabbir | 2019-07-27 | NQ1003 | 7.9 | 251 | 7.9 | 252 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7776 | 983.9997 | 83.2382
SYL-E.1.RR.1211.1 | 24581819201429 | Jaintapur, Chiknagul, Umonpur, Samim Ahmed | 2019-07-27 | NQ1003 | 52.3 | 253 | 52.3 | 254 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 52.3 | 52.3 | 3.138 | 3.138 | 0.0007168 | 100% | 0% | 3.138 | 3.138 | 0.0011869 | 28 | 0.062906 | 0.062906 |  | 0 | 0 | 7776 | 983.9997 | 551.058
SYL-E.1.RR.1212.1 | 25001799202322 | Jaintapur, Hemobatopara, Abdul Jabbar | 2019-07-28 | NQ1003 | 8.2 | 265 | 8.2 | 266 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7776 | 983.9997 | 86.3991
SYL-E.1.RR.1213.1 | 25002149202347 | Jaintapur, Hemobatopara, Khaner Tong, Rupa Mia | 2019-07-28 | NQ1003 | 9.3 | 267 | 8.6 | 268 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7776 | 983.9997 | 90.6137
SYL-E.1.RR.1214.1 | 25002149202347 | Jaintapur, Hemobatopara, Khaner Tong, Sona Mia | 2019-07-28 | NQ1003 | 13.4 | 269 | 13.4 | 270 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7776 | 983.9997 | 141.1888
SYL-E.1.RR.1215.1 | 25002499202399 | Jaintapur, Hemobatopara, Horipur, Nuruddin | 2019-07-28 | NQ1003 | 13.4 | 271 | 13.5 | 272 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7776 | 983.9997 | 142.2425
SYL-E.1.RR.1216.1 | 25003519202418 | Jaintapur, Hemobatopara, Horipur, Somsaruddin | 2019-07-28 | NQ1003 | 10.6 | 273 | 10.6 | 274 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7776 | 983.9997 | 111.6867
SYL-E.1.RR.1217.1 | 25003769202438 | Jaintapur, Hemobatopara, Horipur, Roisuddin | 2019-07-28 | NQ1003 | 10.5 | 275 | 10.5 | 276 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7776 | 983.9997 | 110.6331
SYL-E.1.RR.1218.1 | 25003769202438 | Jaintapur, Hemobatopara, Horipur, Abdullah | 2019-07-28 | NQ1003 | 3 | 277 | 3 | 278 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7776 | 983.9997 | 31.6094
SYL-E.1.RR.1219.1 | 25003699202404 | Jaintapur, Hemobatopara, Horipur, Helal | 2019-07-28 | NQ1003 | 12.7 | 279 | 12.7 | 280 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7776 | 983.9997 | 133.8133
SYL-E.1.RR.1220.1 | 25003749202388 | Jaintapur, Hemobatopara, Horipur, Ludai Mia | 2019-07-28 | NQ1003 | 6.7 | 281 | 6.7 | 282 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7776 | 983.9997 | 70.5944
SYL-E.1.RR.1221.1 | 24545399157121 | Khadim Nagor, Dashpara, Dashpara R/A, Rd # 03, H # 04 | 2019-08-29 | NQ1003 | 12.9 | 515 | 12.9 | 516 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7632 | 1127.9997 | 135.9206
SYL-E.1.RR.1222.1 | 24545399157121 | Khadim Nagor, Dashpara, Dashpara R/A, Rd # 03, H # 05 | 2019-08-29 | NQ1003 | 14.7 | 517 | 14.7 | 518 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7632 | 1127.9997 | 154.8863
SYL-E.1.RR.1223.1 | 24544579157189 | Khadim Nagor, Dashpara R/A, Kamal Mia | 2019-08-31 | MN1032 | 2.4 | 296 | 2.3 | 297 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7632 | 1127.9997 | 24.2339
SYL-E.1.RR.1224.1 | 24544319157195 | Khadim Nagor, Dashpar, H # 85, Rahman Villa | 2019-08-31 | MN1032 | 9.7 | 298 | 9.7 | 299 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7632 | 1127.9997 | 102.2039
SYL-E.1.RR.1225.1 | 24542699157202 | Khadim Nagor, Dashpara, Boro Bari, Shohidul Islam Shahin | 2019-08-31 | MN1032 | 10.1 | 300 | 9.7 | 301 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7632 | 1127.9997 | 102.2039
SYL-E.1.RR.1226.1 | 24543029157254 | Khadim Nagor, Dashpara, Shona Miah | 2019-08-31 | MN1032 | 10.2 | 308 | 10.2 | 309 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7632 | 1127.9997 | 107.4721
SYL-E.1.RR.1227.1 | 24543419157240 | Khadim Nagor, Dashpara R/A, Kamal Uddin | 2019-08-31 | MN1032 | 13.8 | 312 | 13.8 | 313 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7632 | 1127.9997 | 145.4034
SYL-E.1.RR.1228.1 | 24543149157236 | Khadim Nagor, Dashpara R/A, Lutfor Rahman | 2019-08-31 | MN1032 | 2.2 | 310 | 2.2 | 311 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7632 | 1127.9997 | 23.1803
SYL-E.1.RR.1228.2 | 24543149157236 | Khadim Nagor, Dashpara R/A, Lutfor Rahman | 2021-02-15 | MN1018 | 11.3 | 120 | 11.2 | 121 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7632 | 1127.9997 | 118.0086
SYL-E.1.RR.1229.1 | 24543669157218 | Khadim Nagor, Balutikor, H # 2, Jabban Monjil | 2019-08-31 | MN1032 | 1.8 | 314 | 1.7 | 315 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7632 | 1127.9997 | 17.912
SYL-E.1.RR.1231.1 | 24541279155458 | Shahpora, Moniporipara, Nipon R/A, Ram Krisno | 2019-09-04 | MN1032 | 5.3 | 3 | 5.3 | 4 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7680 | 1079.9997 | 55.8434
SYL-E.1.RR.1232.1 | 24541179155467 | Shahpora, Moniporipara, Nipon R/A, H # 58 | 2019-09-04 | MN1032 | 11 | 5 | 11 | 6 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7680 | 1079.9997 | 115.9013
SYL-E.1.RR.1233.1 | 24541179155467 | Shahpora, Moniporipara, Nipon R/A, H # 59 | 2019-09-04 | MN1032 | 4.4 | 7 | 4.4 | 8 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7680 | 1079.9997 | 46.3605
SYL-E.1.RR.1234.1 | 24541209155482 | Shahpora, Moniporipara, Nipon R/A, Borkotullah | 2019-09-04 | MN1032 | 11 | 9 | 11 | 10 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7680 | 1079.9997 | 115.9013
SYL-E.1.RR.1234.2 | 24541209155482 | Shahpora, Moniporipara, Nipon R/A, Borkotullah | 2020-10-21 | NQ1000 | 11 | 9 | 11 | 10 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7680 | 1079.9997 | 115.9013
SYL-E.1.RR.1235.1 | 24541239155488 | Shahpora, Moniporipara, Nipon R/A, Moslim Khan | 2019-09-04 | MN1032 | 3.2 | 146 | 3.2 | 147 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7680 | 1079.9997 | 33.7167
SYL-E.1.RR.1236.1 | 24541189155478 | Shahpora, Moniporipara, Nipon R/A, H # 61 | 2019-09-04 | MN1032 | 8.8 | 13 | 8.8 | 14 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7680 | 1079.9997 | 92.721
SYL-E.1.RR.1237.1 | 24541119155429 | Shahpora, Moniporipara, Nipon R/A, Shilpi House | 2019-09-04 | MN1032 | 14.8 | 15 | 14.8 | 16 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 7680 | 1079.9997 | 155.9399
SYL-E.1.RR.1238.1 | 24545219156013 | Khadim Nagar, Bahubali R/A, H # 26/A | 2019-09-05 | MN1032 | 13 | 31 | 13.1 | 32 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7632 | 1127.9997 | 138.0279
SYL-E.1.RR.1239.1 | 24545139156017 | Khadim Nagar, Bahubali R/A, H # 23/A | 2019-09-05 | MN1032 | 13.7 | 33 | 13.7 | 34 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7632 | 1127.9997 | 144.3498
SYL-E.1.RR.1240.1 | 24545139156017 | Khadim Nagar, Bahubali R/A, H # 24/A | 2019-09-05 | MN1032 | 10.6 | 35 | 10.5 | 36 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7632 | 1127.9997 | 110.6331
SYL-E.1.RR.1241.1 | 24544889156007 | Khadim Nagar, Bahubali R/A, Md. Tayeb Ali | 2019-09-05 | MN1032 | 11.5 | 37 | 11.3 | 38 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7632 | 1127.9997 | 119.0622
SYL-E.1.RR.1251.1 | 24533979152505 | Mirabazar, Noyapara, Uddipon, H # 80 | 2019-07-23 | NQ1003 | 9.9 | 158 | 9.9 | 159 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7512 | 1247.9997 | 104.3112
SYL-E.1.RR.1252.1 | 24533879153008 | Mirabazar, Kharpara R/A, Mitali, H # 60/2 | 2019-07-23 | NQ1003 | 6 | 162 | 6 | 163 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7512 | 1247.9997 | 63.2189
SYL-E.1.RR.1253.1 | 24533879153008 | Mirabazar, Kharpara R/A, Mitali, H # 13, Kazi Ashraf Uddin Advocate | 2019-07-23 | NQ1003 | 8.7 | 164 | 8.7 | 165 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7512 | 1247.9997 | 91.6674
SYL-E.1.RR.1253.2 | 24533879153008 | Mirabazar, Kharpara R/A, Mitali, H # 13, Kazi Ashraf Uddin Advocate | 2021-02-11 | LX1011 | 7.5 | 110 | 7.5 | 111 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7512 | 1247.9997 | 79.0236
SYL-E.1.RR.1254.1 | 24533829153042 | East Mirabazar, Kharpara R/A, Mitali, H # 50, Taher Manjil | 2019-07-23 | NQ1003 | 3.4 | 167 | 3.4 | 168 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7512 | 1247.9997 | 35.824
SYL-E.1.RR.1255.1 | 24533309153039 | East Mirabazar, Kharpara R/A, Mitali, H # 25/3 | 2019-07-23 | NQ1003 | 4 | 169 | 4 | 170 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 8280 | 479.9997 | 42.1459
SYL-E.1.RR.1256.1 | 24533309153039 | East Mirabazar, Kharpara R/A, Mitali, H # 25/A, Sabbir Ahammed | 2019-07-23 | NQ1003 | 60.1 | 171 | 60.1 | 172 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 60.1 | 60.1 | 3.606 | 3.606 | 0.0007168 | 100% | 0% | 3.606 | 3.606 | 0.0011869 | 28 | 0.072288 | 0.072288 |  | 0 | 0 | 7512 | 1247.9997 | 633.2425
SYL-E.1.RR.1257.1 | 24551789157571 | Shahparan, Talepara, Back Side Of Shiraz Member Bari, Nurul Haque | 2019-07-24 | NQ1003 | 2.2 | 197 | 2.2 | 198 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7800 | 959.9997 | 23.1803
SYL-E.1.RR.1258.1 | 24551789157571 | Shahparan, Talepara, Back Side Of Shiraz Member Bari, Nurul Haque | 2019-07-24 | NQ1003 | 1.4 | 199 | 1.4 | 200 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7800 | 959.9997 | 14.7511
SYL-E.1.RR.1259.1 | 24551789157571 | Shahparan, Talepara, Back Side Of Shiraz Member Bari, Nurul Haque | 2019-07-24 | NQ1003 | 4.9 | 203 | 4.9 | 204 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7800 | 959.9997 | 51.6288
SYL-E.1.RR.1260.1 | 24551789157571 | Shahparan, Talepara, Back Side Of Shiraz Member Bari, Nurul Haque | 2019-07-24 | NQ1003 | 1.9 | 205 | 1.9 | 206 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7800 | 959.9997 | 20.0193
SYL-E.1.RR.1261.1 | 24551789157571 | Shahparan, Talepara, Shiraz Uddin | 2019-07-24 | NQ1003 | 5.7 | 207 | 5.7 | 208 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7800 | 959.9997 | 60.0579
SYL-E.1.RR.1262.1 | 24551629157589 | Shahparan, Talepara, Beside Of Shiraz Member Bari, Nazrul Islam Lahin | 2019-07-24 | NQ1003 | 3.4 | 209 | 3.4 | 210 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7800 | 959.9997 | 35.824
SYL-E.1.RR.1263.1 | 24551519157587 | Shahparan, Talepara, Beside Of Shiraz Member Bari, Mostakim Ali Maya | 2019-07-24 | NQ1003 | 6.3 | 211 | 6.3 | 212 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7800 | 959.9997 | 66.3798
SYL-E.1.RR.1264.1 | 24551519157587 | Shahparan, Talepara, Beside Of Shiraz Member Bari, Shomjed Ali | 2019-07-24 | NQ1003 | 5 | 213 | 4.6 | 214 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7800 | 959.9997 | 48.4678
SYL-E.1.RR.1265.1 | 24551529158013 | Shahparan, Talepara, Mokaddes | 2019-07-24 | NQ1003 | 3.4 | 215 | 3.4 | 216 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7800 | 959.9997 | 35.824
SYL-E.1.RR.1266.1 | 24551529158013 | Shahparan, Talepara, Mokaddes | 2019-07-24 | NQ1003 | 4.2 | 217 | 4.2 | 218 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7800 | 959.9997 | 44.2532
SYL-E.1.RR.1267.1 | 24551529158013 | Shahparan, Talepara, Mokaddes | 2019-07-24 | NQ1003 | 6.7 | 219 | 6.7 | 220 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7800 | 959.9997 | 70.5944
SYL-E.1.RR.1268.1 | 24555229158216 | Khadimpara, Pirer Chalk, Rd # 2, Jaman Villa | 2019-07-25 | NQ1003 | 12.8 | 221 | 12.4 | 222 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7800 | 959.9997 | 130.6524
SYL-E.1.RR.1269.1 | 24555289158198 | Khadimpara, Pirer Chalk, Rd # 2, Ismail Villa | 2019-07-25 | NQ1003 | 9.4 | 223 | 9.4 | 224 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7800 | 959.9997 | 99.0429
SYL-E.1.RR.1270.1 | 24555359158189 | Khadimpara, Pirer Chalk, Rd # 2, Abdul Hannan | 2019-07-25 | NQ1003 | 2.4 | 225 | 2.4 | 226 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7800 | 959.9997 | 25.2876
SYL-E.1.RR.1271.1 | 24555549158194 | Khadimpara, Pirer Chalk, Rd # 2, Syed Manjil,Shopno Nir | 2019-07-25 | NQ1003 | 3.2 | 227 | 3.2 | 228 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7800 | 959.9997 | 33.7167
SYL-E.1.RR.1272.1 | 24555549158194 | Khadimpara, Pirer Chalk, Rd # 2, Syed Manjil,Shopno Nir | 2019-07-25 | NQ1003 | 10.6 | 229 | 10.6 | 230 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7800 | 959.9997 | 111.6867
SYL-E.1.RR.1273.1 | 24560239158238 | Khadimpara, Pirer Chalk, Rd # 2, Mulai Tila, Tokles Ahmed Chowdhury | 2019-07-25 | NQ1003 | 5.7 | 231 | 5.7 | 232 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7800 | 959.9997 | 60.0579
SYL-E.1.RR.1274.1 | 24560609158169 | Khadimpara, Pirer Chalk, Rd # 2, Hoq Villa, Anhara Begum | 2019-07-25 | NQ1003 | 11 | 233 | 11 | 234 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7800 | 959.9997 | 115.9013
SYL-E.1.RR.1275.1 | 24560929158169 | Khadimpara, Pirer Chalk, Rd # 2, Abul Munshi | 2019-07-25 | NQ1003 | 10.8 | 235 | 10.8 | 236 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7800 | 959.9997 | 113.794
SYL-E.1.RR.1275.2 | 24560929158169 | Khadimpara, Pirer Chalk, Rd # 2, Abul Munshi | 2021-02-25 | MN1018 | 6.2 | 169 | 6.2 | 170 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7800 | 959.9997 | 65.3262
SYL-E.1.RR.1276.1 | 24571439200110 | Zointapur, Thakurermati, H # 71, Hazi Ataur Rahman | 2019-07-27 | MP1006 | 16.3 | 249 | 15.9 | 250 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 7776 | 983.9997 | 167.5301
SYL-E.1.RR.1276.2 | 24571439200110 | Zointapur, Thakurermati, H # 71, Hazi Ataur Rahman | 2021-02-23 | LX1011 | 9.3 | 152 | 9.3 | 153 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7776 | 983.9997 | 97.9893
SYL-E.1.RR.1277.1 | 24571179200116 | Zointapur, Thakurermati, Faizul Hasan | 2019-07-27 | MP1006 | 11.9 | 251 | 11.9 | 252 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7776 | 983.9997 | 125.3841
SYL-E.1.RR.1278.1 | 24571039200148 | Zointapur, Thakurermati, Kamal Ahmod | 2019-07-27 | MP1006 | 11.9 | 253 | 11.9 | 254 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7776 | 983.9997 | 125.3841
SYL-E.1.RR.1279.1 | 24570989200147 | Zointapur, Thakurermati, H # 8, Jamaluddin | 2019-07-27 | MP1006 | 4.7 | 255 | 4.7 | 256 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7776 | 983.9997 | 49.5215
SYL-E.1.RR.1280.1 | 25001519202321 | Horipur, Vatpara, Himu-Eidgah Road, Helaluddin | 2019-07-28 | MP1006 | 16.8 | 275 | 16.8 | 276 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 7776 | 983.9997 | 177.0129
SYL-E.1.RR.1281.1 | 25001519202321 | Horipur, Vatpara, Himu-Eidgah Road, Hazi Abdul Jalil | 2019-07-28 | MP1006 | 8.5 | 279 | 8.5 | 280 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7776 | 983.9997 | 89.5601
SYL-E.1.RR.1282.1 | 25001519202321 | Horipur, Vatpara, Himu-Eidgah Road, Shorifuddin | 2019-07-28 | MP1006 | 10.3 | 281 | 10.3 | 282 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7776 | 983.9997 | 108.5258
SYL-E.1.RR.1283.1 | 25001519202309 | Horipur, Vatpara, Himu-Eidgah Road, Nurul Hoque | 2019-07-28 | MP1006 | 3.5 | 283 | 3.5 | 284 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7776 | 983.9997 | 36.8777
SYL-E.1.RR.1284.1 | 25001519202309 | Horipur, Vatpara, Himu-Eidgah Road, Samsul Hoque | 2019-07-28 | MP1006 | 6.1 | 285 | 6.1 | 286 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7776 | 983.9997 | 64.2725
SYL-E.1.RR.1285.1 | 24583279202162 | Zointapur, Shikarkha, Sirazuddin | 2019-07-28 | MP1006 | 9.1 | 287 | 9.1 | 288 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7776 | 983.9997 | 95.882
SYL-E.1.RR.1286.1 | 24533829154456 | Majortila, South Islampur R/A, Falguni-67 | 2019-08-28 | NQ1003 | 22.4 | 467 | 22.4 | 468 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 22.4 | 22.4 | 1.344 | 1.344 | 0.0007168 | 100% | 0% | 1.344 | 1.344 | 0.0011869 | 28 | 0.026943 | 0.026943 |  | 0 | 0 | 7656 | 1103.9997 | 236.0172
SYL-E.1.RR.1287.1 | 24533739154455 | Majortila, South Islampur R/A, Falguni-68 | 2019-08-28 | NQ1003 | 12.1 | 465 | 12.2 | 466 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7656 | 1103.9997 | 128.5451
SYL-E.1.RR.1288.1 | 24533799154496 | Majortila, South Islampur , Falguni R/A, Hafiz Fakur Uddin, H # 38/4 | 2019-08-28 | NQ1003 | 13 | 469 | 13 | 470 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7656 | 1103.9997 | 136.9743
SYL-E.1.RR.1289.1 | 24533799154496 | Majortila, South Islampur , Falguni R/A, Alam Mia, H # 38/5 | 2019-08-28 | NQ1003 | 11.6 | 471 | 11.7 | 472 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7656 | 1103.9997 | 123.2768
SYL-E.1.RR.1290.1 | 24533799154496 | Majortila, South Islampur , Falguni R/A, Basid Mia, H # 36 | 2019-08-28 | NQ1003 | 30.3 | 473 | 30.3 | 474 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 30.3 | 30.3 | 1.818 | 1.818 | 0.0007168 | 100% | 0% | 1.818 | 1.818 | 0.0011869 | 28 | 0.036445 | 0.036445 |  | 0 | 0 | 7656 | 1103.9997 | 319.2554
SYL-E.1.RR.1290.2 | 24533799154496 | Majortila, South Islampur , Falguni R/A, Basid Mia, H # 36 | 2021-11-02 | LU1001 | 6.9 | 127 | 6.9 | 128 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7656 | 1103.9997 | 72.7017
SYL-E.1.RR.1291.1 | 24533379154503 | Majortila, South Islampur , Falguni R/A, H # 45 | 2019-08-28 | NQ1003 | 26.6 | 475 | 26.6 | 476 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 26.6 | 26.6 | 1.596 | 1.596 | 0.0007168 | 100% | 0% | 1.596 | 1.596 | 0.0011869 | 28 | 0.031994 | 0.031994 |  | 0 | 0 | 7656 | 1103.9997 | 280.2704
SYL-E.1.RR.1292.1 | 24533379154503 | Majortila, South Islampur , Falguni R/A, Taharul Jaman | 2019-08-28 | NQ1003 | 7.5 | 477 | 7.5 | 478 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7656 | 1103.9997 | 79.0236
SYL-E.1.RR.1293.1 | 24533379154503 | Majortila, South Islampur , Falguni R/A, Taharul Jaman | 2019-08-28 | NQ1003 | 7 | 479 | 7 | 480 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7656 | 1103.9997 | 73.7554
SYL-E.1.RR.1294.1 | 24533309154504 | Majortila, South Islampur , Falguni R/A, Akmot Hosen | 2019-08-28 | NQ1003 | 11 | 481 | 11 | 482 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7656 | 1103.9997 | 115.9013
SYL-E.1.RR.1295.1 | 24534199155013 | Majortila, Nathpara , Uattara R/A, Sobuj Mia | 2019-08-28 | NQ1003 | 16 | 485 | 16 | 486 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 7656 | 1103.9997 | 168.5837
SYL-E.1.RR.1296.1 | 24534339155079 | Majortila, Nathpara , Uattara R/A, H # 164, Rajot Kotir | 2019-08-28 | NQ1003 | 7.6 | 487 | 7.6 | 488 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7656 | 1103.9997 | 80.0773
SYL-E.1.RR.1297.1 | 24534159155079 | Majortila, Nathpara , Uattara R/A, Molypur Kayestu | 2019-08-28 | NQ1003 | 12.2 | 489 | 12.2 | 490 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7656 | 1103.9997 | 128.5451
SYL-E.1.RR.1298.1 | 24534159155079 | Majortila, Nathpara , Uattara R/A, Sobir Dabu Nath | 2019-08-28 | NQ1003 | 9.8 | 491 | 9.8 | 492 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7656 | 1103.9997 | 103.2575
SYL-E.1.RR.1301.1 | 24534309153463 | Shibgonj, Hatimbag R/A, Rd# 1, Block-D, Abdus Samad, H# 80 | 2019-07-23 | NQ1009 | 23 | 194 | 23 | 195 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 23 | 23 | 1.38 | 1.38 | 0.0007168 | 100% | 0% | 1.38 | 1.38 | 0.0011869 | 28 | 0.027664 | 0.027664 |  | 0 | 0 | 7752 | 1007.9997 | 242.3391
SYL-E.1.RR.1302.1 | 24533469152460 | Naiorpul, Bongobir R/A, Block-B, Sakib | 2019-07-23 | NQ1009 | 31.1 | 196 | 31.1 | 197 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 31.1 | 31.1 | 1.866 | 1.866 | 0.0007168 | 100% | 0% | 1.866 | 1.866 | 0.0011869 | 28 | 0.037407 | 0.037407 |  | 0 | 0 | 7512 | 1247.9997 | 327.6846
SYL-E.1.RR.1303.1 | 24533469152460 | Naiorpul, Bongobir R/A, Block-B, Nur Islam | 2019-07-23 | NQ1009 | 12.5 | 198 | 12.3 | 199 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7512 | 1247.9997 | 129.5987
SYL-E.1.RR.1304.1 | 24533469152460 | Naiorpul, Bongobir R/A, Block-B, H# 64 | 2019-07-23 | NQ1009 | 10.7 | 200 | 10.7 | 201 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7512 | 1247.9997 | 112.7403
SYL-E.1.RR.1305.1 | 24533429152453 | Naiorpul, Bongobir R/A, Block-B, H# 64, Shamsuddin | 2019-07-23 | NQ1009 | 11 | 202 | 11 | 203 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7512 | 1247.9997 | 115.9013
SYL-E.1.RR.1306.1 | 24560679158560 | Shahporan, Botesshor, Jalalabad , Anamur Rahman | 2019-07-25 | NQ1009 | 4.9 | 256 | 4.9 | 257 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7800 | 959.9997 | 51.6288
SYL-E.1.RR.1306.2 | 24560679158560 | Shahporan, Botesshor, Jalalabad , Anamur Rahman | 2021-02-23 | MN1018 | 11.5 | 152 | 11.6 | 153 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7800 | 959.9997 | 122.2232
SYL-E.1.RR.1307.1 | 24560359158554 | Shahporan, Botesshor, Jalalabad, Rafiq | 2019-07-25 | NQ1009 | 9.4 | 258 | 9.4 | 259 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7800 | 959.9997 | 99.0429
SYL-E.1.RR.1308.1 | 24560349158553 | Shahporan, Botesshor, Jalalabad, Tawhid Ali | 2019-07-25 | NQ1009 | 9.5 | 260 | 9.5 | 261 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7800 | 959.9997 | 100.0966
SYL-E.1.RR.1309.1 | 24560309158543 | Shahporan, Botesshor, Chuyabohor, Rafiqul Islam | 2019-07-25 | NQ1009 | 11.1 | 262 | 11.1 | 263 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7800 | 959.9997 | 116.9549
SYL-E.1.RR.1310.1 | 24560309158543 | Shahporan, Botesshor, Chuyabohor, Jahir Ali | 2019-07-25 | NQ1009 | 10.5 | 264 | 10.3 | 265 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7800 | 959.9997 | 108.5258
SYL-E.1.RR.1310.2 | 24560309158543 | Shahporan, Botesshor, Chuyabohor, Jahir Ali | 2021-02-23 | MN1018 | 4.2 | 150 | 4.2 | 151 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7800 | 959.9997 | 44.2532
SYL-E.1.RR.1311.1 | 24560259158546 | Shahporan, Botesshor, Chuyabohor, Kazimonjil, H # 254 | 2019-07-25 | NQ1009 | 10.9 | 266 | 10.9 | 267 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7800 | 959.9997 | 114.8476
SYL-E.1.RR.1312.1 | 24560099158544 | Shahporan, Botesshor, Chuyabohor, Shahidul Islam | 2019-07-25 | NQ1009 | 8.3 | 268 | 8.3 | 269 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7800 | 959.9997 | 87.4528
SYL-E.1.RR.1313.1 | 24555439158536 | Shahporan, Botesshor, Chuyabohor, Rabeya Begum | 2019-07-25 | NQ1009 | 10.5 | 270 | 10.5 | 271 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7800 | 959.9997 | 110.6331
SYL-E.1.RR.1314.1 | 24555419158520 | Shahporan, Botesshor, Chuyabohor, Dhoroni | 2019-07-25 | NQ1009 | 10.9 | 272 | 10.9 | 273 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7800 | 959.9997 | 114.8476
SYL-E.1.RR.1315.1 | 24555279158521 | Shahporan, Botesshor, Chuyabohor, Mohorom Ali | 2019-07-25 | NQ1009 | 10.2 | 274 | 10.2 | 275 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7800 | 959.9997 | 107.4721
SYL-E.1.RR.1316.1 | 24562659159312 | Jaintica, Chiknagul, Ghater Choti, Takurer mati, Suratun Nesa | 2019-07-27 | NQ1009 | 11.5 | 296 | 11.5 | 297 | 2022-01-01 | [9 empty] | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0
SYL-E.1.RR.1317.1 | 24562889159309 | Jaintica, Chiknagul, West Takurer mati, Nurun Nahar | 2019-07-27 | NQ1009 | 9.7 | 298 | 9.7 | 299 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7800 | 959.9997 | 102.2039
SYL-E.1.RR.1318.1 | 24562889159309 | Jaintica, Chiknagul, West Takurer mati, Monirul Islam | 2019-07-27 | NQ1009 | 10.2 | 300 | 10.2 | 301 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7800 | 959.9997 | 107.4721
SYL-E.1.RR.1319.1 | 24562889159309 | Jaintica, Chiknagul, West Takurer mati, Abdul Jalil | 2019-07-27 | NQ1009 | 3.4 | 304 | 3.4 | 305 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7800 | 959.9997 | 35.824
SYL-E.1.RR.1320.1 | 24562889159309 | Jaintica, Chiknagul, West Takurer mati, Abbas Ali | 2019-07-27 | NQ1009 | 13.2 | 306 | 13.5 | 307 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7800 | 959.9997 | 142.2425
SYL-E.1.RR.1321.1 | 24562969159308 | Jaintica, Chiknagul, West Takurer mati, Musabbir Hossain | 2019-07-27 | NQ1009 | 11.3 | 308 | 11.3 | 309 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7800 | 959.9997 | 119.0622
SYL-E.1.RR.1322.1 | 24562599159382 | Jaintica, Chiknagul, Ghater Choti, Abdul Muhid | 2019-07-27 | NQ1009 | 5.3 | 310 | 5.3 | 311 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7800 | 959.9997 | 55.8434
SYL-E.1.RR.1323.1 | 24562659159375 | Jaintica, Chiknagul, Ghater Choti, Hossain Ali | 2019-07-27 | NQ1009 | 12 | 312 | 12 | 313 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7800 | 959.9997 | 126.4378
SYL-E.1.RR.1324.1 | 24562649159377 | Jaintica, Chiknagul, Ghater Choti, Ataul Haque | 2019-07-27 | NQ1009 | 10.4 | 314 | 10.4 | 315 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7800 | 959.9997 | 109.5794
SYL-E.1.RR.1325.1 | 24562739159385 | Jaintica, Chiknagul, Ghater Choti, Gul Mohammad | 2019-07-27 | NQ1009 | 14.9 | 316 | 14.9 | 317 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7800 | 959.9997 | 156.9936
SYL-E.1.RR.1326.1 | 24562789159404 | Jaintica, Chiknagul, Ghater Choti, Ismail Ali | 2019-07-27 | NQ1009 | 7.3 | 318 | 6.7 | 319 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7800 | 959.9997 | 70.5944
SYL-E.1.RR.1326.2 | 24562789159404 | Jaintica, Chiknagul, Ghater Choti, Ismail Ali | 2022-11-22 | NQ1007 | 4.3 | 181 | 4.3 | 182 | 2022-11-22 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 0 | 959.9997 | 4.9651
SYL-E.1.RR.1327.1 | 24584449202110 | Jaintica, Horipur, Shikar kha, Tamabil Road, Mohammad Ali | 2019-07-27 | NQ1009 | 3.3 | 320 | 3.3 | 321 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7776 | 983.9997 | 34.7704
SYL-E.1.RR.1328.1 | 24534149154533 | Mejortila, Falguni R/A, Paki Mia | 2019-08-28 | LX1011 | 13.3 | 331 | 13.3 | 332 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7656 | 1103.9997 | 140.1352
SYL-E.1.RR.1329.1 | 24534019154567 | Mejortila, Falguni R/A, Block-D, H # 84/1 | 2019-08-28 | LX1011 | 12 | 333 | 11.6 | 334 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7656 | 1103.9997 | 122.2232
SYL-E.1.RR.1330.1 | 24534019154567 | Mejortila, Falguni R/A, Block-D, Moyaz bin jabal kuranik institute, H # 89 | 2019-08-28 | LX1011 | 11.3 | 335 | 11.3 | 336 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7656 | 1103.9997 | 119.0622
SYL-E.1.RR.1331.1 | 24533649154541 | Mejortila, Falguni R/A, Abdul Mannan Villa, H # 75 | 2019-08-28 | LX1011 | 10.7 | 337 | 10.7 | 338 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7656 | 1103.9997 | 112.7403
SYL-E.1.RR.1332.1 | 24533649154541 | Mejortila, Falguni R/A, Rahman Palace, H # 64 | 2019-08-28 | LX1011 | 7.1 | 339 | 7.1 | 340 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7656 | 1103.9997 | 74.809
SYL-E.1.RR.1333.1 | 24532839154487 | Mejortila, West Vatpara, Kirod Ronjon De | 2019-08-28 | LX1011 | 10.7 | 341 | 10.7 | 342 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7656 | 1103.9997 | 112.7403
SYL-E.1.RR.1334.1 | 24532869154477 | Mejortila, West Vatpara, Rontu De | 2019-08-28 | LX1011 | 11.7 | 343 | 11.7 | 344 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7656 | 1103.9997 | 123.2768
SYL-E.1.RR.1335.1 | 24532869154477 | Mejortila, West Vatpara, Badol De | 2019-08-28 | LX1011 | 15.7 | 347 | 15.6 | 348 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7656 | 1103.9997 | 164.3691
SYL-E.1.RR.1336.1 | 24532239154537 | Mejortila, West Vatpara, Aprupa-63 | 2019-08-28 | LX1011 | 12.8 | 349 | 12.8 | 350 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7656 | 1103.9997 | 134.867
SYL-E.1.RR.1336.2 | 24532239154537 | Mejortila, West Vatpara, Aprupa-63 | 2021-11-02 | LU1001 | 5.8 | 129 | 5.8 | 130 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7656 | 1103.9997 | 61.1116
SYL-E.1.RR.1337.1 | 24532239154537 | Mejortila, West Vatpara, Churai Bibi | 2019-08-28 | LX1011 | 11.4 | 351 | 11.4 | 352 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7656 | 1103.9997 | 120.1159
SYL-E.1.RR.1338.1 | 24545149157222 | Atgaon, Daspara, Sofiqur Rahman | 2019-08-29 | LX1011 | 14.5 | 363 | 14.5 | 364 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7632 | 1127.9997 | 152.779
SYL-E.1.RR.1339.1 | 24545109157225 | Atgaon, Daspara, Shayesta | 2019-08-29 | LX1011 | 11.9 | 365 | 11.9 | 366 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7632 | 1127.9997 | 125.3841
SYL-E.1.RR.1340.1 | 24545109157225 | Atgaon, Daspara, Nur Mia | 2019-08-29 | LX1011 | 11.6 | 367 | 11.6 | 368 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7632 | 1127.9997 | 122.2232
SYL-E.1.RR.1341.1 | 24544489157192 | Atgaon, Daspara, Ala Mia | 2019-08-29 | LX1011 | 7.9 | 369 | 7.9 | 370 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7632 | 1127.9997 | 83.2382
SYL-E.1.RR.1342.1 | 24544489157192 | Atgaon, Daspara, A. Malik | 2019-08-29 | LX1011 | 11.1 | 371 | 11.1 | 372 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7632 | 1127.9997 | 116.9549
SYL-E.1.RR.1343.1 | 24543049155497 | Khadimnagar, Shahaporan R/A, Rd # B, H # 1 | 2019-09-04 | LX1011 | 15.1 | 1 | 15.1 | 2 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7680 | 1079.9997 | 159.1009
SYL-E.1.RR.1344.1 | 24542879155497 | Khadimnagar, Shahaporan R/A, Rd # B, H # 5 | 2019-09-04 | LX1011 | 4.5 | 3 | 4.5 | 4 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7680 | 1079.9997 | 47.4142
SYL-E.1.RR.1344.2 | 24542879155497 | Khadimnagar, Shahaporan R/A, Rd # B, H # 5 | 2022-06-07 | LU1001 | 52.8 | 196 | 52.8 | 197 | 2022-06-07 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 52.8 | 52.8 | 3.168 | 3.168 | 0.0007168 | 100% | 0% | 3.168 | 3.168 | 0.0011869 | 28 | 0.063508 | 0.063508 |  | 0 | 0 | 3912 | 1079.9997 | 317.0297
SYL-E.1.RR.1345.1 | 24542879155497 | Khadimnagar, Shahaporan R/A, Rd # B, H # 9 | 2019-09-04 | LX1011 | 15.9 | 5 | 15.9 | 6 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 7680 | 1079.9997 | 167.5301
SYL-E.1.RR.1346.1 | 24532319154117 | Noyabari, Mirapara, Burhan Uddin Road, Saidur Rahman | 2019-09-04 | LX1011 | 11.4 | 7 | 11.4 | 8 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7608 | 1151.9997 | 120.1159
SYL-E.1.RR.1347.1 | 24513919157069 | Golapganj, Hatimnagar, Turugbagh, Mosjid Road, Sayed Ahbab Ahmed | 2019-09-05 | LX1011 | 5 | 23 | 5 | 24 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7464 | 1295.9997 | 52.6824
SYL-E.1.RR.1348.1 | 24513919157069 | Golapganj, Hatimnagar, Turugbagh, Mosjid Road, Sayed Kholilur Rahman | 2019-09-05 | LX1011 | 12.6 | 25 | 12.6 | 26 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7464 | 1295.9997 | 132.7597
SYL-E.1.RR.1349.1 | 24513539157062 | Golapganj, Hatimnagar, Turugbagh, Mosjid Road, Sayed Saidur Rahman | 2019-09-05 | LX1011 | 22.3 | 27 | 22.3 | 28 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 7464 | 1295.9997 | 234.9635
SYL-E.1.RR.1350.1 | 24513509157038 | Golapganj, Hatimnagar, Turugbagh, Mosjid Road, Jakaria Akther | 2019-09-05 | LX1011 | 8.3 | 29 | 8.3 | 30 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7464 | 1295.9997 | 87.4528
SYL-E.1.RR.1351.1 | 24534119152582 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-14/1 | 2019-07-23 | NQ1009 | 10.8 | 161 | 10.8 | 162 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7512 | 1247.9997 | 113.794
SYL-E.1.RR.1351.2 | 24534119152582 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-14/1 | 2021-10-28 | LU1001 | 3.3 | 102 | 3.3 | 103 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7512 | 1247.9997 | 34.7704
SYL-E.1.RR.1352.1 | 24534139152588 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-15 | 2019-07-23 | NQ1009 | 4.7 | 163 | 4.7 | 164 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7512 | 1247.9997 | 49.5215
SYL-E.1.RR.1353.1 | 24533859153006 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-23/2 | 2019-07-23 | NQ1009 | 10 | 165 | 10 | 166 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7512 | 1247.9997 | 105.3648
SYL-E.1.RR.1354.1 | 24533749152574 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Uddipon-24/9 | 2019-07-23 | NQ1009 | 11.2 | 167 | 11.2 | 168 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7512 | 1247.9997 | 118.0086
SYL-E.1.RR.1355.1 | 24533879152534 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Jame Mosjid | 2019-07-23 | NQ1009 | 9.3 | 169 | 9.3 | 170 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7512 | 1247.9997 | 97.9893
SYL-E.1.RR.1356.1 | 24533879152534 | Sylhet Sodor, Miara bazar,Uddipon Road # 1, Jame Mosjid | 2019-07-23 | NQ1009 | 10.1 | 171 | 9.7 | 172 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7512 | 1247.9997 | 102.2039
SYL-E.1.RR.1357.1 | 24554439158059 | Khadim Nagar, Sha Sundor Road, Pirer Bazar, Genaral Iron | 2019-07-24 | NQ1009 | 37.1 | 204 | 37.1 | 205 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 37.1 | 37.1 | 2.226 | 2.226 | 0.0007168 | 100% | 0% | 2.226 | 2.226 | 0.0011869 | 28 | 0.044624 | 0.044624 |  | 0 | 0 | 7800 | 959.9997 | 390.9035
SYL-E.1.RR.1358.1 | 24554489158034 | Khadim Nagar, Sha Sundor Road, Pirer Bazar, Unayted R/A, Nojiruddin | 2019-07-24 | NQ1009 | 10.5 | 206 | 10.5 | 207 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7800 | 959.9997 | 110.6331
SYL-E.1.RR.1359.1 | 24554579158044 | Khadim Nagar, Sha Sundor Road, Pirer Bazar, Unayted R/A, Luthfar Kotir | 2019-07-24 | NQ1009 | 20.2 | 208 | 20.2 | 209 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 20.2 | 20.2 | 1.212 | 1.212 | 0.0007168 | 100% | 0% | 1.212 | 1.212 | 0.0011869 | 28 | 0.024296 | 0.024296 |  | 0 | 0 | 7800 | 959.9997 | 212.8369
SYL-E.1.RR.1360.1 | 24554609158045 | Khadim Nagar, Sha Sundor Road, Pirer Bazar, Unayted R/A, Mehedi Hossen | 2019-07-24 | NQ1009 | 11.8 | 210 | 11.8 | 211 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7800 | 959.9997 | 124.3305
SYL-E.1.RR.1361.1 | 24554779158042 | Khadim Nagar, Sha Sundor Road, Pirer Bazar, Unayted R/A, Saleh Ahmmed | 2019-07-24 | NQ1009 | 31.5 | 212 | 31.5 | 213 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 31.5 | 31.5 | 1.89 | 1.89 | 0.0007168 | 100% | 0% | 1.89 | 1.89 | 0.0011869 | 28 | 0.037888 | 0.037888 |  | 0 | 0 | 7800 | 959.9997 | 331.8992
SYL-E.1.RR.1362.1 | 24554389158031 | Khadim Nagar, Sha Sundor Road, Pirer Bazar, Chowdhury Villa | 2019-07-24 | NQ1009 | 9.1 | 214 | 9.1 | 215 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7800 | 959.9997 | 95.882
SYL-E.1.RR.1363.1 | 24554389158031 | Khadim Nagar, Sha Sundor Road, Pirer Bazar, Chowdhury Villa | 2019-07-24 | NQ1009 | 5.6 | 216 | 5.6 | 217 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7800 | 959.9997 | 59.0043
SYL-E.1.RR.1364.1 | 24561699159178 | Shaparan, Jalalabad Cantonment ,Batessor ,Kresna Rani | 2019-07-27 | NQ1009 | 8 | 276 | 8 | 277 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7800 | 959.9997 | 84.2919
SYL-E.1.RR.1365.1 | 24561699159178 | Shaparan, Jalalabad Cantonment ,Batessor ,Kresna Rani | 2019-07-27 | NQ1009 | 7.5 | 278 | 7.5 | 279 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7800 | 959.9997 | 79.0236
SYL-E.1.RR.1365.2 | 24561699159178 | Shaparan, Jalalabad Cantonment ,Batessor ,Kresna Rani | 2021-02-23 | MN1018 | 6 | 148 | 6 | 149 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7800 | 959.9997 | 63.2189
SYL-E.1.RR.1366.1 | 24561719159258 | Shaparan, Jalalabad Cantonment ,Londony Road ,Abdul Aziz | 2019-07-27 | NQ1009 | 10.9 | 280 | 10.9 | 281 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7800 | 959.9997 | 114.8476
SYL-E.1.RR.1367.1 | 24561699159240 | Shaparan, Jalalabad Cantonment ,Londony Road ,Dr. Bojlu | 2019-07-27 | NQ1009 | 9.4 | 282 | 9.4 | 283 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7800 | 959.9997 | 99.0429
SYL-E.1.RR.1368.1 | 24561649159242 | Shaparan, Jalalabad Cantonment ,Londony Road , Alomgir | 2019-07-27 | NQ1009 | 12.1 | 284 | 12.1 | 285 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7800 | 959.9997 | 127.4914
SYL-E.1.RR.1369.1 | 24561549159240 | Shaparan, Jalalabad Cantonment ,Londony Road , Harun Vabon | 2019-07-27 | NQ1009 | 8.6 | 286 | 8.6 | 287 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7800 | 959.9997 | 90.6137
SYL-E.1.RR.1370.1 | 24561369159262 | Shaparan, Jalalabad Cantonment ,Londony Road , Altaful Haque | 2019-07-27 | NQ1009 | 12.7 | 288 | 12.7 | 289 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7800 | 959.9997 | 133.8133
SYL-E.1.RR.1371.1 | 24561749159231 | Shaparan, Cantonment ,Tamabil Hwy Road , Najiuddin | 2019-07-27 | NQ1009 | 11.2 | 290 | 11.3 | 291 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7800 | 959.9997 | 119.0622
SYL-E.1.RR.1372.1 | 24562119159315 | Shaparan, Cantonment ,Tamabil Hwy Road , Asraf Ali | 2019-07-27 | NQ1009 | 5.6 | 292 | 5.6 | 293 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7800 | 959.9997 | 59.0043
SYL-E.1.RR.1373.1 | 24562259159334 | Shaparan, Cantonment ,Tamabil Hwy Road , Syed Ali | 2019-07-27 | NQ1009 | 5.8 | 294 | 6 | 295 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7800 | 959.9997 | 63.2189
SYL-E.1.RR.1374.1 | 25001699202320 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Iqbal Uddin | 2019-07-28 | NQ1009 | 9.3 | 322 | 9.3 | 323 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7776 | 983.9997 | 97.9893
SYL-E.1.RR.1374.2 | 25001699202320 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Iqbal Uddin | 2019-07-28 | NQ1009 | 13 | 324 | 13 | 325 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7776 | 983.9997 | 136.9743
SYL-E.1.RR.1375.1 | 25001639202300 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Abdul Mazid | 2019-07-28 | NQ1009 | 6 | 326 | 6 | 327 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7776 | 983.9997 | 63.2189
SYL-E.1.RR.1376.1 | 25001639202300 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Abdul Mazid | 2019-07-28 | NQ1009 | 7.8 | 328 | 7.8 | 329 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7776 | 983.9997 | 82.1846
SYL-E.1.RR.1377.1 | 25001639202300 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Abdul Mazid | 2019-07-28 | NQ1009 | 4.5 | 330 | 4.5 | 331 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7776 | 983.9997 | 47.4142
SYL-E.1.RR.1377.2 | 25001639202300 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Abdul Mazid | 2020-10-21 | NQ1002 | 9 | 297 | 9 | 298 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7776 | 983.9997 | 94.8283
SYL-E.1.RR.1378.1 | 25001639202300 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Abdul Mazid | 2019-07-28 | NQ1009 | 11.3 | 332 | 11.3 | 333 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7776 | 983.9997 | 119.0622
SYL-E.1.RR.1378.2 | 25001639202300 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Abdul Mazid | 2020-10-21 | NQ1002 | 4.1 | 299 | 4.1 | 300 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7776 | 983.9997 | 43.1996
SYL-E.1.RR.1379.1 | 25001789202315 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Shaduddin | 2019-07-28 | NQ1009 | 12.1 | 334 | 12.1 | 335 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7776 | 983.9997 | 127.4914
SYL-E.1.RR.1380.1 | 25001999202318 | Hemubato para ,Hemu Majortal Road ,Ward#02 ,Abdul Motin | 2019-07-28 | NQ1009 | 4.8 | 336 | 4.8 | 337 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7776 | 983.9997 | 50.5751
SYL-E.1.RR.1381.1 | 24534159154517 | Mejortila, South Islampur, Falguni R/A, H # 56/1 | 2019-08-28 | LX1011 | 26.6 | 325 | 26.6 | 326 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 26.6 | 26.6 | 1.596 | 1.596 | 0.0007168 | 100% | 0% | 1.596 | 1.596 | 0.0011869 | 28 | 0.031994 | 0.031994 |  | 0 | 0 | 7656 | 1103.9997 | 280.2704
SYL-E.1.RR.1382.1 | 24534039154519 | Mejortila, South Islampur, Falguni R/A, H # 55 | 2019-08-28 | LX1011 | 9.9 | 327 | 9.9 | 328 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7656 | 1103.9997 | 104.3112
SYL-E.1.RR.1383.1 | 24534149154522 | Mejortila, South Islampur, Falguni R/A, H # 56 | 2019-08-28 | LX1011 | 12 | 329 | 12 | 330 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7656 | 1103.9997 | 126.4378
SYL-E.1.RR.1384.1 | 24534709155049 | Mejortila, Nupur R/A, H # 3 | 2019-08-29 | LX1011 | 9.3 | 353 | 9.3 | 354 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7656 | 1103.9997 | 97.9893
SYL-E.1.RR.1385.1 | 24534709155049 | Mejortila, Nupur R/A, H # 5 | 2019-08-29 | LX1011 | 11.2 | 355 | 11.2 | 356 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7656 | 1103.9997 | 118.0086
SYL-E.1.RR.1386.1 | 24534709155049 | Mejortila, Nupur R/A, H # 33 | 2019-08-29 | LX1011 | 12 | 357 | 12 | 358 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7656 | 1103.9997 | 126.4378
SYL-E.1.RR.1387.1 | 24534739155059 | Mejortila, Nupur R/A, H # 8 | 2019-08-29 | LX1011 | 9.8 | 359 | 9.8 | 360 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7656 | 1103.9997 | 103.2575
SYL-E.1.RR.1388.1 | 24534799155084 | Mejortila, Nupur R/A, Moloy Chorkroborty | 2019-08-29 | LX1011 | 7.3 | 361 | 7.3 | 362 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7656 | 1103.9997 | 76.9163
SYL-E.1.RR.1389.1 | 24542249155445 | Khadim nagar, Nipobon R/A, Road # 2/2, H # 1, Ashok Ali | 2019-09-04 | MN1032 | 14.3 | 1 | 14.3 | 2 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7680 | 1079.9997 | 150.6717
SYL-E.1.RR.1390.1 | 24535459154013 | Sylhet, Tilagor, Gopaltila R/A, Somdha Rani | 2019-09-04 | NQ1008 | 5 | 21 | 5 | 22 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7752 | 1007.9997 | 52.6824
SYL-E.1.RR.1391.1 | 24535489154024 | Sylhet, Tilagor, Gopaltila R/A, Opurbo Chondro | 2019-09-04 | NQ1008 | 5.4 | 23 | 5.2 | 24 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7752 | 1007.9997 | 54.7897
SYL-E.1.RR.1401.1 | 24533889155069 | Debpur, Nathpara, Uttara R/A, Naresh Chandro Debnath, H # 165 | 2019-08-29 | NQ1003 | 19.9 | 497 | 19.9 | 498 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0 | 7656 | 1103.9997 | 209.676
SYL-E.1.RR.1402.1 | 24533979155067 | Debpur, Nathpara, Uttara R/A, Block-D, Dilip Kanto Ray, H # 165/1 | 2019-08-29 | NQ1003 | 6.7 | 499 | 6.7 | 500 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7656 | 1103.9997 | 70.5944
SYL-E.1.RR.1403.1 | 24533989155040 | Debpur, Nathpara, Uttara R/A, Block-D, Aftab Ali | 2019-08-29 | NQ1003 | 4.6 | 501 | 4.6 | 502 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7656 | 1103.9997 | 48.4678
SYL-E.1.RR.1403.2 | 24533989155040 | Debpur, Nathpara, Uttara R/A, Block-D, Aftab Ali | 2019-08-29 | NQ1003 | 12.5 | 503 | 13.1 | 504 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7656 | 1103.9997 | 138.0279
SYL-E.1.RR.1404.1 | 24534369155017 | Debpur, Uttara R/A, Block-B, Probir Dey, H # 86 | 2019-08-29 | NQ1003 | 11 | 505 | 11 | 506 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7656 | 1103.9997 | 115.9013
SYL-E.1.RR.1405.1 | 24534999154574 | Majortila, Islampur, Nurpur R/A, Nagar Monjil, H # 8 | 2019-08-29 | NQ1003 | 10.3 | 507 | 10.3 | 508 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7656 | 1103.9997 | 108.5258
SYL-E.1.RR.1405.2 | 24534999154574 | Majortila, Islampur, Nurpur R/A, Nagar Monjil, H # 8 | 2021-02-17 | LX1011 | 11.9 | 145 | 11.9 | 146 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7656 | 1103.9997 | 125.3841
SYL-E.1.RR.1406.1 | 24534789154571 | Majortila, Islampur, Nurpur R/A, Nironjon, H # 13 | 2019-08-29 | NQ1003 | 7.7 | 509 | 7.2 | 510 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7656 | 1103.9997 | 75.8627
SYL-E.1.RR.1407.1 | 24535169154564 | Majortila, Islampur, Nurpur R/A, Hazi Chomok Ali Khan, H # 6/A | 2019-08-29 | NQ1003 | 13.3 | 511 | 13.3 | 512 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7656 | 1103.9997 | 140.1352
SYL-E.1.RR.1416.1 | 24544599156505 | Khadimnogor, Surma Gate, Alibugh, Social Girls Rehabiliation Center | 2019-08-31 | NQ1008 | 3.1 | 241 | 3.1 | 242 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7632 | 1127.9997 | 32.6631
SYL-E.1.RR.1417.1 | 24531149154116 | Mirapara, Mirapara R/A, Block - A, H # 130, Md. Ataur Rahman | 2019-09-04 | LX1011 | 3.8 | 11 | 3.8 | 12 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-E.1.RR.1418.1 | 24531029154128 | Mirapara, Mirapara R/A, Block - B, H # 162, Shirin Monjil | 2019-09-04 | LX1011 | 6 | 13 | 6 | 14 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7464 | 1295.9997 | 63.2189
SYL-E.1.RR.1419.1 | 24523679154168 | Kushighat, Mirer Chok, Borhan Uddin Road, Abdul Motin | 2019-09-04 | LX1011 | 13 | 15 | 13 | 16 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7464 | 1295.9997 | 136.9743
SYL-E.1.RR.1420.1 | 24523359154203 | Kushighat, Mirer Chok, Borhan Uddin Road, Azam | 2019-09-04 | LX1011 | 6.8 | 19 | 6.8 | 20 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7464 | 1295.9997 | 71.6481
SYL-E.1.RR.1421.1 | 24523249154338 | Kushighat, Mirer Chok, Borhan Uddin Road, Abdur Rahman | 2019-09-04 | LX1011 | 12.2 | 21 | 11.7 | 22 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7464 | 1295.9997 | 123.2768
SYL-E.1.RR.1422.1 | 24524459154080 | East Kushighat, Kushighat Bazar, Sirajul Islam | 2019-09-05 | LX1011 | 2.6 | 33 | 2.6 | 34 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7464 | 1295.9997 | 27.3949
SYL-E.1.RR.1423.1 | 24524089153465 | Kushighat, Borhanabad, Syed Borhanuddin Road, Md. Mustak Ahmed | 2019-09-05 | LX1011 | 4.1 | 35 | 4.1 | 36 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7464 | 1295.9997 | 43.1996
SYL-E.1.RR.1424.1 | 24523849153323 | Kushighat, Noagaon, Burhanuddin Road, Asha - 54, Kholil Monjil | 2019-09-05 | LX1011 | 8.3 | 37 | 8.3 | 38 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7464 | 1295.9997 | 87.4528
SYL-E.1.RR.1425.1 | 24524699153320 | East Shadatikor, Asha R/A, H # 46, Sayesta Mia | 2019-09-05 | LX1011 | 15.2 | 39 | 14.5 | 40 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7464 | 1295.9997 | 152.779
SYL-E.1.RR.1441.1 | 24540179153568 | Sylhet, Tilagor, Gopaltila R/A, Rd # 2 ,H # 57, Surendro Malakar | 2019-09-04 | NQ1008 | 7.7 | 1 | 7.7 | 2 | 2022-01-01 | [9 empty] | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0
SYL-E.1.RR.1442.1 | 24540059153568 | Sylhet, Tilagor, Gopaltila R/A, Rd # 2, Fatirunnesa | 2019-09-04 | NQ1008 | 3.4 | 3 | 3.4 | 4 | 2022-01-01 | 2022-11-20 | NQ1007 | 0.8 | 167 | 0.8 | 168 | 2022-11-20 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7752 | 1007.9997
SYL-E.1.RR.1443.1 | 24535839153597 | Sylhet, Tilagor, Gopaltila R/A, Rd # 1, H # 41, Roma Kanto Deb | 2019-09-04 | NQ1008 | 6.2 | 5 | 6.2 | 6 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7752 | 1007.9997 | 65.3262
SYL-E.1.RR.1444.1 | 24535839153597 | Sylhet, Tilagor, Gopaltila R/A, Rd # 1, H # 41, Roma Kanto Deb | 2019-09-04 | NQ1008 | 4.2 | 7 | 4.2 | 8 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7752 | 1007.9997 | 44.2532
SYL-E.1.RR.1445.1 | 24535749153596 | Sylhet, Tilagor, Gopaltila R/A, Rd # 1, Ronjit Chokroborty / Nirmola Kutir | 2019-09-04 | NQ1008 | 5.3 | 9 | 5.3 | 10 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7752 | 1007.9997 | 55.8434
SYL-E.1.RR.1446.1 | 24535749153596 | Sylhet, Tilagor, Gopaltila R/A, Rd # 1, Ronjit Chokroborty / Nirmola Kutir | 2019-09-04 | NQ1008 | 2.7 | 11 | 2.7 | 12 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7752 | 1007.9997 | 28.4485
SYL-E.1.RR.1447.1 | 24535729153596 | Sylhet, Tilagor, Gopaltila R/A, Rd # 1, Kumar Babu | 2019-09-04 | NQ1008 | 10.3 | 13 | 10.3 | 14 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7752 | 1007.9997 | 108.5258
SYL-E.1.RR.1448.1 | 24535489153577 | Sylhet, Tilagor, Gopaltila R/A, Rd # 1, Bijoy Das | 2019-09-04 | NQ1008 | 4 | 15 | 4 | 16 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7752 | 1007.9997 | 42.1459
SYL-E.1.RR.1449.1 | 24535459154013 | Sylhet, Tilagor, Gopaltila R/A, Taposh Pal | 2019-09-04 | NQ1008 | 24.8 | 17 | 24.8 | 18 | 2022-01-01 | 2022-11-20 | NQ1007 |  |  | 0 | 173 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7752 | 1007.9997
SYL-E.1.RR.1450.1 | 24535459154013 | Sylhet, Tilagor, Gopaltila R/A, Benu Chondro | 2019-09-04 | NQ1008 | 3.6 | 19 | 3.6 | 20 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7752 | 1007.9997 | 37.9313
SYL-E.1.RR.1451.1 | 24540389153576 | M.C College Road, Madanibag R/A, H # 76/1 A | 2019-09-04 | NQ1008 | 6.2 | 41 | 6.2 | 42 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7752 | 1007.9997 | 65.3262
SYL-E.1.RR.1452.1 | 24544789155572 | Shahporan Gate, Bahubal R/A, Block-A, Rd # 1, H # 14 | 2019-09-05 | NQ1008 | 2.5 | 61 | 2.3 | 62 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7776 | 983.9997 | 24.2339
SYL-E.1.RR.1453.1 | 24544789155579 | Shahporan Gate, Bahubal R/A, Block-A, Rd # 1, H # 15 | 2019-09-05 | NQ1008 | 11.3 | 65 | 11.3 | 66 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7776 | 983.9997 | 119.0622
SYL-E.1.RR.1454.1 | 24544909155565 | Shahporan Gate, Bahubal R/A, Block-A, Rd # 1, H # 18 | 2019-09-05 | NQ1008 | 24.4 | 67 | 24.1 | 68 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 24.1 | 24.1 | 1.446 | 1.446 | 0.0007168 | 100% | 0% | 1.446 | 1.446 | 0.0011869 | 28 | 0.028987 | 0.028987 |  | 0 | 0 | 7776 | 983.9997 | 253.9292
SYL-E.1.RR.1455.1 | 24545379155518 | Khadim Nagar, Bahubol R/A, H # 5, Shamima Akter Rina | 2019-09-11 | NQ1008 | 34.3 | 105 | 33.8 | 106 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 33.8 | 33.8 | 2.028 | 2.028 | 0.0007168 | 100% | 0% | 2.028 | 2.028 | 0.0011869 | 28 | 0.040654 | 0.040654 |  | 0 | 0 | 7776 | 983.9997 | 356.1331
SYL-E.1.RR.1456.1 | 24545389155517 | Khadim Nagar, Bahubol R/A, Islam Uddin | 2019-09-11 | NQ1008 | 13 | 107 | 13 | 108 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7776 | 983.9997 | 136.9743
SYL-E.1.RR.1457.1 | 24545499155513 | Khadim Nagar, Bahubol R/A, Mamun | 2019-09-11 | NQ1008 | 20 | 109 | 20 | 110 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 7776 | 983.9997 | 210.7296
SYL-E.1.RR.1458.1 | 24522949155169 | Sylhet, Shahporan, Muktirchok, Surma Nandi | 2019-09-05 | NQ1008 | 5.2 | 57 | 5.2 | 58 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7464 | 1295.9997 | 54.7897
SYL-E.1.RR.1459.1 | 24522969155148 | Sylhet, Shahporan, Muktirchok, Abdul Jalil | 2019-09-05 | NQ1008 | 3.9 | 59 | 3.9 | 60 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7464 | 1295.9997 | 41.0923
SYL-E.1.RR.1511.1 | 24514399156541 | Turuk bag, Poschim Para,Islam Mia | 2019-09-05 | MN1032 | 12.4 | 17 | 12.5 | 18 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7464 | 1295.9997 | 131.706
SYL-E.1.RR.1512.1 | 24513969156538 | Turuk bag, Poschim Para, Harun Mia | 2019-09-05 | MN1032 | 10.8 | 19 | 10.5 | 20 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7464 | 1295.9997 | 110.6331
SYL-E.1.RR.1513.1 | 24513969156538 | Turuk bag, Poschim Para, Sana Mia | 2019-09-05 | MN1032 | 3.8 | 21 | 3.8 | 22 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-E.1.RR.1514.1 | 24513589156527 | Turuk bag, Poschim Para, Md.Shahab Uddin | 2019-09-05 | MN1032 | 29.2 | 23 | 29.2 | 24 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 29.2 | 29.2 | 1.752 | 1.752 | 0.0007168 | 100% | 0% | 1.752 | 1.752 | 0.0011869 | 28 | 0.035122 | 0.035122 |  | 0 | 0 | 7464 | 1295.9997 | 307.6653
SYL-E.1.RR.1515.1 | 24513679156483 | Turuk bag, Poschim Para, Md.Gous | 2019-09-05 | MN1032 | 11.8 | 25 | 11.8 | 26 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7464 | 1295.9997 | 124.3305
SYL-E.1.RR.1516.1 | 24520289156179 | Pirer chok, Middle para, Rofiq Mia | 2019-09-05 | MN1032 | 6.2 | 27 | 6.1 | 28 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7464 | 1295.9997 | 64.2725
SYL-E.1.RR.1517.1 | 24515649156143 | Pirer chok, Middle para, Abdul Razzak | 2019-09-05 | MN1032 | 9.9 | 29 | 9.9 | 30 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7464 | 1295.9997 | 104.3112
SYL-E.1.RR.1551.1 | 24513929156586 | Sylhet, Golapganj, Turukbag, Ana Mia | 2019-09-05 | NQ1008 | 3.2 | 43 | 3.2 | 44 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7464 | 1295.9997 | 33.7167
SYL-E.1.RR.1552.1 | 24513769156583 | Sylhet, Golapganj, Turukbag, Cherag Mia | 2019-09-05 | NQ1008 | 2.8 | 45 | 2.8 | 46 | 2022-01-01 | 2022-11-08 | NQ1007 | 0.7 | 149 | 0.7 | 150 | 2022-11-08 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7464 | 1295.9997
SYL-E.1.RR.1553.1 | 24513429156585 | Sylhet, Golapganj, Turukbag, Sofiq Uddin | 2019-09-05 | NQ1008 | 7.8 | 47 | 7.8 | 48 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7464 | 1295.9997 | 82.1846
SYL-E.1.RR.1554.1 | 24513039156553 | Sylhet, Golapganj, Turukbag, Ali Akbor | 2019-09-05 | NQ1008 | 11.9 | 49 | 11.9 | 50 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7464 | 1295.9997 | 125.3841
SYL-E.1.RR.1555.1 | 24515099156347 | Sylhet, Golapganj, Nulua, Abdul Latif | 2019-09-05 | NQ1008 | 14 | 51 | 13.2 | 52 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7464 | 1295.9997 | 139.0816
SYL-E.1.RR.1556.1 | 24515039156347 | Sylhet, Golapganj, Nulua, Hosen Ali | 2019-09-05 | NQ1008 | 4.3 | 53 | 4.3 | 54 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7464 | 1295.9997 | 45.3069
SYL-E.1.RR.1557.1 | 24514759156339 | Sylhet, Golapganj, Nulua, Nuru Islam | 2019-09-05 | NQ1008 | 28.3 | 55 | 28.3 | 56 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 28.3 | 28.3 | 1.698 | 1.698 | 0.0007168 | 100% | 0% | 1.698 | 1.698 | 0.0011869 | 28 | 0.034039 | 0.034039 |  | 0 | 0 | 7464 | 1295.9997 | 298.1824
SYL-E.1.RR.1571.1 | 24523279155184 | Shahaporan, Muktirchak, Burhan Uddin Road, Moulobi Abdur Jobbar | 2019-09-05 | LX1011 | 9.3 | 31 | 9.3 | 32 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7464 | 1295.9997 | 97.9893
SYL-E.1.RR.1572.1 | 24533279154015 | Tilagor, Shaplabagh R/A, Block-B, Road # 2, H # 35, Safu | 2019-09-11 | MN1032 | 17.8 | 85 | 17.8 | 86 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 7680 | 1079.9997 | 187.5494
SYL-E.1.RR.1573.1 | 24533919154061 | Tilagor, Shaplabagh R/A, Block-B, Road # 3, H # 2/1, Shammi Villa | 2019-09-11 | MN1032 | 10.3 | 89 | 10.3 | 90 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7680 | 1079.9997 | 108.5258
SYL-E.1.RR.1581.1 | 24532859154040 | Shaplabag R/A, Block - C, Rd # 2, H # 31/1 | 2019-09-11 | MN1032 | 14.3 | 87 | 14.3 | 88 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7608 | 1151.9997 | 150.6717
SYL-E.1.RR.1582.1 | 24533499154057 | Tilagor, Shaplabag R/A, Rd # 3, H # 21 | 2019-09-11 | MN1032 | 10 | 91 | 10.3 | 92 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7680 | 1079.9997 | 108.5258
SYL-E.1.RR.1583.1 | 24533499154057 | Tilagor, Shaplabag R/A, Rd # 3, H # 17, Ripon House | 2019-09-11 | MN1032 | 3.7 | 93 | 3.7 | 94 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7680 | 1079.9997 | 38.985
SYL-E.1.RR.1591.1 | 24545529155507 | Sylhet, Shahporan, Bahubol R/A, Ali Aktar Chowdhury | 2019-09-11 | NQ1008 | 4.5 | 111 | 4.5 | 112 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7776 | 983.9997 | 47.4142
SYL-E.1.RR.1592.1 | 24545889155497 | Sylhet, Shahporan, Bahubol R/A, Waliur Rohman | 2019-09-11 | NQ1008 | 10.4 | 113 | 10 | 114 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7776 | 983.9997 | 105.3648
SYL-E.1.RR.1593.1 | 24540969154001 | Sylhet, MC College Teachers Quarter | 2019-09-11 | NQ1008 | 7.2 | 115 | 7.2 | 116 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7752 | 1007.9997 | 75.8627
SYL-E.1.RR.1594.1 | 24541129154116 | Sylhet, Alurtola Road, Government Quarter | 2019-09-11 | NQ1008 | 6.9 | 117 | 6.9 | 118 | 2022-01-01 | [9 empty] | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0
SYL-E.1.RR.1595.1 | 24542879154024 | Sylhet, Krishi University, Shuhasini Hall | 2019-09-11 | NQ1008 | 4.4 | 119 | 4.4 | 120 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7752 | 1007.9997 | 46.3605
SYL-F.RR.1.1 | 24402959155563 | Fenchuganj, NGFFL, Faridpur, Boro Bari, Hazi Moinuddin | 2019-08-31 | MP1032 | 3 | 385 | 3 | 386 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6552 | 2207.9997 | 31.6094
SYL-F.RR.2.1 | 24403469156020 | Fenchuganj, NGFFL, Faridpur, Hazera Begum | 2019-08-31 | MP1032 | 11.1 | 387 | 10.4 | 388 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6552 | 2207.9997 | 109.5794
SYL-F.RR.2.2 | 24403469156020 | Fenchuganj, NGFFL, Faridpur, Hazera Begum | 2021-09-06 | LX1011 | 20.9 | 307 | 20.9 | 308 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 20.9 | 20.9 | 1.254 | 1.254 | 0.0007168 | 100% | 0% | 1.254 | 1.254 | 0.0011869 | 28 | 0.025138 | 0.025138 |  | 0 | 0 | 6552 | 2207.9997 | 220.2125
SYL-F.RR.3.1 | 24403099156039 | Fenchuganj, NGFFL, Faridpur, Tobarak Ali | 2019-08-31 | MP1032 | 4.6 | 391 | 4.6 | 392 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6552 | 2207.9997 | 48.4678
SYL-F.RR.4.1 | 24403099156039 | Fenchuganj, NGFFL, Faridpur, Ali Hossain | 2019-08-31 | MP1032 | 5.1 | 395 | 5.1 | 396 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6552 | 2207.9997 | 53.7361
SYL-F.RR.5.1 | 24401579156016 | Fenchuganj, NGFFL, Purba Karmada, Farhad | 2019-08-31 | MP1032 | 12 | 397 | 12.1 | 398 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6504 | 2255.9997 | 127.4914
SYL-F.RR.6.1 | 24401579156016 | Fenchuganj, NGFFL, Purba Karmda, Shamsuddin | 2019-08-31 | MP1032 | 2.3 | 399 | 2.3 | 400 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6504 | 2255.9997 | 24.2339
SYL-F.RR.7.1 | 24400369156019 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Mahendra Lal Das | 2019-09-01 | MP1032 | 2.2 | 409 | 2.3 | 410 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6504 | 2255.9997 | 24.2339
SYL-F.RR.8.1 | 24400499156047 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Sultan Mia | 2019-09-01 | MP1032 | 3.4 | 411 | 3.4 | 412 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6504 | 2255.9997 | 35.824
SYL-F.RR.9.1 | 24400499156047 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Sanu Mia | 2019-09-01 | MP1032 | 3 | 413 | 3 | 414 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6504 | 2255.9997 | 31.6094
SYL-F.RR.10.1 | 24400459156083 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Chittaranjan Chowdhury | 2019-09-01 | MP1032 | 10.6 | 415 | 10.6 | 416 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6504 | 2255.9997 | 111.6867
SYL-F.RR.11.1 | 24400459156083 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Girendra Kumar Dev | 2019-09-01 | MP1032 | 12.7 | 417 | 12.8 | 418 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6504 | 2255.9997 | 134.867
SYL-F.RR.12.1 | 24400589156091 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Zilu Mia | 2019-09-01 | MP1032 | 8.8 | 419 | 8.8 | 420 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 6504 | 2255.9997 | 92.721
SYL-F.RR.13.1 | 24400049156068 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Sanjit Roy | 2019-09-01 | MP1032 | 2 | 421 | 2 | 422 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6504 | 2255.9997 | 21.073
SYL-F.RR.14.1 | 24395699156083 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Salekul Haque | 2019-09-01 | MP1032 | 5.8 | 423 | 5.8 | 424 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 6504 | 2255.9997 | 61.1116
SYL-F.RR.15.1 | 24395929156119 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Md. Abdur Rahman | 2019-09-01 | MP1032 | 7 | 427 | 6.7 | 428 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6504 | 2255.9997 | 70.5944
SYL-F.RR.16.1 | 24394949156137 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Firoz Khan | 2019-09-02 | MP1032 | 5.5 | 443 | 5.1 | 444 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6504 | 2255.9997 | 53.7361
SYL-F.RR.17.1 | 24400499156129 | Fenchuganj, Shahjalal Shar Karkhana, Nijampur, Lokman Mia | 2019-09-02 | MP1032 | 12.4 | 445 | 12.4 | 446 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6504 | 2255.9997 | 130.6524
SYL-F.RR.18.1 | 24411559157177 | Fenchuganj, K.M. Tilla, Abdul Monnan | 2019-09-03 | MP1032 | 3 | 461 | 3 | 462 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6600 | 2159.9997 | 31.6094
SYL-F.RR.19.1 | 24411329157218 | Fenchuganj, Noa Tilla, Aktar Hossain | 2019-09-03 | MP1032 | 12.7 | 463 | 12.5 | 464 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6600 | 2159.9997 | 131.706
SYL-F.RR.20.1 | 24411749157264 | Fenchuganj, Noa Tilla, Bodrul Islam | 2019-09-03 | MP1032 | 4.2 | 465 | 4.2 | 466 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6600 | 2159.9997 | 44.2532
SYL-F.RR.21.1 | 24411749157264 | Fenchuganj, Noa Tilla, Moslekh | 2019-09-03 | MP1032 | 4.5 | 467 | 4.5 | 468 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 6600 | 2159.9997 | 47.4142
SYL-F.RR.22.1 | 24401189155358 | Fenchuganj, NGFFl, Karmada, Aftab | 2019-09-04 | MP1032 | 3.2 | 1 | 2.9 | 2 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6504 | 2255.9997 | 30.5558
SYL-F.RR.23.1 | 24401289155370 | Fenchuganj, NGFFl, Karmada, Siraj | 2019-09-04 | MP1032 | 11.5 | 3 | 11.3 | 4 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6504 | 2255.9997 | 119.0622
SYL-F.RR.23.2 | 24401289155370 | Fenchuganj, NGFFl, Karmada, Siraj | 2022-09-29 | MN1018 | 15.9 | 19 | 15.9 | 20 | 2022-09-29 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 0 | 2255.9997 | 43.1447
SYL-F.RR.24.1 | 24395759155429 | Fenchuganj, NGFFl, Kachua Bahar, Sonu Mia | 2019-09-04 | MP1032 | 13.3 | 5 | 13.3 | 6 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6504 | 2255.9997 | 140.1352
SYL-F.RR.25.1 | 24394289155468 | Fenchuganj, NGFFl, Kachua Bahar, Harun Mia | 2019-09-04 | MP1032 | 6.2 | 7 | 6.2 | 8 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6504 | 2255.9997 | 65.3262
SYL-F.RR.26.1 | 24400159155332 | Fenchuganj, Kochuabor, Pankhi Mia | 2019-09-05 | MP1032 | 8.5 | 13 | 8.5 | 14 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6504 | 2255.9997 | 89.5601
SYL-F.RR.27.1 | 24395389156206 | Fenchuganj, Nijampur, Redwan | 2019-09-05 | MP1032 | 10.9 | 15 | 10.9 | 16 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6504 | 2255.9997 | 114.8476
SYL-F.RR.27.2 | 24395389156206 | Fenchuganj, Nijampur, Redwan | 2019-09-05 | MP1032 | 13.5 | 17 | 13.5 | 18 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6504 | 2255.9997 | 142.2425
SYL-F.RR.28.1 | 24395389156206 | Fenchuganj, Nijampur, Sufian | 2019-09-05 | MP1032 | 11.4 | 19 | 11.4 | 20 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6504 | 2255.9997 | 120.1159
SYL-F.RR.29.1 | 24395859156254 | Fenchuganj, Nijampur, Mahmud Ali | 2019-09-05 | MP1032 | 12.8 | 21 | 12.7 | 22 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6504 | 2255.9997 | 133.8133
SYL-F.RR.51.1 | 24401249155545 | Fenchugonj, East Kormoda, Bijoy Mala | 2019-08-31 | MP1032 | 8.6 | 401 | 8.3 | 402 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6504 | 2255.9997 | 87.4528
SYL-F.RR.52.1 | 24400659155585 | Fenchugonj, Nijampur, Bijit | 2019-08-31 | MP1032 | 5.4 | 403 | 5.4 | 404 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6504 | 2255.9997 | 56.897
SYL-F.RR.53.1 | 24400119155559 | Fenchugonj, Nijampur, Ajay | 2019-08-31 | MP1032 | 8.9 | 405 | 8.9 | 406 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6504 | 2255.9997 | 93.7747
SYL-F.RR.54.1 | 24400149156009 | Fenchugonj, Nijampur, Serajul | 2019-08-31 | MP1032 | 11.5 | 407 | 11.5 | 408 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6504 | 2255.9997 | 121.1695
SYL-F.RR.55.1 | 24394759156075 | Fenchuganj, Nijampur, Abu Bakkar | 2019-09-01 | MP1032 | 11.2 | 429 | 11.2 | 430 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6504 | 2255.9997 | 118.0086
SYL-F.RR.56.1 | 24394529156062 | Fenchuganj, Nijampur, Ibrahim | 2019-09-01 | MP1032 | 7.3 | 431 | 7.3 | 432 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6504 | 2255.9997 | 76.9163
SYL-F.RR.56.2 | 24394529156062 | Fenchuganj, Nijampur, Ibrahim | 2021-01-18 | LX1011 | 1.4 | 24 | 1.4 | 25 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 6504 | 2255.9997 | 14.7511
SYL-F.RR.57.1 | 24394529156062 | Fenchuganj, Nijampur, Idris Mia | 2019-09-01 | MP1032 | 25.7 | 433 | 25.7 | 434 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 25.7 | 25.7 | 1.542 | 1.542 | 0.0007168 | 100% | 0% | 1.542 | 1.542 | 0.0011869 | 28 | 0.030912 | 0.030912 |  | 0 | 0 | 6504 | 2255.9997 | 270.7876
SYL-F.RR.58.1 | 24394799156093 | Fenchuganj, Nijampur, Alamgir | 2019-09-01 | MP1032 | 17.4 | 435 | 17.4 | 436 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 6504 | 2255.9997 | 183.3348
SYL-F.RR.59.1 | 24395019156122 | Fenchuganj, Nijampur, Lokman | 2019-09-01 | MP1032 | 13.3 | 437 | 13.3 | 438 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 6504 | 2255.9997 | 140.1352
SYL-F.RR.60.1 | 24394759156141 | Fenchuganj, Nijampur, Gaisuddin | 2019-09-01 | MP1032 | 6.6 | 439 | 6.6 | 440 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 6504 | 2255.9997 | 69.5408
SYL-F.RR.61.1 | 24411099156162 | Fenchuganj, Fokirbari, Nur Islam | 2019-09-02 | MP1032 | 12.6 | 447 | 12.6 | 448 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6552 | 2207.9997 | 132.7597
SYL-F.RR.62.1 | 24410119156187 | Fenchuganj, Fokirpara, Nur Islam | 2019-09-02 | MP1032 | 6.2 | 449 | 6.2 | 450 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6552 | 2207.9997 | 65.3262
SYL-F.RR.63.1 | 24410849157116 | Fenchuganj, Maijgaon, Beside Sonali Bank | 2019-09-02 | MP1032 | 2.9 | 451 | 2.9 | 452 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 6600 | 2159.9997 | 30.5558
SYL-F.RR.64.1 | 24411229157104 | Fenchuganj, Maijgaon, South Bazar, Sukel | 2019-09-02 | MP1032 | 11.1 | 453 | 11.1 | 454 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6600 | 2159.9997 | 116.9549
SYL-F.RR.65.1 | 24411529157072 | Fenchuganj, Maijgaon, South Bazar, Abdul Haq | 2019-09-02 | MP1032 | 6.1 | 457 | 6.1 | 458 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6600 | 2159.9997 | 64.2725
SYL-F.RR.66.1 | 24411569157060 | Fenchuganj, Maijgaon, South Bazar, Tofodar Villa | 2019-09-02 | MP1032 | 27.1 | 459 | 27.1 | 460 | 2022-01-01 | [9 empty] | 27.1 | 27.1 | 1.626 | 1.626 | 0.0007168 | 100% | 0% | 1.626 | 1.626 | 0.0011869 | 28 | 0.032596 | 0.032596 |  | 0 | 0
SYL-F.RR.67.1 | 24413699157285 | Fenchuganj, Maijgoan, K M Tila, Jabed Ali | 2019-09-03 | MP1032 | 4.9 | 469 | 4.9 | 470 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6600 | 2159.9997 | 51.6288
SYL-F.RR.68.1 | 24413699157285 | Fenchuganj, Maijgoan, K M Tila, Md Potik Mia | 2019-09-03 | MP1032 | 3.8 | 471 | 3.8 | 472 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6600 | 2159.9997 | 40.0386
SYL-F.RR.69.1 | 24413189157256 | Fenchuganj, Maijgoan, K M Tila, Amir Ali | 2019-09-03 | MP1032 | 16.4 | 473 | 17.1 | 474 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 6600 | 2159.9997 | 180.1738
SYL-F.RR.70.1 | 24420369157210 | Fenchuganj, Schattish, Ayan Ali | 2019-09-03 | MP1032 | 4.1 | 475 | 4.1 | 476 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6576 | 2183.9997 | 43.1996
SYL-F.RR.70.2 | 24420369157210 | Fenchuganj, Schattish, Ayan Ali | 2019-09-03 | MP1032 | 2.3 | 477 | 2.3 | 478 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6576 | 2183.9997 | 24.2339
SYL-F.RR.70.3 | 24420369157210 | Fenchuganj, Schattish, Ayan Ali | 2019-09-03 | MP1032 | 7.5 | 479 | 7.5 | 480 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6576 | 2183.9997 | 79.0236
SYL-F.RR.71.1 | 24413539156001 | Fenchugonj, Mominpur, Shakir Ali | 2019-09-04 | MP1032 | 11.5 | 9 | 11.5 | 10 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6552 | 2207.9997 | 121.1695
SYL-F.RR.72.1 | 24410639155059 | Fenchuganj, Fenchuganj Combined Cycle Power Plant, Near PDB Ansar Camp, Padma Residential Building | 2019-09-05 | MP1032 | 11.8 | 23 | 11.8 | 24 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6504 | 2255.9997 | 124.3305
SYL-F.RR.73.1 | 24410699155077 | Fenchuganj, Fenchuganj Combined Cycle Power Plant, Near PDB Ansar Camp, Khoai Residential Building | 2019-09-05 | MP1032 | 8.5 | 25 | 8.5 | 26 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 6504 | 2255.9997 | 89.5601
SYL-F.RR.74.1 | 24410479155102 | Fenchuganj, Fenchuganj Combined Cycle Power Plant, Near PDB Ansar Camp, Shurma Residential Building | 2019-09-05 | MP1032 | 58.3 | 27 | 58.3 | 28 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 58.3 | 58.3 | 3.498 | 3.498 | 0.0007168 | 100% | 0% | 3.498 | 3.498 | 0.0011869 | 28 | 0.070123 | 0.070123 |  | 0 | 0 | 6504 | 2255.9997 | 614.2769
SYL-F.RR.101.1 | 24410459155569 | Fensuganj, North Foridpur, Nurpur Road, Sirajul Islam | 2019-08-31 | NQ1005 | 8.1 | 326 | 8.1 | 327 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6552 | 2207.9997 | 85.3455
SYL-F.RR.101.2 | 24410459155569 | Fensuganj, North Foridpur, Nurpur Road, Sirajul Islam | 2021-01-20 | LX1011 | 12.7 | 30 | 12.5 | 31 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6552 | 2207.9997 | 131.706
SYL-F.RR.102.1 | 24410569156005 | Fensuganj, North Foridpur, Nurpur Road, Abdul Jabbar | 2019-08-31 | NQ1005 | 24.5 | 328 | 24.5 | 329 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 6552 | 2207.9997 | 258.1438
SYL-F.RR.103.1 | 24410499156030 | Fensuganj, North Foridpur, Nurpur Road, Mahatab Uddin | 2019-08-31 | NQ1005 | 12.4 | 330 | 12.4 | 331 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6552 | 2207.9997 | 130.6524
SYL-F.RR.104.1 | 24410539156043 | Fensuganj, North Foridpur, Nurpur Road, Mobasser Ali | 2019-08-31 | NQ1005 | 15.7 | 332 | 15.7 | 333 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 6552 | 2207.9997 | 165.4228
SYL-F.RR.105.1 | 24411539156034 | Fensuganj, Nurpur, Nurpur Road, Mukter Chowdhury | 2019-08-31 | NQ1005 | 12.9 | 334 | 12.9 | 335 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6552 | 2207.9997 | 135.9206
SYL-F.RR.106.1 | 24411689156023 | Fensuganj, Nurpur, Nurpur Road, Fornt of Dorgapur Govt. Primary School, Alauddin Chowdhury | 2019-08-31 | NQ1005 | 14.6 | 336 | 14.6 | 337 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 6552 | 2207.9997 | 153.8326
SYL-F.RR.107.1 | 24411629156146 | Fensuganj, Fokirpara, Fokirpara Road, Badrul Islam | 2019-08-31 | NQ1005 | 11.7 | 338 | 11.7 | 339 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6552 | 2207.9997 | 123.2768
SYL-F.RR.108.1 | 24411799156101 | Fensuganj, Fokirpara, Fokirpara Road, Zakir Hossen | 2019-08-31 | NQ1005 | 6.1 | 342 | 6.1 | 343 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 6552 | 2207.9997 | 64.2725
SYL-F.RR.109.1 | 24410619156576 | Fenchuganj, Maisegaon, 2 No Maisegaon Union Porishod Road, Johir Ali | 2019-09-01 | NQ1005 | 13 | 362 | 12.9 | 363 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6600 | 2159.9997 | 135.9206
SYL-F.RR.109.2 | 24410619156576 | Fenchuganj, Maisegaon, 2 No Maisegaon Union Porishod Road, Johir Ali | 2021-01-21 | LX1011 | 3.2 | 45 | 3.2 | 46 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6600 | 2159.9997 | 33.7167
SYL-F.RR.110.1 | 24405239156536 | Fenchuganj, Maisegaon, 2 No Maisegaon Union Porishod Road, Abdul Manik | 2019-09-02 | NQ1005 | 5.1 | 364 | 5.1 | 365 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6600 | 2159.9997 | 53.7361
SYL-F.RR.111.1 | 24405119156510 | Fenchuganj, Maisegaon, 2 No Maisegaon Union Porishod Road, Abdul Awal Koyes | 2019-09-02 | NQ1005 | 13.5 | 367 | 13.5 | 368 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 6600 | 2159.9997 | 142.2425
SYL-F.RR.111.2 | 24405119156510 | Fenchuganj, Maisegaon, 2 No Maisegaon Union Porishod Road, Abdul Awal Koyes | 2022-10-03 | MN1018 | 2.2 | 22 | 2.2 | 23 | 2022-10-03 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 0 | 2159.9997 | 5.7157
SYL-F.RR.112.1 | 24405119156510 | Fenchuganj, Maisegaon, 2 No Maisegaon Union Porishod Road, Tonjub Ali | 2019-09-02 | NQ1005 | 6.8 | 369 | 6.8 | 370 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6600 | 2159.9997 | 71.6481
SYL-F.RR.113.1 | 24410309157283 | Fenchuganj, Maisegaon, Shorifganj, Shorifganj Road, Abdul Munim | 2019-09-03 | NQ1005 | 13.3 | 386 | 13.2 | 387 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6600 | 2159.9997 | 139.0816
SYL-F.RR.114.1 | 24410309157283 | Fenchuganj, Maisegaon, Shorifganj, Shorifganj Road, Abdul Hoque | 2019-09-03 | NQ1005 | 22.9 | 388 | 22.6 | 389 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 22.6 | 22.6 | 1.356 | 1.356 | 0.0007168 | 100% | 0% | 1.356 | 1.356 | 0.0011869 | 28 | 0.027183 | 0.027183 |  | 0 | 0 | 6600 | 2159.9997 | 238.1245
SYL-F.RR.115.1 | 24410729157334 | Fenchuganj, Maisegaon, Golahat,Golahat Road, Tojomul Ali | 2019-09-03 | NQ1005 | 5.5 | 390 | 5.5 | 391 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 6600 | 2159.9997 | 57.9506
SYL-F.RR.116.1 | 24404839157409 | Fenchuganj, Maisegaon, Purangaon, Purangaon Road, Amir Ali | 2019-09-03 | NQ1005 | 13.4 | 392 | 13.4 | 393 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6600 | 2159.9997 | 141.1888
SYL-F.RR.117.1 | 24404839157409 | Fenchuganj, Maisegaon, Purangaon, Purangaon Road, Ikbal Hossen | 2019-09-03 | NQ1005 | 12.6 | 394 | 12.6 | 395 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6600 | 2159.9997 | 132.7597
SYL-F.RR.118.1 | 24404419157388 | Fenchuganj, Maisegaon, Purangaon, Purangaon Road, Belal Ahmed | 2019-09-03 | NQ1005 | 16.4 | 396 | 16.4 | 397 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 6600 | 2159.9997 | 172.7983
SYL-F.RR.118.2 | 24404419157388 | Fenchuganj, Maisegaon, Purangaon, Purangaon Road, Belal Ahmed | 2021-01-21 | LX1011 | 16.5 | 39 | 16.5 | 40 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 6600 | 2159.9997 | 173.8519
SYL-F.RR.119.1 | 24405259157271 | Fenchuganj, Maisegaon, Shorifganj, Mollatila, Srity Nibas, Lavlu Mia | 2019-09-04 | NQ1005 | 12.2 | 1 | 12.2 | 2 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6600 | 2159.9997 | 128.5451
SYL-F.RR.120.1 | 24405219157275 | Fenchuganj, Maisegaon, Shorifganj, Mollatila, Hero Child Pre-Caded Academy, Sagorika | 2019-09-04 | NQ1005 | 12.8 | 3 | 12.8 | 4 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 6600 | 2159.9997 | 134.867
SYL-F.RR.121.1 | 24394479156225 | Fenchuganj, Puranbazar, Sarkarkhana, Puranbazar Masjid Road, Mim Villa, Taher | 2019-09-05 | NQ1005 | 19.9 | 17 | 19.9 | 18 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 19.9 | 19.9 | 1.194 | 1.194 | 0.0007168 | 100% | 0% | 1.194 | 1.194 | 0.0011869 | 28 | 0.023936 | 0.023936 |  | 0 | 0 | 6504 | 2255.9997 | 209.676
SYL-F.RR.122.1 | 24394519156232 | Fenchuganj, Puranbazar, Sarkarkhana, Puranbazar Masjid Road, Anamul Korim | 2019-09-05 | NQ1005 | 16.1 | 19 | 16.1 | 20 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 6504 | 2255.9997 | 169.6373
SYL-F.RR.123.1 | 24394459156255 | Fenchuganj, Puranbazar, Sarkarkhana, Near Puranbazar Masjid, Raja Mia | 2019-09-05 | NQ1005 | 8.7 | 21 | 8.7 | 22 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6504 | 2255.9997 | 91.6674
SYL-F.RR.124.1 | 24394599156266 | Fenchuganj, Puranbazar, Sarkarkhana, Puranbazar Masjid Road, Fazlur Rahman | 2019-09-05 | NQ1005 | 9.7 | 23 | 9.7 | 24 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 6504 | 2255.9997 | 102.2039
SYL-F.RR.125.1 | 24394599156266 | Fenchuganj, Puranbazar, Sarkarkhana, Puranbazar Masjid Road, charag Ali | 2019-09-05 | NQ1005 | 11.4 | 25 | 11.4 | 26 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6504 | 2255.9997 | 120.1159
SYL-F.RR.126.1 | 24394339156243 | Fenchuganj, Puranbazar R /A, Block # B, Rd # 01, Monu Mia | 2019-09-05 | NQ1005 | 25.9 | 29 | 25.9 | 30 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 25.9 | 25.9 | 1.554 | 1.554 | 0.0007168 | 100% | 0% | 1.554 | 1.554 | 0.0011869 | 28 | 0.031152 | 0.031152 |  | 0 | 0 | 6504 | 2255.9997 | 272.8949
SYL-F.RR.127.1 | 24394249156242 | Fenchuganj, Puranbazar R /A, Block # B, Rd # 01, Chowdhury Bhabon, Akib Chowdhury | 2019-09-05 | NQ1005 | 11.9 | 31 | 11.9 | 32 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6504 | 2255.9997 | 125.3841
SYL-F.RR.128.1 | 24394249156225 | Fenchuganj, Puranbazar, Sarkarkhana, Near Momin Varaitis Store, Monir Mia | 2019-09-05 | NQ1005 | 7.6 | 36 | 7.6 | 37 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6504 | 2255.9997 | 80.0773
SYL-F.RR.151.1 | 24404119155371 | Fenchuganj, West Faridpur, Word # 3, Abdul Ali | 2019-08-31 | NQ1005 | 12.6 | 314 | 12.6 | 315 | 2022-01-01 | [9 empty] | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0
SYL-F.RR.152.1 | 24404369155358 | Fenchuganj, West Faridpur, Word # 3, Maynuddin | 2019-08-31 | NQ1005 | 5.4 | 316 | 5.4 | 317 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6504 | 2255.9997 | 56.897
SYL-F.RR.153.1 | 24403729155365 | Fenchuganj, West Faridpur, Word # 3, Rofik Mia | 2019-08-31 | NQ1005 | 7.3 | 318 | 7.3 | 319 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6504 | 2255.9997 | 76.9163
SYL-F.RR.154.1 | 24403339155365 | Fenchuganj, West Faridpur, Word # 3,Abdul Jomir | 2019-08-31 | NQ1005 | 11.6 | 320 | 11.6 | 321 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6504 | 2255.9997 | 122.2232
SYL-F.RR.155.1 | 24402979155383 | Fenchuganj, West Faridpur, Word # 3, Monir Member | 2019-08-31 | NQ1005 | 13.5 | 322 | 13.2 | 323 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6504 | 2255.9997 | 139.0816
SYL-F.RR.156.1 | 24402799155388 | Fenchuganj, West Faridpur, Word # 3, Ajahar Alli | 2019-08-31 | NQ1005 | 6.7 | 324 | 6.7 | 325 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 6504 | 2255.9997 | 70.5944
SYL-F.RR.157.1 | 24412039156150 | Fenchuganj, Korimpur, Fokirpara, Word # 5, Abdul Hamid (Raju) | 2019-09-01 | NQ1005 | 6.1 | 344 | 6.2 | 345 | 2022-01-01 | [9 empty] | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0
SYL-F.RR.158.1 | 24411529156183 | Fenchuganj, Korimpur, Fokirpara, Word # 5, Anam Ali | 2019-09-01 | NQ1005 | 2.2 | 346 | 2.2 | 347 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6552 | 2207.9997 | 23.1803
SYL-F.RR.159.1 | 24411639156220 | Fenchuganj, Korimpur, korimpur Jame Mosjid, Word # 5, Abdul Ajij | 2019-09-01 | NQ1005 | 17.6 | 348 | 17.6 | 349 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 6552 | 2207.9997 | 185.4421
SYL-F.RR.160.1 | 24411619156334 | Fenchuganj, Korimpur, Word # 5, Moymun Nessa | 2019-09-01 | NQ1005 | 12.3 | 350 | 11.7 | 351 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 6552 | 2207.9997 | 123.2768
SYL-F.RR.161.1 | 24411389156319 | Fenchuganj, Korimpur, Word # 5, Mojibur Rohman | 2019-09-01 | NQ1005 | 14.1 | 352 | 14.1 | 353 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 6552 | 2207.9997 | 148.5644
SYL-F.RR.162.1 | 24410249156290 | Fenchuganj, Korimpur, Word # 5, Sohel Mia | 2019-09-01 | NQ1005 | 7.6 | 354 | 7.6 | 355 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6552 | 2207.9997 | 80.0773
SYL-F.RR.163.1 | 24410079156289 | Fenchuganj, Korimpur, Word # 5, Selim Khan | 2019-09-01 | NQ1005 | 8.7 | 356 | 8.7 | 357 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6552 | 2207.9997 | 91.6674
SYL-F.RR.163.2 | 24410079156289 | Fenchuganj, Korimpur, Word # 5, Selim Khan | 2021-01-20 | LX1011 | 4.6 | 28 | 4.6 | 29 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 6552 | 2207.9997 | 48.4678
SYL-F.RR.164.1 | 24404989156250 | Fenchuganj, Korimpur, Word # 5, Najrul Islam | 2019-09-01 | NQ1005 | 3.6 | 360 | 3.6 | 361 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6552 | 2207.9997 | 37.9313
SYL-F.RR.165.1 | 24410729157065 | Fenchuganj, Maijgaon, New Railway Station, Kholilur Rohman | 2019-09-02 | NQ1005 | 34.9 | 371 | 34.9 | 372 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 34.9 | 34.9 | 2.094 | 2.094 | 0.0007168 | 100% | 0% | 2.094 | 2.094 | 0.0011869 | 28 | 0.041978 | 0.041978 |  | 0 | 0 | 6600 | 2159.9997 | 367.7232
SYL-F.RR.165.2 | 24410729157065 | Fenchuganj, Maijgaon, New Railway Station, Kholilur Rohman | 2021-09-08 | NQ1007 | 6.3 | 14 | 6.3 | 15 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6600 | 2159.9997 | 66.3798
SYL-F.RR.166.1 | 24405299157108 | Fenchuganj, Maijgaon, Shorifgonj, Block-A, Khalid | 2019-09-02 | NQ1005 | 11.6 | 373 | 11.6 | 374 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6600 | 2159.9997 | 122.2232
SYL-F.RR.167.1 | 24404439157124 | Fenchuganj, Maijgaon, Shorifgonj, Abul Khoirati | 2019-09-02 | NQ1005 | 7.8 | 375 | 7.8 | 376 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6600 | 2159.9997 | 82.1846
SYL-F.RR.168.1 | 24404769157180 | Fenchuganj, Maijgaon, Shorifgonj, Word # 7, Monor Mia | 2019-09-02 | NQ1005 | 16 | 377 | 16 | 378 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 6600 | 2159.9997 | 168.5837
SYL-F.RR.169.1 | 24404829157190 | Fenchuganj, Maijgaon, Shorifgonj, Word # 7, Salam Member | 2019-09-02 | NQ1005 | 12.3 | 379 | 12.3 | 380 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6600 | 2159.9997 | 129.5987
SYL-F.RR.170.1 | 24404829157190 | Fenchuganj, Maijgaon, Shorifgonj, Word # 7, Salam Member | 2019-09-02 | NQ1005 | 3.2 | 382 | 3.2 | 383 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 6600 | 2159.9997 | 33.7167
SYL-F.RR.171.1 | 24405399157202 | Fenchuganj, Maijgaon, Shorifgonj, Word # 7, Rofik Mia | 2019-09-02 | NQ1005 | 7.8 | 384 | 7.8 | 385 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6600 | 2159.9997 | 82.1846
SYL-F.RR.172.1 | 24410199157206 | Fenchuganj, Maijgaon Bazar, Golam Robanni | 2019-09-03 | NQ1005 | 15.3 | 398 | 15.3 | 399 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 6600 | 2159.9997 | 161.2082
SYL-F.RR.173.1 | 24410219157205 | Fenchuganj, Maijgaon Bazar, Nanu mia | 2019-09-03 | NQ1005 | 9.4 | 402 | 9.4 | 403 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 6600 | 2159.9997 | 99.0429
SYL-F.RR.174.1 | 24414179155540 | Fenchuganj, Mominpur, Word # 2, Nurul Hossen | 2019-09-04 | NQ1005 | 15.9 | 5 | 15.9 | 6 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 6576 | 2183.9997 | 167.5301
SYL-F.RR.175.1 | 24414179155540 | Fenchuganj, Mominpur, Word # 2, Kawsar Ahmed | 2019-09-04 | NQ1005 | 6.3 | 7 | 6.3 | 8 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6576 | 2183.9997 | 66.3798
SYL-F.RR.176.1 | 24414179155540 | Fenchuganj, Mominpur, Word # 2, Kawsar Ahmed | 2019-09-04 | NQ1005 | 12.2 | 9 | 12.2 | 10 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6576 | 2183.9997 | 128.5451
SYL-F.RR.177.1 | 24394659155244 | Fenchuganj, Kachuabohor, Word # 2, Lilu Mia | 2019-09-05 | NQ1005 | 13 | 11 | 13 | 12 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 6504 | 2255.9997 | 136.9743
SYL-F.RR.178.1 | 24394609155246 | Fenchuganj, Kachuabohor, Word # 2, Akbor Ali | 2019-09-05 | NQ1005 | 6.4 | 13 | 6.4 | 14 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6504 | 2255.9997 | 67.4335
SYL-F.RR.201.1 | 24405539155595 | Fenchuganj, North Fridpur, Anawer Khan | 2019-08-31 | NQ1009 | 12.5 | 311 | 12.5 | 312 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 6552 | 2207.9997 | 131.706
SYL-F.RR.202.1 | 24405539155595 | Fenchuganj, North Fridpur, Mahabubul Alam | 2019-08-31 | NQ1009 | 11.4 | 313 | 11.4 | 314 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 6552 | 2207.9997 | 120.1159
SYL-F.RR.203.1 | 24412169156012 | Fenchuganj, Nurpur, Azizul Islam Chowdhury | 2019-08-31 | NQ1009 | 7.4 | 315 | 7.4 | 316 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6552 | 2207.9997 | 77.97
SYL-F.RR.204.1 | 24412929155592 | Fenchuganj, Nurpur, Delour Hoshen Chowdhury Jame Mosjid | 2019-08-31 | NQ1009 | 9.1 | 317 | 9 | 318 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6552 | 2207.9997 | 94.8283
SYL-F.RR.205.1 | 24413089156018 | Fenchuganj, Nurpur, M.P. Bari, Shahidus Samad Chowdhury | 2019-08-31 | NQ1009 | 10.6 | 319 | 10.6 | 320 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6552 | 2207.9997 | 111.6867
SYL-F.RR.206.1 | 24413819156103 | Fenchuganj, Nurpur, Nouagaw, Ananta, Kumer Das | 2019-08-31 | NQ1009 | 8.7 | 321 | 8.7 | 322 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6552 | 2207.9997 | 91.6674
SYL-F.RR.207.1 | 24413819156103 | Fenchuganj, Nurpur, Nouagaw, Md. Faruk Mia | 2019-08-31 | NQ1009 | 12.3 | 323 | 12.3 | 324 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6552 | 2207.9997 | 129.5987
SYL-F.RR.208.1 | 24413819156116 | Fenchuganj, Nurpur, Nouagaw, Muktar Ali | 2019-08-31 | NQ1009 | 9.2 | 325 | 8.9 | 326 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6552 | 2207.9997 | 93.7747
SYL-F.RR.209.1 | 24413549156103 | Fenchuganj, Nurpur, Shufian Ahmed | 2019-08-31 | NQ1009 | 9.5 | 327 | 9.5 | 328 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6552 | 2207.9997 | 100.0966
SYL-F.RR.210.1 | 24413389156183 | Fenchuganj, Nurpur, Uttortila, Md. Fuad | 2019-08-31 | NQ1009 | 10.1 | 329 | 9.8 | 330 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 6552 | 2207.9997 | 103.2575
SYL-F.RR.211.1 | 24413389156183 | Fenchuganj, Nurpur, Uttortila, Mohsin Ali | 2019-08-31 | NQ1009 | 7.8 | 331 | 7.8 | 332 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6552 | 2207.9997 | 82.1846
SYL-F.RR.212.1 | 24414939156499 | Fenchuganj, Rajonpur, General Osmani Road, Bachu Member | 2019-09-01 | NQ1009 | 2.2 | 347 | 2.2 | 348 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6600 | 2159.9997 | 23.1803
SYL-F.RR.213.1 | 24414889156479 | Fenchuganj, Rajonpur, General Osmani Road, Badsha Mia | 2019-09-01 | NQ1009 | 1.1 | 349 | 1.1 | 350 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 6600 | 2159.9997 | 11.5901
SYL-F.RR.214.1 | 24414889156479 | Fenchuganj, Rajonpur, General Osmani Road, Konoy Mia | 2019-09-01 | NQ1009 | 4.4 | 351 | 4.4 | 352 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 6600 | 2159.9997 | 46.3605
SYL-F.RR.215.1 | 24414889156479 | Fenchuganj, Rajonpur, General Osmani Road, Pakhi Mia | 2019-09-01 | NQ1009 | 9.5 | 353 | 9.5 | 354 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6600 | 2159.9997 | 100.0966
SYL-F.RR.216.1 | 24415139156521 | Fenchuganj, Rajonpur, General Osmani Road, Sayed Moksod Ahmed | 2019-09-01 | NQ1009 | 2.5 | 355 | 2.5 | 356 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6600 | 2159.9997 | 26.3412
SYL-F.RR.217.1 | 24415249156527 | Fenchuganj, Rajonpur, General Osmani Road, Alam Monjil | 2019-09-01 | NQ1009 | 1.7 | 357 | 1.7 | 358 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6600 | 2159.9997 | 17.912
SYL-F.RR.218.1 | 24414069156496 | Fenchuganj, Rajonpur, Ruhul Amin | 2019-09-01 | NQ1009 | 1.5 | 359 | 1.5 | 360 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 6600 | 2159.9997 | 15.8047
SYL-F.RR.219.1 | 24413769156534 | Fenchuganj, Rajonpur, Mokam Bari, Shamsul Hoque | 2019-09-01 | NQ1009 | 36.9 | 361 | 36.9 | 362 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 36.9 | 36.9 | 2.214 | 2.214 | 0.0007168 | 100% | 0% | 2.214 | 2.214 | 0.0011869 | 28 | 0.044383 | 0.044383 |  | 0 | 0 | 6600 | 2159.9997 | 388.7962
SYL-F.RR.220.1 | 24413929156531 | Fenchuganj, Rajonpur, Samad, Nearby Rajonpur Puraton Jame Mosjid | 2019-09-01 | NQ1009 | 1.2 | 365 | 1.2 | 366 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6600 | 2159.9997 | 12.6438
SYL-F.RR.221.1 | 24414039156530 | Fenchuganj, Rajonpur, Sinu Mia, Nearby Rajonpur Puraton Jame Mosjid | 2019-09-01 | NQ1009 | 5.3 | 367 | 4.9 | 368 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 6600 | 2159.9997 | 51.6288
SYL-F.RR.222.1 | 24414259156534 | Fenchuganj, Rajonpur, Osmani Road, Kamrul Mia | 2019-09-02 | NQ1009 | 11.2 | 369 | 11.2 | 370 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6600 | 2159.9997 | 118.0086
SYL-F.RR.223.1 | 24413209156593 | Fenchuganj, Pathantila, Osmani Road, Aftab Uddin | 2019-09-02 | NQ1009 | 12.4 | 371 | 12.4 | 372 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6600 | 2159.9997 | 130.6524
SYL-F.RR.224.1 | 24413209156593 | Fenchuganj, Pathantila, Osmani Road, Shahin Khan | 2019-09-02 | NQ1009 | 3.1 | 373 | 3.1 | 374 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6600 | 2159.9997 | 32.6631
SYL-F.RR.225.1 | 24412509156581 | Fenchuganj, Pathantila, Katabari, Tarek Ahmed Khan | 2019-09-02 | NQ1009 | 1.8 | 375 | 1.8 | 376 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 6600 | 2159.9997 | 18.9657
SYL-F.RR.226.1 | 24414619157108 | Fenchuganj, Chattish, Hazi Md. Firoz Ali | 2019-09-03 | NQ1009 | 2.4 | 395 | 2.4 | 396 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6576 | 2183.9997 | 25.2876
SYL-F.RR.227.1 | 24414789157106 | Fenchuganj, Chattish, Md. Borhan Uddin | 2019-09-03 | NQ1009 | 13.4 | 397 | 13.4 | 398 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 6576 | 2183.9997 | 141.1888
SYL-F.RR.228.1 | 24414739157127 | Fenchuganj, Chattish, Monower Ali (Member) | 2019-09-03 | NQ1009 | 15.1 | 399 | 15.1 | 400 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 6576 | 2183.9997 | 159.1009
SYL-F.RR.229.1 | 24404869157586 | Fenchuganj, Bialybazar, Kaiostogram, Jomiruddin | 2019-09-04 | NQ1009 | 11.2 | 1 | 11.2 | 2 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6600 | 2159.9997 | 118.0086
SYL-F.RR.230.1 | 24391219159043 | Fenchuganj, Maijgaon Union, Momin Chara Tea Garden, Manager's Banglo | 2019-09-04 | NQ1009 | 12.1 | 3 | 12.1 | 4 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6600 | 2159.9997 | 127.4914
SYL-F.RR.230.2 | 24391219159043 | Fenchuganj, Maijgaon Union, Momin Chara Tea Garden, Manager's Banglo | 2022-04-03 | NQ1007 | 4.7 | 117 | 4.7 | 118 | 2022-04-03 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 4392 | 2159.9997 | 37.0393
SYL-F.RR.231.1 | 24394859155271 | Fenchuganj, Kochuabahar, Khokon | 2019-09-05 | NQ1009 | 11.1 | 9 | 11.1 | 10 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6504 | 2255.9997 | 116.9549
SYL-F.RR.232.1 | 24394859155271 | Fenchuganj, Kochuabahar, Siddik Ali | 2019-09-05 | NQ1009 | 9 | 11 | 8.9 | 12 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6504 | 2255.9997 | 93.7747
SYL-F.RR.233.1 | 24395879156278 | Fenchuganj, Nizampur, Zihad Ahmed | 2019-09-05 | NQ1009 | 4.1 | 13 | 4.1 | 14 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6504 | 2255.9997 | 43.1996
SYL-F.RR.234.1 | 24395909156291 | Fenchuganj, Nizampur, Md Delour Hosen / Md. Sabbir Hosen | 2019-09-05 | NQ1009 | 3.8 | 15 | 3.8 | 16 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6504 | 2255.9997 | 40.0386
SYL-F.RR.235.1 | 24395909156291 | Fenchuganj, Nizampur, Back site of Delour Hosen | 2019-09-05 | NQ1009 | 10.5 | 17 | 10.5 | 18 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6504 | 2255.9997 | 110.6331
SYL-F.RR.251.1 | 24404369155402 | Fenchuganj, West Faridpur, Abdur Nur | 2019-08-31 | NQ1009 | 4 | 303 | 4 | 304 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 24 | 0 | 6480 | 2255.9997 | 42.0305
SYL-F.RR.252.1 | 24403639155589 | Fenchuganj, Faridpur, Majergaw, Jalal Mia | 2019-08-31 | NQ1009 | 1.2 | 305 | 1.2 | 306 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 6552 | 2207.9997 | 12.6438
SYL-F.RR.253.1 | 24404059155519 | Fenchuganj, Faridpur, Majergaw, Ator Ali | 2019-08-31 | NQ1009 | 4.3 | 307 | 4.3 | 308 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 6552 | 2207.9997 | 45.3069
SYL-F.RR.254.1 | 24404059155519 | Fenchuganj, Faridpur, Majergaw, Abdul Basir | 2019-08-31 | NQ1009 | 1.7 | 309 | 1.7 | 310 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 6552 | 2207.9997 | 17.912
SYL-F.RR.255.1 | 24413309156157 | Fenchuganj, Nurpur, Uttar Tilla, Tabarak Ali | 2019-09-01 | NQ1009 | 9.5 | 333 | 9.5 | 334 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6552 | 2207.9997 | 100.0966
SYL-F.RR.256.1 | 24413169156145 | Fenchuganj, Nurpur, Uttar Tilla, Chowdhury Md. Adil (Akoddos) | 2019-09-01 | NQ1009 | 2.3 | 335 | 2.3 | 336 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 6552 | 2207.9997 | 24.2339
SYL-F.RR.257.1 | 24412689156080 | Fenchuganj, Nurpur, Nurpur Road, Akram Hossen | 2019-09-01 | NQ1009 | 3 | 337 | 3 | 338 | 2022-01-01 | [9 empty] | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0
SYL-F.RR.258.1 | 24412689156080 | Fenchuganj, Nurpur, Nurpur Road, Helal Ahmed | 2019-09-01 | NQ1009 | 2.4 | 341 | 2.4 | 342 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 6552 | 2207.9997 | 25.2876
SYL-F.RR.259.1 | 24415579156458 | Fenchuganj, Rajonpur, Thana Road, Sunahor Ali | 2019-09-01 | NQ1009 | 10 | 343 | 10 | 344 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6576 | 2183.9997 | 105.3648
SYL-F.RR.259.2 | 24415579156458 | Fenchuganj, Rajonpur, Thana Road, Sunahor Ali | 2021-09-07 | NQ1007 | 7.8 | 12 | 7.8 | 13 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 6576 | 2183.9997 | 82.1846
SYL-F.RR.260.1 | 24415579156458 | Fenchuganj, Rajonpur, Thana Road, Mohiuddin Belal | 2019-09-01 | NQ1009 | 2.5 | 345 | 2.5 | 346 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 6576 | 2183.9997 | 26.3412
SYL-F.RR.261.1 | 24412249157056 | Fenchuganj, Mugalpur, Osmani Road, Abul Kalam Abdur Rahim | 2019-09-02 | NQ1009 | 11.4 | 377 | 11.5 | 378 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6600 | 2159.9997 | 121.1695
SYL-F.RR.262.1 | 24412569157094 | Fenchuganj, Mugalpur, Nij Chattish Road, Liakot Ali (Julfu) | 2019-09-02 | NQ1009 | 3 | 379 | 3 | 380 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6600 | 2159.9997 | 31.6094
SYL-F.RR.263.1 | 24412479157111 | Fenchuganj, Nij Chattish, Munshi Bari, Abdul Basir | 2019-09-02 | NQ1009 | 4.2 | 381 | 4.2 | 382 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6600 | 2159.9997 | 44.2532
SYL-F.RR.264.1 | 24412479157111 | Fenchuganj, Nij Chattish, Munshi Bari, Abul waish | 2019-09-02 | NQ1009 | 3.1 | 387 | 3.1 | 388 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6600 | 2159.9997 | 32.6631
SYL-F.RR.264.2 | 24412479157111 | Fenchuganj, Nij Chattish, Munshi Bari, Abul waish | 2022-04-03 | NQ1007 | 1.7 | 121 | 1.6 | 122 | 2022-04-03 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 4392 | 2159.9997 | 12.6091
SYL-F.RR.265.1 | 24412349157128 | Fenchuganj, Nij Chattish, Munshi Bari, Abdul Mukit | 2019-09-02 | NQ1009 | 2 | 391 | 2 | 392 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 6600 | 2159.9997 | 21.073
SYL-F.RR.266.1 | 24412159157117 | Fenchuganj, Nij Chattish, Engineer Zakir Hossen | 2019-09-02 | NQ1009 | 4 | 393 | 4 | 394 | 2022-01-01 | 2022-10-03 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 6600 | 2159.9997 | 42.1459
SYL-F.RR.267.1 | 24415589157235 | Fenchuganj, Chattish Maddhapara, Belal Hossen | 2019-09-03 | NQ1009 | 1.9 | 401 | 1.9 | 402 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 6576 | 2183.9997 | 20.0193
SYL-F.RR.268.1 | 24420269157147 | Fenchuganj, Chattish, Nayabari, Surfan Monjil, Anwer Hossen | 2019-09-03 | NQ1009 | 9.2 | 403 | 9.2 | 404 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6576 | 2183.9997 | 96.9356
SYL-F.RR.269.1 | 24420269157147 | Fenchuganj, Chattish, Nayabari, Surfan Monjil, Saydur Rahman | 2019-09-03 | NQ1009 | 2.8 | 409 | 2.8 | 410 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6576 | 2183.9997 | 29.5021
SYL-F.RR.270.1 | 24414429155539 | Fenchuganj, Muminpur, Taher Ali | 2019-09-04 | NQ1009 | 4.2 | 5 | 4.2 | 6 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 6576 | 2183.9997 | 44.2532
SYL-F.RR.271.1 | 24414429155539 | Fenchuganj, Muminpur, Abdul Ahad | 2019-09-04 | NQ1009 | 2.7 | 7 | 2.7 | 8 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 6576 | 2183.9997 | 28.4485
SYL-F.RR.272.1 | 24393219155240 | Fenchuganj, Mirjapur, Tamuj Ali Road, Goutom Ranjan Deb | 2019-09-05 | NQ1009 | 3.6 | 19 | 3.6 | 20 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 6504 | 2255.9997 | 37.9313
SYL-F.RR.273.1 | 24393219155240 | Fenchuganj, Mirjapur, Tamuj Ali Road, Nirmol Kanti Dey | 2019-09-05 | NQ1009 | 11.9 | 21 | 11.9 | 22 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6504 | 2255.9997 | 125.3841
SYL-F.RR.274.1 | 24393459155289 | Fenchuganj, Mirjapur, Tamuj Ali Road, Khacha Mia | 2019-09-05 | NQ1009 | 3.4 | 23 | 3.4 | 24 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6504 | 2255.9997 | 35.824
SYL-F.RR.275.1 | 24393649155257 | Fenchuganj, Kachuabahar, Tamuj Ali Road, Nepal Das | 2019-09-05 | NQ1009 | 7.9 | 25 | 7.9 | 26 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 6504 | 2255.9997 | 83.2382
SYL-F.RR.276.1 | 24393819155277 | Fenchuganj, Kachuabahar, Tamuj Ali Road, Iliyas Mia | 2019-09-05 | NQ1009 | 10.6 | 27 | 10.6 | 28 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 6504 | 2255.9997 | 111.6867
SYL-F.RR.301.1 | 24412359156051 | Fenchuganj, Maijgaon, Nurpur, Adv: Aminul Chowdhory | 2019-08-31 | NQ1007 | 13.6 | 428 | 13.6 | 429 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 6552 | 2207.9997 | 143.2961
SYL-F.RR.302.1 | 24412359156051 | Fenchuganj, Maijgaon, Nurpur, Adv: Aminul Chowdhory | 2019-08-31 | NQ1007 | 9.9 | 434 | 10 | 435 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 6552 | 2207.9997 | 105.3648
SYL-F.RR.303.1 | 24412359156051 | Fenchuganj, Maijgaon, Nurpur, Torik Ali | 2019-08-31 | NQ1007 | 7.3 | 436 | 7.3 | 437 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 6552 | 2207.9997 | 76.9163
SYL-F.RR.304.1 | 24412589156056 | Fenchuganj, Maijgaon, Nurpur, Anamul Hoque Chowdhory | 2019-08-31 | NQ1007 | 7.6 | 438 | 7.6 | 439 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 6552 | 2207.9997 | 80.0773
SYL-F.RR.305.1 | 24412589156056 | Fenchuganj, Maijgaon, Nurpur, Anamul Hoque Chowdhory | 2019-08-31 | NQ1007 | 9.4 | 440 | 10.2 | 441 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6552 | 2207.9997 | 107.4721
SYL-F.RR.306.1 | 24412579156051 | Fenchuganj, Maijgaon, Nurpur, Akkas Ali | 2019-08-31 | NQ1007 | 8.1 | 442 | 8.1 | 443 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6552 | 2207.9997 | 85.3455
SYL-F.RR.307.1 | 24412759156054 | Fenchuganj, Maijgaon, Nurpur, Md. Bulbul Islam | 2019-08-31 | NQ1007 | 12.3 | 444 | 12.3 | 445 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6552 | 2207.9997 | 129.5987
SYL-F.RR.307.2 | 24412759156054 | Fenchuganj, Maijgaon, Nurpur, Md. Bulbul Islam | 2022-03-31 | NQ1007 | 4.9 | 111 | 4.9 | 112 | 2022-03-31 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 4416 | 2207.9997 | 39.0398
SYL-F.RR.308.1 | 24413419156066 | Fenchuganj, Maijgaon, Nurpur, Md. Nasher Ali | 2019-08-31 | NQ1007 | 7.3 | 446 | 7.4 | 447 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6552 | 2207.9997 | 77.97
SYL-F.RR.309.1 | 24413419156066 | Fenchuganj, Maijgaon, Nurpur, Manik Mia | 2019-08-31 | NQ1007 | 11.6 | 448 | 11.6 | 449 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6552 | 2207.9997 | 122.2232
SYL-F.RR.310.1 | 24420299156328 | Fenchuganj, Poschim Bazar, Md. Mashuk Mia, M/S Anower Tredars | 2019-09-01 | NQ1007 | 11.3 | 464 | 11.3 | 465 | 2022-01-01 | [9 empty] | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0
SYL-F.RR.311.1 | 24420299156328 | Fenchuganj, Poschim Bazar, Hazi Borhan Uddin | 2019-09-01 | NQ1007 | 12.9 | 466 | 12.9 | 467 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 6576 | 2183.9997 | 135.9206
SYL-F.RR.313.1 | 24420069156459 | Fenchuganj, Moddho Bazar, Post Office Road, Abbas Uddin | 2019-09-01 | NQ1007 | 9.6 | 472 | 9.6 | 473 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6576 | 2183.9997 | 101.1502
SYL-F.RR.314.1 | 24415819156484 | Fenchuganj, Rajonpur, Post Office Road, Abdul Hai Khosru | 2019-09-01 | NQ1007 | 6.2 | 474 | 6.2 | 475 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 6576 | 2183.9997 | 65.3262
SYL-F.RR.315.1 | 24415819156484 | Fenchuganj, Rajonpur, Post Office Road, Abdul Hai Khosru | 2019-09-01 | NQ1007 | 4.1 | 476 | 4.1 | 477 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6576 | 2183.9997 | 43.1996
SYL-F.RR.316.1 | 24415819156484 | Fenchuganj, Rajonpur, Post Office Road, Abdul Hai Khosru | 2019-09-01 | NQ1007 | 6.4 | 478 | 6.4 | 479 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6576 | 2183.9997 | 67.4335
SYL-F.RR.317.1 | 24415819156484 | Fenchuganj, Rajonpur, Post Office Road, Abdul Hai Khosru | 2019-09-01 | NQ1007 | 14.9 | 480 | 15 | 481 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 6576 | 2183.9997 | 158.0472
SYL-F.RR.318.1 | 24415709156467 | Fenchuganj, Rajonpur, Post Office Road, Mukul Mia | 2019-09-01 | NQ1007 | 9.6 | 482 | 9.6 | 483 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6576 | 2183.9997 | 101.1502
SYL-F.RR.319.1 | 24415709156467 | Fenchuganj, Rajonpur, Post Office Road, Mukul Mia | 2019-09-01 | NQ1007 | 9.3 | 484 | 9.5 | 485 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6576 | 2183.9997 | 100.0966
SYL-F.RR.320.1 | 24411109156107 | Fenchuganj, Maijgaon, Nurpur, Nurpur-Fakirapara Road, Junayed Hosen | 2019-09-02 | NQ1007 | 11.1 | 486 | 11.1 | 487 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 6552 | 2207.9997 | 116.9549
SYL-F.RR.321.1 | 24411069156088 | Fenchuganj, Maijgaon, Nurpur, Nurpur-Fakirapara Road, Monir Mia | 2019-09-02 | NQ1007 | 13.7 | 492 | 13.7 | 493 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6552 | 2207.9997 | 144.3498
SYL-F.RR.322.1 | 24410889156092 | Fenchuganj, Maijgaon, Nurpur, Nurpur-Fakirapara Road, Saidur Rahman | 2019-09-02 | NQ1007 | 12.3 | 494 | 12.3 | 495 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 6552 | 2207.9997 | 129.5987
SYL-F.RR.323.1 | 24410569156086 | Fenchuganj, Maijgaon, Nurpur, Nurpur-Fakirapara Road, Mashuk Mia | 2019-09-02 | NQ1007 | 11.6 | 496 | 11.6 | 497 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 6552 | 2207.9997 | 122.2232
SYL-F.RR.324.1 | 24405509156095 | Fenchuganj, Maijgaon, Fakirpara, Fakirapara Road, Abdul Malek | 2019-09-02 | NQ1007 | 10.2 | 498 | 10.2 | 499 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 6552 | 2207.9997 | 107.4721
SYL-F.RR.325.1 | 24405509156095 | Fenchuganj, Maijgaon, Fakirpara, Fakirapara Road, Abdul Malek | 2019-09-02 | NQ1007 | 5.1 | 500 | 5.1 | 501 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 6552 | 2207.9997 | 53.7361
SYL-F.RR.326.1 | 24405509156095 | Fenchuganj, Maijgaon, Fakirpara, Fakirapara Road, Abdul Malek | 2019-09-02 | NQ1007 | 8.3 | 502 | 8.3 | 503 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 6552 | 2207.9997 | 87.4528
SYL-F.RR.327.1 | 24405509156095 | Fenchuganj, Maijgaon, Fakirpara, Fakirapara Road, Abdul Malek | 2019-09-02 | NQ1007 | 9.6 | 504 | 9.6 | 505 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6552 | 2207.9997 | 101.1502
SYL-F.RR.328.1 | 24405099156076 | Fenchuganj, Maijgaon, Dokkhin Fakirpara, Fakirapara Road, Md. Sahed | 2019-09-02 | NQ1007 | 10.5 | 506 | 10.7 | 507 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 6552 | 2207.9997 | 112.7403
SYL-F.RR.329.1 | 24404399156093 | Fenchuganj, Maijgaon, Dokkhin Fakirpara, Fakirapara Road, Khuku Mia | 2019-09-02 | NQ1007 | 3.1 | 508 | 3.1 | 509 | 2022-01-01 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 6552 | 2207.9997 | 32.6631
SYL-F.RR.329.2 | 24404399156093 | Fenchuganj, Maijgaon, Dokkhin Fakirpara, Fakirapara Road, Khuku Mia | 2022-03-31 | NQ1007 | 12 | 113 | 12 | 114 | 2022-03-31 | 2022-10-01 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 4416 | 2207.9997 | 95.6077
SYL-F.RR.330.1 | 24420269156581 | Fenchuganj, Islampur, Islampur Road, Md. Mohibur Rahman | 2019-09-03 | NQ1007 | 13.9 | 534 | 13.9 | 535 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 6576 | 2183.9997 | 146.4571
SYL-F.RR.331.1 | 24420269156581 | Fenchuganj, Islampur, Islampur Road, Angshu Mia | 2019-09-03 | NQ1007 | 12.6 | 536 | 12.6 | 537 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 6576 | 2183.9997 | 132.7597
SYL-F.RR.332.1 | 24420239156550 | Fenchuganj, Islampur, Islampur Road, Abul Azad Dablu | 2019-09-03 | NQ1007 | 9.2 | 540 | 9.2 | 541 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 6576 | 2183.9997 | 96.9356
SYL-F.RR.333.1 | 24420099156557 | Fenchuganj, Islampur, Islampur Road, Azharul Islam | 2019-09-03 | NQ1007 | 12.7 | 543 | 12.7 | 544 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 6576 | 2183.9997 | 133.8133
SYL-F.RR.334.1 | 24420099156557 | Fenchuganj, Islampur, Islampur Road, Mahafujur Rahman Siblu | 2019-09-03 | NQ1007 | 11.9 | 545 | 11.9 | 546 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6576 | 2183.9997 | 125.3841
SYL-F.RR.335.1 | 24420159156570 | Fenchuganj, Islampur, Islampur Road, Md. Khalekur Rahman | 2019-09-03 | NQ1007 | 4.7 | 547 | 4.7 | 548 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6576 | 2183.9997 | 49.5215
SYL-F.RR.336.1 | 24415819156563 | Fenchuganj, Islampur, Islampur Road, Azad Khan | 2019-09-03 | NQ1007 | 8.9 | 549 | 8.9 | 550 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 6576 | 2183.9997 | 93.7747
SYL-F.RR.337.1 | 24415789156563 | Fenchuganj, Islampur, Islampur Road, Abdul Latif Monjil | 2019-09-03 | NQ1007 | 12.3 | 551 | 12.2 | 552 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 6576 | 2183.9997 | 128.5451
SYL-F.RR.338.1 | 24415329156591 | Fenchuganj, Islampur, Islampur Road, Kazi Md. Abdul Hoque( Kazi Bari) | 2019-09-03 | NQ1007 | 11.8 | 553 | 11.8 | 554 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 6576 | 2183.9997 | 124.3305
SYL-F.RR.339.1 | 24415409156594 | Fenchuganj, Islampur, Islampur Road, Abul Kalam Joblu ( Master) | 2019-09-03 | NQ1007 | 9.9 | 555 | 9.9 | 556 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 6576 | 2183.9997 | 104.3112
SYL-F.RR.340.1 | 24420219157001 | Fenchuganj, Islampur, Fulbari, Rashik Mia | 2019-09-04 | NQ1007 | 9.3 | 1 | 9.3 | 2 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 6576 | 2183.9997 | 97.9893
SYL-F.RR.341.1 | 24420219157001 | Fenchuganj, Islampur, Fulbari, Faruk Mia | 2019-09-04 | NQ1007 | 8.7 | 3 | 8.7 | 4 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 6576 | 2183.9997 | 91.6674
SYL-F.RR.342.1 | 24420089157028 | Fenchuganj, Islampur, Shohidul Islam, Opposite Of Murad Chairman Bari | 2019-09-04 | NQ1007 | 10.5 | 5 | 10.5 | 6 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 6576 | 2183.9997 | 110.6331
SYL-F.RR.343.1 | 24420089157028 | Fenchuganj, Islampur, Murad Chairman | 2019-09-04 | NQ1007 | 8.6 | 7 | 8.6 | 8 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 6576 | 2183.9997 | 90.6137
SYL-F.RR.344.1 | 24420089157028 | Fenchuganj, Islampur, Osman, Beside Of Murad Chairman Bari | 2019-09-04 | NQ1007 | 6.3 | 9 | 6.3 | 10 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6576 | 2183.9997 | 66.3798
SYL-F.RR.345.1 | 24385739156381 | Fenchuganj, Shah-Jalal Fertilizer, BIDC Bazar, Sarkarkhana Road, Ledis Club | 2019-09-05 | NQ1007 | 12.5 | 15 | 12.4 | 16 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 6504 | 2255.9997 | 130.6524
SYL-F.RR.346.1 | 24390689156437 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Officers Quarter, Building # C-2 | 2019-09-05 | NQ1007 | 3.7 | 17 | 3.7 | 18 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6504 | 2255.9997 | 38.985
SYL-F.RR.347.1 | 24390689156437 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Officers Quarter, Building # C-3 | 2019-09-05 | NQ1007 | 3.4 | 19 | 3.4 | 20 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 6504 | 2255.9997 | 35.824
SYL-F.RR.348.1 | 24390689156437 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Officers Quarter, Building # C-3 | 2019-09-05 | NQ1007 | 3.7 | 21 | 3.7 | 22 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 6504 | 2255.9997 | 38.985
SYL-F.RR.349.1 | 24391079156400 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Officers Quarter, Building # D-1 | 2019-09-05 | NQ1007 | 2.2 | 23 | 2.2 | 24 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 6504 | 2255.9997 | 23.1803
SYL-F.RR.350.1 | 24391079156400 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Officers Quarter, Building # D-2 | 2019-09-05 | NQ1007 | 3.8 | 25 | 3.8 | 26 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6504 | 2255.9997 | 40.0386
SYL-F.RR.351.1 | 24401489155397 | Fenchuganj, West Kormoda, Ward # 2, Indu Bari | 2019-08-31 | NQ1007 | 12.1 | 410 | 12.1 | 411 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 6504 | 2255.9997 | 127.4914
SYL-F.RR.352.1 | 24401639155399 | Fenchuganj, West Kormoda, Ward # 2, Deptendra Kumar Pal | 2019-08-31 | NQ1007 | 3 | 412 | 3 | 413 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 6504 | 2255.9997 | 31.6094
SYL-F.RR.352.2 | 24401639155399 | Fenchuganj, West Kormoda, Ward # 2, Deptendra Kumar Pal | 2022-03-30 | NQ1007 | 10.4 | 107 | 10.7 | 108 | 2022-03-30 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 4392 | 2255.9997 | 85.5591
SYL-F.RR.353.1 | 24401709155385 | Fenchuganj, West Kormoda, Ward # 2, Yunus | 2019-08-31 | NQ1007 | 6.5 | 414 | 6.5 | 415 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 6504 | 2255.9997 | 68.4871
SYL-F.RR.354.1 | 24401879155400 | Fenchuganj, West Kormoda, Ward # 2, Bishnu Pal | 2019-08-31 | NQ1007 | 9 | 416 | 9 | 417 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 6504 | 2255.9997 | 94.8283
SYL-F.RR.355.1 | 24401879155400 | Fenchuganj, West Kormoda, Ward # 2, Helal | 2019-08-31 | NQ1007 | 13.7 | 418 | 13.7 | 419 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 6504 | 2255.9997 | 144.3498
SYL-F.RR.356.1 | 24402629155396 | Fenchuganj, West Kormoda, Ward # 2, Abu Sayed Ahmed | 2019-08-31 | NQ1007 | 5.4 | 420 | 5.4 | 421 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 6504 | 2255.9997 | 56.897
SYL-F.RR.356.2 | 24402629155396 | Fenchuganj, West Kormoda, Ward # 2, Abu Sayed Ahmed | 2021-01-18 | LX1011 | 11.2 | 22 | 11.2 | 23 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 6504 | 2255.9997 | 118.0086
SYL-F.RR.357.1 | 24402569155415 | Fenchuganj, West Kormoda, Ward # 2, Shopon Pal | 2019-08-31 | NQ1007 | 12 | 422 | 12 | 423 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 6504 | 2255.9997 | 126.4378
SYL-F.RR.358.1 | 24402979155458 | Fenchuganj, Noya Bazar, Foridpur, Ward # 2, Kanchan Dash | 2019-08-31 | NQ1007 | 13.2 | 424 | 13.2 | 425 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 6504 | 2255.9997 | 139.0816
SYL-F.RR.359.1 | 24402979155458 | Fenchuganj, Noya Bazar, Foridpur, Ward # 2, Sumon Dash | 2019-08-31 | NQ1007 | 10.1 | 426 | 10.1 | 427 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 6504 | 2255.9997 | 106.4185
SYL-F.RR.360.1 | 24403929155440 | Fenchuganj, West Foridpur, Ward # 3, Rehana Malek | 2019-09-01 | NQ1007 | 10.4 | 450 | 10.4 | 451 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6504 | 2255.9997 | 109.5794
SYL-F.RR.361.1 | 24404049155438 | Fenchuganj, West Foridpur, Ward # 3, Mojibur Rahman | 2019-09-01 | NQ1007 | 11.3 | 454 | 11.3 | 455 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 6504 | 2255.9997 | 119.0622
SYL-F.RR.362.1 | 24404159155445 | Fenchuganj, West Foridpur, Ward # 3, Johir Ali | 2019-09-01 | NQ1007 | 4.7 | 456 | 4.7 | 457 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 6504 | 2255.9997 | 49.5215
SYL-F.RR.363.1 | 24404159155445 | Fenchuganj, West Foridpur, Ward # 3, Sonowar Ali | 2019-09-01 | NQ1007 | 6.3 | 458 | 6.3 | 459 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6504 | 2255.9997 | 66.3798
SYL-F.RR.364.1 | 24415089156160 | Fenchuganj, Hospital Road, Upojela Health Complax | 2019-09-01 | NQ1007 | 6.8 | 460 | 6.8 | 461 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 6576 | 2183.9997 | 71.6481
SYL-F.RR.365.1 | 24414799156167 | Fenchuganj, Hospital Road, Upojela Health Complax | 2019-09-01 | NQ1007 | 8.2 | 462 | 8.2 | 463 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 6576 | 2183.9997 | 86.3991
SYL-F.RR.366.1 | 24415469156268 | Fenchuganj, Hospital Road, Joti Bhaban | 2019-09-02 | NQ1007 | 6.4 | 510 | 6.4 | 511 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 6576 | 2183.9997 | 67.4335
SYL-F.RR.367.1 | 24415559156287 | Fenchuganj, Poshchim Bazar, Mosjid Road, Nikhil Babu | 2019-09-02 | NQ1007 | 2.8 | 512 | 2.8 | 513 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 6576 | 2183.9997 | 29.5021
SYL-F.RR.368.1 | 24415559156287 | Fenchuganj, Poshchim Bazar, Mosjid Road, Nikhil Babu | 2019-09-02 | NQ1007 | 10.9 | 514 | 10.9 | 515 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 6576 | 2183.9997 | 114.8476
SYL-F.RR.369.1 | 24415879156250 | Fenchuganj, Poshchim Bazar, Poshchim Bazar Road, Manik Mia | 2019-09-02 | NQ1007 | 7 | 517 | 7 | 518 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6576 | 2183.9997 | 73.7554
SYL-F.RR.370.1 | 24415849156232 | Fenchuganj, Poshchim Bazar, Poshchim Bazar Road, Shohel Ahmed | 2019-09-02 | NQ1007 | 4.8 | 519 | 4.8 | 520 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 6576 | 2183.9997 | 50.5751
SYL-F.RR.371.1 | 24415849156232 | Fenchuganj, Poshchim Bazar, Poshchim Bazar Road, Jahangir Hossen | 2019-09-02 | NQ1007 | 10.4 | 521 | 10.4 | 522 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6576 | 2183.9997 | 109.5794
SYL-F.RR.372.1 | 24415739156233 | Fenchuganj, Poshchim Bazar, Poshchim Bazar Road, Boton Mia | 2019-09-02 | NQ1007 | 10.8 | 524 | 10.8 | 525 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 6576 | 2183.9997 | 113.794
SYL-F.RR.373.1 | 24420099156219 | Fenchuganj, Poshchim Bazar, Poshchim Bazar Road, Babor Ahmed | 2019-09-02 | NQ1007 | 8.1 | 526 | 8.1 | 527 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 6576 | 2183.9997 | 85.3455
SYL-F.RR.374.1 | 24415879156188 | Fenchuganj, Poshchim Bazar, Hospital Road, Provat Chandra Saha | 2019-09-02 | NQ1007 | 6.9 | 528 | 6.9 | 529 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 6576 | 2183.9997 | 72.7017
SYL-F.RR.375.1 | 24415889156172 | Fenchuganj, Poshchim Bazar, Hospital Road, Oliur Rahman, Morning Bird Diagonstic Center | 2019-09-02 | NQ1007 | 26.9 | 530 | 26.9 | 531 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 26.9 | 26.9 | 1.614 | 1.614 | 0.0007168 | 100% | 0% | 1.614 | 1.614 | 0.0011869 | 28 | 0.032355 | 0.032355 |  | 0 | 0 | 6576 | 2183.9997 | 283.4313
SYL-F.RR.376.1 | 24415729156173 | Fenchuganj, Poshchim Bazar, Hospital Road, Nahid Hasan | 2019-09-02 | NQ1007 | 11.9 | 532 | 11.9 | 533 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 6576 | 2183.9997 | 125.3841
SYL-F.RR.377.1 | 24415159157012 | Fenchuganj, Islampur, Islampur Road, Kazi Abdus Shohid Mia | 2019-09-03 | NQ1007 | 9.5 | 557 | 9.5 | 558 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 6576 | 2183.9997 | 100.0966
SYL-F.RR.378.1 | 24415159157012 | Fenchuganj, Islampur, Islampur Road, Kazi Abdus Shohid Mia | 2019-09-03 | NQ1007 | 1.6 | 559 | 1.6 | 560 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 6576 | 2183.9997 | 16.8584
SYL-F.RR.379.1 | 24415629157034 | Fenchuganj, Islampur, Islampur Road, Hazi Akter Hossen Salim | 2019-09-03 | NQ1007 | 6.3 | 561 | 6.3 | 562 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 6576 | 2183.9997 | 66.3798
SYL-F.RR.380.1 | 24415719157045 | Fenchuganj, Islampur, Islampur Road, Danda Bari, Chorkum Ali | 2019-09-03 | NQ1007 | 8.2 | 563 | 8 | 564 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 6576 | 2183.9997 | 84.2919
SYL-F.RR.381.1 | 24414899157091 | Fenchuganj, Islampur, Islampur Road, Sobur Tila, Onu Mia | 2019-09-03 | NQ1007 | 7 | 565 | 7 | 566 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 6576 | 2183.9997 | 73.7554
SYL-F.RR.382.1 | 24414899157091 | Fenchuganj, Islampur, Islampur Road, Sobur Tila, Onu Mia | 2019-09-03 | NQ1007 | 10.4 | 567 | 10.4 | 568 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 6576 | 2183.9997 | 109.5794
SYL-F.RR.383.1 | 24414889157039 | Fenchuganj, Islampur, Islampur Road, Fenchuganj Mohammadia Kamil (MA) Madrasha | 2019-09-03 | NQ1007 | 3.8 | 569 | 3.8 | 570 | 2022-01-01 | 2022-10-02 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 6576 | 2183.9997 | 40.0386
SYL-F.RR.384.1 | 24392479156568 | Fenchuganj, Monipur Tea Estate, Dr. Basith | 2019-09-04 | NQ1007 | 4.5 | 11 | 4.5 | 12 | 2022-01-01 | [9 empty] | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0
SYL-F.RR.385.1 | 24410339155109 | Fenchuganj, Fenchuganj Combained Cycle Power Plant, Ansar Camp Quater | 2019-09-05 | NQ1007 | 4.1 | 40 | 4.1 | 41 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 6504 | 2255.9997 | 43.1996
SYL-F.RR.386.1 | 24410509155070 | Fenchuganj, Fenchuganj Combained Cycle Power Plant, Meghna | 2019-09-05 | NQ1007 | 15.6 | 42 | 15.6 | 43 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 6504 | 2255.9997 | 164.3691
SYL-F.RR.387.1 | 24410509155070 | Fenchuganj, Fenchuganj Combained Cycle Power Plant, Padma | 2019-09-05 | NQ1007 | 5 | 44 | 5 | 45 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 6504 | 2255.9997 | 52.6824
SYL-F.RR.401.1 | 24391079156400 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd,Officers Quarter, Building # D-3 | 2019-09-05 | NQ1007 | 7.5 | 27 | 7.5 | 28 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 6504 | 2255.9997 | 79.0236
SYL-F.RR.402.1 | 24391079156404 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Officers Quarter, Building # E-1 | 2019-09-05 | NQ1007 | 11.5 | 32 | 11.5 | 33 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 6504 | 2255.9997 | 121.1695
SYL-F.RR.403.1 | 24391079156404 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Officers Quarter, Building # E-2 | 2019-09-05 | NQ1007 | 38.6 | 34 | 38.6 | 35 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 38.6 | 38.6 | 2.316 | 2.316 | 0.0007168 | 100% | 0% | 2.316 | 2.316 | 0.0011869 | 28 | 0.046428 | 0.046428 |  | 0 | 0 | 6504 | 2255.9997 | 406.7082
SYL-F.RR.404.1 | 24391889156366 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Stuff Quarter, Building # F-2 | 2019-09-05 | NQ1007 | 9.5 | 36 | 9.6 | 37 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 6504 | 2255.9997 | 101.1502
SYL-F.RR.405.1 | 24391889156366 | Fenchuganj, Shah-Jalal Fertilizer Co. Ltd, Stuff Quarter, Building # F-1 | 2019-09-05 | NQ1007 | 7.4 | 38 | 7.4 | 39 | 2022-01-01 | 2022-09-29 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 6504 | 2255.9997 | 77.97
SYL-G.1.CR.1.1 | 24482559202302 | Golapganj, Dhaka South, Dak Bangla Road, Al Amin Resturent | 2019-09-04 | LP1002 | 12.6 | 1 | 12.6 | 2 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7296 | 1463.9997 | 132.7597
SYL-G.1.CR.2.1 | 24482379202220 | Sylhet, Golapganj, Dhakadakshin, Dattarail,Salam Ga Road, Al Modina Restrent | 2019-09-04 | LU1001 | 6.7 | 15 | 6.7 | 16 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7296 | 1463.9997 | 70.5944
SYL-G.1.CR.3.1 | 24482029202397 | Golapganj, Dhaka South, Mohajon Potti, Mitali Bekary | 2019-09-04 | LP1002 | 11.1 | 17 | 11.1 | 18 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7296 | 1463.9997 | 116.9549
SYL-G.1.RR.1.1 | 24505219158102 | Golapgonj, Kaisthogram, Kosumbag | 2019-08-27 | NQ1002 | 2.6 | 163 | 2.5 | 164 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7272 | 1487.9997 | 26.3412
SYL-G.1.RR.1.2 | 24505219158102 | Golapgonj, Kaisthogram, Kosumbag | 2022-10-31 | NQ1007 | 9.5 | 92 | 9.5 | 93 | 2022-10-31 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 0 | 1487.9997 | 17.0027
SYL-G.1.RR.2.1 | 24504609158099 | Golapgonj, Kaisthogram, Kosumbag, Moiz Uddin | 2019-08-27 | NQ1002 | 10.9 | 167 | 10.4 | 168 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7272 | 1487.9997 | 109.5794
SYL-G.1.RR.2.2 | 24504609158099 | Golapgonj, Kaisthogram, Kosumbag, Moiz Uddin | 2021-02-07 | MN1018 | 13.4 | 82 | 13.4 | 83 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7272 | 1487.9997 | 141.1888
SYL-G.1.RR.5.1 | 24520849201445 | Golapganj, Choughori, Choughori Jame Masjid Road, Farid uddin | 2019-09-01 | LU1001 | 5.7 | 206 | 5.7 | 207 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7416 | 1343.9997 | 60.0579
SYL-G.1.RR.6.1 | 24520849201445 | Golapganj, Choughori, Choughori Jame Masjid Road, Joinal Ahmed | 2019-09-01 | LU1001 | 10.8 | 208 | 10.8 | 209 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7416 | 1343.9997 | 113.794
SYL-G.1.RR.7.1 | 24521339201505 | Golapganj, Choughori, Samsul Alam, (in front of Choughuri Jame Masjd) | 2019-09-01 | LU1001 | 9.1 | 210 | 9.1 | 211 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7416 | 1343.9997 | 95.882
SYL-G.1.RR.8.1 | 24521819201483 | Golapganj, Choughori, Choughori Jame Masjid Road, Hosen Ahmed | 2019-09-01 | LU1001 | 6.8 | 212 | 6.8 | 213 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7416 | 1343.9997 | 71.6481
SYL-G.1.RR.8.2 | 24521819201483 | Golapganj, Choughori, Choughori Jame Masjid Road, Hosen Ahmed | 2022-11-06 | NQ1007 | 3.6 | 139 | 3.6 | 140 | 2022-11-06 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 0 | 1343.9997 | 5.8196
SYL-G.1.RR.9.1 | 24521819201483 | Golapganj, Choughori, Choughori Jame Masjid Road, Zia uddin | 2019-09-01 | LU1001 | 6 | 214 | 6 | 215 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7416 | 1343.9997 | 63.2189
SYL-G.1.RR.10.1 | 24521869201544 | Golapganj, Choughori, South Moholla, A. Razzak | 2019-09-01 | LU1001 | 4.5 | 216 | 4.5 | 217 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7416 | 1343.9997 | 47.4142
SYL-G.1.RR.11.1 | 24530739202461 | Golapganj, Tohipur, Ward # 5, Abul Kalam | 2019-09-02 | LP1002 | 13.1 | 551 | 13.1 | 552 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7416 | 1343.9997 | 138.0279
SYL-G.1.RR.12.1 | 24530349202468 | Golapganj, Tohipur, Ward # 5, Nurul Haq | 2019-09-02 | LP1002 | 15.1 | 553 | 14.1 | 554 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7416 | 1343.9997 | 148.5644
SYL-G.1.RR.13.1 | 24530349202468 | Golapganj, Tohipur, Ward # 5, Samsul Haq | 2019-09-02 | LP1002 | 15.5 | 555 | 15.5 | 556 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 7416 | 1343.9997 | 163.3155
SYL-G.1.RR.14.1 | 24525859202443 | Golapganj, Tohipur, Ward # 5, Jamal | 2019-09-02 | LP1002 | 4.9 | 557 | 4.9 | 558 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7416 | 1343.9997 | 51.6288
SYL-G.1.RR.15.1 | 24525759202438 | Golapganj, Tohipur, Ward # 5, Lutu ma | 2019-09-02 | LP1002 | 10.8 | 559 | 10.3 | 560 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7416 | 1343.9997 | 108.5258
SYL-G.1.RR.16.1 | 24525759202438 | Golapganj, Tohipur, Ward # 5, Abul mia | 2019-09-02 | LP1002 | 7.4 | 561 | 7.4 | 562 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7416 | 1343.9997 | 77.97
SYL-G.1.RR.17.1 | 24524999202576 | Golapganj, Chandanbag, Para Bari, A. Hannan | 2019-09-02 | LP1002 | 13.1 | 563 | 13.1 | 564 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7440 | 1319.9997 | 138.0279
SYL-G.1.RR.18.1 | 24524999202576 | Golapganj, Chandanbag, Para Bari, A. Rahim | 2019-09-02 | LP1002 | 8.8 | 565 | 8.8 | 566 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7440 | 1319.9997 | 92.721
SYL-G.1.RR.18.2 | 24524999202576 | Golapganj, Chandanbag, Para Bari, A. Rahim | 2022-04-10 | LU1001 | 14.8 | 137 | 14.8 | 138 | 2022-04-10 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 5064 | 1319.9997 | 113.6439
SYL-G.1.RR.19.1 | 24521409201398 | Golapganj, Choughori, A. Motin, (Near Ranaping School & Collage) | 2019-09-03 | LP1002 | 14.7 | 577 | 14.7 | 578 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7416 | 1343.9997 | 154.8863
SYL-G.1.RR.20.1 | 24521409201398 | Golapganj, Choughori, Late Asoddor Ali, (Near Ranaping School & Collage) | 2019-09-03 | LP1002 | 11.8 | 579 | 11.8 | 580 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7416 | 1343.9997 | 124.3305
SYL-G.1.RR.21.1 | 24521229201368 | Golapganj, Choughori, Ali Manjil, Sohidur Rahman | 2019-09-03 | LP1002 | 8.5 | 581 | 7.8 | 582 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7416 | 1343.9997 | 82.1846
SYL-G.1.RR.22.1 | 24521229201368 | Golapganj, Choughori, Ali Manjil, Zomir Ahmad | 2019-09-03 | LP1002 | 13.6 | 583 | 13 | 584 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7416 | 1343.9997 | 136.9743
SYL-G.1.RR.23.1 | 24521229201368 | Golapganj, Choughori, Ali Manjil, Masum Ahmad | 2019-09-03 | LP1002 | 15.5 | 585 | 15.5 | 586 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 7416 | 1343.9997 | 163.3155
SYL-G.1.RR.24.1 | 24514059201047 | Golapganj, Daripaton, Noya Bari, Monu mia | 2019-09-03 | LP1002 | 14 | 587 | 13.5 | 588 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7440 | 1319.9997 | 142.2425
SYL-G.1.RR.24.2 | 24514059201047 | Golapganj, Daripaton, Noya Bari, Monu mia | 2020-10-22 | MN1032 | 2.5 | 675 | 2.3 | 676 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7440 | 1319.9997 | 24.2339
SYL-G.1.RR.25.1 | 24514059201047 | Golapganj, Daripaton, Noya Bari, Faisal | 2019-09-03 | LP1002 | 9.4 | 589 | 9.4 | 590 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7440 | 1319.9997 | 99.0429
SYL-G.1.RR.25.2 | 24514059201047 | Golapganj, Daripaton, Noya Bari, Faisal | 2022-11-07 | NQ1007 | 11.8 | 143 | 11.8 | 144 | 2022-11-07 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 0 | 1319.9997 | 18.7347
SYL-G.1.RR.26.1 | 24482099202223 | Golapganj, Dhaka South, Collage Road, Faruk Ahmad | 2019-09-04 | LP1002 | 14.9 | 3 | 14.9 | 4 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7296 | 1463.9997 | 156.9936
SYL-G.1.RR.26.2 | 24482099202223 | Golapganj, Dhaka South, Collage Road, Faruk Ahmad | 2019-09-04 | LP1002 | 8.5 | 5 | 8.5 | 6 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7296 | 1463.9997 | 89.5601
SYL-G.1.RR.27.1 | 24482229202279 | Golapganj, Dhaka South, Misro Para, Gones Pal | 2019-09-04 | LP1002 | 3.9 | 7 | 3.9 | 8 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7296 | 1463.9997 | 41.0923
SYL-G.1.RR.28.1 | 24482229202279 | Golapganj, Dhaka South, Misro Para, Milon Chandra | 2019-09-04 | LP1002 | 4.2 | 11 | 4.2 | 12 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7296 | 1463.9997 | 44.2532
SYL-G.1.RR.29.1 | 24482329202286 | Golapganj, Dhaka South, Misro Para, Sonju Dev | 2019-09-04 | LP1002 | 2.6 | 13 | 2.6 | 14 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7296 | 1463.9997 | 27.3949
SYL-G.1.RR.30.1 | 24482229202356 | Golapganj, Dhaka South, Misro Para, Mohajon Potti, Khosru Membar | 2019-09-04 | LP1002 | 9.6 | 15 | 9.6 | 16 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7296 | 1463.9997 | 101.1502
SYL-G.1.RR.31.1 | 24524599203574 | Golapganj, Fazilpur, Boro Bari, A. Sohid | 2019-09-05 | LP1002 | 7.3 | 33 | 7.3 | 34 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7440 | 1319.9997 | 76.9163
SYL-G.1.RR.32.1 | 24524599203574 | Golapganj, Fazilpur, Boro Bari, Usman uddin | 2019-09-05 | LP1002 | 2.1 | 35 | 2.1 | 36 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7440 | 1319.9997 | 22.1266
SYL-G.1.RR.33.1 | 24524599203574 | Golapganj, Fazilpur, Boro Bari, A. Gofur | 2019-09-05 | LP1002 | 11.6 | 37 | 11.6 | 38 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7440 | 1319.9997 | 122.2232
SYL-G.1.RR.34.1 | 24524599203574 | Golapganj, Fazilpur, Boro Bari, Zia uddin | 2019-09-05 | LP1002 | 11.1 | 39 | 11.1 | 40 | 2022-01-01 | 2022-11-07 | NQ1007 | 1.8 | 141 | 1.8 | 142 | 2022-11-07 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7440 | 1319.9997
SYL-G.1.RR.34.2 | 24524599203574 | Golapganj, Fazilpur, Boro Bari, Zia uddin | 2021-09-14 | NQ1007 | 7.7 | 22 | 7.7 | 23 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7440 | 1319.9997 | 81.1309
SYL-G.1.RR.35.1 | 24524399203576 | Golapganj, Fazilpur, Boro Bari, Altafur Rahman | 2019-09-05 | LP1002 | 38.7 | 41 | 38.7 | 42 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 38.7 | 38.7 | 2.322 | 2.322 | 0.0007168 | 100% | 0% | 2.322 | 2.322 | 0.0011869 | 28 | 0.046548 | 0.046548 |  | 0 | 0 | 7440 | 1319.9997 | 407.7618
SYL-G.1.RR.35.2 | 24524399203576 | Golapganj, Fazilpur, Boro Bari, Altafur Rahman | 2022-11-07 | NQ1007 | 5.6 | 147 | 5.6 | 148 | 2022-11-07 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 0 | 1319.9997 | 8.8911
SYL-G.1.RR.36.1 | 24524059203546 | Golapganj, Fazilpur, Boro Bari, Mokitur Rahman | 2019-09-05 | LP1002 | 5 | 43 | 5 | 44 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7440 | 1319.9997 | 52.6824
SYL-G.1.RR.37.1 | 24524059203546 | Golapganj, Fazilpur, Boro Bari, Jahidul Islam | 2019-09-05 | LP1002 | 6 | 45 | 6 | 46 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7440 | 1319.9997 | 63.2189
SYL-G.1.RR.38.1 | 24524059203546 | Golapganj, Fazilpur, Boro Bari, Fokhrul Islam | 2019-09-05 | LP1002 | 10.6 | 47 | 10 | 48 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7440 | 1319.9997 | 105.3648
SYL-G.1.RR.38.2 | 24524059203546 | Golapganj, Fazilpur, Boro Bari, Fokhrul Islam | 2019-09-05 | LP1002 | 51.8 | 49 | 51.8 | 50 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 51.8 | 51.8 | 3.108 | 3.108 | 0.0007168 | 100% | 0% | 3.108 | 3.108 | 0.0011869 | 28 | 0.062305 | 0.062305 |  | 0 | 0 | 7440 | 1319.9997 | 545.7897
SYL-G.1.RR.39.1 | 24484009203027 | Golapganj, South Raigor, Rafiqul Islam | 2019-09-05 | LP1002 | 11.2 | 51 | 10.8 | 52 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7320 | 1439.9997 | 113.794
SYL-G.1.RR.39.2 | 24484009203027 | Golapganj, South Raigor, Rafiqul Islam | 2021-02-03 | LX1011 | 7.1 | 90 | 7.1 | 91 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7320 | 1439.9997 | 74.809
SYL-G.1.RR.40.1 | 24484529202484 | Golapganj, South Raigor, Alamin | 2019-09-05 | LP1002 | 6.3 | 53 | 6.3 | 54 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7320 | 1439.9997 | 66.3798
SYL-G.1.RR.41.1 | 24452649201063 | Golapganj, Vadeswar, Dokkhin Vag, Rokib Ali Mastar | 2019-09-07 | LP1002 | 7.3 | 55 | 7.3 | 56 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7248 | 1511.9997 | 76.9163
SYL-G.1.RR.42.1 | 24453359201044 | Golapganj, Vadeswar, Dokkhin Vag, Sayed Ahmad | 2019-09-07 | LP1002 | 2.2 | 57 | 2.2 | 58 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7248 | 1511.9997 | 23.1803
SYL-G.1.RR.43.1 | 24453359201044 | Golapganj, Vadeswar, Dokkhin Vag, Sahjalal Siraj | 2019-09-07 | LP1002 | 6.3 | 59 | 6.3 | 60 | 2022-01-01 | [9 empty] | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0
SYL-G.1.RR.44.1 | 24453359201044 | Golapganj, Vadeswar, Dokkhin Vag, A. Khalek Siraj | 2019-09-07 | LP1002 | 14.5 | 61 | 14.2 | 62 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7248 | 1511.9997 | 149.618
SYL-G.1.RR.45.1 | 24453239201112 | Golapganj, Vadeswar, Hospital Road, Fotik | 2019-09-07 | LP1002 | 2.7 | 63 | 2.7 | 64 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7248 | 1511.9997 | 28.4485
SYL-G.1.RR.46.1 | 24453239201112 | Golapganj, Vadeswar, Hospital Road, Nanu | 2019-09-07 | LP1002 | 11.6 | 65 | 11.6 | 66 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7248 | 1511.9997 | 122.2232
SYL-G.1.RR.47.1 | 24453799200549 | Golapganj, Vadeswar, Moddho Dokkhin Vag, Mostak | 2019-09-07 | LP1002 | 5.6 | 67 | 5.6 | 68 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7248 | 1511.9997 | 59.0043
SYL-G.1.RR.48.1 | 24452709200594 | Golapganj, Vadeswar, Dokkhin Vag, Alauddin | 2019-09-07 | LP1002 | 6.1 | 69 | 6.1 | 70 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7248 | 1511.9997 | 64.2725
SYL-G.1.RR.49.1 | 24454589200433 | Golapganj, Vadeswar, West Vag, Late Hazi Azhar Ali | 2019-09-08 | LP1002 | 8.1 | 77 | 8.1 | 78 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7248 | 1511.9997 | 85.3455
SYL-G.1.RR.50.1 | 24454159200436 | Golapganj, Vadeswar, Dokkhin Vag, West Tila, A. Nur | 2019-09-08 | LP1002 | 11.5 | 79 | 11.5 | 80 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7248 | 1511.9997 | 121.1695
SYL-G.1.RR.50.2 | 24454159200436 | Golapganj, Vadeswar, Dokkhin Vag, West Tila, A. Nur | 2021-02-02 | LX1011 | 12.8 | 84 | 12.8 | 85 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7248 | 1511.9997 | 134.867
SYL-G.1.RR.51.1 | 24512469200526 | Sylhet, Golapganj, Choumohani, Dhaka Dokkhin Road, Shafi | 2019-08-31 | LP1002 | 6.5 | 513 | 6.5 | 514 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7344 | 1415.9997 | 68.4871
SYL-G.1.RR.52.1 | 24512459200530 | Sylhet, Golapganj, Choumohani, Dhaka Dokkhin Road, Shahabuddin | 2019-08-31 | LP1002 | 20.4 | 515 | 20.5 | 516 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 20.5 | 20.5 | 1.23 | 1.23 | 0.0007168 | 100% | 0% | 1.23 | 1.23 | 0.0011869 | 28 | 0.024657 | 0.024657 |  | 0 | 0 | 7344 | 1415.9997 | 215.9979
SYL-G.1.RR.53.1 | 24512459200530 | Sylhet, Golapganj, Choumohani, Dhaka Dokkhin Road, H # 10, Hazi Mohibur Rohoman | 2019-08-31 | LP1002 | 14.7 | 517 | 14.7 | 518 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7344 | 1415.9997 | 154.8863
SYL-G.1.RR.54.1 | 24512609200560 | Sylhet, Golapganj, Choumohani, Dhaka Dokkhin Road, Astokin Ali | 2019-08-31 | LP1002 | 14.2 | 519 | 14.2 | 520 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7344 | 1415.9997 | 149.618
SYL-G.1.RR.55.1 | 24512409200566 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Mokadas Ali | 2019-08-31 | LP1002 | 15.7 | 521 | 15.7 | 522 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 7344 | 1415.9997 | 165.4228
SYL-G.1.RR.55.2 | 24512409200566 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Mokadas Ali | 2022-11-03 | NQ1007 | 3.7 | 126 | 3.7 | 127 | 2022-11-03 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 0 | 1415.9997 | 6.3017
SYL-G.1.RR.56.1 | 24512359200579 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Nur Islam | 2019-08-31 | LP1002 | 5.6 | 525 | 5.6 | 526 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7344 | 1415.9997 | 59.0043
SYL-G.1.RR.57.1 | 24512359200579 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Beside Nur Islam | 2019-08-31 | LP1002 | 4.4 | 527 | 4.2 | 528 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7344 | 1415.9997 | 44.2532
SYL-G.1.RR.57.2 | 24512359200579 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Beside Nur Islam | 2021-02-08 | MN1018 | 22.4 | 88 | 22.4 | 89 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 22.4 | 22.4 | 1.344 | 1.344 | 0.0007168 | 100% | 0% | 1.344 | 1.344 | 0.0011869 | 28 | 0.026943 | 0.026943 |  | 0 | 0 | 7344 | 1415.9997 | 236.0172
SYL-G.1.RR.58.1 | 24512269200572 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Nozrul Islam | 2019-08-31 | LP1002 | 5.8 | 529 | 5.8 | 530 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7344 | 1415.9997 | 61.1116
SYL-G.1.RR.58.2 | 24512269200572 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Nozrul Islam | 2021-02-08 | MN1018 | 8 | 86 | 8 | 87 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7344 | 1415.9997 | 84.2919
SYL-G.1.RR.59.1 | 24512089201000 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Jamal Ahamod, Oppside Of LP Gas Ltd. | 2019-08-31 | LP1002 | 19.2 | 531 | 19.5 | 532 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 19.5 | 19.5 | 1.17 | 1.17 | 0.0007168 | 100% | 0% | 1.17 | 1.17 | 0.0011869 | 28 | 0.023454 | 0.023454 |  | 0 | 0 | 7344 | 1415.9997 | 205.4614
SYL-G.1.RR.60.1 | 24511329201012 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Md. Mojammel | 2019-08-31 | LP1002 | 11 | 533 | 10.9 | 534 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7344 | 1415.9997 | 114.8476
SYL-G.1.RR.61.1 | 24511469201019 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Shofq Uddin | 2019-09-01 | LP1002 | 11.5 | 535 | 11.5 | 536 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7344 | 1415.9997 | 121.1695
SYL-G.1.RR.62.1 | 24511469201019 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Habibur Rohaman Salim | 2019-09-01 | LP1002 | 10.2 | 537 | 10.2 | 538 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7344 | 1415.9997 | 107.4721
SYL-G.1.RR.63.1 | 24511379201006 | Golapganj, Tokor Bari, Dhaka Dokkhin Road, Monsar Ali | 2019-09-01 | LP1002 | 6.9 | 539 | 6.9 | 540 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7344 | 1415.9997 | 72.7017
SYL-G.1.RR.64.1 | 24505869201141 | Golapganj, Ronokali, Uttor Porusabha, Md. Faruk | 2019-09-01 | LP1002 | 9.1 | 541 | 9.1 | 542 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7392 | 1367.9997 | 95.882
SYL-G.1.RR.65.1 | 24505719201101 | Golapganj, Ronokali, Dhaka Dokkhin Road, Hasna Khan Vila | 2019-09-01 | LP1002 | 4.7 | 543 | 4.7 | 544 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7392 | 1367.9997 | 49.5215
SYL-G.1.RR.66.1 | 24505279201205 | Golapganj, Ronokali, Dhaka Dokkhin Road, Askir Mia | 2019-09-01 | LP1002 | 20.6 | 545 | 20.6 | 546 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 20.6 | 20.6 | 1.236 | 1.236 | 0.0007168 | 100% | 0% | 1.236 | 1.236 | 0.0011869 | 28 | 0.024778 | 0.024778 |  | 0 | 0 | 7392 | 1367.9997 | 217.0515
SYL-G.1.RR.67.1 | 24505089201233 | Golapganj, Ronokali, Dhaka Dokkhin Road, Altab Chowdhory | 2019-09-01 | LP1002 | 9.3 | 547 | 9.7 | 548 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7392 | 1367.9997 | 102.2039
SYL-G.1.RR.68.1 | 24504649201117 | Golapganj, Ronokali, Dhaka Dokkhin Road, S.P Lutfor | 2019-09-01 | LP1002 | 11.1 | 549 | 12.2 | 550 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7392 | 1367.9997 | 128.5451
SYL-G.1.RR.69.1 | 24530679203321 | Golapganj, Ranapink Bazar, A. MaliK | 2019-09-02 | LP1002 | 12.8 | 567 | 12.8 | 568 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7440 | 1319.9997 | 134.867
SYL-G.1.RR.70.1 | 24530679203321 | Golapganj, Ranapink Bazar, Tazul Islam | 2019-09-02 | LP1002 | 16.2 | 569 | 16.2 | 570 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 7440 | 1319.9997 | 170.691
SYL-G.1.RR.71.1 | 24530169203311 | Golapganj, Ranapink, Cottrish, Fozlur Korim | 2019-09-02 | LP1002 | 9 | 571 | 9 | 572 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7440 | 1319.9997 | 94.8283
SYL-G.1.RR.72.1 | 24525869203306 | Golapganj, Ranapink, Cottrish, Hazi Leakot Ali | 2019-09-02 | LP1002 | 9.2 | 573 | 9.2 | 574 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7440 | 1319.9997 | 96.9356
SYL-G.1.RR.73.1 | 24530869204040 | Golapganj, Fazlpur, Shafa Monjl, A. Mojid | 2019-09-02 | LP1002 | 69.4 | 575 | 69.4 | 576 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 69.4 | 69.4 | 4.164 | 4.164 | 0.0007168 | 100% | 0% | 4.164 | 4.164 | 0.0011869 | 28 | 0.083474 | 0.083474 |  | 0 | 0 | 7440 | 1319.9997 | 731.2318
SYL-G.1.RR.74.1 | 24502169201357 | Golapganj, Ranakhali, Nur Para, Dhaka Dokkhin Road, Salim Ahamad | 2019-09-03 | LP1002 | 12.9 | 591 | 13.2 | 592 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7392 | 1367.9997 | 139.0816
SYL-G.1.RR.75.1 | 24502339201365 | Golapganj, Ranakhali, Nur Para, Dhaka Dokkhin Road, Bahar Uddin | 2019-09-03 | LP1002 | 11 | 593 | 11 | 594 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7392 | 1367.9997 | 115.9013
SYL-G.1.RR.76.1 | 24495979201445 | Golapganj, Ranakhali, Dhaka Dokkhin Road, Azib Ali | 2019-09-03 | LP1002 | 7 | 595 | 7 | 596 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7320 | 1439.9997 | 73.7554
SYL-G.1.RR.77.1 | 24495979201445 | Golapganj, Ranakhali, Dhaka Dokkhin Road, Nozib Ali | 2019-09-03 | LP1002 | 11.6 | 597 | 11.6 | 598 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7320 | 1439.9997 | 122.2232
SYL-G.1.RR.78.1 | 24495979201445 | Golapganj, Ranakhali, Dhaka Dokkhin Road, Tozib Ali | 2019-09-03 | LP1002 | 3.4 | 599 | 3.4 | 600 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7320 | 1439.9997 | 35.824
SYL-G.1.RR.79.1 | 24495559202392 | Golapganj, Dhara Bhohon, Khoyaj Ahamod Loskar | 2019-09-03 | LP1002 | 11.7 | 601 | 11.7 | 602 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7320 | 1439.9997 | 123.2768
SYL-G.1.RR.80.1 | 24490239201597 | Dhaka Dokkhin, Dattarail, A. Barak | 2019-09-04 | LP1002 | 3.6 | 19 | 3.4 | 20 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7320 | 1439.9997 | 35.824
SYL-G.1.RR.81.1 | 24490239201597 | Dhaka Dokkhin, Dattarail, Rofique Uddin | 2019-09-04 | LP1002 | 10.7 | 21 | 10.7 | 22 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7320 | 1439.9997 | 112.7403
SYL-G.1.RR.82.1 | 24490239201597 | Dhaka Dokkhin, Dattarail, A. Noor | 2019-09-04 | LP1002 | 13.3 | 23 | 13.3 | 24 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7320 | 1439.9997 | 140.1352
SYL-G.1.RR.83.1 | 24453819201070 | Golapganj, Bhadeshwar, Dokkhin Bhag, Digerpar, Soyed Bodirul Haque | 2019-09-07 | LP1002 | 3.6 | 71 | 3.6 | 72 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7248 | 1511.9997 | 37.9313
SYL-G.1.RR.84.1 | 24453819201070 | Golapganj, Bhadeshwar, Dokkhin Bhag, Digerpar, Al Bab Hossan | 2019-09-07 | LP1002 | 1.6 | 73 | 1.6 | 74 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7248 | 1511.9997 | 16.8584
SYL-G.1.RR.85.1 | 24454539200509 | Golapganj, Bhadeshwar, Dokkhin Bhag, Dorgadair, Tarak Ahamod | 2019-09-07 | LP1002 | 2.9 | 75 | 2.9 | 76 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7248 | 1511.9997 | 30.5558
SYL-G.1.RR.86.1 | 24494379202337 | Golapganj, Dhara Bohor, Taz Monjil, Abdus Salam | 2019-09-09 | LP1002 | 2.3 | 89 | 2.3 | 90 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7320 | 1439.9997 | 24.2339
SYL-G.1.RR.87.1 | 24494029202466 | Gopalganj, Shil Ghat Tikor Para, Anamul Haque Babul | 2019-09-09 | LP1002 | 11.5 | 91 | 11.5 | 92 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7320 | 1439.9997 | 121.1695
SYL-G.1.RR.87.2 | 24494029202466 | Gopalganj, Shil Ghat Tikor Para, Anamul Haque Babul | 2022-04-11 | LU1001 | 24 | 139 | 23.7 | 140 | 2022-04-11 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 23.7 | 23.7 | 1.422 | 1.422 | 0.0007168 | 100% | 0% | 1.422 | 1.422 | 0.0011869 | 28 | 0.028506 | 0.028506 |  | 0 | 0 | 4920 | 1439.9997 | 181.2996
SYL-G.1.RR.88.1 | 24493099202446 | Gopalganj, Shil Ghat Tikor Para, Dawloer Hossan | 2019-09-09 | LP1002 | 5.4 | 93 | 5.4 | 94 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7320 | 1439.9997 | 56.897
SYL-G.1.RR.89.1 | 24493079203048 | Gopalganj, Shil Ghat Tikor Para, Beside Of Shil Ghat Prmary School, Faruk Mia | 2019-09-09 | LP1002 | 10.7 | 95 | 10.1 | 96 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7320 | 1439.9997 | 106.4185
SYL-G.1.RR.90.1 | 24493049203051 | Gopalganj, Shil Ghat Tikor Para, Beside Of Shil Ghat Primary School, A. Hadi | 2019-09-09 | LP1002 | 14.4 | 97 | 14.4 | 98 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7320 | 1439.9997 | 151.7253
SYL-G.1.RR.91.1 | 24492579203048 | Gopalganj, Shil Ghat, Raygor, A. Aziz | 2019-09-09 | LP1002 | 4.9 | 99 | 4.9 | 100 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7320 | 1439.9997 | 51.6288
SYL-G.1.RR.92.1 | 24492349202590 | Gopalganj, North Raygor, Gonas | 2019-09-09 | LP1002 | 13.9 | 103 | 13.9 | 104 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7320 | 1439.9997 | 146.4571
SYL-G.1.RR.93.1 | 24495479201149 | Gopalganj, Baro kut, Jamal uddin | 2019-09-09 | LP1002 | 3.8 | 105 | 3.8 | 106 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7320 | 1439.9997 | 40.0386
SYL-G.1.RR.94.1 | 24504039200137 | Golapganj, Ghosh Gau, Netay Das | 2019-09-11 | LP1002 | 6.2 | 123 | 6.2 | 124 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7344 | 1415.9997 | 65.3262
SYL-G.1.RR.94.2 | 24504039200137 | Golapganj, Ghosh Gau, Netay Das | 2019-09-11 | LP1002 | 15.8 | 125 | 16.1 | 126 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 7344 | 1415.9997 | 169.6373
SYL-G.1.RR.95.1 | 24503969200131 | Golapganj, Ghosh Gau, Shojt Das | 2019-09-11 | LP1002 | 4.9 | 127 | 4.7 | 128 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7344 | 1415.9997 | 49.5215
SYL-G.1.RR.96.1 | 24503789200108 | Golapganj, Ghosh Gau, Dilu Das | 2019-09-11 | LP1002 | 4.1 | 129 | 4.1 | 130 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7344 | 1415.9997 | 43.1996
SYL-G.1.RR.96.2 | 24503789200108 | Golapganj, Ghosh Gau, Dilu Das | 2022-11-03 | NQ1007 | 24.5 | 124 | 24.5 | 125 | 2022-11-03 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 0 | 1415.9997 | 41.7273
SYL-G.1.RR.97.1 | 24504719200246 | Golapganj, East Ghosh Gau, Adluddin | 2019-09-11 | LP1002 | 38 | 131 | 38 | 132 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 38 | 38 | 2.28 | 2.28 | 0.0007168 | 100% | 0% | 2.28 | 2.28 | 0.0011869 | 28 | 0.045706 | 0.045706 |  | 0 | 0 | 7344 | 1415.9997 | 400.3863
SYL-G.1.RR.97.2 | 24504719200246 | Golapganj, East Ghosh Gau, Adluddin | 2022-04-12 | LU1001 | 11.5 | 149 | 11.4 | 150 | 2022-04-12 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 4920 | 1415.9997 | 86.8783
SYL-G.1.RR.98.1 | 24510469159508 | Glapganj, Fulbari, Ucha Bari, Rahan Uddin Chowdhory | 2019-09-11 | LP1002 | 6 | 133 | 6 | 134 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7272 | 1487.9997 | 63.2189
SYL-G.1.RR.99.1 | 24510469159508 | Glapganj, Fulbari, Ucha Bari, Beside Of Rahan Uddin Chowdhory | 2019-09-11 | LP1002 | 8.1 | 135 | 8.1 | 136 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7272 | 1487.9997 | 85.3455
SYL-G.1.RR.100.1 | 24482979157564 | Golapganj, South Laxmipasha, Laxmipasha Bazer, A. Mmin Khan Sabul | 2019-09-12 | LP1002 | 2.2 | 147 | 2.2 | 148 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7224 | 1535.9997 | 23.1803
SYL-G.1.RR.101.1 | 24514329201308 | Golapganj, Darepaton Road # 3, Darepaton Main Mosque And Sahe Eidga, Chrag Mia | 2019-09-01 | MN1018 | 5.9 | 518 | 5.5 | 519 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7440 | 1319.9997 | 57.9506
SYL-G.1.RR.102.1 | 24514329201308 | Golapganj, Darepaton Road # 3, Darepaton Main Mosque And Sahe Eidga, Dudu Mia | 2019-09-01 | MN1018 | 9.5 | 520 | 9.5 | 521 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7440 | 1319.9997 | 100.0966
SYL-G.1.RR.103.1 | 24514419201342 | Golapganj, Darepaton Road # 3, Darepaton Main Mosque And Sahe Eidga, Abdul Motin | 2019-09-01 | MN1018 | 2.5 | 522 | 2.5 | 523 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7440 | 1319.9997 | 26.3412
SYL-G.1.RR.104.1 | 24514189201261 | Golapganj, Darepaton Road # 3, Darepaton Main Mosque And Sahe Eidga, Atur Rahman | 2019-09-01 | MN1018 | 12.1 | 524 | 11.7 | 525 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7440 | 1319.9997 | 123.2768
SYL-G.1.RR.105.1 | 24514189201261 | Golapganj, Darepaton Road # 3, Darepaton Main Mosque And Sahe Eidga, Samim Ahmed | 2019-09-01 | MN1018 | 9.6 | 530 | 10.5 | 531 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7440 | 1319.9997 | 110.6331
SYL-G.1.RR.106.1 | 24523829201596 | Golapganj, 2 No Golapganj Union, Goispur, Jalal | 2019-09-01 | MN1018 | 11.2 | 532 | 11.1 | 533 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7416 | 1343.9997 | 116.9549
SYL-G.1.RR.107.1 | 24523649202045 | Golapganj, 2 No Golapganj Union, Goispur, Brohon Uddin | 2019-09-01 | MN1018 | 5.3 | 534 | 5.3 | 535 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7416 | 1343.9997 | 55.8434
SYL-G.1.RR.108.1 | 24523649202045 | Golapganj, 2 No Golapganj Union, Goispur, Abdur Rahim | 2019-09-02 | MN1018 | 12.6 | 540 | 12.6 | 541 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7416 | 1343.9997 | 132.7597
SYL-G.1.RR.109.1 | 24523649202045 | Golapganj, 2 No Golapganj Union, Goispur, Sonjit Ali | 2019-09-02 | MN1018 | 3.9 | 544 | 3.9 | 545 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7416 | 1343.9997 | 41.0923
SYL-G.1.RR.110.1 | 24523499202039 | Golapganj, 2 No Golapganj Union, Goispur, Alauddin | 2019-09-02 | MN1018 | 4.6 | 546 | 4.6 | 547 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7416 | 1343.9997 | 48.4678
SYL-G.1.RR.110.2 | 24523499202039 | Golapganj, 2 No Golapganj Union, Goispur, Alauddin | 2021-09-15 | LX1011 | 9 | 626 | 9 | 627 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7416 | 1343.9997 | 94.8283
SYL-G.1.RR.111.1 | 24523489202127 | Golapganj, 2 No Golapganj Union, Goispur, Emamuddin | 2019-09-02 | MN1018 | 10.4 | 548 | 10.4 | 549 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7416 | 1343.9997 | 109.5794
SYL-G.1.RR.112.1 | 24523489202127 | Golapganj, 2 No Golapganj Union, Goispur, Serajuddin | 2019-09-02 | MN1018 | 11.5 | 550 | 11.5 | 551 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7416 | 1343.9997 | 121.1695
SYL-G.1.RR.113.1 | 24523799202146 | Golapganj, 2 No Golapganj Union, Goispur, MD Monsur Momriel | 2019-09-02 | MN1018 | 1.8 | 552 | 1.8 | 553 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7416 | 1343.9997 | 18.9657
SYL-G.1.RR.114.1 | 24523529102164 | Golapganj, 2 No Golapganj Union, Goispur, Afther Ali | 2019-09-02 | MN1018 | 11.6 | 554 | 11.6 | 555 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7416 | 1343.9997 | 122.2232
SYL-G.1.RR.115.1 | 24523459202175 | Golapganj, 2 No Golapganj Union, Goispur, Nazrul Islam | 2019-09-02 | MN1018 | 6.8 | 556 | 6.8 | 557 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7416 | 1343.9997 | 71.6481
SYL-G.1.RR.116.1 | 24523189201491 | Golapganj,Chokoria Bazar Union, Goispur,Asab Ali | 2019-09-02 | MN1018 | 64.9 | 558 | 64.9 | 559 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 64.9 | 64.9 | 3.894 | 3.894 | 0.0007168 | 100% | 0% | 3.894 | 3.894 | 0.0011869 | 28 | 0.078061 | 0.078061 |  | 0 | 0 | 7416 | 1343.9997 | 683.8176
SYL-G.1.RR.117.1 | 24525719202247 | Golapganj, Uttor Goispur, Pattiura, Asraf Ali | 2019-09-03 | MN1018 | 10.3 | 578 | 10.3 | 579 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7416 | 1343.9997 | 108.5258
SYL-G.1.RR.118.1 | 24514839201166 | Golapganj, Daripaton Digher par, Abdul Kabir | 2019-09-03 | MN1018 | 7 | 580 | 7 | 581 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7416 | 1343.9997 | 73.7554
SYL-G.1.RR.119.1 | 24514839201166 | Golapganj, Daripaton Digher par, Liton Ahmed | 2019-09-03 | MN1018 | 9.4 | 582 | 9.4 | 583 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7416 | 1343.9997 | 99.0429
SYL-G.1.RR.120.1 | 24514879201153 | Golapganj, Daripaton Digher par, Anisur Rahman | 2019-09-03 | MN1018 | 15 | 584 | 14.5 | 585 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7416 | 1343.9997 | 152.779
SYL-G.1.RR.121.1 | 24515099201145 | Golapganj, Daripaton Digher par, Intaz ali | 2019-09-03 | MN1018 | 11.3 | 586 | 11.3 | 587 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7416 | 1343.9997 | 119.0622
SYL-G.1.RR.122.1 | 24515229201146 | Golapganj, Daripaton Digher par, Aftab ali | 2019-09-03 | MN1018 | 9.7 | 588 | 9.7 | 589 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7416 | 1343.9997 | 102.2039
SYL-G.1.RR.123.1 | 24515339201176 | Golapganj, Daripaton Digher par, Jonil Moyor | 2019-09-03 | MN1018 | 3.3 | 590 | 3.3 | 591 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7416 | 1343.9997 | 34.7704
SYL-G.1.RR.124.1 | 24515339201176 | Golapganj, Daripaton Digher par, Abul hasnat | 2019-09-03 | MN1018 | 5.5 | 592 | 5.5 | 593 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7416 | 1343.9997 | 57.9506
SYL-G.1.RR.125.1 | 24514949201168 | Golapganj, Daripaton Digher par, Abdus basid | 2019-09-03 | MN1018 | 4 | 594 | 4 | 595 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7416 | 1343.9997 | 42.1459
SYL-G.1.RR.126.1 | 24483129202304 | Golapganj, 6 No U.P. Road, Dhakadakshin Bazzar, Kichukshan Neer | 2019-09-04 | MN1018 | 15.8 | 3 | 15.8 | 4 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7320 | 1439.9997 | 166.4764
SYL-G.1.RR.127.1 | 24483129202304 | Golapganj, 6 No U.P. Road, Dhakadakshin Bazzar, OPU VILA | 2019-09-04 | MN1018 | 7.9 | 7 | 7.9 | 8 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7320 | 1439.9997 | 83.2382
SYL-G.1.RR.128.1 | 24483689202364 | Golapganj, 6 No U.P. Road, Dhakadakshin Bazzar, Abdur Rob | 2019-09-04 | MN1018 | 41.8 | 9 | 41 | 10 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 41 | 41 | 2.46 | 2.46 | 0.0007168 | 100% | 0% | 2.46 | 2.46 | 0.0011869 | 28 | 0.049315 | 0.049315 |  | 0 | 0 | 7320 | 1439.9997 | 431.9957
SYL-G.1.RR.129.1 | 24483749202298 | Golapganj, 6 No U.P. Road, Dhakadakshin Bazzar, Asraf Ali | 2019-09-04 | MN1018 | 15.3 | 11 | 15.3 | 12 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 7320 | 1439.9997 | 161.2082
SYL-G.1.RR.130.1 | 24483749202298 | Golapganj, 6 No U.P. Road, Dhakadakshin Bazzar, Asraf Ali Gong | 2019-09-04 | MN1018 | 2.8 | 13 | 2.8 | 14 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7320 | 1439.9997 | 29.5021
SYL-G.1.RR.131.1 | 24481839202444 | Golapganj, Dhakadakshin East Bazzar,Mozamal Ali | 2019-09-04 | MN1018 | 27.9 | 15 | 27.9 | 16 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 27.9 | 27.9 | 1.674 | 1.674 | 0.0007168 | 100% | 0% | 1.674 | 1.674 | 0.0011869 | 28 | 0.033558 | 0.033558 |  | 0 | 0 | 7296 | 1463.9997 | 293.9678
SYL-G.1.RR.131.2 | 24481839202444 | Golapganj, Dhakadakshin East Bazzar,Mozamal Ali | 2019-09-04 | MN1018 | 13 | 17 | 13 | 18 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7296 | 1463.9997 | 136.9743
SYL-G.1.RR.132.1 | 24481739202497 | Golapganj, 6 No Dhakadakshin U.P. Road East Bazar, Samsu | 2019-09-04 | MN1018 | 10.8 | 19 | 10.5 | 20 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7296 | 1463.9997 | 110.6331
SYL-G.1.RR.133.1 | 24481659202476 | Golapganj, 6 No Dhakadakshin U.P. Road East Bazar, Nobab Monjil | 2019-09-04 | MN1018 | 6.8 | 21 | 6.8 | 22 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7296 | 1463.9997 | 71.6481
SYL-G.1.RR.134.1 | 24481659202476 | Golapganj, 6 No Dhakadakshin U.P. Road East Bazar, Nobab Monjil | 2019-09-04 | MN1018 | 5.7 | 23 | 5.7 | 24 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7296 | 1463.9997 | 60.0579
SYL-G.1.RR.135.1 | 24480889202494 | Golapganj, 6 No Dhakadakshin, Nogor, Faruk Ahmed | 2019-09-05 | MN1018 | 16.5 | 33 | 16 | 34 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 7296 | 1463.9997 | 168.5837
SYL-G.1.RR.136.1 | 24480759202485 | Golapganj, 6 No Dhakadakshin, Nogor, Road # 3/1, Block # C, H # 27, Abdul Kader Anu Mia | 2019-09-05 | MN1018 | 21.4 | 35 | 20.9 | 36 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 20.9 | 20.9 | 1.254 | 1.254 | 0.0007168 | 100% | 0% | 1.254 | 1.254 | 0.0011869 | 28 | 0.025138 | 0.025138 |  | 0 | 0 | 7296 | 1463.9997 | 220.2125
SYL-G.1.RR.137.1 | 24480759202485 | Golapganj, 6 No Dhakadakshin, Nogor, Road # 3/1, Block # C, H # 16, Riachod Villa | 2019-09-05 | MN1018 | 7.3 | 39 | 7.3 | 40 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7296 | 1463.9997 | 76.9163
SYL-G.1.RR.138.1 | 24480649202494 | Golapganj, 6 No Dhakadakshin, Nogor, Abdul Bari | 2019-09-05 | MN1018 | 11.4 | 41 | 11.4 | 42 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7296 | 1463.9997 | 120.1159
SYL-G.1.RR.139.1 | 24480649202494 | Golapganj, 6 No Dhakadakshin, Nogor, Abdul Gofur | 2019-09-05 | MN1018 | 6.5 | 43 | 6.5 | 44 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7296 | 1463.9997 | 68.4871
SYL-G.1.RR.140.1 | 24480649202494 | Golapganj, 6 No Dhakadakshin, Nogor, Abdul Saltan | 2019-09-05 | MN1018 | 6.5 | 47 | 6 | 48 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7296 | 1463.9997 | 63.2189
SYL-G.1.RR.141.1 | 24480569202505 | Golapganj, 6 No Dhakadakshin, Nogor, Iqbal Ahmed | 2019-09-05 | MN1018 | 3.4 | 49 | 3.1 | 50 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7296 | 1463.9997 | 32.6631
SYL-G.1.RR.142.1 | 24480569202505 | Golapganj, 6 No Dhakadakshin, Nogor, Rofiqu uddin | 2019-09-05 | MN1018 | 1.8 | 51 | 1.8 | 52 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7296 | 1463.9997 | 18.9657
SYL-G.1.RR.143.1 | 24480569202505 | Golapganj, 6 No Dhakadakshin, Nogor, Jewel Ahmed | 2019-09-05 | MN1018 | 9.1 | 55 | 9.1 | 56 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7296 | 1463.9997 | 95.882
SYL-G.1.RR.144.1 | 24480419202496 | Golapganj, 6 No Dhakadakshin, Nogor, Fazlu Mia | 2019-09-05 | MN1018 | 5.7 | 57 | 5.7 | 58 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7296 | 1463.9997 | 60.0579
SYL-G.1.RR.145.1 | 24480419202496 | Golapganj, 6 No Dhakadakshin, Nogor, Mozibar Rahman | 2019-09-05 | MN1018 | 7 | 59 | 6.5 | 60 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7296 | 1463.9997 | 68.4871
SYL-G.1.RR.146.1 | 24480419202481 | Golapganj, 6 No Dhakadakshin, Nogor, Chraguddin | 2019-09-05 | MN1018 | 11 | 61 | 10.8 | 62 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7296 | 1463.9997 | 113.794
SYL-G.1.RR.147.1 | 24480229202477 | Golapganj, 6 No Dhakadakshin, Nogor, Sajib Ali | 2019-09-05 | MN1018 | 14.8 | 63 | 14.8 | 64 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 7296 | 1463.9997 | 155.9399
SYL-G.1.RR.148.1 | 24455019201101 | Vobshwar, South Mokam Bazar, Dargadair, Kamal Ahmed | 2019-09-07 | MN1018 | 16 | 97 | 16 | 98 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 7248 | 1511.9997 | 168.5837
SYL-G.1.RR.149.1 | 24454909201049 | Vobshwar, South Mokam Bazar, Dargadair, College Road, Osman Ahmed | 2019-09-07 | MN1018 | 14.1 | 99 | 14.1 | 100 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7248 | 1511.9997 | 148.5644
SYL-G.1.RR.150.1 | 24454729201048 | Vobshwar, South Mokam Bazar, Dargadair, Shak Para, Jazor Ali | 2019-09-07 | MN1018 | 10.5 | 101 | 10.5 | 102 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7248 | 1511.9997 | 110.6331
SYL-G.1.RR.150.2 | 24454729201048 | Vobshwar, South Mokam Bazar, Dargadair, Shak Para, Jazor Ali | 2019-09-07 | MN1018 | 38.4 | 103 | 38.4 | 104 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 38.4 | 38.4 | 2.304 | 2.304 | 0.0007168 | 100% | 0% | 2.304 | 2.304 | 0.0011869 | 28 | 0.046187 | 0.046187 |  | 0 | 0 | 7248 | 1511.9997 | 404.6009
SYL-G.1.RR.151.1 | 24512379200506 | Sylhet, Golapganj, Dhaka Dakkhin Road, Agroni R/A, Block-A, H# 7, Beside Atik Monjil | 2019-08-31 | MN1018 | 3 | 491 | 3 | 492 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7344 | 1415.9997 | 31.6094
SYL-G.1.RR.152.1 | 24512379200506 | Sylhet, Golapganj, Dhaka Dakkhin Road, Agroni R/A, Block-A, H# 2, Atik Monjil | 2019-08-31 | MN1018 | 3 | 493 | 2.9 | 494 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7344 | 1415.9997 | 30.5558
SYL-G.1.RR.153.1 | 24512309200495 | Sylhet, Golapganj, Dhaka Dakkhin Road, Agroni R/A, Block-A, H# 5, Hafizur Rahman | 2019-08-31 | MN1018 | 2.9 | 495 | 2.9 | 496 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7344 | 1415.9997 | 30.5558
SYL-G.1.RR.154.1 | 24512209200485 | Sylhet, Golapganj, Dhaka Dakkhin Road, Agroni R/A, Block-A, Beside Pouro Bhabon,Romana Cottage, Md. Nanu Mia(Hasanuzzaman) | 2019-08-31 | MN1018 | 6.4 | 498 | 6.4 | 499 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7344 | 1415.9997 | 67.4335
SYL-G.1.RR.155.1 | 24510579201129 | Sylhet, Golapganj, RonKali Uttor (Beside Dhaka Dakkhin Road), Selim | 2019-08-31 | MN1018 | 8.1 | 500 | 7.5 | 501 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7392 | 1367.9997 | 79.0236
SYL-G.1.RR.156.1 | 24512719159521 | Gulapganj, Baro Mukam Road, Abdul Mannan | 2019-09-01 | MN1018 | 18.2 | 502 | 18.2 | 503 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 7344 | 1415.9997 | 191.764
SYL-G.1.RR.157.1 | 24512729159511 | Gulapganj, Baro Mukam Road, Siraz Uddin Irah | 2019-09-01 | MN1018 | 8.7 | 504 | 8.7 | 505 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7344 | 1415.9997 | 91.6674
SYL-G.1.RR.158.1 | 24512729159511 | Gulapganj, Baro Mukam Road, Mukhles Ali | 2019-09-01 | MN1018 | 10.9 | 506 | 10.9 | 507 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7344 | 1415.9997 | 114.8476
SYL-G.1.RR.159.1 | 24511769200249 | Gulapganj, Dhakbangla, College Road, Ashar Alo Shisu Shikon Kendro | 2019-09-01 | MN1018 | 8.8 | 508 | 8.8 | 509 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7344 | 1415.9997 | 92.721
SYL-G.1.RR.160.1 | 24511819200175 | Golapganj,College Road, Fulbari Purbapara, Habibur Rahman | 2019-09-01 | MN1018 | 11.1 | 510 | 11.1 | 511 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7344 | 1415.9997 | 116.9549
SYL-G.1.RR.161.1 | 24511909200150 | Golapganj,College Road, Fulbari Purbapara, Fakhar Uddin | 2019-09-01 | MN1018 | 2.3 | 512 | 2.3 | 513 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7344 | 1415.9997 | 24.2339
SYL-G.1.RR.162.1 | 24512419159598 | Golapganj,College Road, Fulbari Purbapara, Janu Mia | 2019-09-01 | MN1018 | 1 | 514 | 1 | 515 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 7344 | 1415.9997 | 10.5365
SYL-G.1.RR.163.1 | 24512239159595 | Golapganj,College Road, Fulbari Purbapara, Hossen Ahmed | 2019-09-01 | MN1018 | 5.9 | 516 | 5.9 | 517 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7344 | 1415.9997 | 62.1652
SYL-G.1.RR.164.1 | 24524489202397 | Gulapganj, Chondonbag, T.C Road, Ashraful Alam Chowdury | 2019-09-02 | MN1018 | 1.3 | 560 | 1.3 | 561 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7416 | 1343.9997 | 13.6974
SYL-G.1.RR.165.1 | 24524369202404 | Gulapganj, Chondonbag, T.C Road, Abdul Kader Chowdury | 2019-09-02 | MN1018 | 44.6 | 562 | 44.6 | 563 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 44.6 | 44.6 | 2.676 | 2.676 | 0.0007168 | 100% | 0% | 2.676 | 2.676 | 0.0011869 | 28 | 0.053645 | 0.053645 |  | 0 | 0 | 7416 | 1343.9997 | 469.9271
SYL-G.1.RR.166.1 | 24523939202460 | Gulapganj, Chondonbag, Shamul Haque | 2019-09-02 | MN1018 | 16.8 | 564 | 16.8 | 565 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 7416 | 1343.9997 | 177.0129
SYL-G.1.RR.167.1 | 24523869202478 | Gulapganj , Chondonbag, Abdul Haque | 2019-09-02 | MN1018 | 16.5 | 566 | 16.5 | 567 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 7416 | 1343.9997 | 173.8519
SYL-G.1.RR.168.1 | 24523629202509 | Gulapganj, Chondonbag, Chondbag Puraton Jame Mosjid, Folik Uddin | 2019-09-02 | MN1018 | 9.3 | 568 | 9.3 | 569 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7416 | 1343.9997 | 97.9893
SYL-G.1.RR.169.1 | 24523629202509 | Gulapganj, Chondonbag, Chondbag Puraton Jame Mosjid, Boshir Uddin | 2019-09-02 | MN1018 | 9.1 | 570 | 9.1 | 571 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7416 | 1343.9997 | 95.882
SYL-G.1.RR.170.1 | 24523629202509 | Gulapganj, Chondonbag, Chondbag Puraton Jame Mosjid, Helal Uddin | 2019-09-02 | MN1018 | 9.9 | 572 | 9.9 | 573 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7416 | 1343.9997 | 104.3112
SYL-G.1.RR.171.1 | 24523229202303 | Gulapganj, Guaspur, Montor Bari, Abdul Musabbir Loskor | 2019-09-02 | MN1018 | 35.2 | 574 | 35.2 | 575 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 35.2 | 35.2 | 2.112 | 2.112 | 0.0007168 | 100% | 0% | 2.112 | 2.112 | 0.0011869 | 28 | 0.042338 | 0.042338 |  | 0 | 0 | 7416 | 1343.9997 | 370.8841
SYL-G.1.RR.172.1 | 24500319201416 | Gulapganj, Dhaka Dokkhin Road, Ronokheli, South Nuru Para,Saleh Ahmed | 2019-09-03 | MN1018 | 2.6 | 596 | 2.6 | 597 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7320 | 1439.9997 | 27.3949
SYL-G.1.RR.173.1 | 24493099201462 | Gulapganj, Darabohor, Gias Uddin | 2019-09-03 | MN1018 | 17.2 | 598 | 17.2 | 599 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 7320 | 1439.9997 | 181.2275
SYL-G.1.RR.174.1 | 24492739201454 | Gulapganj , Darabohor, Khushir Bari, Nurul Hamid | 2019-09-03 | MN1018 | 15 | 600 | 15 | 601 | 2022-01-01 | 2022-11-02 | NQ1007 |  |  | 0 | 112 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7320 | 1439.9997
SYL-G.1.RR.175.1 | 24492169201594 | Gulapganj, Darabohor Puran Bari, Jamshed Ali | 2019-09-03 | MN1018 | 9.7 | 602 | 9.7 | 603 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7320 | 1439.9997 | 102.2039
SYL-G.1.RR.176.1 | 24485839202026 | Gulapganj, Dhaka Dokkhin Road, Hatimganj, Dottorail, A Kuddus Ali | 2019-09-04 | MN1018 | 5.1 | 25 | 5.1 | 26 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7320 | 1439.9997 | 53.7361
SYL-G.1.RR.177.1 | 24485839202026 | Gulapganj, Dhaka Dokkhin Road, Hatimganj, Dottorail, Hazi Bodrul Islam Jamal | 2019-09-04 | MN1018 | 10.5 | 27 | 10.5 | 28 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7320 | 1439.9997 | 110.6331
SYL-G.1.RR.178.1 | 24485659202033 | Gulapganj, Dhaka Dokkhin Road, Hatimganj, Dottorail, Hazi Taher Ali | 2019-09-04 | MN1018 | 6.6 | 29 | 6.7 | 30 | 2022-01-01 | 2022-11-02 | NQ1007 |  |  | 0 | 110 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7320 | 1439.9997
SYL-G.1.RR.179.1 | 24493009201104 | Gulapganj, Baro Coat, Ouch Para, Saleh Ahmed | 2019-09-04 | MN1018 | 23.3 | 31 | 23.3 | 32 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 23.3 | 23.3 | 1.398 | 1.398 | 0.0007168 | 100% | 0% | 1.398 | 1.398 | 0.0011869 | 28 | 0.028025 | 0.028025 |  | 0 | 0 | 7320 | 1439.9997 | 245.5
SYL-G.1.RR.180.1 | 24481049202517 | Gulapganj, Dhaka Dakshin, Moddo Nagor, Shamsul Bari | 2019-09-05 | MN1018 | 11.8 | 65 | 11.8 | 66 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7296 | 1463.9997 | 124.3305
SYL-G.1.RR.181.1 | 24480769202530 | Gulapganj, Dhaka Dakshin, Moddo Nagor, Md. Alim Uddin | 2019-09-05 | MN1018 | 6.2 | 67 | 6.2 | 68 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7296 | 1463.9997 | 65.3262
SYL-G.1.RR.182.1 | 24480649202526 | Gulapganj, Dhaka Dakshin, Nagor, Doctor Ayub Ali | 2019-09-05 | MN1018 | 13.8 | 69 | 13.8 | 70 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7296 | 1463.9997 | 145.4034
SYL-G.1.RR.183.1 | 24480629202564 | Gulapganj, Dhaka Dakshin, Nagor, Saleh Ahmed, Beside Eidgah Mosjid | 2019-09-05 | MN1018 | 3.5 | 71 | 3.5 | 72 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7296 | 1463.9997 | 36.8777
SYL-G.1.RR.184.1 | 24465149201405 | Gulapganj, Purba Bhadeshwar, Naliari, Salim Uddin | 2019-09-05 | MN1018 | 10.1 | 73 | 10.1 | 74 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7296 | 1463.9997 | 106.4185
SYL-G.1.RR.184.2 | 24465149201405 | Gulapganj, Purba Bhadeshwar, Naliari, Salim Uddin | 2022-11-01 | NQ1007 | 12.4 | 105 | 12.4 | 106 | 2022-11-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 0 | 1463.9997 | 21.835
SYL-G.1.RR.185.1 | 24462649201316 | Gulapganj, Fotehkhani, Purba Bhadeshwar, Purbag Jame Mosjid, Jamil Chowdury | 2019-09-07 | MN1018 | 10.9 | 75 | 10.9 | 76 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7296 | 1463.9997 | 114.8476
SYL-G.1.RR.186.1 | 24463309201300 | Gulapganj, Fotehkhani, Purba Bhadeshwar, Hosen Ali | 2019-09-07 | MN1018 | 8.4 | 77 | 8.4 | 78 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7296 | 1463.9997 | 88.5064
SYL-G.1.RR.187.1 | 24463279201265 | Gulapganj, Fotehkhani, Purba Bhadeshwar, Fakrul Ahmed | 2019-09-07 | MN1018 | 6.5 | 79 | 6.5 | 80 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7296 | 1463.9997 | 68.4871
SYL-G.1.RR.188.1 | 24463449201244 | Gulapganj, Fotehkhani, Purba Bhadeshwar, West Side Of Jaigidar Bari Koborstan, Shahin Akter Jaigidar | 2019-09-07 | MN1018 | 29 | 81 | 29 | 82 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 29 | 29 | 1.74 | 1.74 | 0.0007168 | 100% | 0% | 1.74 | 1.74 | 0.0011869 | 28 | 0.034881 | 0.034881 |  | 0 | 0 | 7296 | 1463.9997 | 305.558
SYL-G.1.RR.189.1 | 24463709201263 | Gulapganj, Fotehkhani, Purba Bhadeshwar, Mohammad Ali (Al- Modina Madrasa Goli) | 2019-09-07 | MN1018 | 5.6 | 83 | 5.6 | 84 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7296 | 1463.9997 | 59.0043
SYL-G.1.RR.190.1 | 24463709201263 | Gulapganj, Fotehkhani, Purba Bhadeshwar, Abdur Rahman (Al- Modina Madrasa Goli) | 2019-09-07 | MN1018 | 4.5 | 85 | 4.5 | 86 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7296 | 1463.9997 | 47.4142
SYL-G.1.RR.191.1 | 24463399201199 | Gulapganj, Purbag Fokirtul, Mukam Bari, Sayed Salek Uddin | 2019-09-07 | MN1018 | 26.2 | 87 | 26.2 | 88 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 26.2 | 26.2 | 1.572 | 1.572 | 0.0007168 | 100% | 0% | 1.572 | 1.572 | 0.0011869 | 28 | 0.031513 | 0.031513 |  | 0 | 0 | 7296 | 1463.9997 | 276.0558
SYL-G.1.RR.191.2 | 24463399201199 | Gulapganj, Purbag Fokirtul, Mukam Bari, Sayed Salek Uddin | 2019-09-07 | MN1018 | 4.3 | 89 | 4.3 | 90 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7296 | 1463.9997 | 45.3069
SYL-G.1.RR.192.1 | 24463959201219 | Gulapganj, Purba Bhadeshwar, Fokirtul, Moksudur Rahman Babul | 2019-09-07 | MN1018 | 28.1 | 91 | 28.1 | 92 | 2022-01-01 | 2022-11-01 | NQ1007 | 10.1 | 102 | 10.1 | 103 | 2022-11-01 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7296 | 1463.9997
SYL-G.1.RR.192.2 | 24463959201219 | Gulapganj, Purba Bhadeshwar, Fokirtul, Moksudur Rahman Babul | 2019-09-07 | MN1018 | 13.7 | 93 | 13.7 | 94 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7296 | 1463.9997 | 144.3498
SYL-G.1.RR.193.1 | 24464419201102 | Gulapganj, Purba Bhadeshwar, Fokirtul, Mahmud Ali | 2019-09-07 | MN1018 | 1.8 | 95 | 1.8 | 96 | 2022-01-01 | 2022-11-01 | NQ1007 | 0.6 | 100 | 0.6 | 101 | 2022-11-01 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7296 | 1463.9997
SYL-G.1.RR.194.1 | 24504569202426 | Gulapganj, Amnia Poschimpara Road, Block #A, H#32,Sofiqur Rahman | 2019-09-09 | MN1018 | 2.3 | 115 | 2.3 | 116 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7392 | 1367.9997 | 24.2339
SYL-G.1.RR.195.1 | 24504569202473 | Gulapganj, Amnia Poschimpara, Nur Uddin | 2019-09-09 | MN1018 | 5.5 | 117 | 5.5 | 118 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7392 | 1367.9997 | 57.9506
SYL-G.1.RR.196.1 | 24504959202500 | Gulapganj, Amnia Poschimpara, M.A Kabir | 2019-09-09 | MN1018 | 10.4 | 119 | 10.5 | 120 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7392 | 1367.9997 | 110.6331
SYL-G.1.RR.197.1 | 24505239202500 | Gulapganj, Amnia Bazar, Sofiq Uddin | 2019-09-09 | MN1018 | 10 | 121 | 10 | 122 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7392 | 1367.9997 | 105.3648
SYL-G.1.RR.197.2 | 24505239202500 | Gulapganj, Amnia Bazar, Sofiq Uddin | 2022-04-13 | LU1001 | 6.6 | 153 | 6.6 | 154 | 2022-04-13 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 4944 | 1367.9997 | 50.1075
SYL-G.1.RR.198.1 | 24505259202522 | Gulapganj, Amnia Bazar, Abdul Ahad | 2019-09-09 | MN1018 | 10.7 | 123 | 10.7 | 124 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7392 | 1367.9997 | 112.7403
SYL-G.1.RR.199.1 | 24505249202587 | Gulapganj, Amnia, Goni Mia | 2019-09-09 | MN1018 | 11.7 | 125 | 11.8 | 126 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7392 | 1367.9997 | 124.3305
SYL-G.1.RR.200.1 | 24505249202587 | Gulapganj, Amnia, Near By Amnia Bazar, Sayed Hazi Rokib Ali | 2019-09-09 | MN1018 | 13.8 | 127 | 13.9 | 128 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7392 | 1367.9997 | 146.4571
SYL-G.1.RR.201.1 | 24512359200371 | Sylhet, Golapganj, Thanar Ghat, Godaon Road, Shafiul Haque | 2019-08-31 | LU1001 | 3.2 | 174 | 3 | 175 | 2022-01-01 | [9 empty] | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0
SYL-G.1.RR.202.1 | 24512159200354 | Sylhet, Golapganj, Thanar Ghat, Godaon Road, Abdul Ahad | 2019-08-31 | LU1001 | 10.3 | 176 | 10.3 | 177 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7344 | 1415.9997 | 108.5258
SYL-G.1.RR.203.1 | 24511939200314 | Sylhet, Golapganj, Thanar Ghat, Godaon Road, Abdul Jabbar | 2019-08-31 | LU1001 | 10.9 | 178 | 10.9 | 179 | 2022-01-01 | [9 empty] | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0
SYL-G.1.RR.204.1 | 24514069200405 | Sylhet, Golapganj, Sorosoti, Sormadise, Nazrul | 2019-08-31 | LU1001 | 5.9 | 180 | 5.9 | 181 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7344 | 1415.9997 | 62.1652
SYL-G.1.RR.204.2 | 24514069200405 | Sylhet, Golapganj, Sorosoti, Sormadise, Nazrul | 2021-09-15 | NQ1007 | 4.7 | 27 | 4.7 | 28 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7344 | 1415.9997 | 49.5215
SYL-G.1.RR.205.1 | 24514069200405 | Sylhet, Golapganj, Sorosoti, Sormadise, Sharif | 2019-08-31 | LU1001 | 9.9 | 182 | 10.3 | 183 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7344 | 1415.9997 | 108.5258
SYL-G.1.RR.206.1 | 24514069200405 | Sylhet, Golapganj, Sorosoti, Sormadise, Jalal | 2019-08-31 | LU1001 | 6.4 | 184 | 6.4 | 185 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7344 | 1415.9997 | 67.4335
SYL-G.1.RR.207.1 | 24514709200460 | Sylhet, Golapganj, Sorosoti, Sormadise, Hafiz | 2019-08-31 | LU1001 | 11.9 | 186 | 11.4 | 187 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7344 | 1415.9997 | 120.1159
SYL-G.1.RR.208.1 | 24522339201506 | Sylhet, Golapganj, Choughoria, Khondokar Kholai Mia | 2019-09-01 | LU1001 | 9.3 | 218 | 9.3 | 219 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7416 | 1343.9997 | 97.9893
SYL-G.1.RR.209.1 | 24522339201506 | Sylhet, Golapganj, Choughoria, Khondokar Salim | 2019-09-01 | LU1001 | 8.5 | 220 | 8.2 | 221 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7416 | 1343.9997 | 86.3991
SYL-G.1.RR.210.1 | 24522259201505 | Sylhet, Golapganj, Choughoria, Rores Uddin | 2019-09-01 | LU1001 | 8.9 | 222 | 8.9 | 223 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7416 | 1343.9997 | 93.7747
SYL-G.1.RR.211.1 | 24522819201496 | Sylhet, Golapganj, Choughori, Mozir | 2019-09-02 | LU1001 | 3.5 | 224 | 3.6 | 225 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7416 | 1343.9997 | 37.9313
SYL-G.1.RR.211.2 | 24522819201496 | Sylhet, Golapganj, Choughori, Mozir | 2022-04-16 | LU1001 | 14.1 | 157 | 14.1 | 158 | 2022-04-16 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 4896 | 1343.9997 | 105.8267
SYL-G.1.RR.212.1 | 24522689201532 | Sylhet, Golapganj, Choughori, Hafiz Ahamad | 2019-09-02 | LU1001 | 12.2 | 226 | 12.2 | 227 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7416 | 1343.9997 | 128.5451
SYL-G.1.RR.213.1 | 24522839201524 | Sylhet, Golapganj, Choughori, Nuru Rahaman | 2019-09-02 | LU1001 | 11 | 228 | 11 | 229 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7416 | 1343.9997 | 115.9013
SYL-G.1.RR.214.1 | 24522999201561 | Sylhet, Golapganj, Choughori, Abdul Hasib | 2019-09-02 | LU1001 | 5.2 | 230 | 5.2 | 231 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7416 | 1343.9997 | 54.7897
SYL-G.1.RR.215.1 | 24522999201561 | Sylhet, Golapganj, Choughori, Abdul Rahim | 2019-09-02 | LU1001 | 3.9 | 232 | 3.9 | 233 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7416 | 1343.9997 | 41.0923
SYL-G.1.RR.216.1 | 24522159202001 | Sylhet, Golapganj, Choughori, Ackaduma, Ruhal | 2019-09-02 | LU1001 | 3.5 | 234 | 3.7 | 235 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7416 | 1343.9997 | 38.985
SYL-G.1.RR.216.2 | 24522159202001 | Sylhet, Golapganj, Choughori, Ackaduma, Ruhal | 2019-09-02 | LU1001 | 10.1 | 236 | 10.2 | 237 | 2022-01-01 | 2022-11-06 | NQ1007 | 1.5 | 137 | 1.5 | 138 | 2022-11-06 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7416 | 1343.9997
SYL-G.1.RR.217.1 | 24522259202023 | Sylhet, Golapganj, Choughori, Ackaduma, Mature Rahaman | 2019-09-02 | LU1001 | 6.6 | 238 | 6.8 | 239 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7416 | 1343.9997 | 71.6481
SYL-G.1.RR.218.1 | 24520869202078 | Sylhet, Golapganj, Girdo, Soba | 2019-09-02 | LU1001 | 2.8 | 240 | 2.8 | 241 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7416 | 1343.9997 | 29.5021
SYL-G.1.RR.219.1 | 24520069202214 | Sylhet, Golapganj, Girdh, Mokoddos Ali | 2019-09-03 | LU1001 | 8.3 | 250 | 8.3 | 251 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7416 | 1343.9997 | 87.4528
SYL-G.1.RR.220.1 | 24520069202214 | Sylhet, Golapganj, Girdh, Jabbar | 2019-09-03 | LU1001 | 6.1 | 252 | 6.1 | 253 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7416 | 1343.9997 | 64.2725
SYL-G.1.RR.221.1 | 24515749202202 | Sylhet, Golapganj, Girdh, Abdul Rahim | 2019-09-03 | LU1001 | 10.3 | 254 | 10.3 | 255 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7416 | 1343.9997 | 108.5258
SYL-G.1.RR.221.2 | 24521149202333 | Sylhet, Golapganj, Girdh, Abdul Rahim | 2022-04-16 | LU1001 | 11.2 | 155 | 11.2 | 156 | 2022-04-16 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 4896 | 1343.9997 | 84.0609
SYL-G.1.RR.222.1 | 24521149202333 | Sylhet, Golapganj, Guga, Okile Uddine | 2019-09-03 | LU1001 | 10.6 | 256 | 10.6 | 257 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7416 | 1343.9997 | 111.6867
SYL-G.1.RR.223.1 | 24511599200284 | Sylhet, Golapganj, Duck Bangla Road, Kamor Uddin | 2019-09-03 | LU1001 | 13.2 | 258 | 13.2 | 259 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7344 | 1415.9997 | 139.0816
SYL-G.1.RR.223.2 | 24511599200284 | Sylhet, Golapganj, Duck Bangla Road, Kamor Uddin | 2019-09-03 | LU1001 | 22 | 260 | 22 | 261 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 22 | 22 | 1.32 | 1.32 | 0.0007168 | 100% | 0% | 1.32 | 1.32 | 0.0011869 | 28 | 0.026461 | 0.026461 |  | 0 | 0 | 7344 | 1415.9997 | 231.8026
SYL-G.1.RR.224.1 | 24510219201221 | Sylhet, Golapganj, Ronokali Uttar, Helal | 2019-09-03 | LU1001 | 10.3 | 262 | 10.3 | 263 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7392 | 1367.9997 | 108.5258
SYL-G.1.RR.225.1 | 24510579201226 | Sylhet, Golapganj, Ronokali Uttar, Tayabali house | 2019-09-03 | LU1001 | 9.9 | 264 | 9.9 | 265 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7392 | 1367.9997 | 104.3112
SYL-G.1.RR.226.1 | 24483819202083 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Nuruzzaman | 2019-09-04 | LU1001 | 12.3 | 1 | 12.3 | 2 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7320 | 1439.9997 | 129.5987
SYL-G.1.RR.227.1 | 24484019202091 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Hakim | 2019-09-04 | LU1001 | 7 | 3 | 7 | 4 | 2022-01-01 | [9 empty] | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 | 2022-01-01 12:00 | 0 | 0
SYL-G.1.RR.228.1 | 24484019202091 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Moklas | 2019-09-04 | LU1001 | 11.1 | 5 | 11.1 | 6 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7320 | 1439.9997 | 116.9549
SYL-G.1.RR.228.2 | 24484019202091 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Moklas | 2022-11-02 | NQ1007 | 6.7 | 113 | 6.7 | 114 | 2022-11-02 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 0 | 1439.9997 | 11.6046
SYL-G.1.RR.229.1 | 24484019202091 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Abdul Jalil | 2019-09-04 | LU1001 | 11.4 | 7 | 11.3 | 8 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7320 | 1439.9997 | 119.0622
SYL-G.1.RR.230.1 | 24484019202091 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Abdul Odud | 2019-09-04 | LU1001 | 12.2 | 9 | 12.2 | 10 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7320 | 1439.9997 | 128.5451
SYL-G.1.RR.231.1 | 24483659202095 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Nunu Mia | 2019-09-04 | LU1001 | 12.6 | 11 | 12.6 | 12 | 2022-01-01 | 2022-11-02 | NQ1007 |  |  | 0 | 109 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7320 | 1439.9997
SYL-G.1.RR.232.1 | 24483659202095 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Sabin | 2019-09-04 | LU1001 | 13.1 | 13 | 13.1 | 14 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7320 | 1439.9997 | 138.0279
SYL-G.1.RR.233.1 | 24481639202190 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Collage Road, Bijun Babu | 2019-09-04 | LU1001 | 32.4 | 17 | 32.3 | 18 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 32.3 | 32.3 | 1.938 | 1.938 | 0.0007168 | 100% | 0% | 1.938 | 1.938 | 0.0011869 | 28 | 0.03885 | 0.03885 |  | 0 | 0 | 7296 | 1463.9997 | 340.3283
SYL-G.1.RR.233.2 | 24481639202190 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Collage Road, Bijun Babu | 2021-02-03 | MN1018 | 38.7 | 65 | 38.7 | 66 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 38.7 | 38.7 | 2.322 | 2.322 | 0.0007168 | 100% | 0% | 2.322 | 2.322 | 0.0011869 | 28 | 0.046548 | 0.046548 |  | 0 | 0 | 7296 | 1463.9997 | 407.7618
SYL-G.1.RR.234.1 | 24481639202190 | Sylhet, Golapganj, Dhakadakshin, Dattarail, Collage Road, Arune Babu | 2019-09-04 | LU1001 | 19.8 | 19 | 19.8 | 20 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 19.8 | 19.8 | 1.188 | 1.188 | 0.0007168 | 100% | 0% | 1.188 | 1.188 | 0.0011869 | 28 | 0.023815 | 0.023815 |  | 0 | 0 | 7296 | 1463.9997 | 208.6223
SYL-G.1.RR.235.1 | 24475039202111 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Salim Ahmad | 2019-09-05 | LU1001 | 8.9 | 33 | 8.9 | 34 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7296 | 1463.9997 | 93.7747
SYL-G.1.RR.236.1 | 24475039202111 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Abul Hosen | 2019-09-05 | LU1001 | 11.6 | 35 | 11.3 | 36 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7296 | 1463.9997 | 119.0622
SYL-G.1.RR.236.2 | 24475039202111 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Abul Hosen | 2022-11-01 | NQ1007 | 12.3 | 107 | 12.3 | 108 | 2022-11-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 0 | 1463.9997 | 21.659
SYL-G.1.RR.237.1 | 24474619202156 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Abu Hosen | 2019-09-05 | LU1001 | 10.9 | 37 | 10.9 | 38 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7296 | 1463.9997 | 114.8476
SYL-G.1.RR.238.1 | 24474619202156 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Abu Hosen | 2019-09-05 | LU1001 | 11.1 | 39 | 10.7 | 40 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7296 | 1463.9997 | 112.7403
SYL-G.1.RR.239.1 | 24474699202169 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Easraf Ali | 2019-09-05 | LU1001 | 5.9 | 41 | 5.9 | 42 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7296 | 1463.9997 | 62.1652
SYL-G.1.RR.240.1 | 24474539202149 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Anower Hosen | 2019-09-05 | LU1001 | 8 | 43 | 8 | 44 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7296 | 1463.9997 | 84.2919
SYL-G.1.RR.240.2 | 24474539202149 | Sylhet, Golapganj, Dhakadakshin, Dakkhin Kanishail, Anower Hosen | 2022-04-09 | LU1001 | 8.8 | 133 | 8.8 | 134 | 2022-04-09 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 4944 | 1463.9997 | 67.8261
SYL-G.1.RR.241.1 | 24461969201344 | Sylhet, Golapganj, Vadessor, Purbovag, Rajapur, Samsuddin | 2019-09-07 | LU1001 | 6.7 | 59 | 6.7 | 60 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7248 | 1511.9997 | 70.5944
SYL-G.1.RR.242.1 | 24461949201324 | Sylhet, Golapganj, Vadessor, Purbovag, Rajapur, Kutub Uddin | 2019-09-07 | LU1001 | 12.5 | 61 | 12 | 62 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7248 | 1511.9997 | 126.4378
SYL-G.1.RR.243.1 | 24462289201210 | Sylhet, Golapganj, Vadessor, Purbovag, Celimkhani, Mosabbir Ali | 2019-09-07 | LU1001 | 4.9 | 63 | 4.9 | 64 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7248 | 1511.9997 | 51.6288
SYL-G.1.RR.244.1 | 24462459201202 | Sylhet, Golapganj, Vadessor, Purbovag, Celimkhani, Shafiq Ahmed | 2019-09-07 | LU1001 | 11.1 | 65 | 11.1 | 66 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7248 | 1511.9997 | 116.9549
SYL-G.1.RR.245.1 | 24462459201202 | Sylhet, Golapganj, Vadessor, Purbovag, Celimkhani, Atik Ahmed | 2019-09-07 | LU1001 | 11.2 | 67 | 11.3 | 68 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7248 | 1511.9997 | 119.0622
SYL-G.1.RR.246.1 | 24461639201141 | Sylhet, Golapganj, Vadessor, Purbovag, Kolasohor, Tofazzal | 2019-09-07 | LU1001 | 8.9 | 69 | 8.9 | 70 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7248 | 1511.9997 | 93.7747
SYL-G.1.RR.247.1 | 24461639201141 | Sylhet, Golapganj, Vadessor, Purbovag, Kolasohor, Mojibor | 2019-09-07 | LU1001 | 9.5 | 73 | 9.5 | 74 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7248 | 1511.9997 | 100.0966
SYL-G.1.RR.248.1 | 24461229200478 | Sylhet, Golapganj, Vadessor, Dokhar Para, Abdul Jabed | 2019-09-08 | LU1001 | 12.3 | 85 | 12 | 86 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7248 | 1511.9997 | 126.4378
SYL-G.1.RR.249.1 | 24461369200509 | Sylhet, Golapganj, Vadessor, Dokhar Para, Abdul Jabed | 2019-09-08 | LU1001 | 12.5 | 87 | 12.5 | 88 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7248 | 1511.9997 | 131.706
SYL-G.1.RR.250.1 | 24461359200446 | Sylhet, Golapganj, Vadessor, Dokhar Para, Esmile Ali | 2019-09-08 | LU1001 | 7 | 89 | 7 | 90 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7248 | 1511.9997 | 73.7554
SYL-G.1.RR.251.1 | 24513629200501 | Golapganj, 4 No Word, Bhelasha R/A, Rd # 1, H # 5 | 2019-09-01 | LU1001 | 4.5 | 188 | 4.5 | 189 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7440 | 1319.9997 | 47.4142
SYL-G.1.RR.252.1 | 24513999200518 | Golapganj, 4 No Word, Borobari, Gochuddin | 2019-09-01 | LU1001 | 11.8 | 190 | 11.8 | 191 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7440 | 1319.9997 | 124.3305
SYL-G.1.RR.253.1 | 24514019200534 | Golapganj, Sawrasati Borobari, Shamim Ahammed | 2019-09-01 | LU1001 | 12.2 | 192 | 12.2 | 193 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7440 | 1319.9997 | 128.5451
SYL-G.1.RR.254.1 | 24514159200520 | Golapganj, Sawrasati Borobari, Koyez Ahammed | 2019-09-01 | LU1001 | 11.2 | 194 | 11.2 | 195 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7440 | 1319.9997 | 118.0086
SYL-G.1.RR.255.1 | 24514159200520 | Golapganj, Sawrasati Borobari, Shanur Ahammed | 2019-09-01 | LU1001 | 7.5 | 196 | 7.5 | 197 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7440 | 1319.9997 | 79.0236
SYL-G.1.RR.256.1 | 24514289200521 | Golapganj, Sawrasati Borobari, Dudu Mia | 2019-09-01 | LU1001 | 7.4 | 198 | 7.4 | 199 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7440 | 1319.9997 | 77.97
SYL-G.1.RR.257.1 | 24514289200521 | Golapganj, Sawrasati Borobari, Sayek Ahammed | 2019-09-01 | LU1001 | 9.9 | 200 | 9.9 | 201 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7440 | 1319.9997 | 104.3112
SYL-G.1.RR.258.1 | 24514359200527 | Golapganj, Sawrasati Borobari, Nazrul Islam | 2019-09-01 | LU1001 | 5.2 | 202 | 5.2 | 203 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7440 | 1319.9997 | 54.7897
SYL-G.1.RR.259.1 | 24513739200580 | Golapganj, Dalipaton West Para, Ripon | 2019-09-01 | LU1001 | 2.7 | 204 | 2.7 | 205 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7440 | 1319.9997 | 28.4485
SYL-G.1.RR.260.1 | 24513639200586 | Golapganj, Daripathon Para, Ruhul Amin | 2019-09-02 | LU1001 | 3.3 | 242 | 3.3 | 243 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7440 | 1319.9997 | 34.7704
SYL-G.1.RR.261.1 | 24513929200592 | Golapganj, Daripathon Para, Mostakin Ali | 2019-09-02 | LU1001 | 8.3 | 244 | 8.3 | 245 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7440 | 1319.9997 | 87.4528
SYL-G.1.RR.262.1 | 24514109201020 | Golapganj, Daripathon West Para, Bagan Bari, Serajuddin | 2019-09-02 | LU1001 | 12.3 | 246 | 12.3 | 247 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7440 | 1319.9997 | 129.5987
SYL-G.1.RR.263.1 | 24514159201023 | Golapganj, Daripathon West Para, Bagan Bari, Jomir Villa, Sabiya Begum | 2019-09-02 | LU1001 | 4.3 | 248 | 4.3 | 249 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7440 | 1319.9997 | 45.3069
SYL-G.1.RR.264.1 | 24503029201160 | Golapganj, Ronkeli, Nozmul Islam Chowdhury | 2019-09-03 | LU1001 | 10.3 | 266 | 10.3 | 267 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7392 | 1367.9997 | 108.5258
SYL-G.1.RR.265.1 | 24503029201160 | Golapganj, Ronkeli, Imam Ahammed Chowdhury | 2019-09-03 | LU1001 | 7.6 | 268 | 7.6 | 269 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7392 | 1367.9997 | 80.0773
SYL-G.1.RR.266.1 | 24503029201160 | Golapganj, Ronkeli, Nozibur Rahaman Chowdhury | 2019-09-03 | LU1001 | 6.3 | 270 | 6.3 | 271 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7392 | 1367.9997 | 66.3798
SYL-G.1.RR.267.1 | 24503029201160 | Golapganj, Ronkeli, Malek Ahammed Chowdhury | 2019-09-03 | LU1001 | 10.3 | 272 | 10.3 | 273 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7392 | 1367.9997 | 108.5258
SYL-G.1.RR.268.1 | 24503029201160 | Golapganj, Ronkeli, Malek Ahammed | 2019-09-03 | LU1001 | 9.3 | 274 | 9.3 | 275 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7392 | 1367.9997 | 97.9893
SYL-G.1.RR.269.1 | 24503029201160 | Golapganj, Ronkeli, Jeny Chowdhury | 2019-09-03 | LU1001 | 11.1 | 276 | 11.1 | 277 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7392 | 1367.9997 | 116.9549
SYL-G.1.RR.270.1 | 24502809201159 | Golapganj, Ronkeli, Rezaul Karim Chowdhury | 2019-09-03 | LU1001 | 10.5 | 278 | 10.5 | 279 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7392 | 1367.9997 | 110.6331
SYL-G.1.RR.270.2 | 24502809201159 | Golapganj, Ronkeli, Rezaul Karim Chowdhury | 2022-11-05 | NQ1007 | 13.3 | 133 | 13.4 | 134 | 2022-11-05 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 0 | 1367.9997 | 22.0487
SYL-G.1.RR.271.1 | 24475709202253 | Golapganj, Dhaka dakshin, Kanishail, Sharif | 2019-09-04 | LU1001 | 5.8 | 21 | 5.8 | 22 | 2022-01-01 | 2022-11-01 | NQ1007 |  |  | 0 | 104 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7296 | 1463.9997
SYL-G.1.RR.271.2 | 24475709202253 | Golapganj, Dhaka dakshin, Kanishail, Sharif | 2019-09-04 | LU1001 | 12.4 | 23 | 12.4 | 24 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7296 | 1463.9997 | 130.6524
SYL-G.1.RR.272.1 | 24475709202266 | Golapganj, Dhaka dakshin, Kanishail, Shahid | 2019-09-04 | LU1001 | 5 | 25 | 5 | 26 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7296 | 1463.9997 | 52.6824
SYL-G.1.RR.273.1 | 24475719202269 | Golapganj, Dhaka dakshin, Kanishail, Abdul Motin | 2019-09-04 | LU1001 | 7.4 | 27 | 7.4 | 28 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7296 | 1463.9997 | 77.97
SYL-G.1.RR.274.1 | 24475359202228 | Golapganj, Dhaka dakshin, Kanishail, Abdul Shahid | 2019-09-04 | LU1001 | 10.6 | 29 | 10.6 | 30 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7296 | 1463.9997 | 111.6867
SYL-G.1.RR.275.1 | 24475089202222 | Golapganj, Dhaka dakshin, Kanishail, Selim Ahammed | 2019-09-04 | LU1001 | 10.3 | 31 | 10.2 | 32 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7296 | 1463.9997 | 107.4721
SYL-G.1.RR.276.1 | 24472239202225 | Golapganj, South Kanishail, Vhareyrah Mosque Road, Mahatab Uddin | 2019-09-05 | LU1001 | 3.8 | 45 | 3.8 | 46 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7296 | 1463.9997 | 40.0386
SYL-G.1.RR.277.1 | 24472359202186 | Golapganj, South Kanishail, Vhareyrah Mosque Road, Surman Ali | 2019-09-05 | LU1001 | 10.1 | 47 | 10.1 | 48 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7296 | 1463.9997 | 106.4185
SYL-G.1.RR.278.1 | 24472359202186 | Golapganj, South Kanishail, Vhareyrah Mosque Road, Rubel Ahammed | 2019-09-05 | LU1001 | 2.2 | 51 | 2.2 | 52 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7296 | 1463.9997 | 23.1803
SYL-G.1.RR.279.1 | 24472229202170 | Golapganj, South Kanishail, Vhareyrah Mosque Road, Baies Uddin | 2019-09-05 | LU1001 | 9.2 | 53 | 9.2 | 54 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7296 | 1463.9997 | 96.9356
SYL-G.1.RR.279.2 | 24472229202170 | Golapganj, South Kanishail, Vhareyrah Mosque Road, Baies Uddin | 2022-04-09 | LU1001 | 2.2 | 131 | 2.2 | 132 | 2022-04-09 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 4944 | 1463.9997 | 16.9565
SYL-G.1.RR.280.1 | 24472209202137 | Golapganj, South Kanishail, Vhareyrah Mosque Road, Khalilur Rahaman | 2019-09-05 | LU1001 | 11.6 | 55 | 11.6 | 56 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7296 | 1463.9997 | 122.2232
SYL-G.1.RR.281.1 | 24472599202128 | Golapganj, South Kanishail, Vhareyrah Mosque Road, Ansar Ali | 2019-09-05 | LU1001 | 5 | 57 | 5 | 58 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7296 | 1463.9997 | 52.6824
SYL-G.1.RR.282.1 | 24460219201135 | Maiz Bhag, Bhadeshwar, Maiz Bhag Road, Sattar Mia | 2019-09-07 | LU1001 | 6.4 | 75 | 6.4 | 76 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7248 | 1511.9997 | 67.4335
SYL-G.1.RR.283.1 | 24460639201078 | Maiz Bhag, Bhadeshwar, Maiz Bhag Road, Seraj Monjil | 2019-09-07 | LU1001 | 11.4 | 77 | 11.4 | 78 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7248 | 1511.9997 | 120.1159
SYL-G.1.RR.284.1 | 24460749201086 | Maiz Bhag, Bhadeshwar, Maiz Bhag Road, Lalin Ahmed | 2019-09-07 | LU1001 | 10.9 | 79 | 10.9 | 80 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7248 | 1511.9997 | 114.8476
SYL-G.1.RR.285.1 | 24460749201086 | Maiz Bhag, Bhadeshwar, Maiz Bhag Road, Abdur Rahim | 2019-09-07 | LU1001 | 11.8 | 81 | 11.8 | 82 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7248 | 1511.9997 | 124.3305
SYL-G.1.RR.286.1 | 24461059201018 | Maiz Bhag, Bhadeshwar, Dhakhar Para, Anam Uddin | 2019-09-07 | LU1001 | 21.6 | 83 | 21.6 | 84 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 7248 | 1511.9997 | 227.588
SYL-G.1.RR.287.1 | 24495759201311 | Golapganj, Upar Barokut, Giyasuddin Ahammed Chowdhury Road, Aftab Ali | 2019-09-08 | LU1001 | 11.1 | 105 | 11.1 | 106 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7320 | 1439.9997 | 116.9549
SYL-G.1.RR.287.2 | 24495759201311 | Golapganj, Upar Barokut, Giyasuddin Ahammed Chowdhury Road, Aftab Ali | 2022-11-02 | NQ1007 | 4.4 | 115 | 4.4 | 116 | 2022-11-02 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 0 | 1439.9997 | 7.6209
SYL-G.1.RR.288.1 | 24474529202352 | Golapganj, Uttor Kanishail, Md. Nojib Ali | 2019-09-09 | LU1001 | 5 | 111 | 5 | 112 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7296 | 1463.9997 | 52.6824
SYL-G.1.RR.289.1 | 24474869202375 | Golapganj, Uttor Kanishail, Khalilur Rahaman | 2019-09-09 | LU1001 | 5.8 | 115 | 5.8 | 116 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7296 | 1463.9997 | 61.1116
SYL-G.1.RR.290.1 | 24475069202372 | Golapganj, Uttor Kanishail, Aman & Omar Villa | 2019-09-09 | LU1001 | 3.1 | 117 | 3.1 | 118 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7296 | 1463.9997 | 32.6631
SYL-G.1.RR.291.1 | 24475069202372 | Golapganj, Uttor Kanishail, Abdul Khalek | 2019-09-09 | LU1001 | 12.1 | 119 | 12.1 | 120 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7296 | 1463.9997 | 127.4914
SYL-G.1.RR.292.1 | 24475069202372 | Golapganj, Uttor Kanishail, Nazimuddin | 2019-09-09 | LU1001 | 7.9 | 121 | 7.9 | 122 | 2022-01-01 | 2022-11-01 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7296 | 1463.9997 | 83.2382
SYL-G.1.RR.293.1 | 24480459159192 | Golapganj, Lokkhonabondh, Shabuddin | 2019-09-11 | LU1001 | 12.4 | 123 | 12 | 124 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7224 | 1535.9997 | 126.4378
SYL-G.1.RR.294.1 | 24480459159192 | Golapganj, Lokkhonabondh, Hasibur Rahaman | 2019-09-11 | LU1001 | 12.8 | 125 | 12.8 | 126 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7224 | 1535.9997 | 134.867
SYL-G.1.RR.295.1 | 24475809159226 | Golapganj, Lokkhonabondh, Md. Jakariyar | 2019-09-11 | LU1001 | 12.2 | 127 | 12.2 | 128 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7224 | 1535.9997 | 128.5451
SYL-G.1.RR.296.1 | 24475179159238 | Golapganj, Lokkhonabondh, Islam | 2019-09-11 | LU1001 | 7.9 | 129 | 7.9 | 130 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7224 | 1535.9997 | 83.2382
SYL-G.1.RR.297.1 | 24475179159238 | Golapganj, Lokkhonabondh, Lulu Mia | 2019-09-11 | LU1001 | 5.4 | 131 | 5.4 | 132 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7224 | 1535.9997 | 56.897
SYL-G.1.RR.297.2 | 24475179159238 | Golapganj, Lokkhonabondh, Lulu Mia | 2022-10-29 | NQ1007 | 5.5 | 88 | 5.5 | 89 | 2022-10-29 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 0 | 1535.9997 | 10.1612
SYL-G.1.RR.298.1 | 24474909159239 | Golapganj, Lokkhonabondh, Serajul | 2019-09-11 | LU1001 | 7.7 | 133 | 7.7 | 134 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7224 | 1535.9997 | 81.1309
SYL-G.1.RR.299.1 | 24474849159195 | Golapganj, Lokkhonabondh, Abul Hasan | 2019-09-11 | LU1001 | 11.2 | 135 | 11.2 | 136 | 2022-01-01 | 2022-10-29 | NQ1007 | 2.5 | 86 | 2.5 | 87 | 2022-10-29 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7224 | 1535.9997
SYL-G.1.RR.300.1 | 24483679158131 | Golapganj, Lakshmipasa, Mawlana Bari, Abdur Rahaman | 2019-09-11 | LU1001 | 5.4 | 137 | 5 | 138 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7224 | 1535.9997 | 52.6824
SYL-G.1.RR.301.1 | 24513859201260 | Golapganj, Dari Paton, Yakub Ali | 2019-09-01 | NQ1000 | 6.5 | 643 | 6.6 | 644 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7440 | 1319.9997 | 69.5408
SYL-G.1.RR.302.1 | 24513859201260 | Golapganj, Dari Paton, Abdur Rakib | 2019-09-01 | NQ1000 | 6.1 | 645 | 6.1 | 646 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7440 | 1319.9997 | 64.2725
SYL-G.1.RR.303.1 | 24513989201263 | Golapganj, Dari Paton, Kayes Ahmed | 2019-09-01 | NQ1000 | 5.6 | 647 | 5.7 | 648 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7440 | 1319.9997 | 60.0579
SYL-G.1.RR.304.1 | 24513989201263 | Golapganj, Dari Paton, Moyna Mia | 2019-09-01 | NQ1000 | 5.5 | 649 | 5.2 | 650 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7440 | 1319.9997 | 54.7897
SYL-G.1.RR.305.1 | 24513989201255 | Golapganj, Dari Paton, Monohor Ali | 2019-09-01 | NQ1000 | 10.4 | 651 | 10 | 652 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7440 | 1319.9997 | 105.3648
SYL-G.1.RR.306.1 | 24514049201265 | Golapganj, Dari Paton, Foyzur Rahman | 2019-09-01 | NQ1000 | 2.9 | 653 | 2.9 | 654 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7440 | 1319.9997 | 30.5558
SYL-G.1.RR.307.1 | 24513689201201 | Golapganj, Dari Paton, Rd # 2, Harunur Rashid | 2019-09-01 | NQ1000 | 8.1 | 655 | 8.1 | 656 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7440 | 1319.9997 | 85.3455
SYL-G.1.RR.308.1 | 24513689201201 | Golapganj, Dari Paton, Rd # 2, Abdul Hannan | 2019-09-01 | NQ1000 | 12.2 | 657 | 12.2 | 658 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7440 | 1319.9997 | 128.5451
SYL-G.1.RR.309.1 | 24513759201139 | Golapganj, Dari Paton, Rd # 2, Mushahid Ali | 2019-09-01 | NQ1000 | 22.9 | 659 | 21.9 | 660 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 21.9 | 21.9 | 1.314 | 1.314 | 0.0007168 | 100% | 0% | 1.314 | 1.314 | 0.0011869 | 28 | 0.026341 | 0.026341 |  | 0 | 0 | 7440 | 1319.9997 | 230.7489
SYL-G.1.RR.310.1 | 24513839201103 | Golapganj, Dari Paton, Rd # 2, Sayarunnesa Mahal, Sayarunnesa | 2019-09-01 | NQ1000 | 8.8 | 661 | 8.8 | 662 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7440 | 1319.9997 | 92.721
SYL-G.1.RR.311.1 | 24525579202227 | Golapganj, North Goyaspur, Jitu Mia | 2019-09-02 | NQ1000 | 7.8 | 663 | 7.2 | 664 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7416 | 1343.9997 | 75.8627
SYL-G.1.RR.311.2 | 24525579202227 | Golapganj, North Goyaspur, Jitu Mia | 2019-09-02 | NQ1000 | 81 | 665 | 81.1 | 666 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 81.1 | 81.1 | 4.866 | 4.866 | 0.0007168 | 100% | 0% | 4.866 | 4.866 | 0.0011869 | 28 | 0.097547 | 0.097547 |  | 0 | 0 | 7416 | 1343.9997 | 854.5086
SYL-G.1.RR.312.1 | 24525719202272 | Golapganj, North Goyaspur, Giyasuddin | 2019-09-02 | NQ1000 | 1.7 | 667 | 1.7 | 668 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7416 | 1343.9997 | 17.912
SYL-G.1.RR.313.1 | 24525719202272 | Golapganj, North Goyaspur, Reza | 2019-09-02 | NQ1000 | 3.5 | 670 | 3.5 | 671 | 2022-01-01 | 2022-11-06 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7416 | 1343.9997 | 36.8777
SYL-G.1.RR.314.1 | 24525599203087 | Golapganj, East Chandanbhag, Khaled Ahmed | 2019-09-02 | NQ1000 | 8.1 | 672 | 8.1 | 673 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7440 | 1319.9997 | 85.3455
SYL-G.1.RR.315.1 | 24522889203022 | Golapganj, East Chandanbhag, Abdul Hanif | 2019-09-02 | NQ1000 | 5.5 | 674 | 5.5 | 675 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7440 | 1319.9997 | 57.9506
SYL-G.1.RR.315.2 | 24522889203022 | Golapganj, East Chandanbhag, Abdul Hanif | 2019-09-02 | NQ1000 | 7.1 | 676 | 7.1 | 677 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7440 | 1319.9997 | 74.809
SYL-G.1.RR.316.1 | 24522309203026 | Golapganj, East Chandanbhag, Rahat Sultana | 2019-09-03 | NQ1000 | 6.3 | 692 | 6.3 | 693 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7440 | 1319.9997 | 66.3798
SYL-G.1.RR.316.2 | 24522309203026 | Golapganj, East Chandanbhag, Rahat Sultana | 2019-09-03 | NQ1000 | 51.6 | 696 | 51.6 | 697 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 51.6 | 51.6 | 3.096 | 3.096 | 0.0007168 | 100% | 0% | 3.096 | 3.096 | 0.0011869 | 28 | 0.062064 | 0.062064 |  | 0 | 0 | 7440 | 1319.9997 | 543.6824
SYL-G.1.RR.317.1 | 24513269201341 | Golapganj, Daripatan, Uchabari, Abdur Rahaman Villa (Freedom Fighter) | 2019-09-03 | NQ1000 | 10.6 | 698 | 10.6 | 699 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7440 | 1319.9997 | 111.6867
SYL-G.1.RR.318.1 | 24513399201344 | Golapganj, Daripatan, Uchabari, Burhanuddin | 2019-09-03 | NQ1000 | 4.4 | 700 | 4.4 | 701 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7440 | 1319.9997 | 46.3605
SYL-G.1.RR.318.2 | 24513399201344 | Golapganj, Daripatan, Uchabari, Burhanuddin | 2021-02-08 | LX1011 | 4.6 | 100 | 4.6 | 101 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7440 | 1319.9997 | 48.4678
SYL-G.1.RR.319.1 | 24513479201351 | Golapganj, Daripatan, Uchabari, Rahimuddin | 2019-09-03 | NQ1000 | 7.1 | 702 | 7.1 | 703 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7440 | 1319.9997 | 74.809
SYL-G.1.RR.320.1 | 24510499201431 | Golapganj, Ronkeli Uttor, Awtadur Rhaman | 2019-09-03 | NQ1000 | 5.1 | 704 | 4.8 | 705 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7392 | 1367.9997 | 50.5751
SYL-G.1.RR.321.1 | 24510499201431 | Golapganj, Ronkeli Uttor, Awtadur Rhaman | 2019-09-03 | NQ1000 | 6 | 706 | 6 | 707 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7392 | 1367.9997 | 63.2189
SYL-G.1.RR.321.2 | 24510499201431 | Golapganj, Ronkeli Uttor, Awtadur Rhaman | 2021-09-16 | NQ1007 | 14.8 | 29 | 14.8 | 30 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 7392 | 1367.9997 | 155.9399
SYL-G.1.RR.322.1 | 24482519202338 | Golapganj, Dhakadakshin, Sunampur Road, Abdul Hannan | 2019-09-04 | NQ1000 | 12.1 | 1 | 11.7 | 2 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7320 | 1439.9997 | 123.2768
SYL-G.1.RR.322.2 | 24482519202338 | Golapganj, Dhakadakshin, Sunampur Road, Abdul Hannan | 2019-09-04 | NQ1000 | 6.9 | 3 | 6.9 | 4 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7320 | 1439.9997 | 72.7017
SYL-G.1.RR.323.1 | 24482619202365 | Golapganj, Dhakadakshin, East Bazar,Mukibur Rahaman (Bulu Mia) | 2019-09-04 | NQ1000 | 4.6 | 5 | 4.6 | 6 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7320 | 1439.9997 | 48.4678
SYL-G.1.RR.323.2 | 24482619202365 | Golapganj, Dhakadakshin, East Bazar,Mukibur Rahaman (Bulu Mia) | 2019-09-04 | NQ1000 | 9.9 | 7 | 9.2 | 8 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7320 | 1439.9997 | 96.9356
SYL-G.1.RR.324.1 | 24482709202358 | Golapganj, Dhakadakshin, East Bazar, Dipak | 2019-09-04 | NQ1000 | 4.6 | 9 | 4.6 | 10 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7320 | 1439.9997 | 48.4678
SYL-G.1.RR.325.1 | 24482919202381 | Golapganj, Dhakadakshin, Sunampur Road, Abdur Rawf | 2019-09-04 | NQ1000 | 8.6 | 11 | 8.6 | 12 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7320 | 1439.9997 | 90.6137
SYL-G.1.RR.326.1 | 24483209202407 | Golapganj, Dhakadakshin, Sunampur Road, Cherakuddin | 2019-09-04 | NQ1000 | 2.8 | 13 | 2.8 | 14 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7320 | 1439.9997 | 29.5021
SYL-G.1.RR.327.1 | 24483329202427 | Golapganj, Dhakadakshin, Raigor, Sunampur Road, Selim Member | 2019-09-04 | NQ1000 | 6.9 | 15 | 6.9 | 16 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7320 | 1439.9997 | 72.7017
SYL-G.1.RR.327.2 | 24483329202427 | Golapganj, Dhakadakshin, Raigor, Sunampur Road, Selim Member | 2019-09-04 | NQ1000 | 1.9 | 17 | 1.9 | 18 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7320 | 1439.9997 | 20.0193
SYL-G.1.RR.328.1 | 24491209203212 | Golapganj, Dhakadakshin, North Raighor,Ukorkandi, Abul Kalam | 2019-09-05 | NQ1000 | 8.3 | 44 | 8.3 | 45 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 1464 | 0 | 5856 | 1439.9997 | 72.8374
SYL-G.1.RR.328.2 | 24491209203212 | Golapganj, Dhakadakshin, North Raighor,Ukorkandi, Abul Kalam | 2019-09-05 | NQ1000 | 10.9 | 46 | 10.7 | 47 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 1464 | 0 | 5856 | 1439.9997 | 93.8988
SYL-G.1.RR.329.1 | 24491909203263 | Golapganj, Dhakadakshin, North Raighor,Ukorkandi, Nunu Miah | 2019-09-05 | NQ1000 | 1.6 | 48 | 1.6 | 49 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7320 | 1439.9997 | 16.8584
SYL-G.1.RR.330.1 | 24491819203311 | Golapganj, Dhakadakshin, North Raighor,Ukorkandi, Shefali Bala | 2019-09-05 | NQ1000 | 5 | 50 | 5 | 51 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7320 | 1439.9997 | 52.6824
SYL-G.1.RR.331.1 | 24491559203331 | Golapganj, Dhakadakshin, North Raighor,Ukorkandi, Saiad Ripon Jamal | 2019-09-05 | NQ1000 | 16.9 | 52 | 16.9 | 53 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 7320 | 1439.9997 | 178.0665
SYL-G.1.RR.332.1 | 24461029201324 | Golapganj, Bhadeshwar, Purbobhag, Hayarunnesa | 2019-09-07 | NQ1000 | 3 | 55 | 3 | 56 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7248 | 1511.9997 | 31.6094
SYL-G.1.RR.333.1 | 24461029201324 | Golapganj, Bhadeshwar, Purbobhag, Sunamuddin | 2019-09-07 | NQ1000 | 10 | 57 | 10 | 58 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7248 | 1511.9997 | 105.3648
SYL-G.1.RR.334.1 | 24461089201332 | Golapganj, Bhadeshwar, Purbobhag, Shanur Ahmad | 2019-09-07 | NQ1000 | 15.8 | 59 | 15.8 | 60 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7248 | 1511.9997 | 166.4764
SYL-G.1.RR.335.1 | 24461089201332 | Golapganj, Bhadeshwar, Purbobhag, Jubayer Ahmad | 2019-09-07 | NQ1000 | 6.6 | 61 | 6.6 | 62 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7248 | 1511.9997 | 69.5408
SYL-G.1.RR.336.1 | 24461089201332 | Golapganj, Bhadeshwar, Purbobhag, Helal | 2019-09-07 | NQ1000 | 8.8 | 63 | 8.8 | 64 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7248 | 1511.9997 | 92.721
SYL-G.1.RR.337.1 | 24461089201332 | Golapganj, Bhadeshwar, Purbobhag, Najma Begum | 2019-09-07 | NQ1000 | 11.8 | 65 | 11.8 | 66 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7248 | 1511.9997 | 124.3305
SYL-G.1.RR.338.1 | 24461219201353 | Golapganj, Bhadeshwar, Purbobhag, Najrul Islam | 2019-09-07 | NQ1000 | 4.7 | 67 | 4.7 | 68 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7248 | 1511.9997 | 49.5215
SYL-G.1.RR.339.1 | 24461439201372 | Golapganj, Bhadeshwar, Purbobhag, Habib (Front Of Rajapur Jame Masjid ) | 2019-09-07 | NQ1000 | 53.6 | 69 | 53.6 | 70 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 53.6 | 53.6 | 3.216 | 3.216 | 0.0007168 | 100% | 0% | 3.216 | 3.216 | 0.0011869 | 28 | 0.06447 | 0.06447 |  | 0 | 0 | 7248 | 1511.9997 | 564.7554
SYL-G.1.RR.340.1 | 24460429201344 | Golapganj, Bhadeshwar, Kalashohor, Nurul Alam | 2019-09-07 | NQ1000 | 9.1 | 71 | 9.1 | 72 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7248 | 1511.9997 | 95.882
SYL-G.1.RR.341.1 | 24460049201282 | Golapganj, Bhadeshwar, Kalashohor, Masum Ahmad | 2019-09-07 | NQ1000 | 11.1 | 73 | 11.1 | 74 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7248 | 1511.9997 | 116.9549
SYL-G.1.RR.341.2 | 24460049201282 | Golapganj, Bhadeshwar, Kalashohor, Masum Ahmad | 2019-09-07 | NQ1000 | 5.6 | 75 | 5.6 | 76 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7248 | 1511.9997 | 59.0043
SYL-G.1.RR.342.1 | 24461219201230 | Golapganj, Bhadeshwar, Naya Bazar, Amjad Ali | 2019-09-07 | NQ1000 | 4.4 | 77 | 4.4 | 78 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7248 | 1511.9997 | 46.3605
SYL-G.1.RR.343.1 | 24460819201212 | Golapganj, Bhadeshwar, Naya Bazar, Hannan Monjil | 2019-09-07 | NQ1000 | 5.5 | 79 | 5.5 | 80 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7248 | 1511.9997 | 57.9506
SYL-G.1.RR.344.1 | 24460139201200 | Golapganj, Bhadeshwar, Maizbhag, Tabaroq Ali | 2019-09-07 | NQ1000 | 11 | 81 | 11 | 82 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7248 | 1511.9997 | 115.9013
SYL-G.1.RR.345.1 | 24455899201159 | Golapganj, Bhadeshwar, Maizbhag, Rustom Ali | 2019-09-07 | NQ1000 | 18.1 | 83 | 18.1 | 84 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 7248 | 1511.9997 | 190.7103
SYL-G.1.RR.346.1 | 24454599201176 | Golapganj, Bhadeshwar, Mokam Bazar, Uttorgao, Mustakim Ali | 2019-09-08 | NQ1000 | 15.1 | 85 | 15.1 | 86 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7248 | 1511.9997 | 159.1009
SYL-G.1.RR.346.2 | 24454599201176 | Golapganj, Bhadeshwar, Mokam Bazar, Uttorgao, Mustakim Ali | 2019-09-08 | NQ1000 | 4.2 | 87 | 4.2 | 88 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7248 | 1511.9997 | 44.2532
SYL-G.1.RR.347.1 | 24454609201193 | Golapganj, Bhadeshwar, Mokam Bazar, Uttorgao, Goni | 2019-09-08 | NQ1000 | 15.7 | 89 | 14.8 | 90 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 7248 | 1511.9997 | 155.9399
SYL-G.1.RR.348.1 | 24460079200428 | Golapganj, Bhadeshwar, West Bhag, Nanu Mia | 2019-09-08 | NQ1000 | 3.4 | 91 | 3.4 | 92 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7248 | 1511.9997 | 35.824
SYL-G.1.RR.349.1 | 24460079200428 | Golapganj, Bhadeshwar, West Bhag, Ayad Ali | 2019-09-08 | NQ1000 | 9.2 | 93 | 9.2 | 94 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7248 | 1511.9997 | 96.9356
SYL-G.1.RR.350.1 | 24455959200422 | Golapganj, Bhadeshwar, West Bhag, Shiraj | 2019-09-08 | NQ1000 | 1.7 | 97 | 1.7 | 98 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7248 | 1511.9997 | 17.912
SYL-G.1.RR.351.1 | 24512939200418 | Golapganj, Sita Fullbari, Shomshir Uddin(Londoni), Monjil | 2019-08-31 | NQ1000 | 42.4 | 600 | 42.8 | 601 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 42.8 | 42.8 | 2.568 | 2.568 | 0.0007168 | 100% | 0% | 2.568 | 2.568 | 0.0011869 | 28 | 0.05148 | 0.05148 |  | 0 | 0 | 7344 | 1415.9997 | 450.9614
SYL-G.1.RR.352.1 | 24513019200433 | Golapganj, Sita Fullbari, Jotindro Babu | 2019-08-31 | NQ1000 | 10.1 | 602 | 10.1 | 603 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7344 | 1415.9997 | 106.4185
SYL-G.1.RR.353.1 | 24513369200395 | Golapganj, Golapganj Bazar, Uttor Bazar, Kulsuma Begum | 2019-08-31 | NQ1000 | 11.4 | 604 | 11.4 | 605 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7344 | 1415.9997 | 120.1159
SYL-G.1.RR.354.1 | 24513419200380 | Golapganj, Golapganj Bazar, Uttor Bazar, Surman Ali | 2019-08-31 | NQ1000 | 9.4 | 606 | 9.4 | 607 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7344 | 1415.9997 | 99.0429
SYL-G.1.RR.355.1 | 24513369200409 | Golapganj, Golapganj Bazar, Uttor Bazar, Rubel Ahmed | 2019-08-31 | NQ1000 | 3.2 | 608 | 3.2 | 609 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7344 | 1415.9997 | 33.7167
SYL-G.1.RR.356.1 | 24513369200409 | Golapganj, Golapganj Bazar, Uttor Bazar, Babul | 2019-08-31 | NQ1000 | 3.3 | 610 | 3.3 | 611 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7344 | 1415.9997 | 34.7704
SYL-G.1.RR.357.1 | 24514239200442 | Golapganj, Soroshoti(Nijganj), Jakaria Hossain | 2019-08-31 | NQ1000 | 11.2 | 612 | 11.2 | 613 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7344 | 1415.9997 | 118.0086
SYL-G.1.RR.358.1 | 24513499200455 | Golapganj, Soroshoti, Selim Mia | 2019-08-31 | NQ1000 | 4.5 | 614 | 4.5 | 615 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7344 | 1415.9997 | 47.4142
SYL-G.1.RR.359.1 | 24514089200406 | Golapganj, Shorosoti, Surma Dayek, Enam Uddin | 2019-09-01 | NQ1000 | 30.2 | 616 | 29.9 | 617 | 2022-01-01 | 2022-11-03 | NQ1007 |  |  | 0 | 117 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7344 | 1415.9997
SYL-G.1.RR.360.1 | 24514169200409 | Golapganj, Shorosoti, Surma Dayek, Altab Uddin | 2019-09-01 | NQ1000 | 2.3 | 618 | 2.3 | 619 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7344 | 1415.9997 | 24.2339
SYL-G.1.RR.361.1 | 24514119200405 | Golapganj, Shorosoti, Surma Dayek, Lal Mia | 2019-09-01 | NQ1000 | 12.8 | 620 | 12.8 | 621 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7344 | 1415.9997 | 134.867
SYL-G.1.RR.362.1 | 24514119200405 | Golapganj, Shorosoti, Surma Dayek, Alkaz Uddin | 2019-09-01 | NQ1000 | 18.9 | 624 | 18.9 | 625 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 7344 | 1415.9997 | 199.1395
SYL-G.1.RR.363.1 | 24514299200407 | Golapganj, Shorosoti, Surma Dayek, Alom Uddin | 2019-09-01 | NQ1000 | 10.9 | 626 | 10.6 | 627 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7344 | 1415.9997 | 111.6867
SYL-G.1.RR.363.2 | 24514299200407 | Golapganj, Shorosoti, Surma Dayek, Alom Uddin | 2021-02-08 | MN1018 | 16.2 | 92 | 16.2 | 93 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 7344 | 1415.9997 | 170.691
SYL-G.1.RR.364.1 | 24514799200394 | Golapganj, Shorosoti, Surma Dayek, Joinal Abedin | 2019-09-01 | NQ1000 | 7.8 | 628 | 7.8 | 629 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7344 | 1415.9997 | 82.1846
SYL-G.1.RR.365.1 | 24514799200394 | Golapganj, Shorosoti, Surma Dayek, Abdul Goni | 2019-09-01 | NQ1000 | 31.4 | 630 | 31 | 631 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 31 | 31 | 1.86 | 1.86 | 0.0007168 | 100% | 0% | 1.86 | 1.86 | 0.0011869 | 28 | 0.037287 | 0.037287 |  | 0 | 0 | 7344 | 1415.9997 | 326.6309
SYL-G.1.RR.366.1 | 24514799200394 | Golapganj, Shorosoti, Surma Dayek, Samsul Haque | 2019-09-01 | NQ1000 | 10.7 | 635 | 10.7 | 636 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7344 | 1415.9997 | 112.7403
SYL-G.1.RR.367.1 | 24515109200375 | Golapganj, Shorosoti, Surma Dayek, Abdur Sohid | 2019-09-01 | NQ1000 | 9.7 | 637 | 9.7 | 638 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7344 | 1415.9997 | 102.2039
SYL-G.1.RR.368.1 | 24513539201041 | Golapganj, Dari Patton, Chairman Bari Goli, Abdul Jolil | 2019-09-01 | NQ1000 | 11.1 | 639 | 11.1 | 640 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7440 | 1319.9997 | 116.9549
SYL-G.1.RR.369.1 | 24513459201062 | Golapganj, Dari Patton, Near Chairman Bari, Dulal Ahmed | 2019-09-01 | NQ1000 | 88.2 | 641 | 88.2 | 642 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 88.2 | 88.2 | 5.292 | 5.292 | 0.0007168 | 100% | 0% | 5.292 | 5.292 | 0.0011869 | 28 | 0.10609 | 0.10609 |  | 0 | 0 | 7440 | 1319.9997 | 929.3176
SYL-G.1.RR.370.1 | 24525789203246 | Golapganj, Chattis, Near Jame Mosjid, Shadikur Rahman | 2019-09-02 | NQ1000 | 17.2 | 680 | 17.2 | 681 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 7440 | 1319.9997 | 181.2275
SYL-G.1.RR.371.1 | 24525789203246 | Golapganj, Chattis, Near Jame Mosjid, Mohammad Fokrul Alom | 2019-09-02 | NQ1000 | 10.4 | 682 | 10.4 | 683 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7440 | 1319.9997 | 109.5794
SYL-G.1.RR.372.1 | 24525789203246 | Golapganj, Chattis, Near Jame Mosjid, Belal Ahmed | 2019-09-02 | NQ1000 | 9.8 | 684 | 9.8 | 685 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7440 | 1319.9997 | 103.2575
SYL-G.1.RR.372.2 | 24525789203246 | Golapganj, Chattis, Near Jame Mosjid, Belal Ahmed | 2021-09-14 | NQ1007 | 3.8 | 24 | 3.8 | 25 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7440 | 1319.9997 | 40.0386
SYL-G.1.RR.373.1 | 24530739203450 | Golapganj, Chattis, Ranapink, Ma jubeda Chowdhury Bari, Aftab | 2019-09-02 | NQ1000 | 10.8 | 686 | 10.8 | 687 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7440 | 1319.9997 | 113.794
SYL-G.1.RR.374.1 | 24530739203450 | Golapganj, Chattis, Ranapink,Ma jubeda Chowdhury Bari, Aftab | 2019-09-02 | NQ1000 | 4.1 | 690 | 4.1 | 691 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7440 | 1319.9997 | 43.1996
SYL-G.1.RR.374.2 | 24530739203450 | Golapganj, Chattis, Ranapink,Ma jubeda Chowdhury Bari, Aftab | 2022-04-10 | LU1001 | 13.2 | 135 | 13.2 | 136 | 2022-04-10 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 5064 | 1319.9997 | 101.3581
SYL-G.1.RR.375.1 | 24505609201433 | Golapganj, Ronokali Uttor, Ronokali Deghir Par Road, Abdul Lotif | 2019-09-03 | NQ1000 | 2.5 | 708 | 2.5 | 709 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7392 | 1367.9997 | 26.3412
SYL-G.1.RR.376.1 | 24505179201430 | Golapganj, Ronokali Uttor, Ronokali Deghir Par Road, Abu Nayem | 2019-09-03 | NQ1000 | 4.5 | 710 | 4.5 | 711 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7392 | 1367.9997 | 47.4142
SYL-G.1.RR.377.1 | 24504799201469 | Golapganj, Ronokali Uttor, Ronokali Deghir Par Road, Sadikur Rahman | 2019-09-03 | NQ1000 | 5.1 | 712 | 5.1 | 713 | 2022-01-01 | 2022-11-05 | NQ1007 |  |  | 0 | 128 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7392 | 1367.9997
SYL-G.1.RR.377.2 | 24504799201469 | Golapganj, Ronokali Uttor, Ronokali Deghir Par Road, Sadikur Rahman | 2022-11-05 | NQ1007 | 3.5 | 131 | 3.5 | 132 | 2022-11-05 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 0 | 1367.9997 | 5.759
SYL-G.1.RR.378.1 | 24504339201455 | Golapganj, Ronokali Uttor, Ronokali Deghir Par, Shamim Uddin | 2019-09-03 | NQ1000 | 6.3 | 714 | 6.3 | 715 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7392 | 1367.9997 | 66.3798
SYL-G.1.RR.379.1 | 24504059201403 | Golapganj, Ronokali Uttor, Ronokali Deghir Par, Moksudul Karim | 2019-09-03 | NQ1000 | 11 | 716 | 11 | 717 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7392 | 1367.9997 | 115.9013
SYL-G.1.RR.380.1 | 24504059201403 | Golapganj, Ronokali Uttor, Ronokali Deghir Par, Mohisanul Karim | 2019-09-03 | NQ1000 | 11.4 | 718 | 11.4 | 719 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 1752 | 0 | 5640 | 1367.9997 | 96.0927
SYL-G.1.RR.381.1 | 24504059201403 | Golapganj, Ronokali Uttor, Ronokali Deghir Par, Samsan Uddin | 2019-09-03 | NQ1000 | 11.8 | 720 | 11.8 | 721 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7392 | 1367.9997 | 124.3305
SYL-G.1.RR.382.1 | 24510809202026 | Golapganj, Ronokali Uttor, Near Sirajul Jabbar Meyor Bari, Abul Islam | 2019-09-03 | NQ1000 | 6.7 | 722 | 6.7 | 723 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7392 | 1367.9997 | 70.5944
SYL-G.1.RR.382.2 | 24510809202026 | Golapganj, Ronokali Uttor, Near Sirajul Jabbar Meyor Bari, Abul Islam | 2019-09-03 | NQ1000 | 15.2 | 724 | 15.2 | 725 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7392 | 1367.9997 | 160.1545
SYL-G.1.RR.383.1 | 24510809202026 | Golapganj, Ronokali Uttor, Near Sirajul Jabbar Meyor Bari, Fokrul Isalm | 2019-09-03 | NQ1000 | 17.7 | 726 | 17.7 | 727 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 7392 | 1367.9997 | 186.4957
SYL-G.1.RR.384.1 | 24485299202471 | Gopalganj, Dhaka Dokkhin, Uttor Rain Ghor, Lutu Miar Bari | 2019-09-04 | NQ1000 | 6.9 | 21 | 6.9 | 22 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7320 | 1439.9997 | 72.7017
SYL-G.1.RR.385.1 | 24485629202479 | Gopalganj, Dhaka Dokkhin, Uttor Rain Ghor, Akkados Ali | 2019-09-04 | NQ1000 | 6.7 | 23 | 6.7 | 24 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7320 | 1439.9997 | 70.5944
SYL-G.1.RR.386.1 | 24492249203120 | Gopalganj, Dhaka Dokkhin, Uttor Rain Ghor, Chunnu Mia | 2019-09-04 | NQ1000 | 2.4 | 25 | 2.5 | 26 | 2022-01-01 | 2022-11-02 | NQ1007 |  |  | 0 | 111 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7320 | 1439.9997
SYL-G.1.RR.387.1 | 24493729203172 | Golapganj, Dhaka Dokkhin, Lombaghaw Shilghat, Motiur Rahman Chowdhury | 2019-09-05 | NQ1000 | 13.8 | 29 | 13.8 | 30 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7320 | 1439.9997 | 145.4034
SYL-G.1.RR.388.1 | 24493149203328 | Golapganj, Dhaka Dokkhin, Silghat, Nowbari, Fazlu Mia | 2019-09-05 | NQ1000 | 13.2 | 31 | 12.8 | 32 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7320 | 1439.9997 | 134.867
SYL-G.1.RR.388.2 | 24493149203328 | Golapganj, Dhaka Dokkhin, Silghat, Nowbari, Fazlu Mia | 2019-09-05 | NQ1000 | 5.1 | 35 | 5.1 | 36 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7320 | 1439.9997 | 53.7361
SYL-G.1.RR.389.1 | 24493149203328 | Golapganj, Dhaka Dokkhin, Silghat, Nowbari, Towhid Ali | 2019-09-05 | NQ1000 | 6.2 | 37 | 6.2 | 38 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7320 | 1439.9997 | 65.3262
SYL-G.1.RR.390.1 | 24493439203315 | Golapganj, Dhaka Dokkhin, Silghat, Nowbari, Shorifuddin | 2019-09-05 | NQ1000 | 23 | 39 | 23 | 40 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 23 | 23 | 1.38 | 1.38 | 0.0007168 | 100% | 0% | 1.38 | 1.38 | 0.0011869 | 28 | 0.027664 | 0.027664 |  | 0 | 0 | 7320 | 1439.9997 | 242.3391
SYL-G.1.RR.391.1 | 24494059203416 | Golapganj, Dhaka Dokkhin, Silghat, Sonar Para, Rokib Ali | 2019-09-05 | NQ1000 | 9.1 | 41 | 8.9 | 42 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7320 | 1439.9997 | 93.7747
SYL-G.1.RR.392.1 | 24513079202065 | Golapganj, Gogharkul West Para, Jomir Ahmed | 2019-09-09 | NQ1000 | 11 | 99 | 11 | 100 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7392 | 1367.9997 | 115.9013
SYL-G.1.RR.393.1 | 24513169202051 | Golapganj, Gogharkul West Para, Towhid Mahmud | 2019-09-09 | NQ1000 | 22 | 101 | 22 | 102 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 22 | 22 | 1.32 | 1.32 | 0.0007168 | 100% | 0% | 1.32 | 1.32 | 0.0011869 | 28 | 0.026461 | 0.026461 |  | 0 | 0 | 7392 | 1367.9997 | 231.8026
SYL-G.1.RR.394.1 | 24513499202018 | Golapganj, Gogharkul West Para, Younus Ahmed | 2019-09-09 | NQ1000 | 2.4 | 103 | 2.4 | 104 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7392 | 1367.9997 | 25.2876
SYL-G.1.RR.395.1 | 24513489202068 | Golapganj, Gogharkul West Para, Rina Begum Chowdhury | 2019-09-09 | NQ1000 | 14.4 | 105 | 14.4 | 106 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7392 | 1367.9997 | 151.7253
SYL-G.1.RR.396.1 | 24511109202355 | Golapganj, Badaronkhali, Mohammad Ali | 2019-09-09 | NQ1000 | 1.9 | 107 | 1.9 | 108 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7392 | 1367.9997 | 20.0193
SYL-G.1.RR.397.1 | 24510379202344 | Golapganj, Badaronkhali, Prosonno Deb Nath | 2019-09-09 | NQ1000 | 10.1 | 109 | 10.1 | 110 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7392 | 1367.9997 | 106.4185
SYL-G.1.RR.398.1 | 24510249202327 | Golapganj, Badaronkhali, Abdul Gofur | 2019-09-09 | NQ1000 | 9.5 | 111 | 9.5 | 112 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7392 | 1367.9997 | 100.0966
SYL-G.1.RR.399.1 | 24484319202425 | Golapganj, Dhaka Dokkhin, South Raighor, Abdul Muktadir | 2019-09-11 | NQ1000 | 21.2 | 123 | 21.1 | 124 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 21.1 | 21.1 | 1.266 | 1.266 | 0.0007168 | 100% | 0% | 1.266 | 1.266 | 0.0011869 | 28 | 0.025379 | 0.025379 |  | 0 | 0 | 7320 | 1439.9997 | 222.3198
SYL-G.1.RR.400.1 | 24470629159017 | Galapganj, Dhaka Dokkhin, Fullshaind, Near Primary School, Showa Mia | 2019-09-12 | NQ1000 | 31.9 | 139 | 31.9 | 140 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 31.9 | 31.9 | 1.914 | 1.914 | 0.0007168 | 100% | 0% | 1.914 | 1.914 | 0.0011869 | 28 | 0.038369 | 0.038369 |  | 0 | 0 | 7224 | 1535.9997 | 336.1138
SYL-G.1.RR.401.1 | 24453079200493 | Golapganj, Vadeswar, Dokkhin Vag, Hazi Tila, Moinuddin | 2019-09-08 | LP1002 | 11 | 81 | 11 | 82 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7248 | 1511.9997 | 115.9013
SYL-G.1.RR.402.1 | 24452359200521 | Golapganj, Vadeswar, Dokkhin Vag, Hafiz Alauddin | 2019-09-08 | LP1002 | 4.5 | 83 | 4.5 | 84 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7248 | 1511.9997 | 47.4142
SYL-G.1.RR.403.1 | 24452359200521 | Golapganj, Vadeswar, Dokkhin Vag, Rakib Uddin | 2019-09-08 | LP1002 | 6.1 | 87 | 6.1 | 88 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7248 | 1511.9997 | 64.2725
SYL-G.1.RR.404.1 | 24510339202071 | Golapganj, North Ronkeli, Bonaki Tilla, Zakerin | 2019-09-09 | LP1002 | 22.8 | 107 | 22.8 | 108 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 22.8 | 22.8 | 1.368 | 1.368 | 0.0007168 | 100% | 0% | 1.368 | 1.368 | 0.0011869 | 28 | 0.027424 | 0.027424 |  | 0 | 0 | 7392 | 1367.9997 | 240.2318
SYL-G.1.RR.404.2 | 24510339202071 | Golapganj, North Ronkeli, Bonaki Tilla, Zakerin | 2022-11-05 | NQ1007 | 6.2 | 129 | 6.2 | 130 | 2022-11-05 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 0 | 1367.9997 | 10.2016
SYL-G.1.RR.405.1 | 24504929200167 | Golapganj, North Ghosgaun, Faruk | 2019-09-09 | LP1002 | 4.2 | 111 | 4.2 | 112 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7344 | 1415.9997 | 44.2532
SYL-G.1.RR.406.1 | 24504929200167 | Golapganj, North Ghosgaun, Mohi | 2019-09-09 | LP1002 | 7.3 | 113 | 7.3 | 114 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7344 | 1415.9997 | 76.9163
SYL-G.1.RR.407.1 | 24504269200170 | Golapganj, North Ghosgaun, Mohibur Rahman | 2019-09-09 | LP1002 | 6.9 | 115 | 6.9 | 116 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7344 | 1415.9997 | 72.7017
SYL-G.1.RR.408.1 | 24504269200170 | Golapganj, North Ghosgaun, Mahtabur Rahman | 2019-09-09 | LP1002 | 53.8 | 117 | 53.8 | 118 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 53.8 | 53.8 | 3.228 | 3.228 | 0.0007168 | 100% | 0% | 3.228 | 3.228 | 0.0011869 | 28 | 0.06471 | 0.06471 |  | 0 | 0 | 7344 | 1415.9997 | 566.8627
SYL-G.1.RR.409.1 | 24504269200170 | Golapganj, North Ghosgaun, Helal Ahmad | 2019-09-09 | LP1002 | 7 | 119 | 7.1 | 120 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7344 | 1415.9997 | 74.809
SYL-G.1.RR.410.1 | 24504449200127 | Golapganj, North Ghosgaun, Sofiq uddin | 2019-09-09 | LP1002 | 12.3 | 121 | 12.4 | 122 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7344 | 1415.9997 | 130.6524
SYL-G.1.RR.410.2 | 24504449200127 | Golapganj, North Ghosgaun, Sofiq uddin | 2022-04-12 | LU1001 | 4.9 | 147 | 4.9 | 148 | 2022-04-12 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 4920 | 1415.9997 | 37.3424
SYL-G.1.RR.411.1 | 24471059158581 | Golapganj, Fulshaind, Nazat Tilla, Mokoddos Ali | 2019-09-11 | LP1002 | 3.5 | 137 | 3.5 | 138 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7224 | 1535.9997 | 36.8777
SYL-G.1.RR.412.1 | 24471059158581 | Golapganj, Fulshaind, Nazat Tilla, Harun Mia | 2019-09-11 | LP1002 | 20 | 139 | 20 | 140 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 7224 | 1535.9997 | 210.7296
SYL-G.1.RR.413.1 | 24470969158594 | Golapganj, Fulshaind, Collage Road, Monir Mia | 2019-09-11 | LP1002 | 2.6 | 141 | 2.6 | 142 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7224 | 1535.9997 | 27.3949
SYL-G.1.RR.414.1 | 24471549158524 | Golapganj, Fulshaind, Ada Tilla, A. Mukit | 2019-09-11 | LP1002 | 12.8 | 143 | 12.8 | 144 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7224 | 1535.9997 | 134.867
SYL-G.1.RR.415.1 | 24482859158114 | Golapganj, Lokkhipasa, Boro Bari, A. Rahim | 2019-09-12 | LP1002 | 11 | 155 | 11 | 156 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7224 | 1535.9997 | 115.9013
SYL-G.1.RR.416.1 | 24482859158114 | Golapganj, Lokkhipasa, Boro Bari, Shetab | 2019-09-12 | LP1002 | 15.9 | 158 | 15.9 | 159 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 7224 | 1535.9997 | 167.5301
SYL-G.1.RR.417.1 | 24481389158146 | Golapganj, Lokkhipasa, Gashiborni, Miftah uddin | 2019-09-12 | LP1002 | 4.7 | 160 | 4.7 | 161 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7224 | 1535.9997 | 49.5215
SYL-G.1.RR.418.1 | 24504759159287 | Golapganj, Ful Bari, South para, Helal Ahmad (Sheful) | 2019-09-14 | LP1002 | 5.4 | 162 | 5.4 | 163 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7344 | 1415.9997 | 56.897
SYL-G.1.RR.419.1 | 24504699159297 | Golapganj, Ful Bari, South para, Tosob Ali | 2019-09-14 | LP1002 | 3.8 | 164 | 3.8 | 165 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7344 | 1415.9997 | 40.0386
SYL-G.1.RR.420.1 | 24504799159335 | Golapganj, Ful Bari, South para, A. Razzak | 2019-09-14 | LP1002 | 40.3 | 166 | 39.5 | 167 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 39.5 | 39.5 | 2.37 | 2.37 | 0.0007168 | 100% | 0% | 2.37 | 2.37 | 0.0011869 | 28 | 0.04751 | 0.04751 |  | 0 | 0 | 7344 | 1415.9997 | 416.191
SYL-G.1.RR.421.1 | 24510679159316 | Golapganj, Ful Bari, North para, Aminul Haq | 2019-09-14 | LP1002 | 3.3 | 168 | 3.3 | 169 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7272 | 1487.9997 | 34.7704
SYL-G.1.RR.421.2 | 24510679159316 | Golapganj, Ful Bari, North para, Aminul Haq | 2019-09-14 | LP1002 | 22.9 | 170 | 22.3 | 171 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 7272 | 1487.9997 | 234.9635
SYL-G.1.RR.451.1 | 24524709203402 | Golapganj, Poschim Fazilpur, Abdul Kuddus, Near Fazilpur Govt. Primary School | 2019-09-05 | LP1002 | 3.4 | 27 | 3.3 | 28 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7440 | 1319.9997 | 34.7704
SYL-G.1.RR.452.1 | 24524809203409 | Golapganj, Poschim Fazilpur, Fayek Chowdhury | 2019-09-05 | LP1002 | 1.5 | 31 | 1.5 | 32 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7440 | 1319.9997 | 15.8047
SYL-G.1.RR.453.1 | 24481409158054 | Golapganj, South Laxmipasha, Master Bari, Md. Shohel | 2019-09-12 | LP1002 | 9.6 | 149 | 9.6 | 150 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7224 | 1535.9997 | 101.1502
SYL-G.1.RR.454.1 | 24481409158088 | Golapganj, South Laxmipasha, Master Bari, Abbas Uddin | 2019-09-12 | LP1002 | 3.8 | 151 | 3.8 | 152 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7224 | 1535.9997 | 40.0386
SYL-G.1.RR.455.1 | 24481409158054 | Golapganj, South Laxmipasha, Master Bari, Mohammad Ali | 2019-09-12 | LP1002 | 10.1 | 153 | 10.1 | 154 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7224 | 1535.9997 | 106.4185
SYL-G.1.RR.456.1 | 24512939158404 | Golapganj, Hazi Pur (Shokna) Hazi Eakbol Hossan | 2019-09-14 | LP1002 | 11.7 | 172 | 11.7 | 173 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7272 | 1487.9997 | 123.2768
SYL-G.1.RR.457.1 | 24512939158404 | Golapganj, Hazi Pur (Shokna) Hazi Eakbol Hossan | 2019-09-14 | LP1002 | 3.8 | 174 | 4 | 175 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7272 | 1487.9997 | 42.1459
SYL-G.1.RR.458.1 | 24512539158391 | Golapganj, Hazi Pur (Shokna) Nurul Islam | 2019-09-14 | LP1002 | 8.6 | 180 | 9.1 | 181 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7272 | 1487.9997 | 95.882
SYL-G.1.RR.459.1 | 24511589158340 | Golapganj, Hazi Pur (Lamapara) Joynal Abden | 2019-09-14 | LP1002 | 15.1 | 182 | 14.9 | 183 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 7272 | 1487.9997 | 156.9936
SYL-G.1.RR.460.1 | 24511889158312 | Golapganj, Hazi Pur (Lamapa) A. Kuddus | 2019-09-14 | LP1002 | 16.7 | 184 | 17.1 | 185 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 7272 | 1487.9997 | 180.1738
SYL-G.1.RR.461.1 | 24511779158305 | Golapganj, Hazi Pur (Lamapa) Samsul Haque | 2019-09-14 | LP1002 | 3.1 | 186 | 3.1 | 187 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7272 | 1487.9997 | 32.6631
SYL-G.1.RR.461.2 | 24511779158305 | Golapganj, Hazi Pur (Lamapa) Samsul Haque | 2019-09-14 | LP1002 | 8.1 | 188 | 8.1 | 189 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7272 | 1487.9997 | 85.3455
SYL-G.1.RR.462.1 | 24511059158345 | Golapganj, Kismot Maijvag (Korompur) Samsudin | 2019-09-14 | LP1002 | 8.1 | 190 | 8.1 | 191 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7272 | 1487.9997 | 85.3455
SYL-G.1.RR.463.1 | 24511059158345 | Golapganj, Kismot Maijvag (Korompur) Tarak Ahamed | 2019-09-14 | LP1002 | 7.8 | 194 | 7.8 | 195 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7272 | 1487.9997 | 82.1846
SYL-G.1.RR.501.1 | 24455389200411 | Golapganj, West Vabshwar, Fazlur Rahman | 2019-09-08 | MN1018 | 11.4 | 105 | 11.2 | 106 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7248 | 1511.9997 | 118.0086
SYL-G.1.RR.502.1 | 24455389200411 | Golapganj, West Vabshwar, Hafizur Rahman | 2019-09-08 | MN1018 | 7.5 | 107 | 7.5 | 108 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7248 | 1511.9997 | 79.0236
SYL-G.1.RR.503.1 | 24455389200411 | Golapganj, West Vabshwar, Safiur Rahman | 2019-09-08 | MN1018 | 2.1 | 109 | 2.1 | 110 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7248 | 1511.9997 | 22.1266
SYL-G.1.RR.504.1 | 24460259200563 | Golapganj, West Vabshwar, Rakib Ali | 2019-09-08 | MN1018 | 10.4 | 111 | 10.4 | 112 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7248 | 1511.9997 | 109.5794
SYL-G.1.RR.505.1 | 24460219200495 | Golapganj, West Vabshwar, Khalad Chowdhury | 2019-09-08 | MN1018 | 18.8 | 113 | 18.8 | 114 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 18.8 | 18.8 | 1.128 | 1.128 | 0.0007168 | 100% | 0% | 1.128 | 1.128 | 0.0011869 | 28 | 0.022613 | 0.022613 |  | 0 | 0 | 7248 | 1511.9997 | 198.0858
SYL-G.1.RR.506.1 | 24502779202550 | Golapganj, 5 No Amura Union, Kodomrosul, Puran Bari, Jakaria | 2019-09-09 | MN1018 | 8.5 | 135 | 8.5 | 136 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7392 | 1367.9997 | 89.5601
SYL-G.1.RR.506.2 | 24502779202550 | Golapganj, 5 No Amura Union, Kodomrosul, Puran Bari, Jakaria | 2022-04-13 | LU1001 | 10.1 | 151 | 10.1 | 152 | 2022-04-13 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 4944 | 1367.9997 | 76.6796
SYL-G.1.RR.507.1 | 24502779202550 | Golapganj, 5 No Amura Union, Kodomrosul, Puran Bari, Nasirullaha | 2019-09-09 | MN1018 | 5.3 | 137 | 5.3 | 138 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7392 | 1367.9997 | 55.8434
SYL-G.1.RR.508.1 | 24502329202596 | Golapganj, 5 No Amura Union, Kodomrosul, Abdul Mukit | 2019-09-09 | MN1018 | 2.9 | 139 | 2.9 | 140 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7392 | 1367.9997 | 30.5558
SYL-G.1.RR.509.1 | 24502439203011 | Golapganj, 5 No Amura Union, Kodomrosul, Nurul Ambia | 2019-09-09 | MN1018 | 10.8 | 141 | 10.8 | 142 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7392 | 1367.9997 | 113.794
SYL-G.1.RR.510.1 | 24480469158483 | Golapganj, Lokhnabondo, Islamabad, Abdul Rouf | 2019-09-11 | MN1018 | 10 | 147 | 10 | 148 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7224 | 1535.9997 | 105.3648
SYL-G.1.RR.511.1 | 24480469158483 | Golapganj, Lokhnabondo, Islamabad, Samsuruddin | 2019-09-11 | MN1018 | 15.2 | 149 | 15.2 | 150 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7224 | 1535.9997 | 160.1545
SYL-G.1.RR.512.1 | 24480259158524 | Golapganj, Lokhnabondo, Islamabad, Abdul Hai | 2019-09-11 | MN1018 | 12.6 | 151 | 12.6 | 152 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7224 | 1535.9997 | 132.7597
SYL-G.1.RR.513.1 | 24475909158470 | Golapganj, Lokhnabondo, Islamabad, Fornt Of L.B Green Flower School, Abdul Korim | 2019-09-11 | MN1018 | 5.4 | 153 | 5.4 | 154 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7224 | 1535.9997 | 56.897
SYL-G.1.RR.514.1 | 24475909158470 | Golapganj, Lokhnabondo, Islamabad, Fornt Of L.B Green Flower School, Lutu Mia | 2019-09-11 | MN1018 | 10.2 | 155 | 10.2 | 156 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7224 | 1535.9997 | 107.4721
SYL-G.1.RR.515.1 | 24475409158510 | Golapganj, Lokhnabondo, Islamabad, Side Of L.B Green Flower School, Azarul Haque | 2019-09-11 | MN1018 | 12.9 | 157 | 12.9 | 158 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7224 | 1535.9997 | 135.9206
SYL-G.1.RR.516.1 | 24475409158510 | Golapganj, Lokhnabondo, Islamabad, Side Of L.B Green Flower School, Hannan | 2019-09-11 | MN1018 | 6.1 | 159 | 6.1 | 160 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7224 | 1535.9997 | 64.2725
SYL-G.1.RR.517.1 | 24475489158511 | Golapganj, Lokhnabondo, Islamabad, Side Of L.B Green Flower School, Ozed Ali | 2019-09-11 | MN1018 | 12.9 | 161 | 12.9 | 162 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7224 | 1535.9997 | 135.9206
SYL-G.1.RR.518.1 | 24490619158065 | Golapganj, Laxmipasa, Uttor Mirpur, Gish Mia | 2019-09-12 | MN1018 | 4.6 | 181 | 4.6 | 182 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7224 | 1535.9997 | 48.4678
SYL-G.1.RR.519.1 | 24490619158065 | Golapganj, Laxmipasa, Uttor Mirpur, Gish Mia | 2019-09-12 | MN1018 | 6.5 | 183 | 6.5 | 184 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7224 | 1535.9997 | 68.4871
SYL-G.1.RR.520.1 | 24490679158063 | Golapganj, Laxmipasa, Uttor Mirpur, Alauddin Villa | 2019-09-12 | MN1018 | 25.4 | 185 | 25.4 | 186 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 25.4 | 25.4 | 1.524 | 1.524 | 0.0007168 | 100% | 0% | 1.524 | 1.524 | 0.0011869 | 28 | 0.030551 | 0.030551 |  | 0 | 0 | 7224 | 1535.9997 | 267.6266
SYL-G.1.RR.521.1 | 24490269158101 | Golapganj, Laxmipasa, Uttor Mirpur, Satik Ali | 2019-09-12 | MN1018 | 2.8 | 187 | 3 | 188 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7224 | 1535.9997 | 31.6094
SYL-G.1.RR.522.1 | 24490269158101 | Golapganj, Laxmipasa, Uttor Mirpur, Safa Begum | 2019-09-12 | MN1018 | 12.5 | 191 | 12.5 | 192 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7224 | 1535.9997 | 131.706
SYL-G.1.RR.522.2 | 24490269158101 | Golapganj, Laxmipasa, Uttor Mirpur, Safa Begum | 2022-04-07 | LU1001 | 4.2 | 129 | 4.2 | 130 | 2022-04-07 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 4920 | 1535.9997 | 32.614
SYL-G.1.RR.523.1 | 24485779158148 | Golapganj, Laxmipasa, Uttor Mirpur, Mosque Font Side, Mokbul Ali | 2019-09-12 | MN1018 | 10.8 | 193 | 10.8 | 194 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7224 | 1535.9997 | 113.794
SYL-G.1.RR.551.1 | 24505159203027 | Gulapganj, Amnia, Amnia-2 Govt. Primary School, Sofiq Uddin Suhag Master | 2019-09-09 | MN1018 | 3.6 | 129 | 3.6 | 130 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7392 | 1367.9997 | 37.9313
SYL-G.1.RR.552.1 | 24504229203022 | Gulapganj, Amnia, Amnia Union Porisod Road,Hazi Abdul Kuddus Monjil | 2019-09-09 | MN1018 | 11.7 | 131 | 11.7 | 132 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7392 | 1367.9997 | 123.2768
SYL-G.1.RR.553.1 | 24503559203035 | Gulapganj, Amnia Maij Para, Union Porisod Road, Forid Uddin Talukder | 2019-09-09 | MN1018 | 1.7 | 133 | 1.7 | 134 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7392 | 1367.9997 | 17.912
SYL-G.1.RR.553.2 | 24503559203035 | Gulapganj, Amnia Maij Para, Union Porisod Road, Forid Uddin Talukder | 2022-11-05 | NQ1007 | 5.5 | 135 | 5.5 | 136 | 2022-11-05 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 0 | 1367.9997 | 9.0498
SYL-G.1.RR.554.1 | 24494779200514 | Gulapganj, Nama Barocot, Abdul Samad | 2019-09-11 | MN1018 | 11.1 | 143 | 11.1 | 144 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7320 | 1439.9997 | 116.9549
SYL-G.1.RR.555.1 | 24494779200514 | Gulapganj, Nama Barocot, Abdul Samad | 2019-09-11 | MN1018 | 12.5 | 145 | 12.5 | 146 | 2022-01-01 | 2022-11-02 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7320 | 1439.9997 | 131.706
SYL-G.1.RR.556.1 | 24482079158500 | Gulapganj, Laxmipasha, Laxmnabonda Madrasa Road, Abul Mia | 2019-09-12 | MN1018 | 11.2 | 163 | 10.6 | 164 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7224 | 1535.9997 | 111.6867
SYL-G.1.RR.557.1 | 24482779158479 | Gulapganj, Chowdury Bazar, Lazmnabonda, Hazipur, Khayruzzaman | 2019-09-12 | MN1018 | 10.5 | 165 | 10.1 | 166 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7224 | 1535.9997 | 106.4185
SYL-G.1.RR.558.1 | 24482779158479 | Gulapganj, Chowdury Bazar, Lazmnabonda, Hazipur, Khosruzzaman | 2019-09-12 | MN1018 | 7.9 | 167 | 7.9 | 168 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7224 | 1535.9997 | 83.2382
SYL-G.1.RR.559.1 | 24483569158565 | Gulapganj, Laxmnabonda Maijpara, Amin Mia | 2019-09-12 | MN1018 | 4.7 | 169 | 4.7 | 170 | 2022-01-01 | [9 empty] | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0
SYL-G.1.RR.560.1 | 24484049158566 | Gulapganj, Laxmnabonda Uttorgaon, Azir Uddin | 2019-09-12 | MN1018 | 6 | 171 | 6 | 172 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7224 | 1535.9997 | 63.2189
SYL-G.1.RR.561.1 | 24484139158561 | Gulapganj, Laxmnabonda Uttorgaon, Chonnu Mia | 2019-09-12 | MN1018 | 7.4 | 173 | 7.4 | 174 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7224 | 1535.9997 | 77.97
SYL-G.1.RR.562.1 | 24484219158557 | Gulapganj, Laxmnabonda Uttorgaon, Cerag Ali | 2019-09-12 | MN1018 | 13 | 175 | 13 | 176 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7224 | 1535.9997 | 136.9743
SYL-G.1.RR.563.1 | 24490669158361 | Gulapganj, Laxmnabonda , Mirerchok, Abdul Motin | 2019-09-12 | MN1018 | 9 | 177 | 9 | 178 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7224 | 1535.9997 | 94.8283
SYL-G.1.RR.564.1 | 24490669158361 | Gulapganj, Laxmnabonda , Mirerchok, Mahmud | 2019-09-12 | MN1018 | 10.3 | 179 | 10.3 | 180 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7224 | 1535.9997 | 108.5258
SYL-G.1.RR.565.1 | 24505009159267 | Gulapganj, Fulbari Dokshin, Mirarpara Jame Mosjid, Md. Jorid Ali | 2019-09-14 | MN1018 | 10.8 | 195 | 10.8 | 196 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7344 | 1415.9997 | 113.794
SYL-G.1.RR.566.1 | 24505059159265 | Gulapganj, Fulbari Dokshin, Near by Mirarpara Jame Mosjid, Late-Koson Ali | 2019-09-14 | MN1018 | 2 | 197 | 2 | 198 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7344 | 1415.9997 | 21.073
SYL-G.1.RR.567.1 | 24505059159265 | Gulapganj, Fulbari Dokshin, Near by Mirarpara Jame Mosjid, Late-Koson Ali | 2019-09-14 | MN1018 | 12.5 | 199 | 12.5 | 200 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7344 | 1415.9997 | 131.706
SYL-G.1.RR.568.1 | 24505589159306 | Gulapganj, Fulbari Dokshin, Rampar Kunachor Road, Mushahid Ali | 2019-09-14 | MN1018 | 10.3 | 201 | 10.3 | 202 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7344 | 1415.9997 | 108.5258
SYL-G.1.RR.568.2 | 24505589159306 | Gulapganj, Fulbari Dokshin, Rampar Kunachor Road, Mushahid Ali | 2022-11-03 | NQ1007 | 11 | 119 | 11 | 120 | 2022-11-03 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 0 | 1415.9997 | 18.7347
SYL-G.1.RR.569.1 | 24511309159306 | Gulapganj, Fulbari Dokshin, Fulbaria Azizia Alia Madrasa, Afsor Ali | 2019-09-14 | MN1018 | 2.6 | 203 | 2.6 | 204 | 2022-01-01 | [9 empty] | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0
SYL-G.1.RR.570.1 | 24511229159270 | Gulapganj, Fulbari Dokshin, Fulbaria Azizia Alia Madrasa, Surman Ali | 2019-09-14 | MN1018 | 12.1 | 205 | 12.1 | 206 | 2022-01-01 | 2022-10-31 | NQ1007 | 2.3 | 96 | 2.3 | 97 | 2022-10-31 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7272 | 1487.9997
SYL-G.1.RR.571.1 | 24510729159224 | Gulapganj, Fulbari Uttorpara, Adom Kha Road, Abdul Kutu | 2019-09-14 | MN1018 | 11 | 207 | 11 | 208 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7272 | 1487.9997 | 115.9013
SYL-G.1.RR.572.1 | 24510759159200 | Gulapganj, Fulbari Uttorpara, Adom Kha Road, Abdul Malik | 2019-09-14 | MN1018 | 10 | 209 | 10 | 210 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7272 | 1487.9997 | 105.3648
SYL-G.1.RR.573.1 | 24510759159200 | Gulapganj, Fulbari Uttorpara, Adom Kha Road, Abdullah Al-Mamun | 2019-09-14 | MN1018 | 12.1 | 211 | 12.1 | 212 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7272 | 1487.9997 | 127.4914
SYL-G.1.RR.574.1 | 24510759159200 | Gulapganj, Fulbari Uttorpara, Adom Kha Road, Soyeb Uddin | 2019-09-14 | MN1018 | 10.2 | 213 | 10.2 | 214 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7272 | 1487.9997 | 107.4721
SYL-G.1.RR.575.1 | 24511009159186 | Gulapganj, Fulbari Uttorpara, Adom Kha Road, Late-Abdul Nur | 2019-09-14 | MN1018 | 4.4 | 215 | 4.4 | 216 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7272 | 1487.9997 | 46.3605
SYL-G.1.RR.575.2 | 24511009159186 | Gulapganj, Fulbari Uttorpara, Adom Kha Road, Late-Abdul Nur | 2021-02-07 | LX1011 | 2.1 | 98 | 2 | 99 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7272 | 1487.9997 | 21.073
SYL-G.1.RR.576.1 | 24511009159295 | Gulapganj, Fulbari Uttorpara, Foyez Ahmed | 2019-09-14 | MN1018 | 24.1 | 217 | 24.1 | 218 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 24.1 | 24.1 | 1.446 | 1.446 | 0.0007168 | 100% | 0% | 1.446 | 1.446 | 0.0011869 | 28 | 0.028987 | 0.028987 |  | 0 | 0 | 7272 | 1487.9997 | 253.9292
SYL-G.1.RR.577.1 | 24511819159265 | Gulapganj, Fulbari Uttorpara, Anam Uddin | 2019-09-14 | MN1018 | 30.2 | 219 | 30.3 | 220 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 30.3 | 30.3 | 1.818 | 1.818 | 0.0007168 | 100% | 0% | 1.818 | 1.818 | 0.0011869 | 28 | 0.036445 | 0.036445 |  | 0 | 0 | 7272 | 1487.9997 | 319.2554
SYL-G.1.RR.578.1 | 24511739159269 | Gulapganj, Fulbari Uttorpara, Nosir Ali | 2019-09-14 | MN1018 | 9.3 | 221 | 9.3 | 222 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7272 | 1487.9997 | 97.9893
SYL-G.1.RR.579.1 | 24512209159310 | Gulapganj, Boitikor Bazar, Jema Chamist | 2019-09-14 | MN1018 | 4.7 | 223 | 4.6 | 224 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7272 | 1487.9997 | 48.4678
SYL-G.1.RR.580.1 | 24505669201323 | Gulapganj, Ranokeli, South Side of Ranokeli Mosjid, Hasnat Ahmed Chowdury | 2019-09-28 | MN1018 | 1.9 | 530 | 1.9 | 531 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7392 | 1367.9997 | 20.0193
SYL-G.1.RR.580.2 | 24505669201323 | Gulapganj, Ranokeli, South Side of Ranokeli Mosjid, Hasnat Ahmed Chowdury | 2021-02-04 | MN1018 | 21.3 | 71 | 21.3 | 72 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 7392 | 1367.9997 | 224.4271
SYL-G.1.RR.581.1 | 24510219201258 | Golapgonj, North Rankelly, Rehena Villa | 2019-09-29 | LU1001 | 4.3 | 491 | 4.3 | 492 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7392 | 1367.9997 | 45.3069
SYL-G.1.RR.601.1 | 24461799200479 | Sylhet, Golapganj, Vadessor, Dokhar Para, Shafique | 2019-09-08 | LU1001 | 10.7 | 91 | 10.7 | 92 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7248 | 1511.9997 | 112.7403
SYL-G.1.RR.602.1 | 24461799200479 | Sylhet, Golapganj, Vadessor, Dokhar Para, Solaiman | 2019-09-08 | LU1001 | 20 | 93 | 20 | 94 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 20 | 20 | 1.2 | 1.2 | 0.0007168 | 100% | 0% | 1.2 | 1.2 | 0.0011869 | 28 | 0.024056 | 0.024056 |  | 0 | 0 | 7248 | 1511.9997 | 210.7296
SYL-G.1.RR.603.1 | 24462919200517 | Sylhet, Golapganj, Vadessor, Korgram, Korir Bazar Road, Bodrul | 2019-09-08 | LU1001 | 11.5 | 95 | 11.2 | 96 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7248 | 1511.9997 | 118.0086
SYL-G.1.RR.604.1 | 24462919200517 | Sylhet, Golapganj, Vadessor, Korgram, Korir Bazar Road, Khosrul | 2019-09-08 | LU1001 | 11.8 | 97 | 11.8 | 98 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7248 | 1511.9997 | 124.3305
SYL-G.1.RR.605.1 | 24463789200549 | Sylhet, Golapganj, Vadessor, Korgram, Lalopara, Samsun Nesa | 2019-09-08 | LU1001 | 10.2 | 99 | 10.2 | 100 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7248 | 1511.9997 | 107.4721
SYL-G.1.RR.606.1 | 24464059200471 | Sylhet, Golapganj, Vadessor, Korgram, Lalopara, Licho Mia | 2019-09-08 | LU1001 | 6.2 | 103 | 6.2 | 104 | 2022-01-01 | 2022-10-30 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7248 | 1511.9997 | 65.3262
SYL-G.1.RR.607.1 | 24475299201022 | Sylhet, Golapganj, Koilastila, Mokitola, Porkasto Bazar, Oliur | 2019-09-09 | LU1001 | 12 | 107 | 12 | 108 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7224 | 1535.9997 | 126.4378
SYL-G.1.RR.608.1 | 24475319201001 | Sylhet, Golapganj, Koilastila, Mokitola, Porkasto Bazar, Koise | 2019-09-09 | LU1001 | 7.4 | 109 | 7.4 | 110 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7224 | 1535.9997 | 77.97
SYL-G.1.RR.609.1 | 24485289158196 | Golapganj, South Lakkhipasa, Medherchock, Alauddin | 2019-09-12 | LU1001 | 9.5 | 179 | 9.5 | 180 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7224 | 1535.9997 | 100.0966
SYL-G.1.RR.610.1 | 24485289158196 | Golapganj, South Lakkhipasa, Medherchock, Bosir Member | 2019-09-12 | LU1001 | 12 | 181 | 12 | 182 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7224 | 1535.9997 | 126.4378
SYL-G.1.RR.610.2 | 24485289158196 | Golapganj, South Lakkhipasa, Medherchock, Bosir Member | 2021-02-01 | MN1018 | 9.9 | 53 | 9.9 | 54 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7224 | 1535.9997 | 104.3112
SYL-G.1.RR.611.1 | 24485289158196 | Golapganj, South Lakkhipasa, Medherchock, Abdul Motin | 2019-09-12 | LU1001 | 7 | 183 | 7 | 184 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7224 | 1535.9997 | 73.7554
SYL-G.1.RR.612.1 | 24513919158292 | Golapganj, Fullbari, Hazipur, Sukna, Sana Mia | 2019-09-14 | LU1001 | 9 | 193 | 9 | 194 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7272 | 1487.9997 | 94.8283
SYL-G.1.RR.613.1 | 24513989158293 | Golapganj, Fullbari, Hazipur, Sukna, Sofian | 2019-09-14 | LU1001 | 6.7 | 195 | 7.1 | 196 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7272 | 1487.9997 | 74.809
SYL-G.1.RR.614.1 | 24514249158296 | Golapganj, Fullbari, Hazipur, Sukna, Maya Begum | 2019-09-14 | LU1001 | 11.1 | 197 | 11.1 | 198 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7272 | 1487.9997 | 116.9549
SYL-G.1.RR.615.1 | 24513399158270 | Golapganj, Fullbari, Hazipur, Sukna, Khalilur | 2019-09-14 | LU1001 | 6.4 | 199 | 6.4 | 200 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7272 | 1487.9997 | 67.4335
SYL-G.1.RR.615.2 | 24513399158270 | Golapganj, Fullbari, Hazipur, Sukna, Khalilur | 2022-04-05 | LU1001 | 15.5 | 125 | 15.4 | 126 | 2022-04-05 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 5016 | 1487.9997 | 120.4738
SYL-G.1.RR.616.1 | 24513319158270 | Golapganj, Fullbari, Hazipur, Sukna, Jomir Ahmad | 2019-09-14 | LU1001 | 10.4 | 201 | 10.4 | 202 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7272 | 1487.9997 | 109.5794
SYL-G.1.RR.617.1 | 24503409158283 | Golapganj, Baraya, Kismot, Maisvag Purbo Para, Alauddin | 2019-09-14 | LU1001 | 14.4 | 203 | 14.4 | 204 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7272 | 1487.9997 | 151.7253
SYL-G.1.RR.618.1 | 24503409158283 | Golapganj, Baraya, Kismot, Maisvag Purbo Para, Rofique Uddin | 2019-09-14 | LU1001 | 17.1 | 205 | 17.1 | 206 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 7272 | 1487.9997 | 180.1738
SYL-G.1.RR.619.1 | 24503239158279 | Golapganj, Baraya, Kismot, Maisvag Purbo Para, Masuk | 2019-09-14 | LU1001 | 10.6 | 207 | 10.6 | 208 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7272 | 1487.9997 | 111.6867
SYL-G.1.RR.620.1 | 24503439156145 | Golapganj, Hatimganj, South Maijvag, Saiful Islam | 2019-09-15 | LU1001 | 12 | 215 | 12 | 216 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7272 | 1487.9997 | 126.4378
SYL-G.1.RR.621.1 | 24503269156146 | Golapganj, Hatimganj, South Maijvag, Foyjun Begum | 2019-09-15 | LU1001 | 9.3 | 217 | 9.3 | 218 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7272 | 1487.9997 | 97.9893
SYL-G.1.RR.621.2 | 24503269156146 | Golapganj, Hatimganj, South Maijvag, Foyjun Begum | 2022-04-05 | LU1001 | 6.5 | 122 | 6.5 | 123 | 2022-04-05 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 5016 | 1487.9997 | 50.8493
SYL-G.1.RR.622.1 | 24503159156143 | Golapganj, Hatimganj, South Maijvag, Abul Kalam Chowdhory | 2019-09-15 | LU1001 | 10.7 | 219 | 10.7 | 220 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7272 | 1487.9997 | 112.7403
SYL-G.1.RR.622.2 | 24503159156143 | Golapganj, Hatimganj, South Maijvag, Abul Kalam Chowdhory | 2019-09-15 | LU1001 | 7.8 | 221 | 7.2 | 222 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7272 | 1487.9997 | 75.8627
SYL-G.1.RR.623.1 | 24503019156143 | Golapganj, Hatimganj, South Maijvag, Sobrag | 2019-09-15 | LU1001 | 9.4 | 223 | 8.8 | 224 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7272 | 1487.9997 | 92.721
SYL-G.1.RR.623.2 | 24503019156143 | Golapganj, Hatimganj, South Maijvag, Sobrag | 2022-04-05 | LU1001 | 10.3 | 120 | 10.3 | 121 | 2022-04-05 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 5016 | 1487.9997 | 80.5767
SYL-G.1.RR.624.1 | 24503019156143 | Golapganj, Hatimganj, South Maijvag, Sehab Uddin | 2019-09-15 | LU1001 | 17.5 | 225 | 17.2 | 226 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 7272 | 1487.9997 | 181.2275
SYL-G.1.RR.625.1 | 24503019156143 | Golapganj, Hatimganj, South Maijvag, Afsar Ahmed | 2019-09-15 | LU1001 | 10.3 | 227 | 10.3 | 228 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7272 | 1487.9997 | 108.5258
SYL-G.1.RR.626.1 | 24502909156141 | Golapganj, Hatimganj, South Maijvag, Helal Uddin Chowdhory | 2019-09-15 | LU1001 | 29.7 | 229 | 29.7 | 230 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 29.7 | 29.7 | 1.782 | 1.782 | 0.0007168 | 100% | 0% | 1.782 | 1.782 | 0.0011869 | 28 | 0.035723 | 0.035723 |  | 0 | 0 | 7272 | 1487.9997 | 312.9335
SYL-G.1.RR.627.1 | 24502669156081 | Golapganj, Hatimganj, South Maijvag, Moklas Ali | 2019-09-15 | LU1001 | 13.5 | 231 | 13.6 | 232 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7272 | 1487.9997 | 143.2961
SYL-G.1.RR.651.1 | 24483679158131 | Golapganj, Lakshmipasa, Mawlana Bari, Abdul Jalil | 2019-09-11 | LU1001 | 9.2 | 139 | 9.2 | 140 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7224 | 1535.9997 | 96.9356
SYL-G.1.RR.652.1 | 24483789158133 | Golapganj, Lakshmipasa, Doctor Bari, Mostafa Kamal | 2019-09-11 | LU1001 | 11.8 | 141 | 11.8 | 142 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7224 | 1535.9997 | 124.3305
SYL-G.1.RR.653.1 | 24483789158133 | Golapganj, Lakshmipasa, Doctor Bari, Abdul Moinuddin | 2019-09-11 | LU1001 | 8.9 | 143 | 8.9 | 144 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7224 | 1535.9997 | 93.7747
SYL-G.1.RR.654.1 | 24483789158133 | Golapganj, Lakshmipasa, Doctor Bari, Monsurul Goni | 2019-09-11 | LU1001 | 12.4 | 145 | 12 | 146 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7224 | 1535.9997 | 126.4378
SYL-G.1.RR.655.1 | 24483869158114 | Golapganj, Lakshmipasa, D.M Muradia Road, Nazimuddin | 2019-09-11 | LU1001 | 7.5 | 147 | 7.5 | 148 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7224 | 1535.9997 | 79.0236
SYL-G.1.RR.656.1 | 24483949158112 | Golapganj, Lakshmipasa, D.M Muradia Road, Helal Uddin | 2019-09-11 | LU1001 | 9.9 | 149 | 9.9 | 150 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7224 | 1535.9997 | 104.3112
SYL-G.1.RR.657.1 | 24484059158106 | Golapganj, Lakshmipasa, Sawdagor Bari, Shohed Ahammed | 2019-09-11 | LU1001 | 10.5 | 151 | 10.5 | 152 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7224 | 1535.9997 | 110.6331
SYL-G.1.RR.658.1 | 24484059158106 | Golapganj, Lakshmipasa, Sawdagor Bari, Golam Mostafa | 2019-09-11 | LU1001 | 7 | 153 | 7 | 154 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7224 | 1535.9997 | 73.7554
SYL-G.1.RR.659.1 | 24484059158106 | Golapganj, Lakshmipasa, Sawdagor Bari, Faizul Islam | 2019-09-11 | LU1001 | 11.3 | 155 | 11.3 | 156 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7224 | 1535.9997 | 119.0622
SYL-G.1.RR.660.1 | 24483959158178 | Golapganj, Lakshmipasa, D. M Muradia Road, Wadud | 2019-09-12 | LU1001 | 10.5 | 157 | 10.5 | 158 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7224 | 1535.9997 | 110.6331
SYL-G.1.RR.661.1 | 24483959158178 | Golapganj, Lakshmipasa, D. M Muradia Road, Fokrul Islam | 2019-09-12 | LU1001 | 12.7 | 159 | 12.4 | 160 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7224 | 1535.9997 | 130.6524
SYL-G.1.RR.662.1 | 24483879158180 | Golapganj, Lakshmipasa, D. M Muradia Road, Mujaid Ahammed | 2019-09-12 | LU1001 | 8.9 | 161 | 8.9 | 162 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7224 | 1535.9997 | 93.7747
SYL-G.1.RR.663.1 | 24483879158180 | Golapganj, Lakshmipasa, D. M Muradia Road, Serajul Ahammed | 2019-09-12 | LU1001 | 9.5 | 163 | 9.5 | 164 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7224 | 1535.9997 | 100.0966
SYL-G.1.RR.664.1 | 24483879158180 | Golapganj, Lakshmipasa, D. M Muradia Road, Mosaddak Ahammed | 2019-09-12 | LU1001 | 8.7 | 165 | 8.7 | 166 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7224 | 1535.9997 | 91.6674
SYL-G.1.RR.665.1 | 24483719158183 | Golapganj, Lakshmipasa, Sultan Muhammad Road, Alauddin | 2019-09-12 | LU1001 | 21.1 | 167 | 21.1 | 168 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 21.1 | 21.1 | 1.266 | 1.266 | 0.0007168 | 100% | 0% | 1.266 | 1.266 | 0.0011869 | 28 | 0.025379 | 0.025379 |  | 0 | 0 | 7224 | 1535.9997 | 222.3198
SYL-G.1.RR.666.1 | 24483719158183 | Golapganj, Lakshmipasa, Sultan Muhammad Road, Emam | 2019-09-12 | LU1001 | 12.6 | 169 | 12.6 | 170 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7224 | 1535.9997 | 132.7597
SYL-G.1.RR.667.1 | 24483689158181 | Golapganj, Lakshmipasa, Sultan Muhammad Road, Aklachur Rahaman | 2019-09-12 | LU1001 | 10.5 | 171 | 10.5 | 172 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7224 | 1535.9997 | 110.6331
SYL-G.1.RR.668.1 | 24483689158181 | Golapganj, Lakshmipasa, Sultan Muhammad Road, Aklachur Rahaman | 2019-09-12 | LU1001 | 6.6 | 173 | 6.6 | 174 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7224 | 1535.9997 | 69.5408
SYL-G.1.RR.669.1 | 24483119158201 | Golapganj, Lakshmipasa, Sultan Muhammad Road, Bodrul Alam | 2019-09-12 | LU1001 | 11.6 | 175 | 11.6 | 176 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7224 | 1535.9997 | 122.2232
SYL-G.1.RR.669.2 | 24483119158201 | Golapganj, Lakshmipasa, Sultan Muhammad Road, Bodrul Alam | 2021-02-01 | MN1018 | 10.7 | 57 | 10.7 | 58 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7224 | 1535.9997 | 112.7403
SYL-G.1.RR.670.1 | 24482949158264 | Golapganj, Lakshmipasa, Shahadat | 2019-09-12 | LU1001 | 10.4 | 177 | 10.4 | 178 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7224 | 1535.9997 | 109.5794
SYL-G.1.RR.671.1 | 24503019159076 | Golapganj, Dakshinbhag (Rampa), Baluchor Road, Abdul Momin | 2019-09-14 | LU1001 | 13.1 | 185 | 13.2 | 186 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7344 | 1415.9997 | 139.0816
SYL-G.1.RR.672.1 | 24502819159075 | Golapganj, Dakshinbhag (Rampa), Baluchor Road, Tomider Ali | 2019-09-14 | LU1001 | 5.6 | 187 | 5.6 | 188 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7344 | 1415.9997 | 59.0043
SYL-G.1.RR.673.1 | 24502769159071 | Golapganj, Dakshinbhag (Rampa), Baluchor Road, Abdul Mukit | 2019-09-14 | LU1001 | 3.4 | 189 | 3.4 | 190 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7344 | 1415.9997 | 35.824
SYL-G.1.RR.674.1 | 24502769159071 | Golapganj, Dakshinbhag (Rampa), Baluchor Road, Masududdin | 2019-09-14 | LU1001 | 8.9 | 191 | 8.8 | 192 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7344 | 1415.9997 | 92.721
SYL-G.1.RR.674.2 | 24502769159071 | Golapganj, Dakshinbhag (Rampa), Baluchor Road, Masududdin | 2022-04-12 | LU1001 | 14.4 | 143 | 14.5 | 144 | 2022-04-12 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 4920 | 1415.9997 | 110.5032
SYL-G.1.RR.675.1 | 24504969157320 | Golapganj, Hathimganj, Izara Para, Kayasto Gram, Abdul Hannan | 2019-09-15 | LU1001 | 8.7 | 209 | 8.7 | 210 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7272 | 1487.9997 | 91.6674
SYL-G.1.RR.676.1 | 24504339156002 | Syhet, Hilalpur, Rofipur Gram, Abdul Alim | 2019-09-15 | LU1001 | 32.1 | 213 | 31.8 | 214 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 31.8 | 31.8 | 1.908 | 1.908 | 0.0007168 | 100% | 0% | 1.908 | 1.908 | 0.0011869 | 28 | 0.038249 | 0.038249 |  | 0 | 0 | 7272 | 1487.9997 | 335.0601
SYL-G.1.RR.676.2 | 24504339156002 | Syhet, Hilalpur, Rofipur Gram, Abdul Alim | 2021-02-07 | MN1018 | 8 | 80 | 8 | 81 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7272 | 1487.9997 | 84.2919
SYL-G.1.RR.701.1 | 24511929202140 | Golapganj, Ghugarkul, Khadem Bari, Nur Mia | 2019-09-09 | NQ1000 | 9.9 | 113 | 9.9 | 114 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7392 | 1367.9997 | 104.3112
SYL-G.1.RR.701.2 | 24511929202140 | Golapganj, Ghugarkul, Khadem Bari, Nur Mia | 2019-09-09 | NQ1000 | 23.4 | 115 | 23 | 116 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 23 | 23 | 1.38 | 1.38 | 0.0007168 | 100% | 0% | 1.38 | 1.38 | 0.0011869 | 28 | 0.027664 | 0.027664 |  | 0 | 0 | 7392 | 1367.9997 | 242.3391
SYL-G.1.RR.702.1 | 24511949202162 | Golapganj, Ghugarkul, Khadem Bari, Hefju Miah | 2019-09-09 | NQ1000 | 4.3 | 117 | 4.3 | 118 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7392 | 1367.9997 | 45.3069
SYL-G.1.RR.703.1 | 24511419202189 | Golapganj, Ghugarkul, Khadem Bari, Helal | 2019-09-09 | NQ1000 | 6.6 | 119 | 6.6 | 120 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7392 | 1367.9997 | 69.5408
SYL-G.1.RR.704.1 | 24511419202189 | Golapganj, Ghugarkul, Khadem Bari, Harun | 2019-09-09 | NQ1000 | 3 | 121 | 3 | 122 | 2022-01-01 | 2022-11-05 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7392 | 1367.9997 | 31.6094
SYL-G.1.RR.705.1 | 24465189158569 | Golapganj, Niz Fulshaind, Pirerchok, Alta Mia | 2019-09-11 | NQ1000 | 6 | 125 | 5.9 | 126 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7224 | 1535.9997 | 62.1652
SYL-G.1.RR.705.2 | 24465189158569 | Golapganj, Niz Fulshaind, Pirerchok, Alta Mia | 2019-09-11 | NQ1000 | 9.8 | 127 | 9.8 | 128 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7224 | 1535.9997 | 103.2575
SYL-G.1.RR.706.1 | 24465189158569 | Golapganj, Niz Fulshaind, Pirerchok, Ana Mia | 2019-09-11 | NQ1000 | 13.5 | 129 | 13.5 | 130 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7224 | 1535.9997 | 142.2425
SYL-G.1.RR.707.1 | 24464969159014 | Golapganj, Niz Fulshaind, Hetepur, Ahmad Ali | 2019-09-11 | NQ1000 | 5.4 | 131 | 5.4 | 132 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7224 | 1535.9997 | 56.897
SYL-G.1.RR.708.1 | 24464969159014 | Golapganj, Niz Fulshaind, Hetepur, Khaleq | 2019-09-11 | NQ1000 | 9.4 | 133 | 9.4 | 134 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7224 | 1535.9997 | 99.0429
SYL-G.1.RR.709.1 | 24464879159006 | Golapganj, Niz Fulshaind, Hetepur, Muskander Ali | 2019-09-11 | NQ1000 | 11.1 | 135 | 11.1 | 136 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7224 | 1535.9997 | 116.9549
SYL-G.1.RR.710.1 | 24464879159006 | Golapganj, Niz Fulshaind, Hetepur, Hossain Ahmad | 2019-09-11 | NQ1000 | 12 | 137 | 11.6 | 138 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7224 | 1535.9997 | 122.2232
SYL-G.1.RR.711.1 | 24465289159503 | Golapganj, Noyai, South Bhag, Akados Ali | 2019-09-12 | NQ1000 | 18.6 | 159 | 18.6 | 160 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 7224 | 1535.9997 | 195.9786
SYL-G.1.RR.712.1 | 24464839159499 | Golapganj, Noyai, South Bhag, Giyasuddin | 2019-09-12 | NQ1000 | 13.2 | 161 | 13.2 | 162 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7224 | 1535.9997 | 139.0816
SYL-G.1.RR.713.1 | 24464629159500 | Golapganj, Noyai, South Bhag, Bokul Chakrobarti | 2019-09-12 | NQ1000 | 13.6 | 164 | 13.6 | 165 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7224 | 1535.9997 | 143.2961
SYL-G.1.RR.714.1 | 24464629159500 | Golapganj, Noyai, South Bhag, Chinmay Chakrobarti | 2019-09-12 | NQ1000 | 3.4 | 166 | 3.4 | 167 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7224 | 1535.9997 | 35.824
SYL-G.1.RR.715.1 | 24514139158519 | Golapganj, Hazipur, Ghonosham, Akbar Ali | 2019-09-14 | NQ1000 | 11.9 | 180 | 11.1 | 181 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7272 | 1487.9997 | 116.9549
SYL-G.1.RR.715.2 | 24514139158519 | Golapganj, Hazipur, Ghonosham, Akbar Ali | 2022-10-31 | NQ1007 | 12 | 98 | 12 | 99 | 2022-10-31 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 0 | 1487.9997 | 21.4771
SYL-G.1.RR.716.1 | 24510949158454 | Golapganj, Korompur, Kissmot Maiz Bhag, Dudu Mia | 2019-09-14 | NQ1000 | 9.4 | 182 | 9.4 | 183 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7272 | 1487.9997 | 99.0429
SYL-G.1.RR.717.1 | 24510949158454 | Golapganj, Korompur, Kissmot Maiz Bhag, Somir | 2019-09-14 | NQ1000 | 6.2 | 184 | 6.2 | 185 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 5880 | 0 | 1392 | 1487.9997 | 21.4771
SYL-G.1.RR.718.1 | 24510949158454 | Golapganj, Korompur, Kissmot Maiz Bhag, Afsar | 2019-09-14 | NQ1000 | 7.8 | 186 | 7.8 | 187 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7272 | 1487.9997 | 82.1846
SYL-G.1.RR.719.1 | 24510949158454 | Golapganj, Korompur, Kissmot Maiz Bhag, Matab | 2019-09-14 | NQ1000 | 2.5 | 188 | 2.5 | 189 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7272 | 1487.9997 | 26.3412
SYL-G.1.RR.720.1 | 24511069158463 | Golapganj, Korompur, Kissmot Maiz Bhag, Faruq | 2019-09-14 | NQ1000 | 1.6 | 190 | 1.6 | 191 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7272 | 1487.9997 | 16.8584
SYL-G.1.RR.721.1 | 24511069158463 | Golapganj, Korompur, Kissmot Maiz Bhag, Shamim | 2019-09-14 | NQ1000 | 3.9 | 192 | 3.9 | 193 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7272 | 1487.9997 | 41.0923
SYL-G.1.RR.721.2 | 24511069158463 | Golapganj, Korompur, Kissmot Maiz Bhag, Shamim | 2019-09-14 | NQ1000 | 11.3 | 194 | 10.9 | 195 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7272 | 1487.9997 | 114.8476
SYL-G.1.RR.722.1 | 24510569158371 | Golapganj, Korompur, Kissmot Maiz Bhag, Shiraj Ali | 2019-09-14 | NQ1000 | 5.2 | 196 | 5.2 | 197 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7272 | 1487.9997 | 54.7897
SYL-G.1.RR.723.1 | 24510359158359 | Golapganj, Korompur, Kissmot Maiz Bhag, Ismail | 2019-09-14 | NQ1000 | 11.9 | 198 | 11.9 | 199 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7272 | 1487.9997 | 125.3841
SYL-G.1.RR.724.1 | 24504899157403 | Golapganj, Kayestogram, Bagmar, Coton Mia | 2019-09-14 | NQ1000 | 6.3 | 200 | 6.3 | 201 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7272 | 1487.9997 | 66.3798
SYL-G.1.RR.724.2 | 24504899157403 | Golapganj, Kayestogram, Bagmar, Coton Mia | 2022-10-31 | NQ1007 | 16.7 | 90 | 16.7 | 91 | 2022-10-31 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 0 | 1487.9997 | 29.889
SYL-G.1.RR.725.1 | 24504899157403 | Golapganj, Kayestogram, Bagmar, Kola Mia | 2019-09-14 | NQ1000 | 9.3 | 202 | 9.3 | 203 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7272 | 1487.9997 | 97.9893
SYL-G.1.RR.751.1 | 24465979159085 | Galapganj, Dhaka Dokkhin, Fullshaind, Hospital Road, Azig Mia | 2019-09-12 | NQ1000 | 13.1 | 141 | 13.1 | 142 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7224 | 1535.9997 | 138.0279
SYL-G.1.RR.752.1 | 24465659159137 | Galapganj, Dhaka Dokkhin, Fullshaind, Dolai Bari, Nur Mosque | 2019-09-12 | NQ1000 | 14.3 | 143 | 14.4 | 144 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7224 | 1535.9997 | 151.7253
SYL-G.1.RR.753.1 | 24465519159226 | Galapganj, Dhaka Dokkhin, Fullshaind, Near Shahi Mosque, Aslam Ali | 2019-09-12 | NQ1000 | 11.3 | 145 | 11.3 | 146 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7224 | 1535.9997 | 119.0622
SYL-G.1.RR.754.1 | 24465519159226 | Galapganj, Dhaka Dokkhin, Fullshaind, Near Shahi Mosque, Haris Ali | 2019-09-12 | NQ1000 | 12.7 | 147 | 12.7 | 148 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7224 | 1535.9997 | 133.8133
SYL-G.1.RR.755.1 | 24465499159329 | Galapganj, Dhaka Dokkhin, Fullshaind Purbo, Manik Uddin | 2019-09-12 | NQ1000 | 10.8 | 153 | 10.8 | 154 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7224 | 1535.9997 | 113.794
SYL-G.1.RR.756.1 | 24465879159381 | Galapganj, Dhaka Dokkhin, Fullshaind Purbo, Elis Uddin | 2019-09-12 | NQ1000 | 13.4 | 155 | 13.2 | 156 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7224 | 1535.9997 | 139.0816
SYL-G.1.RR.757.1 | 24465879159381 | Galapganj, Dhaka Dokkhin, Fullshaind Purbo, Abdul Goni | 2019-09-12 | NQ1000 | 21.2 | 157 | 21.2 | 158 | 2022-01-01 | 2022-10-29 | GS |  |  | 0 |  |  |  |  | 21.2 | 21.2 | 1.272 | 1.272 | 0.0007168 | 100% | 0% | 1.272 | 1.272 | 0.0011869 | 28 | 0.025499 | 0.025499 |  | 0 | 0 | 7224 | 1535.9997 | 223.3734
SYL-G.1.RR.758.1 | 24502079159067 | Golapganj, Dokkhinbag Rampa, Monojjir Ali | 2019-09-14 | NQ1000 | 11.7 | 168 | 11.7 | 169 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7344 | 1415.9997 | 123.2768
SYL-G.1.RR.759.1 | 24502139158599 | Golapganj, Dokkhinbag Rampa, Shabol Ahmed | 2019-09-14 | NQ1000 | 3.7 | 170 | 3.7 | 171 | 2022-01-01 | 2022-11-03 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7344 | 1415.9997 | 38.985
SYL-G.1.RR.760.1 | 24502369159058 | Golapganj, Dokkhinbag Rampa, Abul Kasem | 2019-09-14 | NQ1000 | 10.2 | 172 | 10.2 | 173 | 2022-01-01 | 2022-11-03 | NQ1007 |  |  | 0 | 123 | [7 empty] | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7344 | 1415.9997
SYL-G.1.RR.761.1 | 24510759159317 | Golapganj, Fullbari, Tikor Para, Hossain Mia | 2019-09-14 | NQ1000 | 11.5 | 174 | 11.5 | 175 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7272 | 1487.9997 | 121.1695
SYL-G.1.RR.761.2 | 24510759159317 | Golapganj, Fullbari, Tikor Para, Hossain Mia | 2019-09-14 | NQ1000 | 10.2 | 176 | 10 | 177 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7272 | 1487.9997 | 105.3648
SYL-G.1.RR.762.1 | 24510689159336 | Golapganj, Fullbari, Tikor Para, Kuti Mia | 2019-09-14 | NQ1000 | 5.8 | 178 | 5.8 | 179 | 2022-01-01 | 2022-10-31 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7272 | 1487.9997 | 61.1116
SYL-N.1.CR.2.1 | 24535799152204 | Sylhet Sodor, Mirboxtola, Mirboxtola Road, Ajadi - 95 | 2019-08-24 | LX1011 | 5.3 | 156 | 5.3 | 157 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 8256 | 503.9997 | 55.8434
SYL-N.1.CR.3.1 | 24533309152188 | Sylhet Sodoe, Barutkhana,Lal Bazar Road, Uttoron R/A, Hazi Siraj Mia | 2019-08-25 | LX1011 | 21.1 | 228 | 21.1 | 229 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 21.1 | 21.1 | 1.266 | 1.266 | 0.0007168 | 100% | 0% | 1.266 | 1.266 | 0.0011869 | 28 | 0.025379 | 0.025379 |  | 0 | 0 | 8136 | 623.9997 | 222.3198
SYL-N.1.CR.4.1 | 24532709152380 | Shobhanigat, Kastaghar Road, Kastaghar R/A, MA Enterprise | 2019-08-26 | NQ1003 | 11.3 | 406 | 11.1 | 407 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8184 | 575.9997 | 116.9549
SYL-N.1.RR.1.1 | 24542329153431 | Baluchor, Focus, Block-c, H # 02 | 2019-07-28 | MP1006 | 9.1 | 289 | 9.1 | 290 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8160 | 599.9997 | 95.882
SYL-N.1.RR.2.1 | 24542329153431 | Baluchor, Focus, Block-c, H # 4/1 | 2019-07-28 | MP1006 | 17.1 | 291 | 17.1 | 292 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 17.1 | 17.1 | 1.026 | 1.026 | 0.0007168 | 100% | 0% | 1.026 | 1.026 | 0.0011869 | 28 | 0.020568 | 0.020568 |  | 0 | 0 | 8160 | 599.9997 | 180.1738
SYL-N.1.RR.3.1 | 24542289153413 | Baluchor, Focus, Block-c, H # 9 | 2019-07-28 | MP1006 | 11.2 | 293 | 10.8 | 294 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8160 | 599.9997 | 113.794
SYL-N.1.RR.4.1 | 24542289153413 | Baluchor, Focus, Block-c, H # 8 | 2019-07-28 | MP1006 | 10.6 | 295 | 10.6 | 296 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8160 | 599.9997 | 111.6867
SYL-N.1.RR.5.1 | 24542329153407 | Baluchor, Focus, Block-c, H # 10 | 2019-07-28 | MP1006 | 5.7 | 297 | 5.7 | 298 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 8160 | 599.9997 | 60.0579
SYL-N.1.RR.6.1 | 24542419153446 | Baluchor, Focus, Block-c, H # 27/c | 2019-07-28 | MP1006 | 11.3 | 299 | 10.9 | 300 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8160 | 599.9997 | 114.8476
SYL-N.1.RR.7.1 | 24542459153412 | Baluchor, Focus, Block-C, Md. Khaled Ahmod | 2019-07-29 | MP1006 | 12.5 | 301 | 12.5 | 302 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 8160 | 599.9997 | 131.706
SYL-N.1.RR.8.1 | 24542959153459 | North Baluchor, Al Islah R/A, H # 20/3, Dream Valley | 2019-07-29 | MP1006 | 13.5 | 303 | 13.5 | 304 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 8160 | 599.9997 | 142.2425
SYL-N.1.RR.9.1 | 24542959153459 | North Baluchor, Al Islah R/A, H # 20/3, Dream Valley | 2019-07-29 | MP1006 | 15.8 | 305 | 15.8 | 306 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 8160 | 599.9997 | 166.4764
SYL-N.1.RR.10.1 | 24543539153394 | North Baluchor, Al Islah R/A, Block-B, Rd # 2, H # 30, Anhar Mia | 2019-07-29 | MP1006 | 13 | 307 | 13 | 308 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8160 | 599.9997 | 136.9743
SYL-N.1.RR.11.1 | 24543509153394 | North Baluchor, Al Islah R/A, Block-B, Rd # 2, Beside, H # 30, | 2019-07-29 | MP1006 | 20.3 | 309 | 20.3 | 310 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 20.3 | 20.3 | 1.218 | 1.218 | 0.0007168 | 100% | 0% | 1.218 | 1.218 | 0.0011869 | 28 | 0.024417 | 0.024417 |  | 0 | 0 | 8160 | 599.9997 | 213.8906
SYL-N.1.RR.12.1 | 24543399153397 | North Baluchor, Al Islah R/A, Block-B, Rd # 2, Hiron Mahmud Dipu | 2019-07-29 | MP1006 | 8.4 | 311 | 8.4 | 312 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8160 | 599.9997 | 88.5064
SYL-N.1.RR.13.1 | 24543039153418 | North Baluchor, Al Islah R/A, Nearby Primary School, Opposite Of M. S. Bari | 2019-07-29 | MP1006 | 1.9 | 313 | 1.9 | 314 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8160 | 599.9997 | 20.0193
SYL-N.1.RR.14.1 | 24544089153430 | North Baluchor, Al Islah R/A, Block-B, Rd # 19, H # 228/A | 2019-07-29 | MP1006 | 19.1 | 315 | 19.1 | 316 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 19.1 | 19.1 | 1.146 | 1.146 | 0.0007168 | 100% | 0% | 1.146 | 1.146 | 0.0011869 | 28 | 0.022973 | 0.022973 |  | 0 | 0 | 8160 | 599.9997 | 201.2468
SYL-N.1.RR.15.1 | 24544149153432 | North Baluchor, Al Islah R/A, Block-B, Rd # 19, H # 226 | 2019-07-29 | MP1006 | 11.6 | 317 | 11.6 | 318 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8160 | 599.9997 | 122.2232
SYL-N.1.RR.16.1 | 24543789153430 | North Baluchor, Al Islah R/A, Block-B, Rd # 19, H # 212, Boro Bari | 2019-07-29 | MP1006 | 9.6 | 319 | 9.2 | 320 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8160 | 599.9997 | 96.9356
SYL-N.1.RR.17.1 | 24542619153026 | East Shahi Eidgah, Anamika R/A, Block-B, Rd # 7, H # 36 | 2019-07-30 | MP1006 | 7.9 | 344 | 7.9 | 345 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 8184 | 575.9997 | 83.2382
SYL-N.1.RR.18.1 | 24542619153022 | East Shahi Eidgah, Anamika R/A, Block-B, Rd # 7, H # 30 | 2019-07-30 | MP1006 | 13.7 | 347 | 13.7 | 348 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 8184 | 575.9997 | 144.3498
SYL-N.1.RR.18.2 | 24542619153022 | East Shahi Eidgah, Anamika R/A, Block-B, Rd # 7, H # 30 | 2021-02-14 | MN1032 | 13.1 | 159 | 13.1 | 160 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 8184 | 575.9997 | 138.0279
SYL-N.1.RR.19.1 | 24542719153021 | East Shahi Eidgah, Anamika R/A, Block-B, Rd # 7, H # 31 | 2019-07-30 | MP1006 | 11 | 349 | 10.7 | 350 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8184 | 575.9997 | 112.7403
SYL-N.1.RR.20.1 | 24543149152581 | Shahi Eidgah, Anamika R/A, Sayed Pur House, B-15/12 | 2019-07-30 | MP1006 | 3.2 | 351 | 3.2 | 352 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 8184 | 575.9997 | 33.7167
SYL-N.1.RR.21.1 | 24543149152581 | Shahi Eidgah, Anamika R/A, H # 15/13 B | 2019-07-30 | MP1006 | 9.2 | 353 | 9.4 | 354 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8184 | 575.9997 | 99.0429
SYL-N.1.RR.22.1 | 24542919152459 | Shahi Eidgah, Husnabad R/A, H # 06 | 2019-07-30 | MP1006 | 8.3 | 355 | 8.3 | 356 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 8184 | 575.9997 | 87.4528
SYL-N.1.RR.23.1 | 24542799152483 | Shahi Eidgah, Husnabad R/A, H # 11 | 2019-07-30 | MP1006 | 16.3 | 357 | 16.3 | 358 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 8184 | 575.9997 | 171.7446
SYL-N.1.RR.24.1 | 24542799152483 | Shahi Eidgah, Husnabad R/A, Md.Emran | 2019-07-30 | MP1006 | 18.5 | 359 | 18.2 | 360 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 18.2 | 18.2 | 1.092 | 1.092 | 0.0007168 | 100% | 0% | 1.092 | 1.092 | 0.0011869 | 28 | 0.021891 | 0.021891 |  | 0 | 0 | 8184 | 575.9997 | 191.764
SYL-N.1.RR.25.1 | 24542799152483 | Shahi Eidgah, Husnabad R/A, Md.Shohel | 2019-07-30 | MP1006 | 12 | 361 | 12 | 362 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8184 | 575.9997 | 126.4378
SYL-N.1.RR.26.1 | 24544649152231 | Khasdabir, Borobazar Road, Bandon # B-4 | 2019-07-31 | MP1006 | 10.6 | 375 | 10.6 | 376 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8184 | 575.9997 | 111.6867
SYL-N.1.RR.26.2 | 24544649152231 | Khasdabir, Borobazar Road, Bandon # B-4 | 2022-12-08 | NQ1007 | 3.8 | 278 | 3.8 | 279 | 2022-12-08 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 0 | 575.9997 | 2.6327
SYL-N.1.RR.27.1 | 24544649152231 | Khasdabir, Borobazar Road, H # 9/4 | 2019-07-31 | MP1006 | 4.5 | 377 | 4.5 | 378 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 8184 | 575.9997 | 47.4142
SYL-N.1.RR.28.1 | 24544599152274 | Khasdabir, Israil Mia Road, H # B-30 | 2019-07-31 | MP1006 | 10.5 | 379 | 10.3 | 380 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8184 | 575.9997 | 108.5258
SYL-N.1.RR.29.1 | 24545039152339 | Khasdabir, Israil Mia Road, Minu Khan | 2019-07-31 | MP1006 | 10.3 | 381 | 9.9 | 382 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8184 | 575.9997 | 104.3112
SYL-N.1.RR.30.1 | 24544889152334 | Khasdabir, Israil Mia Road, Kunu Mia/ Salim Ahmed | 2019-07-31 | MP1006 | 11.9 | 383 | 11.5 | 384 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8184 | 575.9997 | 121.1695
SYL-N.1.RR.31.1 | 24544319152252 | Khasdabir, Modina Road, Block - C, Shiblu Ahmed | 2019-07-31 | MP1006 | 8.8 | 385 | 8.8 | 386 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8184 | 575.9997 | 92.721
SYL-N.1.RR.31.2 | 24544319152252 | Khasdabir, Modina Road, Block - C, Shiblu Ahmed | 2021-02-16 | NQ1003 | 4.9 | 262 | 4.9 | 263 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 8184 | 575.9997 | 51.6288
SYL-N.1.RR.32.1 | 24550459152290 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 128/3 | 2019-08-01 | MP1006 | 45.4 | 397 | 45.4 | 398 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 45.4 | 45.4 | 2.724 | 2.724 | 0.0007168 | 100% | 0% | 2.724 | 2.724 | 0.0011869 | 28 | 0.054607 | 0.054607 |  | 0 | 0 | 8184 | 575.9997 | 478.3562
SYL-N.1.RR.33.1 | 24550459152290 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 128/3 | 2019-08-01 | MP1006 | 16.9 | 399 | 16.9 | 400 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 8184 | 575.9997 | 178.0665
SYL-N.1.RR.34.1 | 24550259152304 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 160/3 | 2019-08-01 | MP1006 | 9.1 | 401 | 9.1 | 402 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8184 | 575.9997 | 95.882
SYL-N.1.RR.35.1 | 24550269152324 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 139/3 | 2019-08-01 | MP1006 | 14.5 | 403 | 14 | 404 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 8184 | 575.9997 | 147.5107
SYL-N.1.RR.36.1 | 24550269152343 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 147/3 | 2019-08-01 | MP1006 | 11.3 | 405 | 11.3 | 406 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8184 | 575.9997 | 119.0622
SYL-N.1.RR.37.1 | 24550319152344 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 148/3 | 2019-08-01 | MP1006 | 10.2 | 407 | 10.2 | 408 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8184 | 575.9997 | 107.4721
SYL-N.1.RR.38.1 | 24550449152312 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 130/3 | 2019-08-01 | MP1006 | 9.8 | 411 | 9.7 | 412 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8184 | 575.9997 | 102.2039
SYL-N.1.RR.39.1 | 24550419152315 | Choukidekhi, Rongdhonu R/A, Rd # 3, H # 142/3 | 2019-08-01 | MP1006 | 17.3 | 413 | 16.7 | 414 | 2022-01-01 | 2022-12-08 | NQ1007 | 1.5 | 284 | 1.5 | 285 | 2022-12-08 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8184 | 575.9997
SYL-N.1.RR.40.1 | 24543849152139 | Mozumdarbari, Mojumdari, H # 147/2 | 2019-08-03 | MP1006 | 15.4 | 427 | 15.4 | 428 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 8136 | 623.9997 | 162.2618
SYL-N.1.RR.41.1 | 24544069152132 | Mozumdarbari, Mojumdari, Moshean | 2019-08-03 | MP1006 | 11 | 429 | 11 | 430 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8136 | 623.9997 | 115.9013
SYL-N.1.RR.42.1 | 24543819152116 | Mozumdarbari, Mojumdari, H # 135 | 2019-08-03 | MP1006 | 9.6 | 431 | 9.6 | 432 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8136 | 623.9997 | 101.1502
SYL-N.1.RR.43.1 | 24544049152110 | Mozumdarbari, Mojumdari, Anower Box | 2019-08-03 | MP1006 | 15.3 | 433 | 15.3 | 434 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 8136 | 623.9997 | 161.2082
SYL-N.1.RR.44.1 | 24544829152051 | Provati, East Pirmoholla, Razia Begum | 2019-08-03 | MP1006 | 21.4 | 435 | 21.6 | 436 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 8160 | 599.9997 | 227.588
SYL-N.1.RR.45.1 | 24544829152051 | Provati, East Pirmoholla, Rushana Begum | 2019-08-03 | MP1006 | 14.1 | 437 | 13.8 | 438 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 8160 | 599.9997 | 145.4034
SYL-N.1.RR.46.1 | 24544829152051 | Provati, East Pirmoholla, Husna Begum | 2019-08-03 | MP1006 | 11.1 | 439 | 10.8 | 440 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8160 | 599.9997 | 113.794
SYL-N.1.RR.47.1 | 24544809152040 | Housing Estate R/A, H # 148 Dr.Monib | 2019-08-04 | MP1006 | 9.1 | 461 | 9.1 | 462 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8160 | 599.9997 | 95.882
SYL-N.1.RR.48.1 | 24544629152034 | Housing Estate R/A, Rd # 2, H # 63 A | 2019-08-04 | MP1006 | 8.8 | 463 | 8.8 | 464 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8160 | 599.9997 | 92.721
SYL-N.1.RR.49.1 | 24544159152029 | Amborkhana, Housing Estate R/A, H # 57 | 2019-08-04 | MP1006 | 10.1 | 465 | 10.1 | 466 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8160 | 599.9997 | 106.4185
SYL-N.1.RR.50.1 | 24542859152025 | Housing Estate R/A, Rd # 2, H # 111 | 2019-08-04 | MP1006 | 5.8 | 467 | 5.8 | 468 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8160 | 599.9997 | 61.1116
SYL-N.1.RR.51.1 | 24544079153362 | North Baluchor, Al-Islah R/A, H # 150 | 2019-07-29 | MP1006 | 11.4 | 321 | 11.1 | 322 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8160 | 599.9997 | 116.9549
SYL-N.1.RR.51.2 | 24544079153362 | North Baluchor, Al-Islah R/A, H # 150 | 2021-11-07 | NQ1007 | 6.4 | 87 | 6.4 | 88 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8160 | 599.9997 | 67.4335
SYL-N.1.RR.52.1 | 24544119153351 | North Baluchor, Al-Islah R/A, H # 143 | 2019-07-29 | MP1006 | 6.8 | 323 | 6.8 | 324 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 8160 | 599.9997 | 71.6481
SYL-N.1.RR.53.1 | 24544129153356 | North Baluchor, Al-Islah R/A, H # 132, Rezia Begum | 2019-07-29 | MP1006 | 15.7 | 325 | 15.3 | 326 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 8160 | 599.9997 | 161.2082
SYL-N.1.RR.54.1 | 24544199153347 | North Baluchor, Al-Islah R/A, H # 89, Surot Bibi | 2019-07-29 | MP1006 | 7.6 | 327 | 7.6 | 328 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8160 | 599.9997 | 80.0773
SYL-N.1.RR.55.1 | 24543659153353 | North Baluchor, Al-Islah R/A, H # 74 | 2019-07-29 | MP1006 | 5 | 329 | 5 | 330 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 8160 | 599.9997 | 52.6824
SYL-N.1.RR.56.1 | 24543249153348 | North Baluchor, Al-Islah R/A, Rasel | 2019-07-29 | MP1006 | 17.6 | 331 | 17.3 | 332 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 8160 | 599.9997 | 182.2811
SYL-N.1.RR.57.1 | 24543139153349 | North Baluchor, Al-Islah R/A, H # 26 | 2019-07-29 | MP1006 | 15.7 | 333 | 15.7 | 334 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 8160 | 599.9997 | 165.4228
SYL-N.1.RR.58.1 | 24543079153350 | North Baluchor, Al-Islah R/A, Abdul Mukit | 2019-07-29 | MP1006 | 14.9 | 335 | 14.9 | 336 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 8160 | 599.9997 | 156.9936
SYL-N.1.RR.59.1 | 24542089153215 | Shahi Eadgah, TV Gate, Mitali R/A, H # 161, Istihak Monjil | 2019-07-29 | MP1006 | 15.4 | 337 | 15.4 | 338 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 8160 | 599.9997 | 162.2618
SYL-N.1.RR.60.1 | 24541999153183 | Raynogor, Mitali R/A, H # 73, Zaman House | 2019-07-29 | MP1006 | 9.3 | 339 | 9.3 | 340 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 8160 | 599.9997 | 97.9893
SYL-N.1.RR.61.1 | 24542259153215 | TV Gate, East Shahi Eadgah, Sayed Didar Alam | 2019-07-29 | MP1006 | 15.7 | 341 | 15.6 | 342 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 8160 | 599.9997 | 164.3691
SYL-N.1.RR.62.1 | 24543259152309 | Goaitula, Mollika, Siraj Mia | 2019-07-30 | MP1006 | 10.5 | 363 | 10.5 | 364 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8184 | 575.9997 | 110.6331
SYL-N.1.RR.63.1 | 24543259152309 | Goaitula, Mollika, Ramijuddin | 2019-07-30 | MP1006 | 16.7 | 365 | 16.7 | 366 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 8184 | 575.9997 | 175.9592
SYL-N.1.RR.64.1 | 24543259152309 | Goaitula, Mollika, Hasna Begum | 2019-07-30 | MP1006 | 8.3 | 367 | 8.3 | 368 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 8184 | 575.9997 | 87.4528
SYL-N.1.RR.65.1 | 24543079152249 | Borobazar, Amborkhana, Goli No-9, Abdul Malek | 2019-07-30 | MP1006 | 15.7 | 369 | 15.7 | 370 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 8184 | 575.9997 | 165.4228
SYL-N.1.RR.66.1 | 24543689152330 | Amborkhana, Borobazar R/A, H #103, Md. Abdul Ahad | 2019-07-30 | MP1006 | 10 | 371 | 10 | 372 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8184 | 575.9997 | 105.3648
SYL-N.1.RR.67.1 | 24543459152355 | Amborkhana, Borobazar, Niyamotullah | 2019-07-30 | MP1006 | 18.5 | 373 | 18.5 | 374 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 8184 | 575.9997 | 194.9249
SYL-N.1.RR.67.2 | 24543459152355 | Amborkhana, Borobazar, Niyamotullah | 2022-12-08 | NQ1007 | 4.3 | 282 | 4.3 | 283 | 2022-12-08 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 0 | 575.9997 | 2.9791
SYL-N.1.RR.68.1 | 24544939152243 | Khasdobir, Molla Para R/A, Toronggo-7/1-A, Rehana Begum | 2019-07-31 | MP1006 | 9.8 | 387 | 9.8 | 388 | 2022-01-01 | [9 empty] | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0
SYL-N.1.RR.68.2 | 24544939152243 | Khasdobir, Molla Para R/A, Toronggo-7/1-A, Rehana Begum | 2022-04-26 | LU1001 | 10.3 | 186 | 10.3 | 187 | 2022-04-26 | [9 empty] | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0
SYL-N.1.RR.69.1 | 24544939152249 | Khasdobir, Molla Para R/A, Md. Juber Ali | 2019-07-31 | MP1006 | 12 | 389 | 12 | 390 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8184 | 575.9997 | 126.4378
SYL-N.1.RR.69.2 | 24544939152249 | Khasdobir, Molla Para R/A, Md. Juber Ali | 2021-11-04 | NQ1007 | 11.7 | 83 | 11.7 | 84 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8184 | 575.9997 | 123.2768
SYL-N.1.RR.70.1 | 24544759152279 | Khashdobir, Molla Para R/A, H # 7/16 | 2019-07-31 | MP1006 | 12.4 | 391 | 12.4 | 392 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8184 | 575.9997 | 130.6524
SYL-N.1.RR.71.1 | 24544889152280 | Khashdobir, Molla Para R/A, H # 7/4 | 2019-07-31 | MP1006 | 8.5 | 393 | 7.9 | 394 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 8184 | 575.9997 | 83.2382
SYL-N.1.RR.72.1 | 24545229152321 | East Choukidakhi, Monaf Road, Rupsha R/A, Helal Villa | 2019-07-31 | MP1006 | 10.7 | 395 | 10.7 | 396 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8184 | 575.9997 | 112.7403
SYL-N.1.RR.73.1 | 24543809152090 | Mojumdari, Komlabagan, H # 97/1, Rashed Monjil | 2019-08-01 | MP1006 | 10.4 | 415 | 10.4 | 416 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8136 | 623.9997 | 109.5794
SYL-N.1.RR.74.1 | 24543879152066 | Mojumdari, Komlabagan, H # 119, Dr. Nazma Alam | 2019-08-01 | MP1006 | 6.9 | 417 | 6.9 | 418 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 8136 | 623.9997 | 72.7017
SYL-N.1.RR.75.1 | 24543949152059 | Mojumdari, Komlabagan, H # 120, Abdul Malik | 2019-08-01 | MP1006 | 11.3 | 419 | 11.3 | 420 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8136 | 623.9997 | 119.0622
SYL-N.1.RR.76.1 | 24543949152059 | Mojumdari, Komlabagan, H # 120, Abdul Malik | 2019-08-01 | MP1006 | 11.6 | 421 | 11.6 | 422 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8136 | 623.9997 | 122.2232
SYL-N.1.RR.77.1 | 24544039152075 | Mojumdari, Komlabagan, H # 120, Abdul Malik | 2019-08-01 | MP1006 | 8.5 | 423 | 8.5 | 424 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 8136 | 623.9997 | 89.5601
SYL-N.1.RR.78.1 | 24544039152075 | Mojumdari, Komlabagan, H # 124/1, Alifjan Monjil | 2019-08-01 | MP1006 | 10.1 | 425 | 10.1 | 426 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8136 | 623.9997 | 106.4185
SYL-N.1.RR.79.1 | 24545549152050 | North Pir Moholla, Paharika, H # 72, Rahima Monjil | 2019-08-03 | MP1006 | 2 | 441 | 2 | 442 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 8136 | 623.9997 | 21.073
SYL-N.1.RR.80.1 | 24545559152091 | Badambagicha, Rd # 3, Zahidul Islam | 2019-08-03 | MP1006 | 19.2 | 443 | 19.2 | 444 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 19.2 | 19.2 | 1.152 | 1.152 | 0.0007168 | 100% | 0% | 1.152 | 1.152 | 0.0011869 | 28 | 0.023094 | 0.023094 |  | 0 | 0 | 8136 | 623.9997 | 202.3004
SYL-N.1.RR.81.1 | 24545599152096 | Badambagicha, Rd # 3, H # 20, Mukta Kunjo-2 | 2019-08-03 | MP1006 | 6.1 | 445 | 6.1 | 446 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8136 | 623.9997 | 64.2725
SYL-N.1.RR.82.1 | 24545639152107 | Badambagicha R/A, Rd # 3, H # 06, Baitul Imani | 2019-08-03 | MP1006 | 6.2 | 447 | 6.2 | 448 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8136 | 623.9997 | 65.3262
SYL-N.1.RR.83.1 | 24545889152078 | Badambagicha R/A, Rd # 2, Hazin Sonaullah | 2019-08-03 | MP1006 | 9.8 | 449 | 9.8 | 450 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8136 | 623.9997 | 103.2575
SYL-N.1.RR.84.1 | 24546009152084 | Badambagicha R/A, Shetu Bondhon-23/2, Hazi Bari | 2019-08-03 | MP1006 | 21.1 | 451 | 21.1 | 452 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 21.1 | 21.1 | 1.266 | 1.266 | 0.0007168 | 100% | 0% | 1.266 | 1.266 | 0.0011869 | 28 | 0.025379 | 0.025379 |  | 0 | 0 | 8136 | 623.9997 | 222.3198
SYL-N.1.RR.85.1 | 24550269152065 | Badambagicha R/A, Rd # 2, H # 34, Sayeda Monjil | 2019-08-03 | MP1006 | 17.7 | 453 | 17.7 | 454 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 8136 | 623.9997 | 186.4957
SYL-N.1.RR.86.1 | 24550269152065 | Badambagicha R/A, Rd # 2, H # 33/2, Digholbak Mahol | 2019-08-03 | MP1006 | 10.3 | 455 | 9.5 | 456 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8136 | 623.9997 | 100.0966
SYL-N.1.RR.86.2 | 24550269152065 | Badambagicha R/A, Rd # 2, H # 33/2, Digholbak Mahol | 2020-10-25 | NQ1003 | 2 | 197 | 2 | 198 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 8136 | 623.9997 | 21.073
SYL-N.1.RR.87.1 | 24550169152035 | North Pir Moholla, Paharika, H # 47, Saleha Monzil | 2019-08-03 | MP1006 | 15 | 457 | 15 | 458 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8136 | 623.9997 | 158.0472
SYL-N.1.RR.88.1 | 24545559151596 | North Pir Moholla, Paharika, H # 16/1, Md. Iqbal Raja | 2019-08-03 | MP1006 | 5.8 | 459 | 5.8 | 460 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8136 | 623.9997 | 61.1116
SYL-N.1.RR.89.1 | 24545799152137 | Badambagicha R/A, Rd # 02, H # 2/2, Mina Monjil | 2019-08-04 | MP1006 | 3.3 | 473 | 3.3 | 474 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 8136 | 623.9997 | 34.7704
SYL-N.1.RR.90.1 | 24545849152133 | Badambagicha R/A, Rd # 02, H # 3/2, Moni Villa | 2019-08-04 | MP1006 | 14.7 | 475 | 14.7 | 476 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 8136 | 623.9997 | 154.8863
SYL-N.1.RR.91.1 | 24545909152105 | Badambagicha R/A, Rd # 4, Abdul Malek | 2019-08-04 | MP1006 | 16.8 | 477 | 16.8 | 478 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 8136 | 623.9997 | 177.0129
SYL-N.1.RR.92.1 | 24545979152107 | Badambagicha R/A, Rd # 4, H # 2/1, Sayod Bari | 2019-08-04 | MP1006 | 3.7 | 479 | 3.7 | 480 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 8136 | 623.9997 | 38.985
SYL-N.1.RR.93.1 | 24550389152135 | Badambagicha R/A, Rd # 4, H # 15, Siraj Bhabon | 2019-08-04 | MP1006 | 16.8 | 481 | 16.8 | 482 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 8136 | 623.9997 | 177.0129
SYL-N.1.RR.94.1 | 24550459152162 | Badambagicha R/A, Rd # 1, Shovon Villa | 2019-08-04 | MP1006 | 9.6 | 483 | 9.6 | 484 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8136 | 623.9997 | 101.1502
SYL-N.1.RR.95.1 | 24550499152172 | Badambagicha R/A, Rd # 1, H # 50, Islam | 2019-08-04 | MP1006 | 3.5 | 485 | 3.5 | 486 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 8136 | 623.9997 | 36.8777
SYL-N.1.RR.96.1 | 24550639152165 | Badambagicha R/A, Rd # 1, Liton | 2019-08-04 | MP1006 | 8.2 | 487 | 8.2 | 488 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8136 | 623.9997 | 86.3991
SYL-N.1.RR.96.2 | 24550639152165 | Badambagicha R/A, Rd # 1, Liton | 2021-11-02 | NQ1007 | 6.3 | 75 | 6.3 | 76 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8136 | 623.9997 | 66.3798
SYL-N.1.RR.97.1 | 24550639152165 | Badambagicha R/A, Rd # 1, Hazi Roufuddin | 2019-08-04 | MP1006 | 14.4 | 489 | 14.4 | 490 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 8136 | 623.9997 | 151.7253
SYL-N.1.RR.98.1 | 24550489152170 | Badambagicha R/A, Rd # 1, H # 70, Anwar Monjil | 2019-08-04 | MP1006 | 10 | 491 | 10 | 492 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8136 | 623.9997 | 105.3648
SYL-N.1.RR.100.1 | 24550659151573 | West Pir Moholla, H # 199, Karamot Villa | 2019-08-05 | MP1006 | 18.7 | 495 | 18.7 | 496 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 8136 | 623.9997 | 197.0322
SYL-N.1.RR.101.1 | 24542269153456 | North Baluchar, Focus R/A, H # 2/B, Rahat Ahamed | 2019-07-28 | NQ1003 | 16.3 | 286 | 16 | 287 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 8160 | 599.9997 | 168.5837
SYL-N.1.RR.102.1 | 24542289153482 | North Baluchar, Focus R/A, H # 5, Block-B, Haz-Am House | 2019-07-28 | NQ1003 | 17.4 | 288 | 17.4 | 289 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 8160 | 599.9997 | 183.3348
SYL-N.1.RR.102.2 | 24542289153482 | North Baluchar, Focus R/A, H # 5, Block-B, Haz-Am House | 2022-12-07 | NQ1007 | 4.6 | 270 | 4.6 | 271 | 2022-12-07 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 0 | 599.9997 | 3.3197
SYL-N.1.RR.103.1 | 24542549153492 | North Baluchar, Focus R/A, H # 100/B, Rabaya Villa | 2019-07-28 | NQ1003 | 11.6 | 290 | 11.6 | 291 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8160 | 599.9997 | 122.2232
SYL-N.1.RR.104.1 | 24542589153541 | North Baluchar, Focus R/A, H # 123/B, Shahin Ahamed | 2019-07-28 | NQ1003 | 10.1 | 292 | 10.1 | 293 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8160 | 599.9997 | 106.4185
SYL-N.1.RR.104.2 | 24542589153541 | North Baluchar, Focus R/A, H # 123/B, Shahin Ahamed | 2021-11-07 | NQ1007 | 2.4 | 85 | 2.4 | 86 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 8160 | 599.9997 | 25.2876
SYL-N.1.RR.105.1 | 24542689153558 | North Baluchar, Focus R/A, H # 252/B | 2019-07-28 | NQ1003 | 11.1 | 294 | 10.5 | 295 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8160 | 599.9997 | 110.6331
SYL-N.1.RR.106.1 | 24542669154011 | North Baluchar, Sonar Bangla R/A, Khasa Member | 2019-07-28 | NQ1003 | 11 | 296 | 11 | 297 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8160 | 599.9997 | 115.9013
SYL-N.1.RR.106.2 | 24542669154011 | North Baluchar, Sonar Bangla R/A, Khasa Member | 2019-07-28 | NQ1003 | 12.7 | 298 | 12.7 | 299 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 8160 | 599.9997 | 133.8133
SYL-N.1.RR.107.1 | 24542839154011 | North Baluchar, Sonar Bangla R/A, H # 220, Monuwara Villa | 2019-07-28 | NQ1003 | 4.8 | 300 | 4.8 | 301 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8160 | 599.9997 | 50.5751
SYL-N.1.RR.108.1 | 24543559153593 | North Baluchar, Sonar Bangla Focas, Nurul | 2019-07-29 | NQ1003 | 14 | 302 | 14 | 303 | 2022-01-01 | [9 empty] | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0
SYL-N.1.RR.109.1 | 24544669153542 | North Baluchar, Al Islah R/A, Jonaki Road, Sanjida Tailars | 2019-07-29 | NQ1003 | 19.1 | 304 | 19.5 | 305 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 19.5 | 19.5 | 1.17 | 1.17 | 0.0007168 | 100% | 0% | 1.17 | 1.17 | 0.0011869 | 28 | 0.023454 | 0.023454 |  | 0 | 0 | 8160 | 599.9997 | 205.4614
SYL-N.1.RR.109.2 | 24544669153542 | North Baluchar, Al Islah R/A, Jonaki Road, Sanjida Tailars | 2022-12-07 | NQ1007 | 10.2 | 276 | 10.2 | 277 | 2022-12-07 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 0 | 599.9997 | 7.3611
SYL-N.1.RR.110.1 | 24545089153556 | North Baluchar, Al Islah R/A, Jonaki Road, Trimukhi Point, Abdul Malekh | 2019-07-29 | NQ1003 | 15.5 | 306 | 15.9 | 307 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 8160 | 599.9997 | 167.5301
SYL-N.1.RR.111.1 | 24544709153444 | North Baluchar, Al Islah R/A, H # 325, Md. Monu Mia | 2019-07-29 | NQ1003 | 1 | 310 | 1 | 311 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 8160 | 599.9997 | 10.5365
SYL-N.1.RR.112.1 | 24544709153437 | North Baluchar, Al Islah R/A, H # 303, Pinku Chandra Shah | 2019-07-29 | NQ1003 | 1.3 | 312 | 1.3 | 313 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 8160 | 599.9997 | 13.6974
SYL-N.1.RR.113.1 | 24544439153468 | North Baluchar, Al Islah R/A, Soyed Sofiyan Ahamed | 2019-07-29 | NQ1003 | 5.2 | 314 | 5.2 | 315 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 8160 | 599.9997 | 54.7897
SYL-N.1.RR.113.2 | 24544439153468 | North Baluchar, Al Islah R/A, Soyed Sofiyan Ahamed | 2021-02-14 | MN1032 | 3.9 | 153 | 3.9 | 154 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 8160 | 599.9997 | 41.0923
SYL-N.1.RR.114.1 | 24544419153483 | North Baluchar, Al Islah R/A, Kamal Ahamed | 2019-07-29 | NQ1003 | 15.7 | 316 | 15.7 | 317 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 8160 | 599.9997 | 165.4228
SYL-N.1.RR.115.1 | 24542609152372 | North Kajitula, Chasnipir Road, Kulbakhani R/A, H # 43, Paplu | 2019-07-30 | NQ1003 | 8.9 | 338 | 8.9 | 339 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8184 | 575.9997 | 93.7747
SYL-N.1.RR.116.1 | 24542609152372 | North Kajitula, Chasnipir Road, Kulbakhani R/A, H # 42, Sohel | 2019-07-30 | NQ1003 | 11.7 | 340 | 11.7 | 341 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8184 | 575.9997 | 123.2768
SYL-N.1.RR.117.1 | 24542759152362 | North Kajitula, Chasnipir Road, Kulbakhani R/A, Abdul Khalek | 2019-07-30 | NQ1003 | 13 | 344 | 13 | 345 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8184 | 575.9997 | 136.9743
SYL-N.1.RR.118.1 | 24542759152362 | North Kajitula, Chasnipir Road, Kulbakhani R/A, Tara mia | 2019-07-30 | NQ1003 | 13.6 | 346 | 13.6 | 347 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 8184 | 575.9997 | 143.2961
SYL-N.1.RR.119.1 | 24543569152402 | Goaitula, Mullika, Chasnipir R/A, Bakhat Road, H # 47/3 | 2019-07-30 | NQ1003 | 7.6 | 348 | 7.7 | 349 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 8184 | 575.9997 | 81.1309
SYL-N.1.RR.120.1 | 24543569152409 | Goaitula, Mullika, Chasnipir R/A, Bakhat Road, Ishaq Ali | 2019-07-30 | NQ1003 | 12.4 | 350 | 12.4 | 351 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8184 | 575.9997 | 130.6524
SYL-N.1.RR.121.1 | 24542459152361 | Kolbahani, Electric Supply Road, Kolbahani R/a, Abdul Hannan | 2019-07-31 | NQ1003 | 10 | 370 | 10 | 371 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8184 | 575.9997 | 105.3648
SYL-N.1.RR.122.1 | 24542419152355 | Kolbahani, Electric Supply Road, Kolbahani R/a, Saddam Hossain | 2019-07-31 | NQ1003 | 6.4 | 372 | 6.4 | 373 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8184 | 575.9997 | 67.4335
SYL-N.1.RR.123.1 | 24542259152358 | Kolbahani, Electric Supply Road, Kolbahani R/a, Abdul Khalak | 2019-07-31 | NQ1003 | 17.4 | 374 | 17.4 | 375 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 8184 | 575.9997 | 183.3348
SYL-N.1.RR.124.1 | 24542189152345 | Jalale Kolbahani, Kolbahani R/A, H # 59/2, Nadim Villa | 2019-07-31 | NQ1003 | 7.6 | 376 | 7.6 | 377 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8184 | 575.9997 | 80.0773
SYL-N.1.RR.125.1 | 24542269152334 | Jalale Kolbahani, Kolbahani R/A, H # 59/2, H # 58, Abdul Amin | 2019-07-31 | NQ1003 | 6.2 | 378 | 6.2 | 379 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8184 | 575.9997 | 65.3262
SYL-N.1.RR.125.2 | 24542269152334 | Jalale Kolbahani, Kolbahani R/A, H # 59/2, H # 58, Abdul Amin | 2021-02-16 | NQ1007 | 4.5 | 199 | 4.5 | 200 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 8184 | 575.9997 | 47.4142
SYL-N.1.RR.126.1 | 24542409152312 | Jalale Kolbahani, Kolbahani R/A, H # 25/C, Salah Ahamed | 2019-07-31 | NQ1003 | 14.8 | 380 | 14.9 | 381 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 8184 | 575.9997 | 156.9936
SYL-N.1.RR.127.1 | 24542259152303 | Jalale Kolbahani, Kolbahani R/A, H # 5, Abdul Mojib Chodury | 2019-07-31 | NQ1003 | 14.2 | 382 | 14.2 | 383 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 8184 | 575.9997 | 149.618
SYL-N.1.RR.128.1 | 24542029152342 | Kolbahani, Electric Supply Road, Kolbahani R/a, H # 14, Maya Begum | 2019-07-31 | NQ1003 | 94.2 | 384 | 94.2 | 385 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 94.2 | 94.2 | 5.652 | 5.652 | 0.0007168 | 100% | 0% | 5.652 | 5.652 | 0.0011869 | 28 | 0.1133 | 0.1133 |  | 0 | 0 | 8184 | 575.9997 | 992.5365
SYL-N.1.RR.129.1 | 24544569152364 | Amberkhana, KashDobir Darus Salam Madrasha Road, Amir House | 2019-07-31 | NQ1003 | 11.9 | 386 | 11.9 | 387 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8184 | 575.9997 | 125.3841
SYL-N.1.RR.130.1 | 24545689152306 | Chowkidigi, Rongdhonu R/A, H # 25/1 | 2019-08-01 | NQ1003 | 33.6 | 392 | 33.6 | 393 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 33.6 | 33.6 | 2.016 | 2.016 | 0.0007168 | 100% | 0% | 2.016 | 2.016 | 0.0011869 | 28 | 0.040414 | 0.040414 |  | 0 | 0 | 8184 | 575.9997 | 354.0258
SYL-N.1.RR.131.1 | 24545829152316 | East Chowkidigi, Rongdhonu R/A, Afroz | 2019-08-01 | NQ1003 | 7.8 | 394 | 7.8 | 395 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 8184 | 575.9997 | 82.1846
SYL-N.1.RR.132.1 | 24545849152321 | East Chowkidigi, Rongdhonu R/A, H # 36/1 | 2019-08-01 | NQ1003 | 24.4 | 396 | 24.4 | 397 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 24.4 | 24.4 | 1.464 | 1.464 | 0.0007168 | 100% | 0% | 1.464 | 1.464 | 0.0011869 | 28 | 0.029348 | 0.029348 |  | 0 | 0 | 8184 | 575.9997 | 257.0901
SYL-N.1.RR.133.1 | 24545849152321 | East Chowkidigi, Rongdhonu R/A, H # 35 | 2019-08-01 | NQ1003 | 7.6 | 398 | 7.6 | 399 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8184 | 575.9997 | 80.0773
SYL-N.1.RR.134.1 | 24545809152334 | East Chowkidigi, Rongdhonu R/A, Morad | 2019-08-01 | NQ1003 | 13.7 | 402 | 13.7 | 403 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 8184 | 575.9997 | 144.3498
SYL-N.1.RR.135.1 | 24545659152330 | East Chowkidigi, Rongdhonu R/A, H # 30/1 | 2019-08-01 | NQ1003 | 16 | 404 | 16 | 405 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 8184 | 575.9997 | 168.5837
SYL-N.1.RR.136.1 | 24545679152336 | East Chowkidigi, Rongdhonu R/A, H # 33/1 | 2019-08-01 | NQ1003 | 8.2 | 406 | 8.2 | 407 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8184 | 575.9997 | 86.3991
SYL-N.1.RR.136.2 | 24545679152336 | East Chowkidigi, Rongdhonu R/A, H # 33/1 | 2019-08-01 | NQ1003 | 10.5 | 408 | 10.5 | 409 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8184 | 575.9997 | 110.6331
SYL-N.1.RR.137.1 | 24550059152284 | East Chowkidigi, Rongdhonu R/A, Somon | 2019-08-01 | NQ1003 | 5.7 | 410 | 6.1 | 411 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8184 | 575.9997 | 64.2725
SYL-N.1.RR.137.2 | 24550059152284 | East Chowkidigi, Rongdhonu R/A, Somon | 2021-02-16 | NQ1003 | 8.5 | 257 | 8.5 | 258 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 8184 | 575.9997 | 89.5601
SYL-N.1.RR.138.1 | 24550119152301 | Chowkidigi, Rongdhonu R/A, Light Villa | 2019-08-01 | NQ1003 | 4.7 | 412 | 4.7 | 413 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 8184 | 575.9997 | 49.5215
SYL-N.1.RR.139.1 | 24550629152344 | Chowkidigi,Biman Bondor Road, Rongdhonu R/A, H # 207 | 2019-08-01 | NQ1003 | 12.2 | 416 | 12.2 | 417 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 8184 | 575.9997 | 128.5451
SYL-N.1.RR.140.1 | 24542019152078 | Amberkhana, Monipuripara, H #02 | 2019-08-03 | NQ1003 | 4.9 | 430 | 4.9 | 431 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 8160 | 599.9997 | 51.6288
SYL-N.1.RR.140.2 | 24542019152078 | Amberkhana, Monipuripara, H #02 | 2021-11-03 | NQ1007 | 15.5 | 79 | 15.4 | 80 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 8160 | 599.9997 | 162.2618
SYL-N.1.RR.141.1 | 24542019152078 | Amberkhana, Monipuripara, H #03 | 2019-08-03 | NQ1003 | 11.8 | 436 | 11.8 | 437 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8160 | 599.9997 | 124.3305
SYL-N.1.RR.142.1 | 24542089152083 | Amberkhana, Monipuripara, H #04 | 2019-08-03 | NQ1003 | 21.7 | 438 | 21.7 | 439 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 8160 | 599.9997 | 228.6416
SYL-N.1.RR.143.1 | 24542559152069 | Amberkhana, Monipuripara, H #24 | 2019-08-03 | NQ1003 | 11 | 440 | 11 | 441 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8160 | 599.9997 | 115.9013
SYL-N.1.RR.144.1 | 24542159152034 | Amberkhana, Sombugonj Road, Sobassa R/A, H #11/1 | 2019-08-03 | NQ1003 | 27.8 | 442 | 29 | 443 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 29 | 29 | 1.74 | 1.74 | 0.0007168 | 100% | 0% | 1.74 | 1.74 | 0.0011869 | 28 | 0.034881 | 0.034881 |  | 0 | 0 | 8160 | 599.9997 | 305.558
SYL-N.1.RR.144.2 | 24542159152034 | Amberkhana, Sombugonj Road, Sobassa R/A, H #11/1 | 2021-02-16 | LU1001 | 4.1 | 201 | 4.1 | 202 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 8160 | 599.9997 | 43.1996
SYL-N.1.RR.145.1 | 24542159152034 | Amberkhana, Sombugonj Road, Sobassa R/A, H #11 | 2019-08-03 | NQ1003 | 10.4 | 444 | 11.1 | 445 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8160 | 599.9997 | 116.9549
SYL-N.1.RR.146.1 | 24542229152014 | Amberkhana, Sombugonj Road, Sobassa R/A, H #18, Jayed | 2019-08-03 | NQ1003 | 11.6 | 446 | 11.7 | 447 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8160 | 599.9997 | 123.2768
SYL-N.1.RR.147.1 | 24542229152014 | Amberkhana, Sombugonj Road, Sobassa R/A, H #18, Sayed | 2019-08-03 | NQ1003 | 16 | 448 | 16 | 449 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 8160 | 599.9997 | 168.5837
SYL-N.1.RR.148.1 | 24542709151590 | Amberkhana, Housing Estate Road, Kamal House, H #61/2 | 2019-08-03 | NQ1003 | 6.1 | 451 | 6.1 | 452 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8160 | 599.9997 | 64.2725
SYL-N.1.RR.149.1 | 24544879151528 | Mohammad Nagar, Shah Forid Road, Jalalabad R/ A, H # 47 | 2019-08-04 | NQ1003 | 12.4 | 479 | 12.4 | 480 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8088 | 671.9997 | 130.6524
SYL-N.1.RR.150.1 | 24544739151527 | Mohammad Nagar, Shah Forid Road, Jalalabad R/ A, H # 44 | 2019-08-04 | NQ1003 | 15.9 | 481 | 15.9 | 482 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 8088 | 671.9997 | 167.5301
SYL-N.1.RR.151.1 | 24545849153537 | North Baluchar, Al-Esla, UCEP Solaiman Chowdhury Baluchar School, Jonaki Road, Nurjahan Begum | 2019-07-29 | NQ1003 | 5.2 | 320 | 5.2 | 321 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 8160 | 599.9997 | 54.7897
SYL-N.1.RR.152.1 | 24545859153524 | North Baluchar, Al-Esla, UCEP Solaiman Chowdhury Baluchar School, Jonaki Road, Seraj Mia | 2019-07-29 | NQ1003 | 10.8 | 322 | 10.8 | 323 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8160 | 599.9997 | 113.794
SYL-N.1.RR.153.1 | 24550399153559 | North Baluchar, Jonaki R/A, Jonaki Road, Faruk Mia | 2019-07-29 | NQ1003 | 12.5 | 324 | 12.5 | 325 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 8160 | 599.9997 | 131.706
SYL-N.1.RR.154.1 | 24550839153597 | North Baluchar, Jonaki R/A, Toka Mia | 2019-07-29 | NQ1003 | 5.3 | 328 | 5.3 | 329 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 8160 | 599.9997 | 55.8434
SYL-N.1.RR.155.1 | 24550849154031 | North Baluchar, Jonaki R/A, Abdur Rob | 2019-07-29 | NQ1003 | 12.6 | 330 | 12.6 | 331 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 8160 | 599.9997 | 132.7597
SYL-N.1.RR.156.1 | 24550399154065 | North Baluchar, Jonaki R/A, Shah Alam Membar Bari, Abu Taher | 2019-07-29 | NQ1003 | 2.9 | 334 | 2.9 | 335 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 8160 | 599.9997 | 30.5558
SYL-N.1.RR.157.1 | 24550399154062 | North Baluchar, Jonaki R/A, Shah Alam Membar Bari, Masuk Mia | 2019-07-29 | NQ1003 | 10.3 | 336 | 10.1 | 337 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8160 | 599.9997 | 106.4185
SYL-N.1.RR.158.1 | 24543249152360 | Guaitula, Mollika R/A, Chashinipir Road, Somiruddin | 2019-07-30 | NQ1003 | 14.7 | 352 | 14.7 | 353 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 8184 | 575.9997 | 154.8863
SYL-N.1.RR.159.1 | 24543029152363 | Guaitula, Mollika R/A, Chashinipir Road, Amin Mia | 2019-07-30 | NQ1003 | 12.4 | 354 | 12.4 | 355 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8184 | 575.9997 | 130.6524
SYL-N.1.RR.160.1 | 24542969152362 | Guaitula, Mollika R/A, Chashinipir Road, Shahed Ahmed, H # 24 | 2019-07-30 | NQ1003 | 6.3 | 356 | 5.8 | 357 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8184 | 575.9997 | 61.1116
SYL-N.1.RR.160.2 | 24542969152362 | Guaitula, Mollika R/A, Chashinipir Road, Shahed Ahmed, H # 24 | 2021-02-16 | NQ1007 | 3.8 | 194 | 3.8 | 195 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8184 | 575.9997 | 40.0386
SYL-N.1.RR.161.1 | 24542879152358 | Guaitula, Mollika R/A, Chashinipir Road, Shahera Monjil, H # 25 | 2019-07-30 | NQ1003 | 8.2 | 358 | 8.2 | 359 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8184 | 575.9997 | 86.3991
SYL-N.1.RR.161.2 | 24542879152358 | Guaitula, Mollika R/A, Chashinipir Road, Shahera Monjil, H # 25 | 2021-02-16 | NQ1007 | 4.5 | 196 | 4.5 | 197 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 8184 | 575.9997 | 47.4142
SYL-N.1.RR.162.1 | 24543259152343 | Guaitula, Mollika R/A, Chashinipir Road, Abdus Sattar | 2019-07-30 | NQ1003 | 4.4 | 360 | 4.4 | 361 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 8184 | 575.9997 | 46.3605
SYL-N.1.RR.163.1 | 24542519152289 | Kolbakhani, Ray Hussain, Diganto R/A, Jillur Rahman | 2019-07-30 | NQ1003 | 10.2 | 362 | 10.2 | 363 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8184 | 575.9997 | 107.4721
SYL-N.1.RR.164.1 | 24542569152276 | Kolbakhani, Ray Hussain, Diganto R/A, Abdur Rahman Billu Mia | 2019-07-30 | NQ1003 | 3 | 364 | 3 | 365 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 8184 | 575.9997 | 31.6094
SYL-N.1.RR.165.1 | 24542739152293 | Amborkhana, Ray Hossain R/A, Rahman Monjil, Diganto-63 | 2019-07-30 | NQ1003 | 6.3 | 366 | 6.3 | 367 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8184 | 575.9997 | 66.3798
SYL-N.1.RR.166.1 | 24542829152307 | Amborkhana, Ray Hossain R/A, Solaiman Mia, Diganto-67 | 2019-07-30 | NQ1003 | 11.4 | 368 | 11.2 | 369 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8184 | 575.9997 | 118.0086
SYL-N.1.RR.167.1 | 24545459152281 | Chowkidekhi, Angur Mia Road, Rongdonu R/A, H # 7/3 | 2019-07-31 | NQ1003 | 11.5 | 388 | 11.5 | 389 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8184 | 575.9997 | 121.1695
SYL-N.1.RR.168.1 | 24545749152279 | Chowkidekhi, Rongdonu R/A, H.M. Rahman Monjil, H # 13/C | 2019-07-31 | NQ1003 | 12.7 | 390 | 12.7 | 391 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 8184 | 575.9997 | 133.8133
SYL-N.1.RR.169.1 | 24542529152123 | Amborkhana, Gurny Residential Area, Mohammad Tofayel Ahmed, H # 38 | 2019-08-01 | NQ1003 | 11.8 | 420 | 11.8 | 421 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8160 | 599.9997 | 124.3305
SYL-N.1.RR.170.1 | 24542589152096 | Amborkhana, Gurny Residential Area, Gurny Jame Mosjid | 2019-08-01 | NQ1003 | 8 | 422 | 8 | 423 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 8160 | 599.9997 | 84.2919
SYL-N.1.RR.171.1 | 24542689152064 | Amborkhana, Gurny Residential Area, H # 31/1 | 2019-08-01 | NQ1003 | 14.9 | 424 | 14.9 | 425 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 8160 | 599.9997 | 156.9936
SYL-N.1.RR.172.1 | 24542519152062 | Amborkhana, Gurny Residential Area, Farid Bag, Akhtar Mahal | 2019-08-01 | NQ1003 | 12.2 | 426 | 12.2 | 427 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 8160 | 599.9997 | 128.5451
SYL-N.1.RR.173.1 | 24543089152051 | Amborkhana, Gurny Residential Area, H # 23 | 2019-08-01 | NQ1003 | 11.2 | 428 | 11.1 | 429 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8160 | 599.9997 | 116.9549
SYL-N.1.RR.174.1 | 24542739151575 | Amborkhana, Housing Estate Road, Muradujjaman Chowdhury, H # 67 | 2019-08-03 | NQ1003 | 10.5 | 453 | 10.2 | 454 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8160 | 599.9997 | 107.4721
SYL-N.1.RR.175.1 | 24543299151550 | Amborkhana, Parijath R/A, Abdur Rajjak Chowdhury, H # 08 | 2019-08-03 | NQ1003 | 10 | 455 | 9.9 | 456 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8160 | 599.9997 | 104.3112
SYL-N.1.RR.176.1 | 24543299151550 | Amborkhana, Parijath R/A, Hamida Chowdhury Munni, H # 7 | 2019-08-03 | NQ1003 | 5 | 457 | 5 | 458 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 8160 | 599.9997 | 52.6824
SYL-N.1.RR.177.1 | 24543299151550 | Amborkhana, Parijath R/A, H # 6 | 2019-08-03 | NQ1003 | 5.2 | 459 | 5.2 | 460 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 8160 | 599.9997 | 54.7897
SYL-N.1.RR.178.1 | 24543569151594 | Amborkhana, Green View Housing Estate, Lane # 04/A, H # 71 | 2019-08-03 | NQ1003 | 13.4 | 461 | 12.6 | 462 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 8160 | 599.9997 | 132.7597
SYL-N.1.RR.179.1 | 24543529151574 | Amborkhana, Green View Housing Estate, Lane # 04/A, H # 73 | 2019-08-03 | NQ1003 | 11.5 | 463 | 11.5 | 464 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8160 | 599.9997 | 121.1695
SYL-N.1.RR.180.1 | 24544189151591 | Amborkhana, Housing Estate, Lane # 7/A, H # 85 | 2019-08-03 | NQ1003 | 3.8 | 465 | 3.8 | 466 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8160 | 599.9997 | 40.0386
SYL-N.1.RR.181.1 | 24544979151593 | Amborkhana, Housing Estate, West Pir Mohollah, H # 26 | 2019-08-03 | NQ1003 | 9.6 | 467 | 9.6 | 468 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8088 | 671.9997 | 101.1502
SYL-N.1.RR.182.1 | 24544979151593 | Amborkhana, Housing Estate, West Pir Mohollah, H # 26 | 2019-08-03 | NQ1003 | 12.1 | 469 | 12.1 | 470 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 8088 | 671.9997 | 127.4914
SYL-N.1.RR.183.1 | 24544979151593 | Amborkhana, Housing Estate, West Pir Mohollah, H # 26 | 2019-08-03 | NQ1003 | 11.7 | 471 | 11.7 | 472 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8088 | 671.9997 | 123.2768
SYL-N.1.RR.183.2 | 24544979151593 | Amborkhana, Housing Estate, West Pir Mohollah, H # 26 | 2021-02-17 | LU1001 | 3.9 | 205 | 3.9 | 206 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 8088 | 671.9997 | 41.0923
SYL-N.1.RR.184.1 | 24545089151588 | Amborkhana, Housing Estate, West Pir Mohollah, H # 24/2 | 2019-08-03 | NQ1003 | 10.7 | 473 | 10.9 | 474 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8088 | 671.9997 | 114.8476
SYL-N.1.RR.185.1 | 24545069151581 | Amborkhana, Housing Estate, West Pir Mohollah, H # 25/1 | 2019-08-03 | NQ1003 | 5 | 475 | 5 | 476 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 8088 | 671.9997 | 52.6824
SYL-N.1.RR.186.1 | 24543689152013 | Amborkhana, Housing Estate, Lane # 05, H # Ashaye Bashati, H # 31 | 2019-08-03 | NQ1003 | 11.7 | 477 | 11.7 | 478 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8160 | 599.9997 | 123.2768
SYL-N.1.RR.187.1 | 24544069151517 | Sylhet Sadar, Jalalabad R/A, H # 36/1 | 2019-08-04 | NQ1003 | 13.4 | 495 | 13.4 | 496 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 8088 | 671.9997 | 141.1888
SYL-N.1.RR.188.1 | 24543969151492 | Sylhet Sadar, Jalalabad R/A, H # 36/6 | 2019-08-04 | NQ1003 | 13 | 497 | 13 | 498 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8088 | 671.9997 | 136.9743
SYL-N.1.RR.189.1 | 24543889151545 | Sylhet Sadar, Jalalabad R/A, Alif Monjil, H # 33/1 | 2019-08-04 | NQ1003 | 7.9 | 499 | 7.9 | 500 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 8088 | 671.9997 | 83.2382
SYL-N.1.RR.190.1 | 24543759151562 | Sylhet Sadar, Jalalabad R/A, Angura Villa, H # 31/4 | 2019-08-04 | NQ1003 | 14.9 | 501 | 15 | 502 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8088 | 671.9997 | 158.0472
SYL-N.1.RR.191.1 | 24543649151490 | Sylhet Sadar, Jalalabad R/A, H # 29/4 | 2019-08-04 | NQ1003 | 9.9 | 503 | 9.9 | 504 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8088 | 671.9997 | 104.3112
SYL-N.1.RR.192.1 | 24543579151495 | Sylhet Sadar, Jalalabad R/A, Back Side of Jalalabad Jame Mosjid, H # 26/1 | 2019-08-04 | NQ1003 | 13.5 | 505 | 13.5 | 506 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 8088 | 671.9997 | 142.2425
SYL-N.1.RR.193.1 | 24543579151495 | Sylhet Sadar, Jalalabad R/A, Back Side of Jalalabad Jame Mosjid, H # 26/2 | 2019-08-04 | NQ1003 | 12 | 507 | 11.9 | 508 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8088 | 671.9997 | 125.3841
SYL-N.1.RR.194.1 | 24543409151511 | Sylhet Sadar, Jalalabad R/A, H # 23 | 2019-08-04 | NQ1003 | 11.7 | 509 | 11.7 | 510 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8088 | 671.9997 | 123.2768
SYL-N.1.RR.195.1 | 24543169151530 | Sylhet Sadar, Jalalabad R/A, H # 22/4 | 2019-08-04 | NQ1003 | 14.4 | 511 | 14 | 512 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 8088 | 671.9997 | 147.5107
SYL-N.1.RR.196.1 | 24543169151530 | Sylhet Sadar, Jalalabad R/A, H # 22/5 | 2019-08-04 | NQ1003 | 22.7 | 515 | 22.7 | 516 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 22.7 | 22.7 | 1.362 | 1.362 | 0.0007168 | 100% | 0% | 1.362 | 1.362 | 0.0011869 | 28 | 0.027303 | 0.027303 |  | 0 | 0 | 8088 | 671.9997 | 239.1781
SYL-N.1.RR.197.1 | 24543139151518 | Sylhet Sadar, Jalalabad R/A, H # 21 | 2019-08-05 | NQ1003 | 7.4 | 517 | 7.4 | 518 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 8088 | 671.9997 | 77.97
SYL-N.1.RR.197.2 | 24543139151518 | Sylhet Sadar, Jalalabad R/A, H # 21 | 2022-12-04 | MN1018 | 9.2 | 158 | 9 | 159 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 0 | 671.9997 | 7.2745
SYL-N.1.RR.198.1 | 24543059151477 | Sylhet Sadar, Jalalabad R/A, H # 20/4 | 2019-08-05 | NQ1003 | 5.1 | 519 | 5.1 | 520 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 8088 | 671.9997 | 53.7361
SYL-N.1.RR.199.1 | 24542899151478 | Sylhet Sadar, Jalalabad R/A, Taj Cottage, H # 14/7 | 2019-08-05 | NQ1003 | 6.3 | 521 | 6.3 | 522 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8088 | 671.9997 | 66.3798
SYL-N.1.RR.200.1 | 24542839151521 | Sylhet Sadar, Jalalabad R/A, H # 14 | 2019-08-05 | NQ1003 | 6.4 | 523 | 6.4 | 524 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8088 | 671.9997 | 67.4335
SYL-N.1.RR.201.1 | 24541999153447 | North Baluchor, Focus R/A, Block-A, Doctor Shilpi | 2019-07-28 | NQ1009 | 4.6 | 338 | 4.6 | 339 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 8160 | 599.9997 | 48.4678
SYL-N.1.RR.202.1 | 24542049153434 | North Baluchor, Focus R/A, Block-A, Abdul Motin, H# 44 | 2019-07-28 | NQ1009 | 14.9 | 340 | 14.9 | 341 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 8160 | 599.9997 | 156.9936
SYL-N.1.RR.203.1 | 24541879153421 | North Baluchor, Shantibagh R/A, Block-A, Sirajul Islam | 2019-07-28 | NQ1009 | 12 | 342 | 12 | 343 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8160 | 599.9997 | 126.4378
SYL-N.1.RR.203.2 | 24541879153421 | North Baluchor, Shantibagh R/A, Block-A, Sirajul Islam | 2021-02-14 | LU1001 | 11.6 | 187 | 11.7 | 188 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8160 | 599.9997 | 123.2768
SYL-N.1.RR.204.1 | 24541879153408 | North Baluchor, Shantibagh R/A, Block-A, Dola | 2019-07-28 | NQ1009 | 13.3 | 344 | 13.6 | 345 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 8160 | 599.9997 | 143.2961
SYL-N.1.RR.205.1 | 24542059153420 | North Baluchor, Shantibagh R/A, Block-A, Chowdhury Monjil, H# 36 | 2019-07-28 | NQ1009 | 10.6 | 346 | 10.6 | 347 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8160 | 599.9997 | 111.6867
SYL-N.1.RR.206.1 | 24541439153449 | North Baluchor, Baluchor Road, Block-A, Abdul Motin | 2019-07-28 | NQ1009 | 13 | 348 | 13 | 349 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8160 | 599.9997 | 136.9743
SYL-N.1.RR.207.1 | 24541629153422 | North Baluchor, Main Road, Durgabari Mondir | 2019-07-28 | NQ1009 | 10.8 | 350 | 10.8 | 351 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8160 | 599.9997 | 113.794
SYL-N.1.RR.208.1 | 24541639153365 | Arambagh, Rd# 5, Abu Villa, H# 1 | 2019-07-28 | NQ1009 | 11 | 352 | 11 | 353 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8160 | 599.9997 | 115.9013
SYL-N.1.RR.209.1 | 24542829153466 | North Baluchor, Focus R/A, Block-B, Sirajul islam | 2019-07-29 | NQ1009 | 9.9 | 354 | 9.9 | 355 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8160 | 599.9997 | 104.3112
SYL-N.1.RR.210.1 | 24542759153499 | North Baluchor, Focus R/A, Block-B, Sheikh Bhaban-2, H# 20 | 2019-07-29 | NQ1009 | 12.1 | 356 | 12.1 | 357 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 8160 | 599.9997 | 127.4914
SYL-N.1.RR.211.1 | 24542909153492 | North Baluchor, Focus R/A, Block-B, Prof. Abdul Baki Chowdhury | 2019-07-29 | NQ1009 | 6.1 | 358 | 6.1 | 359 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8160 | 599.9997 | 64.2725
SYL-N.1.RR.212.1 | 24542909153492 | North Baluchor, Focus R/A, Block-B, Masuk Ahmed, H# 28 | 2019-07-29 | NQ1009 | 41 | 360 | 42.7 | 361 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 42.7 | 42.7 | 2.562 | 2.562 | 0.0007168 | 100% | 0% | 2.562 | 2.562 | 0.0011869 | 28 | 0.051359 | 0.051359 |  | 0 | 0 | 8160 | 599.9997 | 449.9077
SYL-N.1.RR.212.2 | 24542909153492 | North Baluchor, Focus R/A, Block-B, Masuk Ahmed, H# 28 | 2022-12-07 | NQ1007 | 3.5 | 268 | 3.5 | 269 | 2022-12-07 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 0 | 599.9997 | 2.5259
SYL-N.1.RR.213.1 | 24543379153500 | North Baluchor, Focus R/A, Block-B, Dr. M.U. Ahmed, H# 41 | 2019-07-29 | NQ1009 | 25.8 | 362 | 25.8 | 363 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 25.8 | 25.8 | 1.548 | 1.548 | 0.0007168 | 100% | 0% | 1.548 | 1.548 | 0.0011869 | 28 | 0.031032 | 0.031032 |  | 0 | 0 | 8160 | 599.9997 | 271.8412
SYL-N.1.RR.214.1 | 24543059153508 | North Baluchor, Focus R/A, Block-B, Ripon, H# 35 | 2019-07-29 | NQ1009 | 9.4 | 366 | 9.4 | 367 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8160 | 599.9997 | 99.0429
SYL-N.1.RR.215.1 | 24543599153501 | North Baluchor, Notun Bazar, Block-B, Full Bhaban, Rahmat Ullah | 2019-07-29 | NQ1009 | 7.4 | 368 | 7.4 | 369 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 8160 | 599.9997 | 77.97
SYL-N.1.RR.216.1 | 24542319152543 | Hazaribagh R/A, Shahi Eidgha, CNG stand, Abdul Hannan | 2019-07-30 | NQ1009 | 11.5 | 389 | 11.5 | 390 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8184 | 575.9997 | 121.1695
SYL-N.1.RR.217.1 | 24542809152538 | Hazaribagh R/A, Shahi Eidgha, Nahid House, H# 50/2 | 2019-07-30 | NQ1009 | 10.7 | 391 | 10.3 | 392 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8184 | 575.9997 | 108.5258
SYL-N.1.RR.218.1 | 24542899152542 | Hazaribagh R/A, Shahi Eidgha, Khokon Mia | 2019-07-30 | NQ1009 | 11.2 | 393 | 11.2 | 394 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8184 | 575.9997 | 118.0086
SYL-N.1.RR.219.1 | 24542899152542 | Hazaribagh R/A, Shahi Eidgha, H# 25 | 2019-07-30 | NQ1009 | 10.2 | 395 | 10.2 | 396 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8184 | 575.9997 | 107.4721
SYL-N.1.RR.220.1 | 24543339152548 | Hazaribagh R/A, Shahi Eidgha, Rokeya Begum, H# 33 | 2019-07-30 | NQ1009 | 5.7 | 397 | 5.3 | 398 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 8184 | 575.9997 | 55.8434
SYL-N.1.RR.221.1 | 24542299152524 | Hazaribagh R/A, Shahi Eidgha, H# 57, Beside of Shahi Eidgha Hazaribagh Masjid | 2019-07-30 | NQ1009 | 3.4 | 401 | 3.4 | 402 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 8184 | 575.9997 | 35.824
SYL-N.1.RR.222.1 | 24543899152311 | Amborkhana, Borobazar R/A, Borobazar Road, H# 138 | 2019-07-31 | NQ1009 | 5.8 | 413 | 5.8 | 414 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8184 | 575.9997 | 61.1116
SYL-N.1.RR.223.1 | 24543929152330 | Amborkhana, Borobazar R/A, Borobazar Road, Mujibur Rahman | 2019-07-31 | NQ1009 | 10.8 | 415 | 10.8 | 416 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8184 | 575.9997 | 113.794
SYL-N.1.RR.224.1 | 24543929152330 | Amborkhana, Borobazar R/A, Borobazar Road, Odudur Rahman | 2019-07-31 | NQ1009 | 11.3 | 419 | 11.3 | 420 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8184 | 575.9997 | 119.0622
SYL-N.1.RR.225.1 | 24544239152292 | Amborkhana, Borobazar R/A, Khastobir Madrasha Road, H# 18 | 2019-07-31 | NQ1009 | 3.8 | 421 | 3.8 | 422 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8184 | 575.9997 | 40.0386
SYL-N.1.RR.226.1 | 24544069152349 | Amborkhana, Borobazar R/A, Khastobir Madrasha Road, Bondhon-E-29 | 2019-07-31 | NQ1009 | 9.2 | 423 | 9.2 | 424 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8184 | 575.9997 | 96.9356
SYL-N.1.RR.227.1 | 24543719152367 | Amborkhana, Borobazar R/A, Khastobir Madrasha Road, Abdul Mojid | 2019-07-31 | NQ1009 | 6.9 | 425 | 6.9 | 426 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 8184 | 575.9997 | 72.7017
SYL-N.1.RR.228.1 | 24543829152359 | Amborkhana, Borobazar R/A, Khastobir Madrasha Road, Muslima Khatun | 2019-07-31 | NQ1009 | 5 | 427 | 5 | 428 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 8184 | 575.9997 | 52.6824
SYL-N.1.RR.229.1 | 24544059152386 | Amborkhana, Borobazar R/A, Khastobir Madrasha Road, Hamim Villa | 2019-07-31 | NQ1009 | 12.2 | 429 | 12.4 | 430 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8184 | 575.9997 | 130.6524
SYL-N.1.RR.230.1 | 24543519152198 | Mojumdari, Airport Road, Hazi Taris Ali, H# 155 | 2019-08-01 | NQ1009 | 6.3 | 444 | 6.3 | 445 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8184 | 575.9997 | 66.3798
SYL-N.1.RR.231.1 | 24543599152198 | Mojumdari, Airport Road, Sajid Villa, Kefayetullah, H# 156 | 2019-08-01 | NQ1009 | 10.5 | 446 | 10.5 | 447 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8184 | 575.9997 | 110.6331
SYL-N.1.RR.232.1 | 24543599152198 | Mojumdari, Airport Road, Sajid Villa, Liyakot Ali, H# 156 | 2019-08-01 | NQ1009 | 13.4 | 448 | 13.4 | 449 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 8184 | 575.9997 | 141.1888
SYL-N.1.RR.233.1 | 24542899152167 | Amborkhana, Airport Road, Mahmudabad, H# 160 | 2019-08-01 | NQ1009 | 14.6 | 450 | 14.6 | 451 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 8184 | 575.9997 | 153.8326
SYL-N.1.RR.234.1 | 24542899152177 | Amborkhana, Airport Road, Mahmudabad, Britinia Samana | 2019-08-01 | NQ1009 | 10.4 | 452 | 10.4 | 453 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8184 | 575.9997 | 109.5794
SYL-N.1.RR.235.1 | 24542899152177 | Amborkhana, Airport Road, Mahmudabad, Britinia Samana | 2019-08-01 | NQ1009 | 10.4 | 454 | 10.5 | 455 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8184 | 575.9997 | 110.6331
SYL-N.1.RR.236.1 | 24542659152173 | Amborkhana, Airport Road, Banashsre R/A, Afiya Chowdhury, H# 11 | 2019-08-01 | NQ1009 | 7.9 | 458 | 7.9 | 459 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 8184 | 575.9997 | 83.2382
SYL-N.1.RR.237.1 | 24542569152181 | Amborkhana, Airport Road, Banashsre R/A, Dr. Hadi Chowdhury | 2019-08-01 | NQ1009 | 10.4 | 460 | 10.4 | 461 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8184 | 575.9997 | 109.5794
SYL-N.1.RR.238.1 | 24542329152130 | Amborkhana, Airport Road, Golden Tower | 2019-08-01 | NQ1009 | 10.3 | 462 | 10.3 | 463 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8160 | 599.9997 | 108.5258
SYL-N.1.RR.239.1 | 24542329152130 | Amborkhana, Airport Road, Golden Tower | 2019-08-01 | NQ1009 | 12.3 | 464 | 12.3 | 465 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 8160 | 599.9997 | 129.5987
SYL-N.1.RR.240.1 | 24542329152130 | Amborkhana, Airport Road, Golden Tower | 2019-08-01 | NQ1009 | 9.1 | 466 | 9.1 | 467 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8160 | 599.9997 | 95.882
SYL-N.1.RR.240.2 | 24542329152130 | Amborkhana, Airport Road, Golden Tower | 2022-04-25 | LU1001 | 20.3 | 184 | 20.3 | 185 | 2022-04-25 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 20.3 | 20.3 | 1.218 | 1.218 | 0.0007168 | 100% | 0% | 1.218 | 1.218 | 0.0011869 | 28 | 0.024417 | 0.024417 |  | 0 | 0 | 5424 | 599.9997 | 147.0864
SYL-N.1.RR.241.1 | 24542329152130 | Amborkhana, Airport Road, Golden Tower | 2019-08-01 | NQ1009 | 6.1 | 469 | 6.5 | 470 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 8160 | 599.9997 | 68.4871
SYL-N.1.RR.242.1 | 24542329152130 | Amborkhana, Airport Road, Golden Tower | 2019-08-01 | NQ1009 | 11.9 | 471 | 11.9 | 472 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8160 | 599.9997 | 125.3841
SYL-N.1.RR.243.1 | 24551849152211 | Airport Road, Lakkatura, Mondop Para, Kamal Uddin | 2019-08-01 | NQ1009 | 9 | 473 | 9 | 474 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8184 | 575.9997 | 94.8283
SYL-N.1.RR.244.1 | 24544349152166 | East Pirmoholla, Lechubagan, Provati-12/A | 2019-08-03 | NQ1009 | 8.8 | 490 | 8.8 | 491 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8136 | 623.9997 | 92.721
SYL-N.1.RR.245.1 | 24544329152151 | East Pirmoholla, Lechubagan, Provati-60/B | 2019-08-03 | NQ1009 | 11 | 492 | 11 | 493 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8136 | 623.9997 | 115.9013
SYL-N.1.RR.246.1 | 24544389152150 | East Pirmoholla, Lechubagan, Provati-16 | 2019-08-03 | NQ1009 | 10.6 | 494 | 10.6 | 495 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8136 | 623.9997 | 111.6867
SYL-N.1.RR.247.1 | 24544299152142 | East Pirmoholla, Lechubagan, Provati-18 | 2019-08-03 | NQ1009 | 5.8 | 496 | 5.6 | 497 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 8136 | 623.9997 | 59.0043
SYL-N.1.RR.248.1 | 24544189152129 | East Pirmoholla, Lechubagan, Provati-65 | 2019-08-03 | NQ1009 | 10.3 | 498 | 10.3 | 499 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8136 | 623.9997 | 108.5258
SYL-N.1.RR.248.2 | 24544189152129 | East Pirmoholla, Lechubagan, Provati-65 | 2021-02-17 | NQ1007 | 2.7 | 204 | 2.7 | 205 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 8136 | 623.9997 | 28.4485
SYL-N.1.RR.249.1 | 24544269152100 | East Pirmoholla, Lechubagan, Minhaz Mia | 2019-08-03 | NQ1009 | 13 | 500 | 13 | 501 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8136 | 623.9997 | 136.9743
SYL-N.1.RR.250.1 | 24544379152125 | East Pirmoholla, Lechubagan, Aftab, Provati-24 | 2019-08-03 | NQ1009 | 9.5 | 502 | 9.5 | 503 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8136 | 623.9997 | 100.0966
SYL-N.1.RR.251.1 | 24545149153437 | Shaparan ,North Baluchor ,Al-Isleh ,Block-c ,Afia | 2019-07-29 | NQ1009 | 11.5 | 370 | 11.5 | 371 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8160 | 599.9997 | 121.1695
SYL-N.1.RR.252.1 | 24544829153423 | Shaparan ,North Baluchor ,Al-Isleh ,Block-c ,Khejir Mia | 2019-07-29 | NQ1009 | 11.5 | 372 | 11.5 | 373 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8160 | 599.9997 | 121.1695
SYL-N.1.RR.253.1 | 24544469153403 | Shaparan ,North Baluchor ,Al-Isleh ,Block-c ,House#299 | 2019-07-29 | NQ1009 | 11.1 | 375 | 11.1 | 376 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8160 | 599.9997 | 116.9549
SYL-N.1.RR.254.1 | 24544539153395 | Shaparan ,North Baluchor ,Al-Isleh ,Block-c ,House#185 | 2019-07-29 | NQ1009 | 9.7 | 377 | 9.7 | 378 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8160 | 599.9997 | 102.2039
SYL-N.1.RR.255.1 | 24544499153390 | Shaparan ,North Baluchor ,Al-Isleh ,Block-c ,House#186/A | 2019-07-29 | NQ1009 | 5.4 | 379 | 5.4 | 380 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 8160 | 599.9997 | 56.897
SYL-N.1.RR.256.1 | 24544579153389 | Shaparan ,North Baluchor ,Al-Isleh ,Block-c ,House#204 | 2019-07-29 | NQ1009 | 2.3 | 381 | 2.3 | 382 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8160 | 599.9997 | 24.2339
SYL-N.1.RR.257.1 | 24544639153393 | Shaparan ,North Baluchor ,Al-Isleh ,Block-c ,House#206 | 2019-07-29 | NQ1009 | 8.5 | 383 | 8.5 | 384 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 8160 | 599.9997 | 89.5601
SYL-N.1.RR.258.1 | 24542329153312 | Shaparan ,Arambag R/A ,Road#02 ,Block-c ,House#26 | 2019-07-29 | NQ1009 | 10.2 | 385 | 10.2 | 386 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8160 | 599.9997 | 107.4721
SYL-N.1.RR.258.2 | 24542329153312 | Shaparan ,Arambag R/A ,Road#02 ,Block-c ,House#26 | 2022-12-07 | NQ1007 | 10 | 274 | 10 | 275 | 2022-12-07 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 0 | 599.9997 | 7.2168
SYL-N.1.RR.259.1 | 24542809153334 | Shaparan ,Arambag R/A ,Road#02 ,Block-c ,House#49 | 2019-07-29 | NQ1009 | 10.8 | 387 | 10.8 | 388 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8160 | 599.9997 | 113.794
SYL-N.1.RR.260.1 | 24542319152223 | Ambarkhana, Boro Bazer Road, Boro bazer R/A, H # 46/5 | 2019-07-30 | NQ1009 | 80.8 | 403 | 80.8 | 404 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 80.8 | 80.8 | 4.848 | 4.848 | 0.0007168 | 100% | 0% | 4.848 | 4.848 | 0.0011869 | 28 | 0.097186 | 0.097186 |  | 0 | 0 | 8184 | 575.9997 | 851.3477
SYL-N.1.RR.261.1 | 24542739152237 | Ambarkhana, Boro Bazer Road, Boro bazer R/A, H # 66 | 2019-07-30 | NQ1009 | 5.4 | 405 | 5.4 | 406 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 8184 | 575.9997 | 56.897
SYL-N.1.RR.262.1 | 24542759152247 | Ambarkhana, Boro Bazer Road, Boro bazer R/A, H # 64 | 2019-07-30 | NQ1009 | 10.2 | 407 | 10.2 | 408 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8184 | 575.9997 | 107.4721
SYL-N.1.RR.263.1 | 24542779152266 | Ambarkhana, Boro Bazer Road, Boro bazer R/A, H # 58 | 2019-07-30 | NQ1009 | 9.7 | 409 | 9.7 | 410 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8184 | 575.9997 | 102.2039
SYL-N.1.RR.264.1 | 24543609152215 | Ambarkhana, Boro Bazer Road, Boro bazer R/A, H # 20 | 2019-07-30 | NQ1009 | 12 | 411 | 12 | 412 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8184 | 575.9997 | 126.4378
SYL-N.1.RR.265.1 | 24544089152220 | Ambarkhana,Boro Bazer Road, Boro Bazer R/A, H # 39 | 2019-07-31 | NQ1009 | 15 | 432 | 15 | 433 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8184 | 575.9997 | 158.0472
SYL-N.1.RR.266.1 | 24544199152238 | Ambarkhana,Boro Bazer Road, Boro Bazer R/A, H # 31/C | 2019-07-31 | NQ1009 | 3.8 | 434 | 3.8 | 435 | 2022-01-01 | [9 empty] | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0
SYL-N.1.RR.267.1 | 24544699152212 | Khasdabir, Airport Road, Torongo R/A, H # 43 | 2019-07-31 | NQ1009 | 10.2 | 436 | 10.1 | 437 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8184 | 575.9997 | 106.4185
SYL-N.1.RR.268.1 | 24544379152223 | Khasdabir, Airport Road, Torongo R/A, H # 1/7 | 2019-07-31 | NQ1009 | 12.3 | 438 | 12.3 | 439 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 8184 | 575.9997 | 129.5987
SYL-N.1.RR.268.2 | 24544379152223 | Khasdabir, Airport Road, Torongo R/A, H # 1/7 | 2021-11-04 | NQ1007 | 12.4 | 81 | 12.4 | 82 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8184 | 575.9997 | 130.6524
SYL-N.1.RR.269.1 | 24544369152221 | Khasdabir, Airport Road, Torongo R/A, H # 5/3 | 2019-07-31 | NQ1009 | 10.2 | 440 | 9.9 | 441 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8184 | 575.9997 | 104.3112
SYL-N.1.RR.270.1 | 24543999152193 | Khasdabir, Airport Road, Torongo R/A, H # 15 | 2019-07-31 | NQ1009 | 12.2 | 442 | 12.2 | 443 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 8184 | 575.9997 | 128.5451
SYL-N.1.RR.271.1 | 24543299152116 | Mojumdar Bari , Airport Road, ward #04 ,House #77 | 2019-08-01 | NQ1009 | 10.7 | 475 | 10.5 | 476 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8160 | 599.9997 | 110.6331
SYL-N.1.RR.272.1 | 24543459152113 | Mojumdar Bari , Airport Road, ward #04 ,House #84 | 2019-08-01 | NQ1009 | 9 | 477 | 9 | 478 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8160 | 599.9997 | 94.8283
SYL-N.1.RR.273.1 | 24543509152108 | Mojumdar Bari , Airport Road, ward #04 ,House #83 | 2019-08-01 | NQ1009 | 3.6 | 479 | 3.7 | 480 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 8160 | 599.9997 | 38.985
SYL-N.1.RR.274.1 | 24543339152098 | Mojumdar Bari , Airport Road, ward #04 ,House #18 | 2019-08-01 | NQ1009 | 7.5 | 481 | 7.5 | 482 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 8160 | 599.9997 | 79.0236
SYL-N.1.RR.275.1 | 24543309152093 | Airport Road ,Mojumdar Bari ,ward #04 ,House #24 | 2019-08-01 | NQ1009 | 4.1 | 483 | 4.1 | 484 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 8160 | 599.9997 | 43.1996
SYL-N.1.RR.276.1 | 24543309152093 | Airport Road ,Mojumdar Bari ,ward #04 ,House #24 | 2019-08-01 | NQ1009 | 71.6 | 485 | 71.6 | 486 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 71.6 | 71.6 | 4.296 | 4.296 | 0.0007168 | 100% | 0% | 4.296 | 4.296 | 0.0011869 | 28 | 0.08612 | 0.08612 |  | 0 | 0 | 8160 | 599.9997 | 754.4121
SYL-N.1.RR.277.1 | 24543009152084 | Airport Road ,Mojumdar Bari ,ward #04 ,House #38/1 | 2019-08-01 | NQ1009 | 21.6 | 487 | 21.3 | 488 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 8160 | 599.9997 | 224.4271
SYL-N.1.RR.278.1 | 24545199152161 | Sylhet Sodor ,Syead Mogni Road ,Ward #06 , H #4/11 | 2019-08-03 | NQ1009 | 11 | 511 | 11 | 512 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8136 | 623.9997 | 115.9013
SYL-N.1.RR.279.1 | 24545359152164 | Sylhet Sodor ,Syead Mogni Road ,Ward #06 , H #4/8 | 2019-08-03 | NQ1009 | 11.2 | 513 | 11.2 | 514 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8136 | 623.9997 | 118.0086
SYL-N.1.RR.280.1 | 24545469152141 | Sylhet Sodor ,Syead Mogni Road ,Ward #06 , H #18/B | 2019-08-03 | NQ1009 | 9.8 | 515 | 9.8 | 516 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8136 | 623.9997 | 103.2575
SYL-N.1.RR.281.1 | 24545539152133 | Sylhet Sodor ,Syead Mogni Road ,Ward #06 , H #18 | 2019-08-03 | NQ1009 | 10.5 | 517 | 10.5 | 518 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8136 | 623.9997 | 110.6331
SYL-N.1.RR.282.1 | 24545579152189 | Sylhet Sodor ,Elashkandi Road ,,Elashkand Para ,Ward #06 ,H#4 | 2019-08-03 | NQ1009 | 10.1 | 519 | 10.2 | 520 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8136 | 623.9997 | 107.4721
SYL-N.1.RR.283.1 | 24545249152182 | Sylhet Sodor ,Elashkandi Road ,,Elashkand Para ,Ward #06 ,H#4/D | 2019-08-03 | NQ1009 | 16.1 | 521 | 16.1 | 522 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 8136 | 623.9997 | 169.6373
SYL-N.1.RR.284.1 | 24545499152203 | Sylhet Sodor ,Elashkandi Road ,,Elashkand Para ,Ward #06 ,H#44 | 2019-08-03 | NQ1009 | 6.4 | 523 | 6.4 | 524 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8136 | 623.9997 | 67.4335
SYL-N.1.RR.285.1 | 24545279152229 | Sylhet Sodor ,Elashkandi Road ,,Elashkand Para ,Ward #06 ,H#5/B | 2019-08-03 | NQ1009 | 15.2 | 525 | 15.2 | 526 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 8136 | 623.9997 | 160.1545
SYL-N.1.RR.286.1 | 24545069152224 | Sylhet Sodor ,Airport Road , Ward #06 ,H #40 | 2019-08-03 | NQ1009 | 22.9 | 527 | 22.9 | 528 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 22.9 | 22.9 | 1.374 | 1.374 | 0.0007168 | 100% | 0% | 1.374 | 1.374 | 0.0011869 | 28 | 0.027544 | 0.027544 |  | 0 | 0 | 8136 | 623.9997 | 241.2854
SYL-N.1.RR.287.1 | 24544879152169 | Sylhet Sodor ,Mojumdari Para ,Torong R/A ,H #4/9/B | 2019-08-03 | NQ1009 | 9.3 | 529 | 9.3 | 530 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 8136 | 623.9997 | 97.9893
SYL-N.1.RR.288.1 | 24544989152170 | Sylhet Sodor ,Mojumdari Para ,Torong R/A ,H #8/7 | 2019-08-03 | NQ1009 | 3.2 | 531 | 3.2 | 532 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 8136 | 623.9997 | 33.7167
SYL-N.1.RR.289.1 | 24544989152170 | Sylhet Sodor ,Mojumdari Para ,Torong R/A ,H #4/8/C | 2019-08-03 | NQ1009 | 5.7 | 535 | 5.7 | 536 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 8136 | 623.9997 | 60.0579
SYL-N.1.RR.289.2 | 24544989152170 | Sylhet Sodor ,Mojumdari Para ,Torong R/A ,H #4/8/C | 2019-08-03 | NQ1009 | 71.7 | 537 | 71.7 | 538 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 71.7 | 71.7 | 4.302 | 4.302 | 0.0007168 | 100% | 0% | 4.302 | 4.302 | 0.0011869 | 28 | 0.08624 | 0.08624 |  | 0 | 0 | 8136 | 623.9997 | 755.4657
SYL-N.1.RR.290.1 | 24544199152179 | Sylhet Sodor , Airport Road , Lichu Bagan R/A ,H # 18 | 2019-08-04 | NQ1009 | 8.4 | 562 | 8.4 | 563 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8136 | 623.9997 | 88.5064
SYL-N.1.RR.291.1 | 24544199152179 | Sylhet Sodor , Airport Road , Lichu Bagan R/A ,H # 16 | 2019-08-04 | NQ1009 | 4.9 | 564 | 4.9 | 565 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 8136 | 623.9997 | 51.6288
SYL-N.1.RR.292.1 | 24545859152258 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , H#64 | 2019-08-04 | NQ1009 | 1.9 | 566 | 1.8 | 567 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 8136 | 623.9997 | 18.9657
SYL-N.1.RR.293.1 | 24545889152259 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , Abdul Kayum | 2019-08-04 | NQ1009 | 23.4 | 568 | 23.4 | 569 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 23.4 | 23.4 | 1.404 | 1.404 | 0.0007168 | 100% | 0% | 1.404 | 1.404 | 0.0011869 | 28 | 0.028145 | 0.028145 |  | 0 | 0 | 8136 | 623.9997 | 246.5537
SYL-N.1.RR.293.2 | 24545889152259 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , Abdul Kayum | 2021-11-02 | NQ1007 | 6.5 | 77 | 6.6 | 78 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 8136 | 623.9997 | 69.5408
SYL-N.1.RR.294.1 | 24550099152264 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , H #72 | 2019-08-04 | NQ1009 | 8.3 | 570 | 8.3 | 571 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 8136 | 623.9997 | 87.4528
SYL-N.1.RR.295.1 | 24550379152232 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , H #75 | 2019-08-04 | NQ1009 | 9.9 | 572 | 9.9 | 573 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8136 | 623.9997 | 104.3112
SYL-N.1.RR.296.1 | 24550789152234 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , Saru Mia | 2019-08-04 | NQ1009 | 8.9 | 574 | 8.9 | 575 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8136 | 623.9997 | 93.7747
SYL-N.1.RR.297.1 | 24550729152230 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , H#184/5 | 2019-08-04 | NQ1009 | 9.9 | 576 | 9.9 | 577 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8136 | 623.9997 | 104.3112
SYL-N.1.RR.298.1 | 24550729152225 | Sylhet Sodor , Airport Road ,Chwkhedakhi , Rindhonu R/A , H#185/5 | 2019-08-04 | NQ1009 | 1.4 | 578 | 1.4 | 579 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 8136 | 623.9997 | 14.7511
SYL-N.1.RR.299.1 | 24545259151530 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,H #40 | 2019-08-05 | NQ1009 | 10.5 | 580 | 10.5 | 581 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8088 | 671.9997 | 110.6331
SYL-N.1.RR.300.1 | 24545269151500 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,Boktia Bagum | 2019-08-05 | NQ1009 | 8.4 | 582 | 8.4 | 583 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8088 | 671.9997 | 88.5064
SYL-N.1.RR.301.1 | 24542859152025 | Housing Estate R/A, Rd # 2, H # 111 | 2019-08-04 | MP1006 | 11 | 469 | 11 | 470 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8160 | 599.9997 | 115.9013
SYL-N.1.RR.302.1 | 24542859152025 | Housing Estate R/A, Rd # 2, H # 111 | 2019-08-04 | MP1006 | 15.9 | 471 | 16 | 472 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 8160 | 599.9997 | 168.5837
SYL-N.1.RR.303.1 | 24550719151507 | Subid Bazar, Bonkolapara, Nurani R/A, H # 114/3 | 2019-08-05 | MP1006 | 22.3 | 515 | 22.3 | 516 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 8016 | 743.9997 | 234.9635
SYL-N.1.RR.304.1 | 24550729151487 | Subid Bazar, Bonkolapara, Nurani R/A, Azij Hoque | 2019-08-05 | MP1006 | 13.9 | 517 | 13.5 | 518 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 8016 | 743.9997 | 142.2425
SYL-N.1.RR.304.2 | 24550729151487 | Subid Bazar, Bonkolapara, Nurani R/A, Azij Hoque | 2021-02-18 | NQ1007 | 4.8 | 206 | 4.8 | 207 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8016 | 743.9997 | 50.5751
SYL-N.1.RR.305.1 | 24550609151480 | Subid Bazar, Bonkolapara, Nurani R/A, H # 109 | 2019-08-05 | MP1006 | 9.9 | 519 | 9.9 | 520 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8016 | 743.9997 | 104.3112
SYL-N.1.RR.306.1 | 24550359151481 | Subid Bazar, Bonkolapara, Nurani R/A, H # 98/3 | 2019-08-05 | MP1006 | 9.5 | 521 | 9.1 | 522 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8016 | 743.9997 | 95.882
SYL-N.1.RR.307.1 | 24550589151480 | Subid Bazar, Bonkolapara, Nurani R/A, H # 108/2 | 2019-08-05 | MP1006 | 2.4 | 523 | 2.4 | 524 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 8016 | 743.9997 | 25.2876
SYL-N.1.RR.308.1 | 24550619151462 | Subid Bazar, Bonkolapara, Nurani R/A, H # 103 | 2019-08-05 | MP1006 | 10.8 | 525 | 10.8 | 526 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8016 | 743.9997 | 113.794
SYL-N.1.RR.309.1 | 24550839151488 | Subid Bazar, Bonkolapara, Nurani R/A, H # 120/1 | 2019-08-05 | MP1006 | 6.5 | 527 | 6.5 | 528 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 8016 | 743.9997 | 68.4871
SYL-N.1.RR.310.1 | 24551019151493 | Subid Bazar, Bonkolapara, Nurani R/A, H # 131 | 2019-08-05 | MP1006 | 10.8 | 529 | 10.8 | 530 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8016 | 743.9997 | 113.794
SYL-N.1.RR.311.1 | 24550949151528 | Subid Bazar, Bonkolapara, Nurani R/A, H # 127/12 | 2019-08-05 | MP1006 | 10.7 | 531 | 10.7 | 532 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8016 | 743.9997 | 112.7403
SYL-N.1.RR.312.1 | 24545099151319 | Subid Bazar, Soyaf Khan Road, Agrani-71 | 2019-08-06 | MP1006 | 12.8 | 553 | 12.8 | 554 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8016 | 743.9997 | 134.867
SYL-N.1.RR.313.1 | 24545099151319 | Subid Bazar, Soyaf Khan Road, Agrani-91 | 2019-08-06 | MP1006 | 16.2 | 555 | 16.2 | 556 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 8016 | 743.9997 | 170.691
SYL-N.1.RR.314.1 | 24544839151320 | Subid Bazar, Soyaf Khan Road, Agrani-68/1 | 2019-08-06 | MP1006 | 8.8 | 557 | 8.8 | 558 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8016 | 743.9997 | 92.721
SYL-N.1.RR.314.2 | 24544839151320 | Subid Bazar, Soyaf Khan Road, Agrani-68/1 | 2021-02-18 | NQ1003 | 11.8 | 272 | 11.5 | 273 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8016 | 743.9997 | 121.1695
SYL-N.1.RR.315.1 | 24544779151299 | Subid Bazar, Soyaf Khan Road, Agrani-58 | 2019-08-06 | MP1006 | 14.4 | 559 | 14.4 | 560 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 8016 | 743.9997 | 151.7253
SYL-N.1.RR.316.1 | 24544529151293 | Subid Bazar, Soyaf Khan Road, Agrani-44/2 | 2019-08-06 | MP1006 | 3.8 | 561 | 3.8 | 562 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8016 | 743.9997 | 40.0386
SYL-N.1.RR.317.1 | 24544729151224 | Subid Bazar, Londoni Road, H # 164 | 2019-08-07 | LX1011 | 15.5 | 21 | 15.5 | 22 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 15.5 | 15.5 | 0.93 | 0.93 | 0.0007168 | 100% | 0% | 0.93 | 0.93 | 0.0011869 | 28 | 0.018643 | 0.018643 |  | 0 | 0 | 8016 | 743.9997 | 163.3155
SYL-N.1.RR.318.1 | 24550849150575 | Pathantula, Korer Para, Mohona, Shushil Chandra Dev | 2019-08-08 | LX1011 | 14 | 45 | 14 | 46 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 8016 | 743.9997 | 147.5107
SYL-N.1.RR.319.1 | 24550849150575 | Pathantula, Korer Para, Mohona-83 | 2019-08-08 | LX1011 | 3.7 | 47 | 3.7 | 48 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 8016 | 743.9997 | 38.985
SYL-N.1.RR.320.1 | 24551509150579 | Pathantula, Korerpara, Mohona R/A, Block-B, H # 31/1 | 2019-08-17 | LX1011 | 2.7 | 55 | 2.7 | 56 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 8016 | 743.9997 | 28.4485
SYL-N.1.RR.321.1 | 24551469150597 | Pathantula, Korerpara, Mohona R/A, Block-B, H # 31 | 2019-08-17 | LX1011 | 4.6 | 63 | 4.6 | 64 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 8016 | 743.9997 | 48.4678
SYL-N.1.RR.322.1 | 24551529150599 | Pathantula, Korerpara, Mohona R/A, Block-B, H # 59 | 2019-08-17 | LX1011 | 11.9 | 65 | 11.9 | 66 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8016 | 743.9997 | 125.3841
SYL-N.1.RR.323.1 | 24551499151002 | Pathantula, Korerpara, Mohona R/A, Block-B, Nazma Begum | 2019-08-17 | LX1011 | 13 | 67 | 13 | 68 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8016 | 743.9997 | 136.9743
SYL-N.1.RR.324.1 | 24534929151482 | Lamabazar, Saraspur, Sayanir R/A, H # 14 | 2019-08-18 | MP1006 | 17.2 | 5 | 17.2 | 6 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 8256 | 503.9997 | 181.2275
SYL-N.1.RR.324.2 | 24534929151482 | Lamabazar, Saraspur, Sayanir R/A, H # 14 | 2020-10-27 | NQ1009 | 7.3 | 191 | 7.3 | 192 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8256 | 503.9997 | 76.9163
SYL-N.1.RR.325.1 | 24534929151482 | Lamabazar, Saraspur, Sayanir R/A, H # 14 | 2019-08-18 | MP1006 | 11.3 | 7 | 11.3 | 8 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8256 | 503.9997 | 119.0622
SYL-N.1.RR.326.1 | 24534929151482 | Lamabazar, Saraspur, Sayanir R/A, H # 14 | 2019-08-18 | MP1006 | 15.7 | 9 | 15.7 | 10 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 8256 | 503.9997 | 165.4228
SYL-N.1.RR.326.2 | 24534929151482 | Lamabazar, Saraspur, Sayanir R/A, H # 14 | 2020-10-27 | NQ1009 | 8.5 | 194 | 8.5 | 195 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 8256 | 503.9997 | 89.5601
SYL-N.1.RR.327.1 | 24534929151482 | Lamabazar, Saraspur, Sayanir R/A, H # 14 | 2019-08-18 | MP1006 | 12.1 | 11 | 12.1 | 12 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 8256 | 503.9997 | 127.4914
SYL-N.1.RR.328.1 | 24534889151484 | Lamabazar, Saraspur, Sayanir R/A, H # 13 | 2019-08-19 | MP1006 | 21.2 | 13 | 21.2 | 14 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 21.2 | 21.2 | 1.272 | 1.272 | 0.0007168 | 100% | 0% | 1.272 | 1.272 | 0.0011869 | 28 | 0.025499 | 0.025499 |  | 0 | 0 | 8256 | 503.9997 | 223.3734
SYL-N.1.RR.329.1 | 24534869151484 | Lamabazar, Saraspur, Sayanir R/A, H # 13/2 | 2019-08-19 | MP1006 | 16.3 | 15 | 16.3 | 16 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 8256 | 503.9997 | 171.7446
SYL-N.1.RR.330.1 | 24534869151484 | Lamabazar, Saraspur, Sayanir R/A, H # 13/3 | 2019-08-19 | MP1006 | 13.8 | 17 | 13.8 | 18 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 8256 | 503.9997 | 145.4034
SYL-N.1.RR.331.1 | 24534819151509 | Dariyapara, Meghna R/A, Block-B, H # 65 | 2019-08-19 | MP1006 | 15 | 19 | 15 | 20 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8256 | 503.9997 | 158.0472
SYL-N.1.RR.332.1 | 24534819151509 | Dariyapara, Meghna R/A, Block-B, H # 83/1 | 2019-08-19 | MP1006 | 13.1 | 21 | 13.1 | 22 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 8256 | 503.9997 | 138.0279
SYL-N.1.RR.333.1 | 24534729151512 | Dariyapara, Meghna R/A, Block-C, H # 20/A | 2019-08-19 | MP1006 | 14.7 | 23 | 14.7 | 24 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 8256 | 503.9997 | 154.8863
SYL-N.1.RR.334.1 | 24533829151462 | Mirza Jangle, Ramer Dighirpar, Swapnil-24/Gha | 2019-08-19 | NQ1003 | 80.2 | 89 | 80.2 | 90 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 80.2 | 80.2 | 4.812 | 4.812 | 0.0007168 | 100% | 0% | 4.812 | 4.812 | 0.0011869 | 28 | 0.096464 | 0.096464 |  | 0 | 0 | 8256 | 503.9997 | 845.0258
SYL-N.1.RR.335.1 | 24533559151479 | Mirza Jangle, Ramer Dighirpar, Swapnil-33 | 2019-08-19 | NQ1003 | 16.8 | 91 | 16.8 | 92 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 8256 | 503.9997 | 177.0129
SYL-N.1.RR.336.1 | 24533649151494 | Mirza Jangle, Ramer Dighirpar, Swapnil-43 | 2019-08-19 | NQ1003 | 11.5 | 94 | 11.5 | 95 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8256 | 503.9997 | 121.1695
SYL-N.1.RR.337.1 | 24533469151506 | Mirza Jangle, Ramer Dighirpar, Swapnil-45 | 2019-08-19 | NQ1003 | 10.7 | 96 | 10.7 | 97 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8256 | 503.9997 | 112.7403
SYL-N.1.RR.338.1 | 24541839152415 | Kazitula, Ucha Sharak R/A, H # 111 | 2019-08-24 | MP1006 | 23.1 | 119 | 22.8 | 120 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 22.8 | 22.8 | 1.368 | 1.368 | 0.0007168 | 100% | 0% | 1.368 | 1.368 | 0.0011869 | 28 | 0.027424 | 0.027424 |  | 0 | 0 | 8184 | 575.9997 | 240.2318
SYL-N.1.RR.339.1 | 24541909152417 | Kazitula, Ucha Sharak , H # 114 | 2019-08-24 | MP1006 | 9.4 | 121 | 9.4 | 122 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8184 | 575.9997 | 99.0429
SYL-N.1.RR.340.1 | 24541929152425 | Kazitula, Ucha Sharak , H # 117 | 2019-08-24 | MP1006 | 13.1 | 123 | 13.1 | 124 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 8184 | 575.9997 | 138.0279
SYL-N.1.RR.341.1 | 24541919152406 | Kazitula, Ucha Sharak , Anower | 2019-08-24 | MP1006 | 4.6 | 125 | 4.6 | 126 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 8184 | 575.9997 | 48.4678
SYL-N.1.RR.342.1 | 24541779152452 | Kazitula, Ucha Sharak , Ontorongo R/A, H # 53, Abdul Motin | 2019-08-24 | MP1006 | 13 | 127 | 13 | 128 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8184 | 575.9997 | 136.9743
SYL-N.1.RR.343.1 | 24535029152165 | Hawa Para, Dishari-34 | 2019-08-25 | MP1006 | 74.4 | 145 | 74.4 | 146 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 74.4 | 74.4 | 4.464 | 4.464 | 0.0007168 | 100% | 0% | 4.464 | 4.464 | 0.0011869 | 28 | 0.089488 | 0.089488 |  | 0 | 0 | 8256 | 503.9997 | 783.9142
SYL-N.1.RR.344.1 | 24535029152165 | Hawa Para, Dishari-35 | 2019-08-25 | MP1006 | 11.5 | 147 | 11.1 | 148 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8256 | 503.9997 | 116.9549
SYL-N.1.RR.345.1 | 24534929152167 | Hawa Para, Dishari-144 | 2019-08-25 | MP1006 | 15.3 | 149 | 15.3 | 150 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 8256 | 503.9997 | 161.2082
SYL-N.1.RR.346.1 | 24534789152172 | Hawa Para Jame Mosjid | 2019-08-25 | MP1006 | 18.4 | 151 | 18.4 | 152 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 8256 | 503.9997 | 193.8713
SYL-N.1.RR.347.1 | 24534579152163 | Hawa Para, Dishari-15 | 2019-08-25 | MP1006 | 23.7 | 153 | 23.7 | 154 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 23.7 | 23.7 | 1.422 | 1.422 | 0.0007168 | 100% | 0% | 1.422 | 1.422 | 0.0011869 | 28 | 0.028506 | 0.028506 |  | 0 | 0 | 8256 | 503.9997 | 249.7146
SYL-N.1.RR.348.1 | 24534579152163 | Hawa Para, Dishari-14 | 2019-08-25 | MP1006 | 14.6 | 155 | 14.6 | 156 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 8256 | 503.9997 | 153.8326
SYL-N.1.RR.349.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 11 | 157 | 11 | 158 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8256 | 503.9997 | 115.9013
SYL-N.1.RR.350.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 23.7 | 159 | 23.7 | 160 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 23.7 | 23.7 | 1.422 | 1.422 | 0.0007168 | 100% | 0% | 1.422 | 1.422 | 0.0011869 | 28 | 0.028506 | 0.028506 |  | 0 | 0 | 8256 | 503.9997 | 249.7146
SYL-N.1.RR.351.1 | 24550929151586 | West Pir Moholla, Md. Azizur Rahman | 2019-08-05 | MP1006 | 25.9 | 497 | 25.9 | 498 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 25.9 | 25.9 | 1.554 | 1.554 | 0.0007168 | 100% | 0% | 1.554 | 1.554 | 0.0011869 | 28 | 0.031152 | 0.031152 |  | 0 | 0 | 8136 | 623.9997 | 272.8949
SYL-N.1.RR.352.1 | 24551109151560 | West Pir Moholla, Madrasa Road, H # 141/44, Abdul Kalam | 2019-08-05 | MP1006 | 11.2 | 499 | 11.2 | 500 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8136 | 623.9997 | 118.0086
SYL-N.1.RR.353.1 | 24551249151563 | West Pir Moholla, Madrasa Road, H # 141/46, Sumon Monjil | 2019-08-05 | MP1006 | 2.6 | 501 | 2.6 | 502 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 8136 | 623.9997 | 27.3949
SYL-N.1.RR.354.1 | 24551279151560 | West Pir Moholla, Madrasa Road, H # 141/47-48, Md Tera Mia | 2019-08-05 | MP1006 | 16.4 | 505 | 17.3 | 506 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 8136 | 623.9997 | 182.2811
SYL-N.1.RR.355.1 | 24551279151560 | West Pir Moholla, Madrasa Road, H # 141/47-48, Md Tera Mia | 2019-08-05 | MP1006 | 2.5 | 507 | 2.5 | 508 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 8136 | 623.9997 | 26.3412
SYL-N.1.RR.356.1 | 24551299151561 | West Pir Moholla, Madrasa Road, H # 141/49, Habibur Rahman | 2019-08-05 | MP1006 | 4 | 509 | 4 | 510 | 2022-01-01 | [9 empty] | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0
SYL-N.1.RR.357.1 | 24550899151552 | West Pir Moholla, Madrasa Road, H # 141/36, Hasan Manjil | 2019-08-05 | MP1006 | 3 | 511 | 3 | 512 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 8136 | 623.9997 | 31.6094
SYL-N.1.RR.358.1 | 24550809151548 | West Pir Moholla, Madrasa Road, H # 141/31, Lutfor Rahman | 2019-08-05 | MP1006 | 12.4 | 513 | 12.4 | 514 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8136 | 623.9997 | 130.6524
SYL-N.1.RR.359.1 | 24550099152019 | North Pir Moholla, H # 15/6, Niyamul | 2019-08-06 | MP1006 | 9.9 | 533 | 9.9 | 534 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8136 | 623.9997 | 104.3112
SYL-N.1.RR.359.2 | 24550099152019 | North Pir Moholla, H # 15/6, Niyamul | 2021-02-17 | NQ1003 | 2.3 | 267 | 2.3 | 268 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8136 | 623.9997 | 24.2339
SYL-N.1.RR.360.1 | 24545939151592 | West Pir Moholla, H # 167/2, Hazi Mokhles | 2019-08-06 | MP1006 | 25.4 | 535 | 25.4 | 536 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 25.4 | 25.4 | 1.524 | 1.524 | 0.0007168 | 100% | 0% | 1.524 | 1.524 | 0.0011869 | 28 | 0.030551 | 0.030551 |  | 0 | 0 | 8136 | 623.9997 | 267.6266
SYL-N.1.RR.361.1 | 24550049151584 | West Pir Moholla, H # 167/3, Baitul Ashraf | 2019-08-06 | MP1006 | 11.2 | 537 | 10.3 | 538 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8136 | 623.9997 | 108.5258
SYL-N.1.RR.362.1 | 24550199151599 | West Pir Moholla, H # 178, Khaja Kutir | 2019-08-06 | MP1006 | 14.7 | 539 | 14.7 | 540 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 8136 | 623.9997 | 154.8863
SYL-N.1.RR.363.1 | 24550719152017 | West Pir Moholla, H # 221/B, Nasiruddin Kamal | 2019-08-06 | MP1006 | 23.4 | 541 | 23.4 | 542 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 23.4 | 23.4 | 1.404 | 1.404 | 0.0007168 | 100% | 0% | 1.404 | 1.404 | 0.0011869 | 28 | 0.028145 | 0.028145 |  | 0 | 0 | 8136 | 623.9997 | 246.5537
SYL-N.1.RR.364.1 | 24550909152014 | West Pir Moholla, H # 220/A, Shajalal Palace | 2019-08-06 | MP1006 | 6.8 | 543 | 6.8 | 544 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 8136 | 623.9997 | 71.6481
SYL-N.1.RR.365.1 | 24551169151590 | West Pir Moholla, Madrasa Road, Rd # 03, H # 9, Fahim Monjil | 2019-08-06 | MP1006 | 9.3 | 545 | 9.2 | 546 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8136 | 623.9997 | 96.9356
SYL-N.1.RR.366.1 | 24551249151588 | West Pir Moholla, Madrasa Road, Rd # 03, H #04, Monwar Ali | 2019-08-06 | MP1006 | 7.8 | 547 | 7.8 | 548 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 8136 | 623.9997 | 82.1846
SYL-N.1.RR.367.1 | 24551389152003 | West Pir Moholla, Madrasa Road, Rd # 04, Zillu Mia | 2019-08-06 | MP1006 | 13.6 | 549 | 13.5 | 550 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 8136 | 623.9997 | 142.2425
SYL-N.1.RR.368.1 | 24551369152012 | West Pir Moholla, Madrasa Road, Rd # 04, Shabuddin | 2019-08-06 | MP1006 | 3.7 | 551 | 3.7 | 552 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 8136 | 623.9997 | 38.985
SYL-N.1.RR.369.1 | 24545629151335 | Subid Bazar, Bonkola Para, Nurani-65/14, Shundor Mia | 2019-08-07 | MP1006 | 58.3 | 1 | 56 | 2 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 56 | 56 | 3.36 | 3.36 | 0.0007168 | 100% | 0% | 3.36 | 3.36 | 0.0011869 | 28 | 0.067357 | 0.067357 |  | 0 | 0 | 8016 | 743.9997 | 590.043
SYL-N.1.RR.370.1 | 24545859151329 | Subid Bazar, Borkola Para, Nurani-65/16E, Bondhon House | 2019-08-07 | LX1011 | 2.3 | 19 | 2.3 | 20 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8016 | 743.9997 | 24.2339
SYL-N.1.RR.371.1 | 24550499151543 | West Pir Moholla, Oikotan-156, Tohel Manjil | 2019-08-08 | LX1011 | 4.3 | 25 | 4.3 | 26 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 8136 | 623.9997 | 45.3069
SYL-N.1.RR.372.1 | 24550099151517 | West Pir Moholla, H # 96/1 | 2019-08-08 | LX1011 | 12.3 | 27 | 12.1 | 28 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 8088 | 671.9997 | 127.4914
SYL-N.1.RR.373.1 | 24545869151508 | West Pir Moholla, H # 93/2, Abdul Jabbar Villa | 2019-08-08 | LX1011 | 10.9 | 29 | 11.3 | 30 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8088 | 671.9997 | 119.0622
SYL-N.1.RR.373.2 | 24545869151508 | West Pir Moholla, H # 93/2, Abdul Jabbar Villa | 2022-12-04 | MN1018 | 10.7 | 151 | 10.7 | 152 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 0 | 671.9997 | 8.6486
SYL-N.1.RR.374.1 | 24545779151499 | West Pir Moholla, H # 82, Siraz | 2019-08-08 | LX1011 | 11.1 | 31 | 11.1 | 32 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8088 | 671.9997 | 116.9549
SYL-N.1.RR.375.1 | 24540379151550 | Dorga Moholla, Alia Madrasha Road, Nilima Mojumdar | 2019-08-18 | LX1011 | 11.9 | 75 | 11.9 | 76 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8160 | 599.9997 | 125.3841
SYL-N.1.RR.376.1 | 24540949151495 | Mirror Moydan, Arnob-05, Late A.W Chowdhury | 2019-08-18 | LX1011 | 5.6 | 77 | 5.6 | 78 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 8160 | 599.9997 | 59.0043
SYL-N.1.RR.377.1 | 24540849151500 | Mirror Moydan, Arnob-02, Giasuddin | 2019-08-18 | LX1011 | 11.4 | 79 | 11.4 | 80 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 8160 | 599.9997 | 120.1159
SYL-N.1.RR.378.1 | 24540959151498 | Mirror Moydan, Arnob-02, Asifuddin | 2019-08-18 | LX1011 | 6.1 | 81 | 6.1 | 82 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8160 | 599.9997 | 64.2725
SYL-N.1.RR.379.1 | 24540749151502 | Mirror Moydan, Arnob-01, Ashraf Manjil | 2019-08-18 | LX1011 | 8.1 | 83 | 8.1 | 84 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 8160 | 599.9997 | 85.3455
SYL-N.1.RR.380.1 | 24540909151535 | Dorga Moholla, Paira-137, Dream House | 2019-08-18 | LX1011 | 11.5 | 85 | 11.5 | 86 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8160 | 599.9997 | 121.1695
SYL-N.1.RR.380.2 | 24540909151535 | Dorga Moholla, Paira-137, Dream House | 2020-10-28 | NQ1009 | 3.6 | 243 | 3.6 | 244 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 8160 | 599.9997 | 37.9313
SYL-N.1.RR.381.1 | 24534099151445 | Mirzajangal, Monipuri Rajbari, H # 28 | 2019-08-19 | MP1006 | 4.6 | 25 | 4.6 | 26 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 8256 | 503.9997 | 48.4678
SYL-N.1.RR.381.2 | 24534099151445 | Mirzajangal, Monipuri Rajbari, H # 28 | 2019-08-19 | MP1006 | 2.4 | 27 | 2.4 | 28 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 8256 | 503.9997 | 25.2876
SYL-N.1.RR.382.1 | 24534099151445 | Mirzajangal, Monipuri Rajbari, H # 27 | 2019-08-19 | MP1006 | 5.5 | 29 | 5.5 | 30 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 8256 | 503.9997 | 57.9506
SYL-N.1.RR.383.1 | 24533709151439 | Mirzajangal, Monipuri Rajbari, H # 12 | 2019-08-19 | MP1006 | 7.4 | 31 | 7.4 | 32 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 8256 | 503.9997 | 77.97
SYL-N.1.RR.384.1 | 24531949151486 | Topkhana, Shurma Velli R/A, H # 118 | 2019-08-21 | NQ1003 | 13.3 | 159 | 13.3 | 160 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 8256 | 503.9997 | 140.1352
SYL-N.1.RR.385.1 | 24531949151486 | Topkhana, Shurma Velli R/A, H # 119 | 2019-08-21 | NQ1003 | 7.6 | 161 | 7.1 | 162 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 8256 | 503.9997 | 74.809
SYL-N.1.RR.386.1 | 24532069151488 | Topkhana, Shurma Villa R/A, H # 122 | 2019-08-21 | NQ1003 | 15 | 163 | 15 | 164 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8256 | 503.9997 | 158.0472
SYL-N.1.RR.387.1 | 24541949152030 | Amborkhana, Rajargoli, H # 46, Md. Moinuddin | 2019-08-21 | NQ1003 | 6.4 | 165 | 6.4 | 166 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8160 | 599.9997 | 67.4335
SYL-N.1.RR.388.1 | 24541459152013 | Amborkhana, Rajargoli, Md. Helal | 2019-08-21 | NQ1003 | 1.9 | 169 | 1.9 | 170 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8160 | 599.9997 | 20.0193
SYL-N.1.RR.389.1 | 24541359152044 | South Surma, 21-Rajargoli, M.S.M Mumin | 2019-08-21 | NQ1003 | 7.5 | 171 | 7.5 | 172 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 8160 | 599.9997 | 79.0236
SYL-N.1.RR.390.1 | 24541229152027 | Dorga Moholla, Rajargoli, H # 95, Mst. Hena Begum | 2019-08-21 | NQ1003 | 13.3 | 173 | 13.3 | 174 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 8160 | 599.9997 | 140.1352
SYL-N.1.RR.391.1 | 24541209152041 | Amborkhana, Rajargoli, H # 18, Md. Ali | 2019-08-21 | NQ1003 | 11.8 | 175 | 11.8 | 176 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8160 | 599.9997 | 124.3305
SYL-N.1.RR.392.1 | 24535499152155 | Chowhatta, Hawapara, Fayes Ahmed Chowdhury | 2019-08-24 | MP1006 | 7.6 | 129 | 7.6 | 130 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8256 | 503.9997 | 80.0773
SYL-N.1.RR.393.1 | 24535519152189 | Chowhatta, Hawapara, H # 54/1, Md. Afjal Mia | 2019-08-24 | MP1006 | 12.8 | 131 | 12.8 | 132 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8256 | 503.9997 | 134.867
SYL-N.1.RR.394.1 | 24535379152166 | Chowhatta, Hawapara, H # 58, Abu Mohammad Asad | 2019-08-24 | MP1006 | 1.9 | 133 | 1.9 | 134 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8256 | 503.9997 | 20.0193
SYL-N.1.RR.395.1 | 24535309152215 | Chowhatta, Hawapara, H # 76, Fatema Monjil | 2019-08-24 | MP1006 | 17.2 | 135 | 17.2 | 136 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 8256 | 503.9997 | 181.2275
SYL-N.1.RR.396.1 | 24535249152232 | Chowhatta, Hawapara, Nayasarak Misson Goli, H # 10, Shuvo Villa | 2019-08-24 | MP1006 | 89.7 | 137 | 89.7 | 138 | 2022-01-01 | [9 empty] | 89.7 | 89.7 | 5.382 | 5.382 | 0.0007168 | 100% | 0% | 5.382 | 5.382 | 0.0011869 | 28 | 0.10789 | 0.10789 |  | 0 | 0
SYL-N.1.RR.397.1 | 24535239152243 | Chowhatta, Nayasarak Misson Goli, H # 09, Peace House | 2019-08-24 | MP1006 | 11.1 | 139 | 11.1 | 140 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8256 | 503.9997 | 116.9549
SYL-N.1.RR.398.1 | 24535239152243 | Chowhatta, Nayasarak Misson Goli, H # 09, Peace House | 2019-08-24 | MP1006 | 5.8 | 141 | 5.8 | 142 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8256 | 503.9997 | 61.1116
SYL-N.1.RR.399.1 | 24535039152199 | Chowhatta, Hawapara, Dishari-99 | 2019-08-24 | MP1006 | 21.7 | 143 | 21.7 | 144 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 8256 | 503.9997 | 228.6416
SYL-N.1.RR.400.1 | 24534689152256 | Jailroad, Nayasarak, H # 3/B, Shuranjit Chowdhury | 2019-08-25 | MP1006 | 8.1 | 213 | 8.1 | 214 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 8280 | 479.9997 | 85.3455
SYL-N.1.RR.401.1 | 24544759151573 | Mohammad Nagar, Jalalabad R/ A, H # 59 | 2019-08-04 | NQ1003 | 13.2 | 483 | 13.3 | 484 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 8088 | 671.9997 | 140.1352
SYL-N.1.RR.402.1 | 24544679151590 | Mohammad Nagar, Jalalabad R/ A, H # 45/9 | 2019-08-04 | NQ1003 | 11.3 | 485 | 11.3 | 486 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8088 | 671.9997 | 119.0622
SYL-N.1.RR.403.1 | 24544439151526 | Mohammad Nagar, Jalalabad R/ A, H # 41/1, Fardus Mia | 2019-08-04 | NQ1003 | 3.3 | 487 | 3.3 | 488 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 8088 | 671.9997 | 34.7704
SYL-N.1.RR.404.1 | 24544529151523 | Mohammad Nagar, Jalalabad R/ A, H # 41/3 | 2019-08-04 | NQ1003 | 8 | 489 | 8 | 490 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 8088 | 671.9997 | 84.2919
SYL-N.1.RR.404.2 | 24544529151523 | Mohammad Nagar, Jalalabad R/ A, H # 41/3 | 2022-12-04 | MN1018 | 7.6 | 153 | 7.6 | 154 | 2022-12-04 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 0 | 671.9997 | 6.1429
SYL-N.1.RR.405.1 | 24544509151513 | Mohammad Nagar, Jalalabad R/ A, H # 41/4, Ahad Villa | 2019-08-04 | NQ1003 | 8.4 | 491 | 8.4 | 492 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8088 | 671.9997 | 88.5064
SYL-N.1.RR.406.1 | 24544279151491 | Mohammad Nagar, Jalalabad R/ A, H # 39/5, Mostakin Monjil | 2019-08-04 | NQ1003 | 11.4 | 493 | 11.7 | 494 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8088 | 671.9997 | 123.2768
SYL-N.1.RR.407.1 | 24542949151457 | Jalalabad, East sobid Bazar, Fazil Chist R/ A, Rofiq Khan | 2019-08-05 | NQ1003 | 15.1 | 535 | 15.1 | 536 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 8088 | 671.9997 | 159.1009
SYL-N.1.RR.408.1 | 24542949151457 | Jalalabad, East sobid Bazar, Fazil Chist R/ A, Harun Khan | 2019-08-05 | NQ1003 | 11.1 | 537 | 11.2 | 538 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8088 | 671.9997 | 118.0086
SYL-N.1.RR.409.1 | 24543029151435 | Jalalabad, East sobid Bazar, Fazil Chist R/ A, Saleh Miah | 2019-08-05 | NQ1003 | 8.9 | 541 | 8.9 | 542 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8088 | 671.9997 | 93.7747
SYL-N.1.RR.410.1 | 24543099151416 | Sobid Bazar, Fazil Chist R/ A, H # 15/2/B | 2019-08-05 | NQ1003 | 17.4 | 545 | 17.4 | 546 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 8088 | 671.9997 | 183.3348
SYL-N.1.RR.411.1 | 24543099151416 | Sobid Bazar, Fazil Chist R/ A, H # 15/2/B | 2019-08-05 | NQ1003 | 9.2 | 547 | 9.2 | 548 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8088 | 671.9997 | 96.9356
SYL-N.1.RR.412.1 | 24543299151424 | Jalalabad, East sobid Bazar, Fazil Chist R/ A, H # 19/2 | 2019-08-05 | NQ1003 | 10.8 | 549 | 10.8 | 550 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8088 | 671.9997 | 113.794
SYL-N.1.RR.413.1 | 24543379151445 | Jalalabad, East sobid Bazar, Fazil Chist R/ A, H # 19/6 | 2019-08-05 | NQ1003 | 12.8 | 551 | 12.8 | 552 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8088 | 671.9997 | 134.867
SYL-N.1.RR.414.1 | 24543609151443 | Jalalabad, East sobid Bazar, Fazil Chist R/ A, H # 26 | 2019-08-05 | NQ1003 | 5.4 | 553 | 5.4 | 554 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 8088 | 671.9997 | 56.897
SYL-N.1.RR.415.1 | 24543949151461 | Jalalabad, East sobid Bazar, Fazil Chist R/ A, H # 28/5/A | 2019-08-05 | NQ1003 | 6.4 | 555 | 6.4 | 556 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8088 | 671.9997 | 67.4335
SYL-N.1.RR.416.1 | 24543919151347 | Subid Bazar, Nurani R/ A, H # 13/4, Rahim Villa | 2019-08-06 | NQ1003 | 22.6 | 585 | 22.6 | 586 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 22.6 | 22.6 | 1.356 | 1.356 | 0.0007168 | 100% | 0% | 1.356 | 1.356 | 0.0011869 | 28 | 0.027183 | 0.027183 |  | 0 | 0 | 8016 | 743.9997 | 238.1245
SYL-N.1.RR.417.1 | 24543809151397 | Subid Bazar, Kolapara Road, Nurani R/A, H # 17/2-A | 2019-08-06 | NQ1003 | 16.9 | 587 | 17.4 | 588 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 8088 | 671.9997 | 183.3348
SYL-N.1.RR.417.2 | 24543809151397 | Subid Bazar, Kolapara Road, Nurani R/A, H # 17/2-A | 2021-02-17 | MN1032 | 9.9 | 180 | 9.9 | 181 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8088 | 671.9997 | 104.3112
SYL-N.1.RR.418.1 | 24543819151401 | Subid Bazar, Kolapara Road, Nurani R/A, Kazi Moynal Hossen | 2019-08-06 | NQ1003 | 11 | 589 | 10.8 | 590 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8088 | 671.9997 | 113.794
SYL-N.1.RR.419.1 | 24543789151415 | Subid Bazar, Kolapara Road, Nurani R/A, H # 17/2-F | 2019-08-06 | NQ1003 | 8.1 | 591 | 8.3 | 592 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 8088 | 671.9997 | 87.4528
SYL-N.1.RR.420.1 | 24543789151415 | Subid Bazar, Kolapara Road, Nurani R/A, Anwara Mansion | 2019-08-06 | NQ1003 | 9 | 593 | 9 | 594 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8088 | 671.9997 | 94.8283
SYL-N.1.RR.421.1 | 24544059151391 | Subid Bazar, BonKolapara Road, Nurani R/A, H # 21/4 | 2019-08-06 | NQ1003 | 11.6 | 595 | 11.5 | 596 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8088 | 671.9997 | 121.1695
SYL-N.1.RR.422.1 | 24544169151378 | Subid Bazar, BonKolapara Road, Nurani R/A, H # 23 | 2019-08-06 | NQ1003 | 11.1 | 597 | 11.1 | 598 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8088 | 671.9997 | 116.9549
SYL-N.1.RR.423.1 | 24544279151374 | Subid Bazar, BonKolapara Road, Nurani R/A, H # 26 | 2019-08-06 | NQ1003 | 11.3 | 599 | 11.3 | 600 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8088 | 671.9997 | 119.0622
SYL-N.1.RR.424.1 | 24544499151207 | Pathantula, Niamotullah Road,Road, Mohuna R/A, H # 13/A | 2019-08-07 | NQ1003 | 10.7 | 21 | 10.7 | 22 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8016 | 743.9997 | 112.7403
SYL-N.1.RR.425.1 | 24544519151220 | Pathantula, Niamotullah Road,Road, Mohuna R/A, H # 14/A | 2019-08-07 | NQ1003 | 10.4 | 23 | 10.5 | 24 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8016 | 743.9997 | 110.6331
SYL-N.1.RR.426.1 | 24544449151235 | Pathantula, Niamotullah Road,Road, Mohuna R/A, H # 16, Kamrujaman | 2019-08-07 | NQ1003 | 10.1 | 25 | 10.1 | 26 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8016 | 743.9997 | 106.4185
SYL-N.1.RR.427.1 | 24544449151235 | Pathantula, Niamotullah Road,Road, Mohuna R/A, H # 16/A, Sonnu Mia | 2019-08-07 | NQ1003 | 10.9 | 27 | 10.9 | 28 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8016 | 743.9997 | 114.8476
SYL-N.1.RR.428.1 | 24544639151160 | Pathantula, Mosjid Road,Road,Amin Khan Goli, Mohuna R/A, H # 26 | 2019-08-07 | NQ1003 | 11 | 29 | 11 | 30 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8016 | 743.9997 | 115.9013
SYL-N.1.RR.429.1 | 24550919150587 | Kubarpara, Mohona R/A, Block # B, Dr. Sobir Kumar Dash | 2019-08-08 | NQ1003 | 10.1 | 37 | 10.1 | 38 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8016 | 743.9997 | 106.4185
SYL-N.1.RR.430.1 | 24550919150587 | Kubarpara, Mohona R/A, Block # B, H # 20 | 2019-08-08 | NQ1003 | 7.6 | 39 | 7.6 | 40 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 1368 | 0 | 6648 | 743.9997 | 67.572
SYL-N.1.RR.431.1 | 24552259150559 | Jalalabad, Hawoldar Para, Kala Bari Road, Rupali Block,Litin Ahmed | 2019-08-17 | NQ1003 | 21.7 | 41 | 21.7 | 42 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 8016 | 743.9997 | 228.6416
SYL-N.1.RR.432.1 | 24552219150538 | Gowabari, Kocharpara, Mohona R/A, Block # D, Sofia Begum | 2019-08-17 | NQ1003 | 8.2 | 47 | 8.2 | 48 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8016 | 743.9997 | 86.3991
SYL-N.1.RR.433.1 | 24552019150565 | Gowabari, Kocharpara, Mohona R/A, Block # D, Jaber Monzil, Abdul Malik | 2019-08-17 | NQ1003 | 10.8 | 49 | 11 | 50 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8016 | 743.9997 | 115.9013
SYL-N.1.RR.434.1 | 24552029150517 | Jalalabad, Hawoldarpara, Koshiara Road, Hawoldarpara R/A, H # 18 | 2019-08-17 | NQ1003 | 10.6 | 51 | 10.6 | 52 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8016 | 743.9997 | 111.6867
SYL-N.1.RR.435.1 | 24551999150500 | Jalalabad, Hawoldarpara, Koshiara Road, Kamal Hossen | 2019-08-17 | NQ1003 | 12.6 | 53 | 12.6 | 54 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 8016 | 743.9997 | 132.7597
SYL-N.1.RR.436.1 | 24541129151406 | Mirer Moydan, Arnob, H # 74/A | 2019-08-18 | NQ1003 | 23.3 | 55 | 23.3 | 56 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 23.3 | 23.3 | 1.398 | 1.398 | 0.0007168 | 100% | 0% | 1.398 | 1.398 | 0.0011869 | 28 | 0.028025 | 0.028025 |  | 0 | 0 | 8160 | 599.9997 | 245.5
SYL-N.1.RR.437.1 | 24541249151418 | Mirer Moydan, Arnob, H # 67 | 2019-08-18 | NQ1003 | 11.9 | 57 | 11.9 | 58 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8160 | 599.9997 | 125.3841
SYL-N.1.RR.438.1 | 24541399151435 | Mirer Moydan, Arnob, H # 61 | 2019-08-18 | NQ1003 | 9.3 | 59 | 9.3 | 60 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 8160 | 599.9997 | 97.9893
SYL-N.1.RR.439.1 | 24541509151415 | Mirer Moydan, Arnob, H # 56 | 2019-08-18 | NQ1003 | 6.3 | 61 | 6.3 | 62 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8160 | 599.9997 | 66.3798
SYL-N.1.RR.440.1 | 24541149151469 | Mirer Moydan, Arnob, H # 21 | 2019-08-18 | NQ1003 | 12.5 | 63 | 12.4 | 64 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8160 | 599.9997 | 130.6524
SYL-N.1.RR.441.1 | 24541139151465 | Mirer Moydan, Arnob, H # 20 | 2019-08-18 | NQ1003 | 10 | 65 | 10 | 66 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8160 | 599.9997 | 105.3648
SYL-N.1.RR.442.1 | 24541379151511 | Jornarpar, Payra R/A, H # 70 | 2019-08-18 | NQ1003 | 1.6 | 67 | 1.6 | 68 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 8160 | 599.9997 | 16.8584
SYL-N.1.RR.443.1 | 24541559151579 | Dorga Moholla, Payra R/A, H # 19 | 2019-08-18 | NQ1003 | 14.5 | 69 | 14.5 | 70 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 8160 | 599.9997 | 152.779
SYL-N.1.RR.444.1 | 24541559151579 | Dorga Moholla, Payra R/A, H # 20 | 2019-08-18 | NQ1003 | 8.1 | 71 | 8.1 | 72 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 8160 | 599.9997 | 85.3455
SYL-N.1.RR.445.1 | 24533919151593 | Jinda Bazar, Jallarpar, Jallarpar R/A, Jallarpar Jame Mosjid | 2019-08-19 | NQ1003 | 18.5 | 73 | 19 | 74 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 8256 | 503.9997 | 200.1931
SYL-N.1.RR.446.1 | 24533579151592 | Jinda Bazar, Jallarpar, Jallarpar R/A, H # 22, Imran Mansion | 2019-08-19 | NQ1003 | 3.1 | 75 | 3.1 | 76 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 8256 | 503.9997 | 32.6631
SYL-N.1.RR.447.1 | 24533519151594 | Jinda Bazar, Jallarpar, Jallarpar R/A, H # 63, Bakth House | 2019-08-19 | NQ1003 | 13 | 77 | 13 | 78 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8256 | 503.9997 | 136.9743
SYL-N.1.RR.448.1 | 24533259151590 | Jinda Bazar, Jallarpar, Jallarpar R/A, H # 38, Farhan Bax | 2019-08-19 | NQ1003 | 24.2 | 79 | 24.2 | 80 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 24.2 | 24.2 | 1.452 | 1.452 | 0.0007168 | 100% | 0% | 1.452 | 1.452 | 0.0011869 | 28 | 0.029108 | 0.029108 |  | 0 | 0 | 8256 | 503.9997 | 254.9828
SYL-N.1.RR.449.1 | 24533259151590 | Jinda Bazar, Jallarpar, Jallarpar R/A, H # 38, Farhan Bax | 2019-08-19 | NQ1003 | 12.9 | 81 | 12.9 | 82 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 8256 | 503.9997 | 135.9206
SYL-N.1.RR.450.1 | 24534229151599 | Jinda Bazar, Jallarpar, Doriapara Road, Magna R/A, Monir Mia | 2019-08-19 | NQ1003 | 9.9 | 83 | 9.9 | 84 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8256 | 503.9997 | 104.3112
SYL-N.1.RR.451.1 | 24542729151539 | Sylhet Sadar, Jalalabad R/A, H # 10/1 | 2019-08-05 | NQ1003 | 10.9 | 525 | 10.9 | 526 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8088 | 671.9997 | 114.8476
SYL-N.1.RR.452.1 | 24542879151543 | Sylhet Sadar, Jalalabad R/A, H # 10/2 | 2019-08-05 | NQ1003 | 28.8 | 527 | 28.8 | 528 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 28.8 | 28.8 | 1.728 | 1.728 | 0.0007168 | 100% | 0% | 1.728 | 1.728 | 0.0011869 | 28 | 0.03464 | 0.03464 |  | 0 | 0 | 8088 | 671.9997 | 303.4507
SYL-N.1.RR.453.1 | 24542879151541 | Sylhet Sadar, Jalalabad R/A, Md. Azizur Rahman, H # 10/5A | 2019-08-05 | NQ1003 | 8.7 | 529 | 8.7 | 530 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8088 | 671.9997 | 91.6674
SYL-N.1.RR.454.1 | 24542879151541 | Sylhet Sadar, Jalalabad R/A, K. M. Brothers Villa, H # 10/4 | 2019-08-05 | NQ1003 | 12.7 | 531 | 12.7 | 532 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 8088 | 671.9997 | 133.8133
SYL-N.1.RR.455.1 | 24542349151521 | Sylhet Sadar, Jalalabad R/A, Farid Ahmed, H # 2 | 2019-08-05 | NQ1003 | 6.3 | 533 | 6.3 | 534 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8088 | 671.9997 | 66.3798
SYL-N.1.RR.456.1 | 24542559151392 | Sylhet Sadar, Subid Bazar, Prantik-33 | 2019-08-06 | NQ1003 | 36.2 | 557 | 36.2 | 558 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 36.2 | 36.2 | 2.172 | 2.172 | 0.0007168 | 100% | 0% | 2.172 | 2.172 | 0.0011869 | 28 | 0.043541 | 0.043541 |  | 0 | 0 | 8088 | 671.9997 | 381.4206
SYL-N.1.RR.457.1 | 24542909151404 | Sylhet Sadar, Subid Bazar, Begum Villa, Mitali-6/5 | 2019-08-06 | NQ1003 | 13.4 | 559 | 13.4 | 560 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 8088 | 671.9997 | 141.1888
SYL-N.1.RR.458.1 | 24543249151382 | Sylhet Sadar, Subid Bazar, Mawlana Asraful Haque, Mitali-10/3C | 2019-08-06 | NQ1003 | 10.8 | 561 | 10.8 | 562 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8088 | 671.9997 | 113.794
SYL-N.1.RR.459.1 | 24543249151382 | Sylhet Sadar, Subid Bazar, Mitali-10/3A | 2019-08-06 | NQ1003 | 4.8 | 565 | 4.8 | 566 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8088 | 671.9997 | 50.5751
SYL-N.1.RR.460.1 | 24542999151359 | Sylhet Sadar, Subid Bazar, Nurani R/A, H # 02 | 2019-08-06 | NQ1003 | 13.5 | 567 | 13.5 | 568 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 8088 | 671.9997 | 142.2425
SYL-N.1.RR.461.1 | 24543269151368 | Sylhet Sadar, Subid Bazar, Nurani R/A, H # 6/A | 2019-08-06 | NQ1003 | 5 | 571 | 5 | 572 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 8088 | 671.9997 | 52.6824
SYL-N.1.RR.462.1 | 24543619151324 | Sylhet Sadar, Subid Bazar, Digirpar, Nurani-11/1 | 2019-08-06 | NQ1003 | 12.4 | 573 | 12.4 | 574 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8016 | 743.9997 | 130.6524
SYL-N.1.RR.463.1 | 24543719151326 | Sylhet Sadar, Subid Bazar, Digirpar, Nurani R/A, H # 12/2 | 2019-08-06 | NQ1003 | 11.5 | 575 | 11.5 | 576 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8016 | 743.9997 | 121.1695
SYL-N.1.RR.464.1 | 24544239151346 | Sylhet Sadar, Subid Bazar, Digirpar, Nurani R/A, H # 13/12 | 2019-08-06 | NQ1003 | 8.5 | 579 | 8.6 | 580 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 8016 | 743.9997 | 90.6137
SYL-N.1.RR.465.1 | 24544329151347 | Sylhet Sadar, Subid Bazar, Digirpar, Nurani R/A, H # 13/13 | 2019-08-06 | NQ1003 | 6.2 | 581 | 6.2 | 582 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8016 | 743.9997 | 65.3262
SYL-N.1.RR.466.1 | 24544329151347 | Sylhet Sadar, Subid Bazar, Digirpar, Nurani R/A, H # 13/15 | 2019-08-06 | NQ1003 | 7 | 583 | 7 | 584 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 8016 | 743.9997 | 73.7554
SYL-N.1.RR.467.1 | 24544599151368 | Sylhet Sadar, Subid Bazar, Nurani Bonkalapara, H # 38 | 2019-08-07 | NQ1003 | 11.6 | 1 | 11.6 | 2 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8016 | 743.9997 | 122.2232
SYL-N.1.RR.467.2 | 24544599151368 | Sylhet Sadar, Subid Bazar, Nurani Bonkalapara, H # 38 | 2020-10-27 | NQ1003 | 1.3 | 201 | 1.3 | 202 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 8016 | 743.9997 | 13.6974
SYL-N.1.RR.468.1 | 24544649151366 | Sylhet Sadar, Subid Bazar, Nurani Bonkalapara, H # 38/2 | 2019-08-07 | NQ1003 | 12.9 | 3 | 12.6 | 4 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 8016 | 743.9997 | 132.7597
SYL-N.1.RR.469.1 | 24544509151338 | Sylhet Sadar, Subid Bazar, Nurani Bonkalapara, H # 38/6 | 2019-08-07 | NQ1003 | 4.4 | 7 | 4.4 | 8 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 8016 | 743.9997 | 46.3605
SYL-N.1.RR.470.1 | 24544449151327 | Sylhet Sadar, Subid Bazar, Londoni Road, Agroni-38 | 2019-08-07 | NQ1003 | 4.5 | 9 | 4.5 | 10 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 8016 | 743.9997 | 47.4142
SYL-N.1.RR.471.1 | 24544559151269 | Sylhet Sadar, Subid Bazar, Londoni Road, Agroni-172/1 | 2019-08-07 | NQ1003 | 11.1 | 11 | 11.1 | 12 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8016 | 743.9997 | 116.9549
SYL-N.1.RR.472.1 | 24544539151265 | Sylhet Sadar, Subid Bazar, Londoni Road, Agroni-173/1 | 2019-08-07 | NQ1003 | 12.9 | 13 | 12.9 | 14 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 8016 | 743.9997 | 135.9206
SYL-N.1.RR.473.1 | 24544499151260 | Sylhet Sadar, Subid Bazar, Londoni Road, Agroni-176B | 2019-08-07 | NQ1003 | 10.9 | 15 | 10.9 | 16 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8016 | 743.9997 | 114.8476
SYL-N.1.RR.474.1 | 24544689151257 | Sylhet Sadar, West Subid Bazar, Londoni Road, Agroni-168/A | 2019-08-08 | NQ1003 | 11.4 | 31 | 10.8 | 32 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8016 | 743.9997 | 113.794
SYL-N.1.RR.475.1 | 24544769151269 | Sylhet Sadar, West Subid Bazar, Londoni Road, Agroni-157/B | 2019-08-08 | NQ1003 | 9.8 | 33 | 9.8 | 34 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8016 | 743.9997 | 103.2575
SYL-N.1.RR.476.1 | 24532659151491 | Sylhet, Taltola, Telehahor, Faruk Ahmed | 2019-08-21 | NQ1003 | 11.8 | 137 | 11.8 | 138 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8256 | 503.9997 | 124.3305
SYL-N.1.RR.477.1 | 24532659151491 | Sylhet, Taltola, Telehahor, Nazrul Islam | 2019-08-21 | NQ1003 | 19.3 | 139 | 18.4 | 140 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 8256 | 503.9997 | 193.8713
SYL-N.1.RR.478.1 | 24532889151500 | Sylhet, Taltola, Masudighirpar, Probaho-35 | 2019-08-21 | NQ1003 | 9.5 | 141 | 8.7 | 142 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8256 | 503.9997 | 91.6674
SYL-N.1.RR.479.1 | 24532969151467 | Sylhet, Taltola, Masudighirpar, Probaho-40 | 2019-08-21 | NQ1003 | 14 | 143 | 14.1 | 144 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 8256 | 503.9997 | 148.5644
SYL-N.1.RR.480.1 | 24532969151467 | Sylhet, Taltola, Masudighirpar, Probaho-40 | 2019-08-21 | NQ1003 | 12 | 145 | 11.4 | 146 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 8256 | 503.9997 | 120.1159
SYL-N.1.RR.481.1 | 24532969151467 | Sylhet, Taltola, Masudighirpar, Probaho-40 | 2019-08-21 | NQ1003 | 12.8 | 147 | 12.8 | 148 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8256 | 503.9997 | 134.867
SYL-N.1.RR.482.1 | 24532949151594 | Sylhet, Taltola, Hotel Shahaban Goli, Yousuf Monjil, H # 18 | 2019-08-21 | NQ1003 | 7.8 | 149 | 7.8 | 150 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 8256 | 503.9997 | 82.1846
SYL-N.1.RR.483.1 | 24532279151454 | Sylhet, North Kazir Bazar, Nearest Lakhi Bakery, Md. Sultan | 2019-08-21 | NQ1003 | 7.5 | 151 | 7.5 | 152 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 8256 | 503.9997 | 79.0236
SYL-N.1.RR.484.1 | 24532169151456 | Sylhet, North Kazir Bazar, Adorsho Opset Printing & Publication | 2019-08-21 | NQ1003 | 13.7 | 153 | 14.8 | 154 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 8256 | 503.9997 | 155.9399
SYL-N.1.RR.485.1 | 24532059151380 | Sylhet, West Kazir Bazar, Mogultula, Ruhul Monjil, Sriti-5 | 2019-08-21 | NQ1003 | 22.9 | 155 | 22.9 | 156 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 22.9 | 22.9 | 1.374 | 1.374 | 0.0007168 | 100% | 0% | 1.374 | 1.374 | 0.0011869 | 28 | 0.027544 | 0.027544 |  | 0 | 0 | 8256 | 503.9997 | 241.2854
SYL-N.1.RR.486.1 | 24532239151382 | Sylhet, West Kazir Bazar, Mogultula, Hasan Villa, Sriti-15 | 2019-08-21 | NQ1003 | 12.4 | 157 | 12.1 | 158 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 8256 | 503.9997 | 127.4914
SYL-N.1.RR.487.1 | 24541939152335 | Amborkhana, North Kazitola, Electric supply Road, H # E-2 | 2019-08-24 | NQ1003 | 12 | 261 | 12 | 262 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8184 | 575.9997 | 126.4378
SYL-N.1.RR.488.1 | 24541719152345 | North Kazitola, Kahen Mia Goli, Josna Monjil | 2019-08-24 | NQ1003 | 16.9 | 263 | 16.9 | 264 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 8184 | 575.9997 | 178.0665
SYL-N.1.RR.489.1 | 24541519152337 | North Kazitola, Kahen Mia Goli, H # E-13 | 2019-08-24 | NQ1003 | 8.8 | 265 | 8.8 | 266 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8184 | 575.9997 | 92.721
SYL-N.1.RR.490.1 | 24541249152355 | North Kazitola, Kahen Mia Goli, Beside Hill View,Convention Center, Rabeya | 2019-08-24 | NQ1003 | 13.2 | 267 | 13.2 | 268 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 8184 | 575.9997 | 139.0816
SYL-N.1.RR.491.1 | 24541579152385 | Kazitola, Mobaruk Bokth Poraton Bari, Habib Bokth | 2019-08-24 | NQ1003 | 11.9 | 269 | 12 | 270 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8184 | 575.9997 | 126.4378
SYL-N.1.RR.491.2 | 24541579152385 | Kazitola, Mobaruk Bokth Poraton Bari, Habib Bokth | 2022-12-08 | MN1018 | 2.1 | 167 | 2.1 | 168 | 2022-12-08 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 0 | 575.9997 | 1.4549
SYL-N.1.RR.492.1 | 24541579152385 | Kazitola, Mobaruk Bokth Poraton Bari, Balal Bokth | 2019-08-24 | NQ1003 | 26.7 | 271 | 26.7 | 272 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 26.7 | 26.7 | 1.602 | 1.602 | 0.0007168 | 100% | 0% | 1.602 | 1.602 | 0.0011869 | 28 | 0.032115 | 0.032115 |  | 0 | 0 | 8184 | 575.9997 | 281.324
SYL-N.1.RR.492.2 | 24541579152385 | Kazitola, Mobaruk Bokth Poraton Bari, Balal Bokth | 2022-05-12 | LU1001 | 13 | 188 | 13 | 189 | 2022-05-12 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 5040 | 575.9997 | 87.8136
SYL-N.1.RR.493.1 | 24540819152413 | Kazitola, Moktub Goli, H # 4/A | 2019-08-24 | NQ1003 | 10.9 | 273 | 10.9 | 274 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8184 | 575.9997 | 114.8476
SYL-N.1.RR.494.1 | 24540829152424 | Kazitola, Moktub Goli, H # 15/C | 2019-08-24 | NQ1003 | 8.3 | 275 | 8.8 | 276 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8184 | 575.9997 | 92.721
SYL-N.1.RR.495.1 | 24540829152424 | Kazitola, Moktub Goli, H # 15/D | 2019-08-24 | NQ1003 | 9 | 277 | 9 | 278 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8184 | 575.9997 | 94.8283
SYL-N.1.RR.496.1 | 24540749152353 | Sylhet, Kazitula, Moktob Goli, H # 26/B | 2019-08-24 | NQ1003 | 21.3 | 279 | 21.3 | 280 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 21.3 | 21.3 | 1.278 | 1.278 | 0.0007168 | 100% | 0% | 1.278 | 1.278 | 0.0011869 | 28 | 0.02562 | 0.02562 |  | 0 | 0 | 8184 | 575.9997 | 224.4271
SYL-N.1.RR.496.2 | 24540749152353 | Sylhet, Kazitula, Moktob Goli, H # 26/B | 2020-10-21 | NQ1003 | 11 | 110 | 9.8 | 111 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8184 | 575.9997 | 103.2575
SYL-N.1.RR.497.1 | 24540749152353 | Sylhet, Kazitula, Moktob Goli, Masuk Monjil, H # 51 | 2019-08-24 | NQ1003 | 11.7 | 281 | 11.6 | 282 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8184 | 575.9997 | 122.2232
SYL-N.1.RR.498.1 | 24540479152354 | Sylhet, Kazitula, Moktob Goli, Hafiz Monjil, H # 44 | 2019-08-24 | NQ1003 | 11 | 283 | 11 | 284 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8184 | 575.9997 | 115.9013
SYL-N.1.RR.499.1 | 24540719152325 | Sylhet, Kazitula, Bihongo-58 | 2019-08-24 | NQ1003 | 3.4 | 289 | 3.4 | 290 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 8184 | 575.9997 | 35.824
SYL-N.1.RR.500.1 | 24540229152305 | Sylhet, Kazitula, Roki Shah, Bihongo-31 | 2019-08-24 | NQ1003 | 11.2 | 291 | 10.5 | 292 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8184 | 575.9997 | 110.6331
SYL-N.1.RR.501.1 | 24544809152088 | East Pirmoholla, Lechubagan, Akbar Villa, Provati-44 | 2019-08-03 | NQ1009 | 14.3 | 505 | 15.9 | 506 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 8136 | 623.9997 | 167.5301
SYL-N.1.RR.502.1 | 24545039152091 | East Pirmoholla, Lechubagan, Junayed, Provati-49/B | 2019-08-03 | NQ1009 | 11.2 | 507 | 11.4 | 508 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 8136 | 623.9997 | 120.1159
SYL-N.1.RR.503.1 | 24545009152115 | East Pirmoholla, Lechubagan, Jabed Mia, Provati-41/1 | 2019-08-03 | NQ1009 | 11 | 509 | 11 | 510 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8136 | 623.9997 | 115.9013
SYL-N.1.RR.504.1 | 24545649152180 | Elashkandi, Rd# 2, Udoyon, Abdul Mojid | 2019-08-04 | NQ1009 | 7.7 | 539 | 7.7 | 540 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 8136 | 623.9997 | 81.1309
SYL-N.1.RR.505.1 | 24545759152188 | Elashkandi, Rd# 2, Ali Villa, Udoyon-28 | 2019-08-04 | NQ1009 | 8.9 | 541 | 8.9 | 542 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8136 | 623.9997 | 93.7747
SYL-N.1.RR.506.1 | 24545759152188 | Elashkandi, Firoza Monjil, Udoyon-29 | 2019-08-04 | NQ1009 | 10.5 | 543 | 10.2 | 544 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8136 | 623.9997 | 107.4721
SYL-N.1.RR.507.1 | 24545769152198 | Elashkandi, Shanti Niketon, Abdul hai, Udoyon-40 | 2019-08-04 | NQ1009 | 12.3 | 545 | 12.1 | 546 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 1788 | 0 | 6348 | 623.9997 | 101.4692
SYL-N.1.RR.508.1 | 24545909152198 | Elashkandi, Rd# 2, Beside of Khan Monjil | 2019-08-04 | NQ1009 | 9.6 | 547 | 9.6 | 548 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8136 | 623.9997 | 101.1502
SYL-N.1.RR.509.1 | 24550019152201 | Elashkandi, Rd# 2, Udoyon-34/2 | 2019-08-04 | NQ1009 | 10.5 | 549 | 10.5 | 550 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8136 | 623.9997 | 110.6331
SYL-N.1.RR.510.1 | 24550209152199 | Chowkideki, Rd# 2, Rongdhonu-90/2 | 2019-08-04 | NQ1009 | 12.4 | 552 | 12.4 | 553 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8136 | 623.9997 | 130.6524
SYL-N.1.RR.511.1 | 24550379152181 | Chowkideki, Rd# 2, Asiya Akter, Rongdhonu-105/2 | 2019-08-04 | NQ1009 | 8.5 | 554 | 9.2 | 555 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8136 | 623.9997 | 96.9356
SYL-N.1.RR.512.1 | 24550519152215 | Chowkideki, Rd# 2, Shahin, Rongdhonu-118/2 | 2019-08-04 | NQ1009 | 20.5 | 556 | 22.1 | 557 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 22.1 | 22.1 | 1.326 | 1.326 | 0.0007168 | 100% | 0% | 1.326 | 1.326 | 0.0011869 | 28 | 0.026582 | 0.026582 |  | 0 | 0 | 8136 | 623.9997 | 232.8562
SYL-N.1.RR.513.1 | 24550519152215 | Chowkideki, Rd# 2, Nur Mia, Rongdhonu-116 | 2019-08-04 | NQ1009 | 9.2 | 558 | 9.2 | 559 | 2022-01-01 | 2022-12-06 | MN1018 | 0.9 | 165 | 0.9 | 166 | 2022-12-06 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8136 | 623.9997
SYL-N.1.RR.513.2 | 24550519152215 | Chowkideki, Rd# 2, Nur Mia, Rongdhonu-116 | 2020-10-22 | NQ1009 | 3.8 | 33 | 3.8 | 34 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8136 | 623.9997 | 40.0386
SYL-N.1.RR.514.1 | 24550519152225 | Chowkideki, Rd# 2, Altu Mia, Rongdhonu-121/2 | 2019-08-04 | NQ1009 | 20.2 | 560 | 20.2 | 561 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 20.2 | 20.2 | 1.212 | 1.212 | 0.0007168 | 100% | 0% | 1.212 | 1.212 | 0.0011869 | 28 | 0.024296 | 0.024296 |  | 0 | 0 | 8136 | 623.9997 | 212.8369
SYL-N.1.RR.515.1 | 24545949151439 | Bonkolapara, Subidbazar, Nurani, Happy Villa, H # 88 | 2019-08-05 | NQ1009 | 23.8 | 604 | 23.8 | 605 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 23.8 | 23.8 | 1.428 | 1.428 | 0.0007168 | 100% | 0% | 1.428 | 1.428 | 0.0011869 | 28 | 0.028627 | 0.028627 |  | 0 | 0 | 8016 | 743.9997 | 250.7683
SYL-N.1.RR.516.1 | 24545949151439 | Bonkolapara, Subidbazar, Nurani, H # 87 | 2019-08-05 | NQ1009 | 13.3 | 606 | 13.3 | 607 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 8280 | 479.9997 | 140.1352
SYL-N.1.RR.517.1 | 24550289151450 | Bonkolapara, Subidbazar, Nurani R/A, H # 99 | 2019-08-05 | NQ1009 | 10.6 | 608 | 10.6 | 609 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8016 | 743.9997 | 111.6867
SYL-N.1.RR.518.1 | 24550289151450 | Bonkolapara, Subidbazar, Nurani R/A, H # 100 | 2019-08-05 | NQ1009 | 11.3 | 610 | 11.3 | 611 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8016 | 743.9997 | 119.0622
SYL-N.1.RR.519.1 | 24550639151447 | Bonkolapara, Subidbazar, Nurani R/A, Shayek Mia | 2019-08-05 | NQ1009 | 10.8 | 612 | 10.8 | 613 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8016 | 743.9997 | 113.794
SYL-N.1.RR.520.1 | 24550669151432 | Bonkolapara, Subidbazar, Nurani R/A, Abdus Salam villa, H # 104/4 | 2019-08-05 | NQ1009 | 6.3 | 614 | 6.3 | 615 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8016 | 743.9997 | 66.3798
SYL-N.1.RR.521.1 | 24550859151443 | Bonkolapara, Subidbazar, Nurani R/A, Bozon Kanti Das, H #105/3 | 2019-08-05 | NQ1009 | 14.2 | 616 | 14.2 | 617 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 8016 | 743.9997 | 149.618
SYL-N.1.RR.522.1 | 24550739151403 | Bonkolapara, Subidbazar, Nurani R/A, Shahjahan, H # 105/11 | 2019-08-05 | NQ1009 | 13.4 | 618 | 13.4 | 619 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 8016 | 743.9997 | 141.1888
SYL-N.1.RR.523.1 | 24550739151403 | Bonkolapara, Subidbazar, Nurani R/A, Jomir Hossain, H # 105/12 | 2019-08-05 | NQ1009 | 9.8 | 620 | 9.8 | 621 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8016 | 743.9997 | 103.2575
SYL-N.1.RR.524.1 | 24550829151366 | Bonkolapara, Subidbazar, Nurani R/A, Manik Mia | 2019-08-05 | NQ1009 | 42.3 | 622 | 42.3 | 623 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 42.3 | 42.3 | 2.538 | 2.538 | 0.0007168 | 100% | 0% | 2.538 | 2.538 | 0.0011869 | 28 | 0.050878 | 0.050878 |  | 0 | 0 | 8016 | 743.9997 | 445.6932
SYL-N.1.RR.525.1 | 24545619151415 | Bonkolapara, Subidbazar, Nurani R/A, Abul Hossain | 2019-08-06 | NQ1009 | 10.7 | 638 | 10.7 | 639 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8016 | 743.9997 | 112.7403
SYL-N.1.RR.526.1 | 24545509151407 | Bonkolapara, Subidbazar, Muglitola, Baitul Falah Jame Masjid | 2019-08-06 | NQ1009 | 9.4 | 640 | 9.4 | 641 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8016 | 743.9997 | 99.0429
SYL-N.1.RR.527.1 | 24545509151407 | Bonkolapara, Subidbazar, Muglitola, Baitul Falah Jame Masjid | 2019-08-06 | NQ1009 | 10.5 | 642 | 10.9 | 643 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8016 | 743.9997 | 114.8476
SYL-N.1.RR.528.1 | 24545509151407 | Bonkolapara, Subidbazar, Nurani R/A, Ataur Rahman, H# 74/5 | 2019-08-06 | NQ1009 | 12.3 | 644 | 12.3 | 645 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 8016 | 743.9997 | 129.5987
SYL-N.1.RR.528.2 | 24545509151407 | Bonkolapara, Subidbazar, Nurani R/A, Ataur Rahman, H# 74/5 | 2019-08-06 | NQ1009 | 9.5 | 646 | 9.5 | 647 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8016 | 743.9997 | 100.0966
SYL-N.1.RR.529.1 | 24545529151381 | Bonkolapara, Subidbazar, Nurani R/A, Muglitoa Road, Ismail Villa, H# 73 | 2019-08-06 | NQ1009 | 26.1 | 649 | 26.1 | 650 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 26.1 | 26.1 | 1.566 | 1.566 | 0.0007168 | 100% | 0% | 1.566 | 1.566 | 0.0011869 | 28 | 0.031393 | 0.031393 |  | 0 | 0 | 8016 | 743.9997 | 275.0022
SYL-N.1.RR.530.1 | 24545389151362 | Bonkolapara, Subidbazar, Nurani R/A, H# 66/1 | 2019-08-06 | NQ1009 | 9.3 | 651 | 9.4 | 652 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8016 | 743.9997 | 99.0429
SYL-N.1.RR.531.1 | 24545179151378 | Bonkolapara, Subidbazar, Nurani R/A, H# 59/1 | 2019-08-06 | NQ1009 | 15.7 | 655 | 15.7 | 656 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 8016 | 743.9997 | 165.4228
SYL-N.1.RR.532.1 | 24544779151389 | Bonkolapara, Subidbazar, Nurani R/A, H# 46, Aminulla | 2019-08-06 | NQ1009 | 8.9 | 658 | 8.9 | 659 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8016 | 743.9997 | 93.7747
SYL-N.1.RR.533.1 | 24544859151220 | Pathantula, Amin Khan Road, Block-A, Beside H # 36 | 2019-08-07 | LX1011 | 9.8 | 23 | 10.3 | 24 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8016 | 743.9997 | 108.5258
SYL-N.1.RR.534.1 | 24550799150573 | Pathantula, Korerpara, Mohona, Palash Datta | 2019-08-08 | LX1011 | 10 | 39 | 10 | 40 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 8016 | 743.9997 | 105.3648
SYL-N.1.RR.535.1 | 24550799150573 | Pathantula, Korerpara, Mohona, Noresh Chandra | 2019-08-08 | LX1011 | 17.7 | 41 | 17.7 | 42 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 8016 | 743.9997 | 186.4957
SYL-N.1.RR.535.2 | 24550799150573 | Pathantula, Korerpara, Mohona, Noresh Chandra | 2020-10-28 | NQ1009 | 12.8 | 259 | 12.8 | 260 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8016 | 743.9997 | 134.867
SYL-N.1.RR.536.1 | 24550759150566 | Pathantula, Korerpara, Mohona-79, Krisno | 2019-08-08 | LX1011 | 11.5 | 43 | 11.5 | 44 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8016 | 743.9997 | 121.1695
SYL-N.1.RR.537.1 | 24534169151489 | Mirzajangal, Monipuri Rajbari, Atiqur Rahman, H # 720 | 2019-08-19 | LX1011 | 12.3 | 103 | 12.3 | 104 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 8256 | 503.9997 | 129.5987
SYL-N.1.RR.538.1 | 24534089151541 | Mirzajangal, Monipuri Rajbari, Dariya Para, Meghna, Block-A, H # 40 | 2019-08-19 | LX1011 | 13.3 | 105 | 13 | 106 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8256 | 503.9997 | 136.9743
SYL-N.1.RR.539.1 | 24534329151493 | Mirzajangal, Monipuri Rajbari, Dariya Para, Meghna, Block-C, Sita Kuthir | 2019-08-19 | LX1011 | 12 | 107 | 12 | 108 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8256 | 503.9997 | 126.4378
SYL-N.1.RR.540.1 | 24534509151542 | Mirzajangal, Dariya Para, Meghna, Block-A, H # 30, Nilkontho Ray | 2019-08-19 | LX1011 | 19 | 109 | 19 | 110 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 8256 | 503.9997 | 200.1931
SYL-N.1.RR.541.1 | 24533549151553 | Jallarpar, Jamtola Road, Soptodipa R/A, Siricoat Monjil, H # 35 | 2019-08-19 | LX1011 | 14.9 | 111 | 14.9 | 112 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.9 | 14.9 | 0.894 | 0.894 | 0.0007168 | 100% | 0% | 0.894 | 0.894 | 0.0011869 | 28 | 0.017922 | 0.017922 |  | 0 | 0 | 8256 | 503.9997 | 156.9936
SYL-N.1.RR.542.1 | 24533549151553 | Jallarpar, Jamtola Road, Soptodipa R/A, Siricoat Monjil, H # 35 | 2019-08-19 | LX1011 | 17 | 115 | 17 | 116 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 8256 | 503.9997 | 179.1202
SYL-N.1.RR.543.1 | 24541179152040 | Amborkhana, Razar Goli, H # 106 | 2019-08-22 | NQ1003 | 15.1 | 177 | 15.1 | 178 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 8160 | 599.9997 | 159.1009
SYL-N.1.RR.544.1 | 24541099152052 | Amborkhana, Razar Goli, Hotel Dorgahin Faruk Ahmed, H # 8 | 2019-08-22 | NQ1003 | 5.8 | 179 | 5.8 | 180 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8160 | 599.9997 | 61.1116
SYL-N.1.RR.545.1 | 24541219152048 | Amborkhana, Razar Goli, Sohel Villa, H # 9/2 | 2019-08-22 | NQ1003 | 10.9 | 181 | 10.9 | 182 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8160 | 599.9997 | 114.8476
SYL-N.1.RR.546.1 | 24540989152060 | Amborkhana, East Dorgah Gate, H # 9 | 2019-08-22 | NQ1003 | 10.3 | 183 | 10.3 | 184 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8160 | 599.9997 | 108.5258
SYL-N.1.RR.547.1 | 24540989152060 | Amborkhana, East Dorgah Gate, Rokeya Begum | 2019-08-22 | NQ1003 | 8.6 | 185 | 8.6 | 186 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 8160 | 599.9997 | 90.6137
SYL-N.1.RR.548.1 | 24540989152060 | Amborkhana, East Dorgah Gate, H # 5 | 2019-08-22 | NQ1003 | 3.6 | 187 | 3.6 | 188 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 8160 | 599.9997 | 37.9313
SYL-N.1.RR.549.1 | 24540909152039 | Amborkhana, Dorgah Gate, Qarashi Bari, Safi | 2019-08-22 | NQ1003 | 9.8 | 191 | 9.8 | 192 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8160 | 599.9997 | 103.2575
SYL-N.1.RR.550.1 | 24540619152023 | Amborkhana, Bhatipara, Dorgah Gate, Rose Garden Tower | 2019-08-22 | NQ1003 | 10.7 | 193 | 10.7 | 194 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8160 | 599.9997 | 112.7403
SYL-N.1.RR.551.1 | 24545169151483 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,H #55 | 2019-08-05 | NQ1009 | 4.4 | 584 | 4.4 | 585 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 8088 | 671.9997 | 46.3605
SYL-N.1.RR.552.1 | 24545129151489 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,H #56 | 2019-08-05 | NQ1009 | 10.7 | 586 | 10.7 | 587 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8088 | 671.9997 | 112.7403
SYL-N.1.RR.553.1 | 24545169151463 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,H#82/23 | 2019-08-05 | NQ1009 | 10.9 | 588 | 10.9 | 589 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8088 | 671.9997 | 114.8476
SYL-N.1.RR.553.2 | 24545169151463 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,H#82/23 | 2020-10-25 | NQ1009 | 6.7 | 89 | 6.7 | 90 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 8088 | 671.9997 | 70.5944
SYL-N.1.RR.554.1 | 24545339151472 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,Abdul Haque | 2019-08-05 | NQ1009 | 6.3 | 590 | 6.3 | 591 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8088 | 671.9997 | 66.3798
SYL-N.1.RR.555.1 | 24545539151453 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,Habib Khan | 2019-08-05 | NQ1009 | 9.6 | 592 | 9.6 | 593 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8088 | 671.9997 | 101.1502
SYL-N.1.RR.555.2 | 24545539151453 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,Habib Khan | 2020-10-25 | NQ1009 | 30.1 | 95 | 30.1 | 96 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 30.1 | 30.1 | 1.806 | 1.806 | 0.0007168 | 100% | 0% | 1.806 | 1.806 | 0.0011869 | 28 | 0.036204 | 0.036204 |  | 0 | 0 | 8088 | 671.9997 | 317.1481
SYL-N.1.RR.556.1 | 24545539151453 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,Karim Khan | 2019-08-05 | NQ1009 | 11.7 | 594 | 11.7 | 595 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8088 | 671.9997 | 123.2768
SYL-N.1.RR.557.1 | 24545539151453 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Oykator R/A ,Onay Khan | 2019-08-05 | NQ1009 | 19.3 | 596 | 19.3 | 597 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 8088 | 671.9997 | 203.3541
SYL-N.1.RR.558.1 | 24545749151464 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Nurani R/A, H # 82/3 | 2019-08-05 | NQ1009 | 10.4 | 598 | 10.4 | 599 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8088 | 671.9997 | 109.5794
SYL-N.1.RR.558.2 | 24545749151464 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Nurani R/A, H # 82/3 | 2021-02-17 | LU1001 | 5 | 207 | 5 | 208 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 8088 | 671.9997 | 52.6824
SYL-N.1.RR.559.1 | 24545729151469 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Nurani R/A, Maynuddin | 2019-08-05 | NQ1009 | 10.5 | 600 | 10.5 | 601 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8088 | 671.9997 | 110.6331
SYL-N.1.RR.560.1 | 24550049151476 | Sylhet Sodor ,North Pirmahalla ,Shah Farid Road ,Nurani R/A, H #84/9/A | 2019-08-05 | NQ1009 | 9.1 | 602 | 9.1 | 603 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8088 | 671.9997 | 95.882
SYL-N.1.RR.561.1 | 24545399151583 | West Pir Moholla, Oikkotan R/A, H # 127/B | 2019-08-06 | NQ1009 | 8.1 | 624 | 8.4 | 625 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8088 | 671.9997 | 88.5064
SYL-N.1.RR.562.1 | 24545569151559 | West Pir Moholla, Oikkotan R/A, H # 114 | 2019-08-06 | NQ1009 | 9.4 | 628 | 9.5 | 629 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8088 | 671.9997 | 100.0966
SYL-N.1.RR.563.1 | 24545959151565 | West Pir Moholla, Oikkotan R/A, Opposite Of H # 134 | 2019-08-06 | NQ1009 | 9.9 | 630 | 9.9 | 631 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8088 | 671.9997 | 104.3112
SYL-N.1.RR.564.1 | 24550089151541 | West Pir Moholla, Oikkotan R/A, H # 137 | 2019-08-06 | NQ1009 | 7.1 | 632 | 7.1 | 633 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 8088 | 671.9997 | 74.809
SYL-N.1.RR.565.1 | 24550089151541 | West Pir Moholla, Oikkotan R/A, H # 137/2 | 2019-08-06 | NQ1009 | 10.2 | 634 | 10.2 | 635 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8088 | 671.9997 | 107.4721
SYL-N.1.RR.566.1 | 24545919151431 | Subid Bazar, Bonkola Para, Nurani R/A, H # 85 | 2019-08-06 | NQ1009 | 60 | 636 | 60.2 | 637 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 60.2 | 60.2 | 3.612 | 3.612 | 0.0007168 | 100% | 0% | 3.612 | 3.612 | 0.0011869 | 28 | 0.072408 | 0.072408 |  | 0 | 0 | 8016 | 743.9997 | 634.2962
SYL-N.1.RR.567.1 | 24550099151350 | Subid Bazar, Bonkolapara, Nurani R/A, H # 65/21 | 2019-08-07 | MP1006 | 129.7 | 3 | 129.7 | 4 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 129.7 | 129.7 | 7.782 | 7.782 | 0.0007168 | 100% | 0% | 7.782 | 7.782 | 0.0011869 | 28 | 0.156 | 0.156 |  | 0 | 0 | 8016 | 743.9997 | 1366.5816
SYL-N.1.RR.568.1 | 24543649151241 | West Subid Bazar, Londoni Road, Agroni R/A, H # 1 | 2019-08-07 | NQ1003 | 5.9 | 17 | 5.9 | 18 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 8016 | 743.9997 | 62.1652
SYL-N.1.RR.569.1 | 24543659151275 | West Subid Bazar, Londoni Road, Agroni R/A, H # 9 | 2019-08-07 | NQ1003 | 4.6 | 19 | 4.5 | 20 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 8016 | 743.9997 | 47.4142
SYL-N.1.RR.570.1 | 24542159151380 | Subid Bazar, Police Line Road, Chondrima R/A, Sylhet Press Club | 2019-08-08 | LX1011 | 17.6 | 33 | 17.6 | 34 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 8088 | 671.9997 | 185.4421
SYL-N.1.RR.571.1 | 24542119151388 | Subid Bazar, Police Line Road, Chondrima R/A, H # 23 | 2019-08-08 | LX1011 | 5.2 | 35 | 5.2 | 36 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 8088 | 671.9997 | 54.7897
SYL-N.1.RR.572.1 | 24542489151378 | Subid Bazar, Police Line Road, Chondrima R/A, Behind Modern Hospital, Siraj Ali | 2019-08-08 | LX1011 | 12 | 37 | 12 | 38 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8088 | 671.9997 | 126.4378
SYL-N.1.RR.573.1 | 24551199150536 | Jalalabad ,Korerpara ,Mohona R/A ,Ward #08 ,H #88/1 | 2019-08-17 | LX1011 | 11.1 | 49 | 11.1 | 50 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8016 | 743.9997 | 116.9549
SYL-N.1.RR.574.1 | 24551139150526 | Jalalabad ,Korerpara ,Mohona R/A ,Ward #08 ,H #88/C | 2019-08-17 | LX1011 | 3.4 | 51 | 3.4 | 52 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 8016 | 743.9997 | 35.824
SYL-N.1.RR.575.1 | 24551269150551 | Jalalabad ,Korerpara ,Mohona R/A ,Ward #08 ,H #94/B | 2019-08-17 | LX1011 | 8.7 | 53 | 8.7 | 54 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8016 | 743.9997 | 91.6674
SYL-N.1.RR.576.1 | 24551349150553 | Jalalabad ,Korerpara ,Mohona R/A ,Ward #08 ,H #101 | 2019-08-17 | LX1011 | 7 | 57 | 7 | 58 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 8016 | 743.9997 | 73.7554
SYL-N.1.RR.577.1 | 24551519150554 | Jalalabad ,Korerpara ,Mohona R/A ,Ward #08 ,H #108 | 2019-08-17 | LX1011 | 9.1 | 59 | 9.1 | 60 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8016 | 743.9997 | 95.882
SYL-N.1.RR.578.1 | 24551439150535 | Jalalabad ,Korerpara ,Mohona R/A ,Ward #08 ,H #106 | 2019-08-17 | LX1011 | 3.5 | 61 | 3.5 | 62 | 2022-01-01 | 2022-12-01 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 8016 | 743.9997 | 36.8777
SYL-N.1.RR.579.1 | 24540029152005 | Sylhet Sodor , Dorga Moholla , Alia Madrasha Road , Jalalia R/A , H#2/3 | 2019-08-18 | LX1011 | 8.7 | 69 | 8.7 | 70 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8160 | 599.9997 | 91.6674
SYL-N.1.RR.580.1 | 24540029152005 | Sylhet Sodor , Dorga Moholla , Alia Madrasha Road , Jalalia R/A , H#04 | 2019-08-18 | LX1011 | 6.2 | 71 | 6.2 | 72 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8160 | 599.9997 | 65.3262
SYL-N.1.RR.581.1 | 24540269152025 | Sylhet Sodor , Dorga Moholla , Alia Madrasha Road , Jalalia R/A , H#14 | 2019-08-18 | LX1011 | 20.5 | 73 | 20.5 | 74 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 20.5 | 20.5 | 1.23 | 1.23 | 0.0007168 | 100% | 0% | 1.23 | 1.23 | 0.0011869 | 28 | 0.024657 | 0.024657 |  | 0 | 0 | 8160 | 599.9997 | 215.9979
SYL-N.1.RR.581.2 | 24540269152025 | Sylhet Sodor , Dorga Moholla , Alia Madrasha Road , Jalalia R/A , H#14 | 2020-10-28 | NQ1009 | 3 | 256 | 3 | 257 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 8160 | 599.9997 | 31.6094
SYL-N.1.RR.582.1 | 24540569151575 | Sylhet Sodor , Dorga Moholla , Alia Madrasha Road , Menargate , Bokul Villa | 2019-08-18 | LX1011 | 10.5 | 87 | 10.5 | 88 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8160 | 599.9997 | 110.6331
SYL-N.1.RR.583.1 | 24541479151531 | Sylhet Sodor , Dorga Moholla , Payra R/A, H #67/1 | 2019-08-18 | LX1011 | 11.9 | 89 | 11.9 | 90 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8160 | 599.9997 | 125.3841
SYL-N.1.RR.584.1 | 24541479151531 | Sylhet Sodor , Dorga Moholla , Payra R/A, H #67/2 | 2019-08-18 | LX1011 | 9.6 | 91 | 9.6 | 92 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8160 | 599.9997 | 101.1502
SYL-N.1.RR.585.1 | 24541479151531 | Sylhet Sodor , Dorga Moholla , Payra R/A, H #61 | 2019-08-18 | LX1011 | 11.8 | 93 | 11.8 | 94 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8160 | 599.9997 | 124.3305
SYL-N.1.RR.586.1 | 24534559151429 | Sylhet Sodor, Lamapara Bazar Road, Lamapara R/A, Sonkor Pal | 2019-08-18 | LX1011 | 19.7 | 95 | 19.7 | 96 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 19.7 | 19.7 | 1.182 | 1.182 | 0.0007168 | 100% | 0% | 1.182 | 1.182 | 0.0011869 | 28 | 0.023695 | 0.023695 |  | 0 | 0 | 8256 | 503.9997 | 207.5687
SYL-N.1.RR.587.1 | 24534559151429 | Sylhet Sodor, Lamapara Bazar Road, Lamapara R/A, Ater Ahamed | 2019-08-18 | LX1011 | 10.1 | 97 | 10.1 | 98 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8256 | 503.9997 | 106.4185
SYL-N.1.RR.588.1 | 24534609151451 | Sylhet Sodor, Lamapara Bazar Road, Lamapara R/A, Bosor Uddin | 2019-08-18 | LX1011 | 10.5 | 99 | 10.5 | 100 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8256 | 503.9997 | 110.6331
SYL-N.1.RR.589.1 | 24534609151451 | Sylhet Sodor, Lamapara Bazar Road, Lamapara R/A, Md. Sodor uddin | 2019-08-18 | LX1011 | 7.4 | 101 | 7.4 | 102 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 8256 | 503.9997 | 77.97
SYL-N.1.RR.590.1 | 24533219151553 | Sylhet Sodor, Jamtola Para, Jamtola Road, Sudipta R/A, H# 22 | 2019-08-19 | LX1011 | 6.2 | 117 | 6.2 | 118 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8256 | 503.9997 | 65.3262
SYL-N.1.RR.591.1 | 24533409151525 | Sylhet Sodor, Mirjajangal Road, Ward #13, H# 55 | 2019-08-19 | LX1011 | 41.6 | 119 | 41.6 | 120 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 41.6 | 41.6 | 2.496 | 2.496 | 0.0007168 | 100% | 0% | 2.496 | 2.496 | 0.0011869 | 28 | 0.050036 | 0.050036 |  | 0 | 0 | 8256 | 503.9997 | 438.3176
SYL-N.1.RR.592.1 | 24533739151512 | Sylhet Sodor, Mirjajangal Road, Ward #13, H# 70 | 2019-08-19 | LX1011 | 1.9 | 121 | 1.9 | 122 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8256 | 503.9997 | 20.0193
SYL-N.1.RR.593.1 | 24533929151529 | Sylhet Sodor, Mirjajangal Road, Ward #13, Sopnil ,R/A, H# 5/1 | 2019-08-19 | LX1011 | 81.3 | 125 | 81.3 | 126 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 81.3 | 81.3 | 4.878 | 4.878 | 0.0007168 | 100% | 0% | 4.878 | 4.878 | 0.0011869 | 28 | 0.097787 | 0.097787 |  | 2376 | 0 | 5880 | 503.9997 | 624.2735
SYL-N.1.RR.594.1 | 24533739151539 | Sylhet Sodor, Mirjajangal Road, Ward #13, Sopnil ,R/A, H# 3/1 | 2019-08-19 | LX1011 | 6.6 | 127 | 6.6 | 128 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 8256 | 503.9997 | 69.5408
SYL-N.1.RR.595.1 | 24533029151385 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, H# 56 | 2019-08-20 | NQ1003 | 21.9 | 121 | 21.8 | 122 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 21.8 | 21.8 | 1.308 | 1.308 | 0.0007168 | 100% | 0% | 1.308 | 1.308 | 0.0011869 | 28 | 0.026221 | 0.026221 |  | 0 | 0 | 8256 | 503.9997 | 229.6953
SYL-N.1.RR.596.1 | 24533109151424 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, H# 68 | 2019-08-20 | NQ1003 | 10.9 | 123 | 10.9 | 124 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8256 | 503.9997 | 114.8476
SYL-N.1.RR.597.1 | 24532939151385 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, H# 81 | 2019-08-20 | NQ1003 | 9.4 | 125 | 9.5 | 126 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8256 | 503.9997 | 100.0966
SYL-N.1.RR.598.1 | 24532589151380 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, H# 30/A | 2019-08-20 | NQ1003 | 9.3 | 127 | 9.3 | 128 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 8256 | 503.9997 | 97.9893
SYL-N.1.RR.599.1 | 24532679151404 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, H# 35/A | 2019-08-20 | NQ1003 | 29.4 | 129 | 29.4 | 130 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 29.4 | 29.4 | 1.764 | 1.764 | 0.0007168 | 100% | 0% | 1.764 | 1.764 | 0.0011869 | 28 | 0.035362 | 0.035362 |  | 0 | 0 | 8256 | 503.9997 | 309.7725
SYL-N.1.RR.600.1 | 24532799151448 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, H# 17 | 2019-08-20 | NQ1003 | 10.9 | 131 | 10.9 | 132 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8256 | 503.9997 | 114.8476
SYL-N.1.RR.601.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 16.4 | 161 | 16.4 | 162 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 8256 | 503.9997 | 172.7983
SYL-N.1.RR.602.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 5.9 | 167 | 5.9 | 168 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 8256 | 503.9997 | 62.1652
SYL-N.1.RR.603.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 6.8 | 169 | 6.8 | 170 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 8256 | 503.9997 | 71.6481
SYL-N.1.RR.604.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 2.6 | 171 | 2.6 | 172 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 8256 | 503.9997 | 27.3949
SYL-N.1.RR.605.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 4.4 | 173 | 4.4 | 174 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 8256 | 503.9997 | 46.3605
SYL-N.1.RR.606.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 15 | 175 | 15 | 176 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 8256 | 503.9997 | 158.0472
SYL-N.1.RR.607.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 10.7 | 177 | 10.7 | 178 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8256 | 503.9997 | 112.7403
SYL-N.1.RR.608.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 13.8 | 179 | 13.8 | 180 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 8256 | 503.9997 | 145.4034
SYL-N.1.RR.609.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 5.8 | 181 | 5.8 | 182 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 8256 | 503.9997 | 61.1116
SYL-N.1.RR.610.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 7.7 | 183 | 7.7 | 184 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 8256 | 503.9997 | 81.1309
SYL-N.1.RR.611.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 12.9 | 185 | 12.9 | 186 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 8136 | 623.9997 | 135.9206
SYL-N.1.RR.611.2 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2021-11-08 | NQ1007 | 12.4 | 93 | 12.4 | 94 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8136 | 623.9997 | 130.6524
SYL-N.1.RR.612.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 16.6 | 187 | 16.6 | 188 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 8136 | 623.9997 | 174.9056
SYL-N.1.RR.613.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 2.8 | 189 | 2.8 | 190 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 8136 | 623.9997 | 29.5021
SYL-N.1.RR.614.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 4.7 | 193 | 4.7 | 194 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 8136 | 623.9997 | 49.5215
SYL-N.1.RR.615.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 2.3 | 195 | 2.3 | 196 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 8136 | 623.9997 | 24.2339
SYL-N.1.RR.616.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 2.5 | 197 | 2.5 | 198 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 8136 | 623.9997 | 26.3412
SYL-N.1.RR.617.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 6.1 | 199 | 6.1 | 200 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8136 | 623.9997 | 64.2725
SYL-N.1.RR.618.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 8.9 | 201 | 8.9 | 202 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8136 | 623.9997 | 93.7747
SYL-N.1.RR.619.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 6.3 | 203 | 6.4 | 204 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8136 | 623.9997 | 67.4335
SYL-N.1.RR.620.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 28.6 | 205 | 28.9 | 206 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 28.9 | 28.9 | 1.734 | 1.734 | 0.0007168 | 100% | 0% | 1.734 | 1.734 | 0.0011869 | 28 | 0.034761 | 0.034761 |  | 0 | 0 | 8136 | 623.9997 | 304.5043
SYL-N.1.RR.621.1 | 24534449152164 | Hawa Para, Dishari-1, Ark Homes | 2019-08-25 | MP1006 | 6.5 | 209 | 6 | 210 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 8136 | 623.9997 | 63.2189
SYL-N.1.RR.622.1 | 24533359152403 | Nayerpul, Block-C, Rubel Ahmed | 2019-08-26 | MP1006 | 7.6 | 263 | 7.6 | 264 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 8184 | 575.9997 | 80.0773
SYL-N.1.RR.623.1 | 24533359152403 | Nayerpul, Block-C, Kabul Ahmed | 2019-08-26 | MP1006 | 11 | 265 | 11 | 266 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8184 | 575.9997 | 115.9013
SYL-N.1.RR.624.1 | 24533549152420 | Nayerpul, Block-C, Bongobir-92 | 2019-08-26 | MP1006 | 16.1 | 267 | 15.9 | 268 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 8184 | 575.9997 | 167.5301
SYL-N.1.RR.624.2 | 24533549152420 | Nayerpul, Block-C, Bongobir-92 | 2021-02-14 | NQ1003 | 3.3 | 247 | 3.3 | 248 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 8184 | 575.9997 | 34.7704
SYL-N.1.RR.625.1 | 24533499152432 | Nayerpul, Block-C, Bongobir-86, Abdul Kadir | 2019-08-26 | MP1006 | 11.8 | 269 | 11.7 | 270 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8184 | 575.9997 | 123.2768
SYL-N.1.RR.626.1 | 24533499152432 | Nayerpul, Block-C, Bongobir-87 | 2019-08-26 | MP1006 | 4 | 271 | 4 | 272 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 8184 | 575.9997 | 42.1459
SYL-N.1.RR.627.1 | 24533409152438 | Nayerpul, Block-C, Bongobir-90 | 2019-08-26 | MP1006 | 11.7 | 273 | 11.7 | 274 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8184 | 575.9997 | 123.2768
SYL-N.1.RR.628.1 | 24533799152408 | Nayerpul, Block-B, Motin Mia | 2019-08-26 | MP1006 | 19.3 | 275 | 19.3 | 276 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 8184 | 575.9997 | 203.3541
SYL-N.1.RR.629.1 | 24530789152370 | Masimpur, Doel-3, Md. Iman Ali | 2019-08-27 | MP1006 | 13.4 | 282 | 13.4 | 283 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 8256 | 503.9997 | 141.1888
SYL-N.1.RR.630.1 | 24530789152370 | Masimpur, Doel-4, Shahaf Uddin | 2019-08-27 | MP1006 | 13.1 | 284 | 12.8 | 285 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8256 | 503.9997 | 134.867
SYL-N.1.RR.631.1 | 24530859152382 | Masimpur, Doel-3/1, Dilip Kuri | 2019-08-27 | MP1006 | 12.1 | 286 | 11.8 | 287 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8256 | 503.9997 | 124.3305
SYL-N.1.RR.632.1 | 24530859152382 | Masimpur, Doel-3/3, Prodip Kuri | 2019-08-27 | MP1006 | 9.4 | 288 | 9.4 | 289 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8256 | 503.9997 | 99.0429
SYL-N.1.RR.633.1 | 24530859152382 | Masimpur, Doel-3/6, Ojit Kuri | 2019-08-27 | MP1006 | 4.7 | 290 | 4.7 | 291 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 8256 | 503.9997 | 49.5215
SYL-N.1.RR.634.1 | 24530859152382 | Masimpur, Doel-3/7, Sunil Kuri | 2019-08-27 | MP1006 | 14 | 292 | 14 | 293 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 8256 | 503.9997 | 147.5107
SYL-N.1.RR.635.1 | 24530889152397 | Masimpur, Doel-3/23, Orgo Vushon Kuri | 2019-08-27 | MP1006 | 10.8 | 294 | 10.8 | 295 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8256 | 503.9997 | 113.794
SYL-N.1.RR.651.1 | 24534649152263 | Jailroad, Nayasarak, H # 3/B, Gourango Bunik | 2019-08-25 | MP1006 | 15.1 | 215 | 15.1 | 216 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 8280 | 479.9997 | 159.1009
SYL-N.1.RR.652.1 | 24534859152280 | Jailroad, Nayasarak, H # 17, Shunil Kormokar | 2019-08-25 | MP1006 | 34.9 | 217 | 34.9 | 218 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 34.9 | 34.9 | 2.094 | 2.094 | 0.0007168 | 100% | 0% | 2.094 | 2.094 | 0.0011869 | 28 | 0.041978 | 0.041978 |  | 0 | 0 | 8280 | 479.9997 | 367.7232
SYL-N.1.RR.653.1 | 24534859152280 | Jailroad, Nayasarak, H # 13, Suvroto Pal | 2019-08-25 | MP1006 | 2 | 219 | 2 | 220 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 8280 | 479.9997 | 21.073
SYL-N.1.RR.654.1 | 24534859152280 | Jailroad, Nayasarak, H # 16, Nilmoni Kormokar | 2019-08-25 | MP1006 | 11.9 | 221 | 11.9 | 222 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8280 | 479.9997 | 125.3841
SYL-N.1.RR.655.1 | 24534859152280 | Jailroad, Nayasarak, Beside Of H # 16 | 2019-08-25 | MP1006 | 5.4 | 223 | 5.4 | 224 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 8280 | 479.9997 | 56.897
SYL-N.1.RR.656.1 | 24535079152289 | Nayasarak, Hazrat Shah Chand Gazi Road, Hoque Villa | 2019-08-25 | MP1006 | 11.8 | 225 | 12.3 | 226 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 8280 | 479.9997 | 129.5987
SYL-N.1.RR.657.1 | 24535169152291 | Nayasarak, Hazrat Shah Chand Gazi Road, Mimaloy | 2019-08-25 | MP1006 | 9.7 | 227 | 9.7 | 228 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8280 | 479.9997 | 102.2039
SYL-N.1.RR.658.1 | 24535059152310 | Nayasarak, Hazrat Shah Chand Gazi Road, H # 47 | 2019-08-25 | MP1006 | 11.8 | 229 | 11.8 | 230 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8280 | 479.9997 | 124.3305
SYL-N.1.RR.659.1 | 24535049152310 | Nayasarak, Hazrat Shah Chand Gazi Road, H # 48 | 2019-08-25 | MP1006 | 5.6 | 231 | 5.6 | 232 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 8280 | 479.9997 | 59.0043
SYL-N.1.RR.660.1 | 24535049152310 | Nayasarak, Hazrat Shah Chand Gazi Road, H # 48 | 2019-08-25 | MP1006 | 13.6 | 233 | 13.6 | 234 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 8280 | 479.9997 | 143.2961
SYL-N.1.RR.661.1 | 24534939152306 | Nayasarak, Hazrat Shah Chand Gazi Road, H # 49/A, Hazari Monjil | 2019-08-25 | MP1006 | 1 | 235 | 1 | 236 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 1 | 1 | 0.06 | 0.06 | 0.0007168 | 100% | 0% | 0.06 | 0.06 | 0.0011869 | 28 | 0.0012028 | 0.0012028 |  | 0 | 0 | 8280 | 479.9997 | 10.5365
SYL-N.1.RR.662.1 | 24534839152293 | Nayasarak, Hazrat Shah Chand Gazi Road, Md. Mukul, H # 53/A | 2019-08-25 | MP1006 | 11.2 | 237 | 11.2 | 238 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8280 | 479.9997 | 118.0086
SYL-N.1.RR.663.1 | 24535399152312 | Nayasarak, Al-Helal R/A, H # 31/A, Jobeda Manjil | 2019-08-26 | MP1006 | 18.1 | 239 | 18.1 | 240 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 8280 | 479.9997 | 190.7103
SYL-N.1.RR.663.2 | 24535399152312 | Nayasarak, Al-Helal R/A, H # 31/A, Jobeda Manjil | 2021-02-14 | NQ1007 | 9.8 | 185 | 9.8 | 186 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8280 | 479.9997 | 103.2575
SYL-N.1.RR.664.1 | 24535389152320 | Nayasarak, Al-Helal R/A, H # 34, Moinuddin | 2019-08-26 | MP1006 | 15.8 | 241 | 15.8 | 242 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 8280 | 479.9997 | 166.4764
SYL-N.1.RR.665.1 | 24535539152304 | Nayasarak, Al-Helal R/A, H # 18, Birahim Uddin | 2019-08-26 | MP1006 | 12.2 | 246 | 12.2 | 247 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 8280 | 479.9997 | 128.5451
SYL-N.1.RR.666.1 | 24535499152309 | Nayasarak, Al-Helal R/A, H # 16, Shorif Ahmad | 2019-08-26 | MP1006 | 9.6 | 248 | 9.6 | 249 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8280 | 479.9997 | 101.1502
SYL-N.1.RR.667.1 | 24534319152322 | Jail Road, North Side Of Dhopadighi, H # 165, Mahfuj | 2019-08-26 | MP1006 | 6.2 | 250 | 6.2 | 251 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8280 | 479.9997 | 65.3262
SYL-N.1.RR.668.1 | 24534309152326 | Jail Road, North Side Of Dhopadighi, Kamal Chairman | 2019-08-26 | MP1006 | 14.7 | 252 | 14.7 | 253 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 8280 | 479.9997 | 154.8863
SYL-N.1.RR.669.1 | 24534309152328 | Jail Road, North Side Of Dhopadighi, H # 151/B, Dr. Altafur Rahman | 2019-08-26 | MP1006 | 32.4 | 255 | 32.4 | 256 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 32.4 | 32.4 | 1.944 | 1.944 | 0.0007168 | 100% | 0% | 1.944 | 1.944 | 0.0011869 | 28 | 0.038971 | 0.038971 |  | 0 | 0 | 8280 | 479.9997 | 341.382
SYL-N.1.RR.670.1 | 24534359152337 | Jail Road, North Side Of Dhopadighi, H # 145, Bokul Chandra Kormokar | 2019-08-26 | MP1006 | 14.2 | 257 | 14.2 | 258 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 8280 | 479.9997 | 149.618
SYL-N.1.RR.671.1 | 24534399152337 | Jail Road, North Side Of Dhopadighi, H # 146, Makhon Chakrabarti | 2019-08-26 | MP1006 | 16.5 | 259 | 16.5 | 260 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 8280 | 479.9997 | 173.8519
SYL-N.1.RR.672.1 | 24534399152337 | Jail Road, North Side Of Dhopadighi, H # 146, Makhon Chakrabarti | 2019-08-26 | MP1006 | 7.3 | 261 | 7.3 | 262 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8280 | 479.9997 | 76.9163
SYL-N.1.RR.673.1 | 24532329152387 | Chalibondor R/A, Shomota-7/2, Norendra Ghos | 2019-08-28 | MP1006 | 5.7 | 296 | 5.7 | 297 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 8184 | 575.9997 | 60.0579
SYL-N.1.RR.674.1 | 24532339152379 | Chalibondor R/A, H # 7/6 | 2019-08-28 | MP1006 | 1.9 | 298 | 1.9 | 299 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 8184 | 575.9997 | 20.0193
SYL-N.1.RR.701.1 | 24534509152009 | Jinda Bazar, Jallarpar, Doriapara Road, Magna R/A, H # B-12/13, Sirajuddin | 2019-08-19 | NQ1003 | 19.7 | 85 | 19.7 | 86 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 19.7 | 19.7 | 1.182 | 1.182 | 0.0007168 | 100% | 0% | 1.182 | 1.182 | 0.0011869 | 28 | 0.023695 | 0.023695 |  | 0 | 0 | 8256 | 503.9997 | 207.5687
SYL-N.1.RR.702.1 | 24534509152009 | Jinda Bazar, Jallarpar, Doriapara Road, Magna R/A, H # B-12/13, Samsuddin | 2019-08-19 | NQ1003 | 36.2 | 87 | 36.2 | 88 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 36.2 | 36.2 | 2.172 | 2.172 | 0.0007168 | 100% | 0% | 2.172 | 2.172 | 0.0011869 | 28 | 0.043541 | 0.043541 |  | 0 | 0 | 8256 | 503.9997 | 381.4206
SYL-N.1.RR.703.1 | 24541579152161 | Amborkhana, Lohapara, H # 12, Mohammed Monzil | 2019-08-22 | NQ1003 | 23.9 | 218 | 23.9 | 219 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 23.9 | 23.9 | 1.434 | 1.434 | 0.0007168 | 100% | 0% | 1.434 | 1.434 | 0.0011869 | 28 | 0.028747 | 0.028747 |  | 0 | 0 | 8256 | 503.9997 | 251.8219
SYL-N.1.RR.704.1 | 24541459152165 | Amborkhana, Lohapara,Engineer Babul Mia | 2019-08-22 | NQ1003 | 12.3 | 220 | 12.3 | 221 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 8256 | 503.9997 | 129.5987
SYL-N.1.RR.705.1 | 24541459152165 | Amborkhana, Lohapara, Asikur Rahman | 2019-08-22 | NQ1003 | 13.5 | 223 | 14.5 | 224 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 8256 | 503.9997 | 152.779
SYL-N.1.RR.706.1 | 24541589152187 | Amborkhana, Lohapara, Kazi Jalal Uddin R/A, H # 22/1 | 2019-08-22 | NQ1003 | 18.5 | 225 | 18.5 | 226 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 8256 | 503.9997 | 194.9249
SYL-N.1.RR.707.1 | 24541589152187 | Amborkhana, Lohapara, Kazi Jalal Uddin R/A, H # 22/1 | 2019-08-22 | NQ1003 | 10.2 | 227 | 10.2 | 228 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8256 | 503.9997 | 107.4721
SYL-N.1.RR.708.1 | 24541449152189 | Amborkhana, Lohapara, Kazi Jalal Uddin R/A, Lippy Tower | 2019-08-22 | NQ1003 | 40.7 | 229 | 41.6 | 230 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 41.6 | 41.6 | 2.496 | 2.496 | 0.0007168 | 100% | 0% | 2.496 | 2.496 | 0.0011869 | 28 | 0.050036 | 0.050036 |  | 0 | 0 | 8256 | 503.9997 | 438.3176
SYL-N.1.RR.709.1 | 24541419152209 | Amborkhana, Lohapara, Kazi Jalal Uddin R/A, H # 35 | 2019-08-22 | NQ1003 | 10.8 | 231 | 10.8 | 232 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8256 | 503.9997 | 113.794
SYL-N.1.RR.710.1 | 24541289152232 | Amborkhana, Lohapara, Kazi Jalal Uddin R/A, H # 54/K | 2019-08-22 | NQ1003 | 8.5 | 233 | 9 | 234 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8256 | 503.9997 | 94.8283
SYL-N.1.RR.711.1 | 24541289152232 | Amborkhana, Lohapara, Kazi Jalal Uddin R/A, H # 52 | 2019-08-22 | NQ1003 | 7.5 | 235 | 7.5 | 236 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 8256 | 503.9997 | 79.0236
SYL-N.1.RR.712.1 | 24541689152261 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, Sayem Ahmed | 2019-08-22 | NQ1003 | 10.2 | 237 | 10.2 | 238 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8256 | 503.9997 | 107.4721
SYL-N.1.RR.713.1 | 24541549152261 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, H # 120/A | 2019-08-22 | NQ1003 | 9.1 | 239 | 9.1 | 240 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 8256 | 503.9997 | 95.882
SYL-N.1.RR.714.1 | 24541499152291 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, H # 113 | 2019-08-22 | NQ1003 | 9.8 | 241 | 9.8 | 242 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8256 | 503.9997 | 103.2575
SYL-N.1.RR.715.1 | 24541529152282 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, Samim | 2019-08-22 | NQ1003 | 6.7 | 243 | 6.7 | 244 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 8256 | 503.9997 | 70.5944
SYL-N.1.RR.716.1 | 24541609152274 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, Hanif | 2019-08-22 | NQ1003 | 19.3 | 245 | 19.3 | 246 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 19.3 | 19.3 | 1.158 | 1.158 | 0.0007168 | 100% | 0% | 1.158 | 1.158 | 0.0011869 | 28 | 0.023214 | 0.023214 |  | 0 | 0 | 8256 | 503.9997 | 203.3541
SYL-N.1.RR.717.1 | 24541609152274 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, Hanif | 2019-08-22 | NQ1003 | 21.5 | 247 | 21.5 | 248 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 21.5 | 21.5 | 1.29 | 1.29 | 0.0007168 | 100% | 0% | 1.29 | 1.29 | 0.0011869 | 28 | 0.02586 | 0.02586 |  | 0 | 0 | 8256 | 503.9997 | 226.5343
SYL-N.1.RR.718.1 | 24541249152280 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, H # 41/D | 2019-08-22 | NQ1003 | 15.8 | 249 | 15.8 | 250 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 8256 | 503.9997 | 166.4764
SYL-N.1.RR.719.1 | 24541209152282 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, H # 38/D | 2019-08-22 | NQ1003 | 13.7 | 253 | 13.7 | 254 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 8256 | 503.9997 | 144.3498
SYL-N.1.RR.719.2 | 24541209152282 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, H # 38/D | 2020-10-21 | NQ1003 | 9.7 | 104 | 9.7 | 105 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8256 | 503.9997 | 102.2039
SYL-N.1.RR.720.1 | 24541119152265 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, Layek Khan | 2019-08-22 | NQ1003 | 15 | 257 | 14.4 | 258 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 8256 | 503.9997 | 151.7253
SYL-N.1.RR.721.1 | 24541119152248 | Amborkhana, Kazitula, Kazi Jalal Uddin R/A, Ana Mia | 2019-08-22 | NQ1003 | 14 | 259 | 13 | 260 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8256 | 503.9997 | 136.9743
SYL-N.1.RR.722.1 | 24540329152258 | Kazitula, Bihongo R/A, H # 59/A | 2019-08-25 | NQ1003 | 8.8 | 297 | 8.8 | 298 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8256 | 503.9997 | 92.721
SYL-N.1.RR.723.1 | 24540329152258 | Kazitula, Bihongo R/A, H # 59/A | 2019-08-25 | NQ1003 | 9.4 | 299 | 9.4 | 300 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8256 | 503.9997 | 99.0429
SYL-N.1.RR.724.1 | 24540609152248 | Kazitula, Bihongo R/A, H # 5/B | 2019-08-25 | NQ1003 | 13 | 301 | 13 | 302 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 8256 | 503.9997 | 136.9743
SYL-N.1.RR.725.1 | 24540609152248 | Kazitula, Bihongo R/A, H # 5/B | 2019-08-25 | NQ1003 | 10.2 | 303 | 10.2 | 304 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8256 | 503.9997 | 107.4721
SYL-N.1.RR.726.1 | 24535639152353 | Sadar Thana, Charadhigirpar, H # 84/A | 2019-08-25 | NQ1003 | 10.2 | 305 | 10.2 | 306 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8280 | 479.9997 | 107.4721
SYL-N.1.RR.727.1 | 24535579152342 | Sadar Thana, Charadhigirpar, H # 4 | 2019-08-25 | NQ1003 | 11.5 | 307 | 11.5 | 308 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8280 | 479.9997 | 121.1695
SYL-N.1.RR.728.1 | 24535579152358 | Charadhigirpar, Al-Amin R/A, H # 81/A | 2019-08-25 | NQ1003 | 130.4 | 311 | 132.7 | 312 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 132.7 | 132.7 | 7.962 | 7.962 | 0.0007168 | 100% | 0% | 7.962 | 7.962 | 0.0011869 | 28 | 0.15961 | 0.15961 |  | 0 | 0 | 8280 | 479.9997 | 1398.1911
SYL-N.1.RR.729.1 | 24535489152369 | Charadhigirpar, Al-Amin R/A, H # 71 | 2019-08-25 | NQ1003 | 11.5 | 309 | 11.5 | 310 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8280 | 479.9997 | 121.1695
SYL-N.1.RR.730.1 | 24535259152391 | Charadhigirpar, Al-Amin R/A, H # 119 | 2019-08-25 | NQ1003 | 17 | 313 | 17 | 314 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 8280 | 479.9997 | 179.1202
SYL-N.1.RR.731.1 | 24535349152391 | Charadhigirpar, Al-Amin R/A, H # 116 | 2019-08-25 | NQ1003 | 7.8 | 315 | 7.8 | 316 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 8280 | 479.9997 | 82.1846
SYL-N.1.RR.732.1 | 24535309152351 | Charadhigirpar, Al-Amin R/A, H # 11 | 2019-08-25 | NQ1003 | 10.3 | 319 | 10.3 | 320 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8280 | 479.9997 | 108.5258
SYL-N.1.RR.733.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 10.2 | 363 | 10.2 | 364 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8184 | 575.9997 | 107.4721
SYL-N.1.RR.734.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 28.4 | 365 | 28.4 | 366 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 28.4 | 28.4 | 1.704 | 1.704 | 0.0007168 | 100% | 0% | 1.704 | 1.704 | 0.0011869 | 28 | 0.034159 | 0.034159 |  | 0 | 0 | 8184 | 575.9997 | 299.2361
SYL-N.1.RR.735.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 17.2 | 367 | 17.2 | 368 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 8184 | 575.9997 | 181.2275
SYL-N.1.RR.736.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 9.1 | 369 | 8.4 | 370 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8184 | 575.9997 | 88.5064
SYL-N.1.RR.737.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 11.9 | 371 | 11.9 | 372 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8184 | 575.9997 | 125.3841
SYL-N.1.RR.738.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 8.9 | 373 | 9 | 374 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8184 | 575.9997 | 94.8283
SYL-N.1.RR.739.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 7 | 375 | 7 | 376 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 8184 | 575.9997 | 73.7554
SYL-N.1.RR.740.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 13.5 | 377 | 13.5 | 378 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 8184 | 575.9997 | 142.2425
SYL-N.1.RR.741.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 8.9 | 379 | 8.9 | 380 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8184 | 575.9997 | 93.7747
SYL-N.1.RR.742.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 11.8 | 381 | 11.8 | 382 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 8184 | 575.9997 | 124.3305
SYL-N.1.RR.743.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 12 | 383 | 12 | 384 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8184 | 575.9997 | 126.4378
SYL-N.1.RR.744.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 12.2 | 385 | 12 | 386 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 8184 | 575.9997 | 126.4378
SYL-N.1.RR.745.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 9.2 | 387 | 9.2 | 388 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8184 | 575.9997 | 96.9356
SYL-N.1.RR.746.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 6.8 | 389 | 6.8 | 390 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 8184 | 575.9997 | 71.6481
SYL-N.1.RR.747.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 5.9 | 391 | 5.9 | 392 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 8184 | 575.9997 | 62.1652
SYL-N.1.RR.747.2 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2021-02-14 | NQ1003 | 7.3 | 245 | 7.4 | 246 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 8184 | 575.9997 | 77.97
SYL-N.1.RR.748.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 11.5 | 393 | 10.6 | 394 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8184 | 575.9997 | 111.6867
SYL-N.1.RR.749.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 9.4 | 396 | 9.4 | 397 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8184 | 575.9997 | 99.0429
SYL-N.1.RR.750.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 8.7 | 398 | 8.7 | 399 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8184 | 575.9997 | 91.6674
SYL-N.1.RR.751.1 | 24540719152282 | Sylhet, Kazitula, Block-A, H # 69 | 2019-08-24 | NQ1003 | 8.7 | 293 | 8.8 | 294 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8256 | 503.9997 | 92.721
SYL-N.1.RR.751.2 | 24540719152282 | Sylhet, Kazitula, Block-A, H # 69 | 2021-02-15 | NQ1007 | 2.5 | 192 | 2.5 | 193 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 8256 | 503.9997 | 26.3412
SYL-N.1.RR.752.1 | 24540619152274 | Sylhet, Kazitula, Block-A, Gias Mia, H # 69 | 2019-08-24 | NQ1003 | 5 | 295 | 5 | 296 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 8256 | 503.9997 | 52.6824
SYL-N.1.RR.753.1 | 24535229152352 | Sylhet, Charadighirpar, Alamin-63 | 2019-08-25 | NQ1003 | 10.4 | 321 | 10.4 | 322 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8280 | 479.9997 | 109.5794
SYL-N.1.RR.754.1 | 24535269152339 | Sylhet, Charadighirpar, Alamin-14 | 2019-08-25 | NQ1003 | 6.9 | 323 | 6.4 | 324 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 8280 | 479.9997 | 67.4335
SYL-N.1.RR.755.1 | 24535199152328 | Sylhet, Charadighirpar, Alamin-15 | 2019-08-25 | NQ1003 | 14.1 | 325 | 13.7 | 326 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 8280 | 479.9997 | 144.3498
SYL-N.1.RR.756.1 | 24535199152328 | Sylhet, Charadighirpar, Alamin-14 | 2019-08-25 | NQ1003 | 3 | 327 | 3 | 328 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 8280 | 479.9997 | 31.6094
SYL-N.1.RR.757.1 | 24535119152343 | Sylhet, Charadighirpar, Janoni Bandon, Alamin-18 | 2019-08-25 | NQ1003 | 9.6 | 329 | 9.6 | 330 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8280 | 479.9997 | 101.1502
SYL-N.1.RR.758.1 | 24535009152338 | Sylhet, Charadighirpar, Shaheb Mia, Alamin-25 | 2019-08-25 | NQ1003 | 5.1 | 331 | 5.1 | 332 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 8280 | 479.9997 | 53.7361
SYL-N.1.RR.759.1 | 24534829152324 | Sylhet, Charadighirpar, Riya Kunjo, Alamin-31 | 2019-08-25 | NQ1003 | 9.8 | 333 | 9.8 | 334 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 8280 | 479.9997 | 103.2575
SYL-N.1.RR.760.1 | 24534809152346 | Sylhet, Sowdagortula R/A, H # 66 | 2019-08-25 | NQ1003 | 10.4 | 335 | 10.4 | 336 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8280 | 479.9997 | 109.5794
SYL-N.1.RR.761.1 | 24534609152387 | Sylhet, Sowdagortula, Biram Sowdagor Pach Pirar Majar, H # 29 | 2019-08-26 | NQ1003 | 11.3 | 337 | 11.3 | 338 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8280 | 479.9997 | 119.0622
SYL-N.1.RR.762.1 | 24534609152387 | Sylhet, Sowdagortula, Biram Sowdagor Pach Pirar Majar, H # 29 | 2019-08-26 | NQ1003 | 3.7 | 341 | 3.7 | 342 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 8280 | 479.9997 | 38.985
SYL-N.1.RR.763.1 | 24534929152397 | Sylhet, Sowdagortula, Abdul Kader, H # 38 | 2019-08-26 | NQ1003 | 10.5 | 343 | 10.5 | 344 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 8280 | 479.9997 | 110.6331
SYL-N.1.RR.764.1 | 24534929152397 | Sylhet, Sowdagortula, Abdul Kader, H # 38 | 2019-08-26 | NQ1003 | 9 | 345 | 9 | 346 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8280 | 479.9997 | 94.8283
SYL-N.1.RR.765.1 | 24534559152352 | Sylhet, Sowdagortula, Dhopadighir Uttorpar, H # 76/A | 2019-08-26 | NQ1003 | 11.2 | 347 | 11.2 | 348 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8280 | 479.9997 | 118.0086
SYL-N.1.RR.765.2 | 24534559152352 | Sylhet, Sowdagortula, Dhopadighir Uttorpar, H # 76/A | 2021-11-11 | NQ1007 | 8.8 | 101 | 8.8 | 102 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8280 | 479.9997 | 92.721
SYL-N.1.RR.766.1 | 24534529152364 | Sylhet, Sowdagortula, Dhopadighir Uttorpar, H # 4 | 2019-08-26 | NQ1003 | 7.3 | 349 | 7.3 | 350 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8280 | 479.9997 | 76.9163
SYL-N.1.RR.767.1 | 24534529152364 | Sylhet, Sowdagortula, Dhopadighir Uttorpar, H # 4 | 2019-08-26 | NQ1003 | 12 | 351 | 11.6 | 352 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8280 | 479.9997 | 122.2232
SYL-N.1.RR.768.1 | 24534429152419 | Sylhet, Kumarpara, Block-A, Faruk Villa, H # 5 | 2019-08-26 | NQ1003 | 13.2 | 353 | 13.2 | 354 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 8280 | 479.9997 | 139.0816
SYL-N.1.RR.769.1 | 24534929152422 | Sylhet, Kumarpara, Main Road, Block-A, H # 36 | 2019-08-26 | NQ1003 | 10.4 | 355 | 10.4 | 356 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8280 | 479.9997 | 109.5794
SYL-N.1.RR.770.1 | 24535129152403 | Sylhet, Kumarpara, Sowdagortula, Main Road, H # 40 | 2019-08-26 | NQ1003 | 10.7 | 359 | 10.7 | 360 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8280 | 479.9997 | 112.7403
SYL-N.1.RR.771.1 | 24531929152326 | Sylhet, Kamalgar, Babu Kuter, H # 122 | 2019-08-28 | NQ1003 | 13.8 | 457 | 13.8 | 458 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 8184 | 575.9997 | 145.4034
SYL-N.1.RR.772.1 | 24531839152328 | Sylhet, Kamalgar, Morom Ali, H # 125 | 2019-08-28 | NQ1003 | 11.4 | 461 | 11.4 | 462 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 8184 | 575.9997 | 120.1159
SYL-N.1.RR.773.1 | 24531829152340 | Sylhet, Kamalgar, Mostak Ahmed, H # 127 | 2019-08-28 | NQ1003 | 4.8 | 459 | 4.8 | 460 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 8184 | 575.9997 | 50.5751
SYL-N.1.RR.774.1 | 24531839152346 | Sylhet, Kamalgar, H # 128 | 2019-08-28 | NQ1003 | 8.2 | 463 | 8.2 | 464 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8184 | 575.9997 | 86.3991
SYL-N.1.RR.801.1 | 24540619152023 | Amborkhana, Bhatipara, Dorgah Gate, Rose Garden Tower | 2019-08-22 | NQ1003 | 11.3 | 195 | 11.5 | 196 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8160 | 599.9997 | 121.1695
SYL-N.1.RR.802.1 | 24540619152023 | Amborkhana, Bhatipara, Dorgah Gate, Rose Garden Tower | 2019-08-22 | NQ1003 | 9.6 | 197 | 9.6 | 198 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 8160 | 599.9997 | 101.1502
SYL-N.1.RR.803.1 | 24540989152085 | Amborkhana, East Dorgah gate, Abdur Razzaq | 2019-08-22 | NQ1003 | 11.2 | 200 | 11.2 | 201 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8160 | 599.9997 | 118.0086
SYL-N.1.RR.803.2 | 24540989152085 | Amborkhana, East Dorgah gate, Abdur Razzaq | 2021-02-16 | MN1032 | 4.6 | 169 | 4.6 | 170 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 8160 | 599.9997 | 48.4678
SYL-N.1.RR.804.1 | 24540989152085 | Amborkhana, East Dorgah gate, Chand Mia | 2019-08-22 | NQ1003 | 12.3 | 202 | 12.3 | 203 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 8160 | 599.9997 | 129.5987
SYL-N.1.RR.805.1 | 24540989152085 | Amborkhana, East Dorgah gate, Gulnahar Begum | 2019-08-22 | NQ1003 | 26.8 | 204 | 26.7 | 205 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 26.7 | 26.7 | 1.602 | 1.602 | 0.0007168 | 100% | 0% | 1.602 | 1.602 | 0.0011869 | 28 | 0.032115 | 0.032115 |  | 0 | 0 | 8160 | 599.9997 | 281.324
SYL-N.1.RR.806.1 | 24540989152085 | Amborkhana, East Dorgah gate, Abdul Hannan | 2019-08-22 | NQ1003 | 29 | 206 | 29 | 207 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 29 | 29 | 1.74 | 1.74 | 0.0007168 | 100% | 0% | 1.74 | 1.74 | 0.0011869 | 28 | 0.034881 | 0.034881 |  | 0 | 0 | 8160 | 599.9997 | 305.558
SYL-N.1.RR.807.1 | 24541179152068 | Amborkhana, East Dorgah gate, Kaniz Fatema Rokeya, H # B-111/1 | 2019-08-22 | NQ1003 | 8.7 | 208 | 8.7 | 209 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8160 | 599.9997 | 91.6674
SYL-N.1.RR.808.1 | 24541569152085 | Amborkhana, East Dorgah gate, Waves-B-96 | 2019-08-22 | NQ1003 | 10.4 | 212 | 11.1 | 213 | 2022-01-01 | 2022-12-07 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8160 | 599.9997 | 116.9549
SYL-N.1.RR.809.1 | 24541199152134 | Amborkhana, Chandontula, East Dorgah gate, H # 42/A | 2019-08-22 | NQ1003 | 12.8 | 214 | 12.8 | 215 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8256 | 503.9997 | 134.867
SYL-N.1.RR.810.1 | 24540819152144 | Amborkhana, Chandontula, East Dorgah gate, Choyon-11/1 | 2019-08-22 | NQ1003 | 5.4 | 216 | 5.4 | 217 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 8256 | 503.9997 | 56.897
SYL-N.1.RR.811.1 | 24540989152153 | Amborkhana, Chandontula, Kamran Ahmed | 2019-08-24 | LX1011 | 38.5 | 136 | 38.5 | 137 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 38.5 | 38.5 | 2.31 | 2.31 | 0.0007168 | 100% | 0% | 2.31 | 2.31 | 0.0011869 | 28 | 0.046308 | 0.046308 |  | 0 | 0 | 8256 | 503.9997 | 405.6545
SYL-N.1.RR.812.1 | 24540989152153 | Amborkhana, Chandontula, Imran Ahmed | 2019-08-24 | LX1011 | 14.3 | 138 | 14.3 | 139 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 8256 | 503.9997 | 150.6717
SYL-N.1.RR.813.1 | 24540989152153 | Amborkhana, Chandontula, Rehana Begum | 2019-08-24 | LX1011 | 21.7 | 140 | 21.7 | 141 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 8256 | 503.9997 | 228.6416
SYL-N.1.RR.814.1 | 24540989152153 | Amborkhana, Chandontula, Jamal Ahmad | 2019-08-24 | LX1011 | 11.7 | 142 | 11.7 | 143 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8256 | 503.9997 | 123.2768
SYL-N.1.RR.815.1 | 24540829152117 | Amborkhana, East Dorgha Gate, beside of Zafran Restaurant | 2019-08-24 | LX1011 | 11 | 144 | 11 | 145 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8256 | 503.9997 | 115.9013
SYL-N.1.RR.816.1 | 24540829152117 | Amborkhana, East Dorgha Gate, Choyon-2/3 | 2019-08-24 | LX1011 | 10.2 | 146 | 10.2 | 147 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 8256 | 503.9997 | 107.4721
SYL-N.1.RR.817.1 | 24540689152158 | Chowhatta, Raza Gowrogobindo hill, Niloy- 54/1 | 2019-08-24 | LX1011 | 12.5 | 148 | 12.5 | 149 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 8256 | 503.9997 | 131.706
SYL-N.1.RR.818.1 | 24535839152197 | Chowhatta, Mirboxtula, Azadi- 101 | 2019-08-24 | LX1011 | 13.7 | 150 | 14.6 | 151 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 8256 | 503.9997 | 153.8326
SYL-N.1.RR.819.1 | 24535839152197 | Chowhatta, Mirboxtula, Azadi- 100 | 2019-08-24 | LX1011 | 12.2 | 154 | 11.9 | 155 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8256 | 503.9997 | 125.3841
SYL-N.1.RR.819.2 | 24535839152197 | Chowhatta, Mirboxtula, Azadi- 100 | 2021-02-15 | NQ1007 | 3.5 | 190 | 3.5 | 191 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 8256 | 503.9997 | 36.8777
SYL-N.1.RR.820.1 | 24535289152157 | Sylhet, Tatipara, Anwara Begum, H # 57 | 2019-08-25 | LX1011 | 11.4 | 174 | 11.5 | 175 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8256 | 503.9997 | 121.1695
SYL-N.1.RR.821.1 | 24535259152133 | Sylhet, Tatipara, H # 43 | 2019-08-25 | LX1011 | 10.8 | 176 | 10.8 | 177 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8256 | 503.9997 | 113.794
SYL-N.1.RR.822.1 | 24534919152111 | Sylhet,Tatipara, Zindabazar, Sarwar, H # 35 | 2019-08-25 | LX1011 | 7.3 | 178 | 7.3 | 179 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 8256 | 503.9997 | 76.9163
SYL-N.1.RR.823.1 | 24534919152111 | Sylhet, Tatipara, Zindabazar, Newton Girls Hostel, H # 30 | 2019-08-25 | LX1011 | 9.9 | 180 | 9.4 | 181 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 8256 | 503.9997 | 99.0429
SYL-N.1.RR.824.1 | 24534679152108 | Sylhet, Tatipara, Zindabazar, Jamal Ahmed, H # 19 | 2019-08-25 | LX1011 | 8.6 | 182 | 8.6 | 183 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 8256 | 503.9997 | 90.6137
SYL-N.1.RR.825.1 | 24534689152099 | Sylhet, Tatipara, Zindabazar, Golam Rabbani, H # 16 | 2019-08-25 | LX1011 | 6.9 | 184 | 6.9 | 185 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 8256 | 503.9997 | 72.7017
SYL-N.1.RR.826.1 | 24534189152127 | Sylhet, East Zindabazar, Hazi Mosharrof | 2019-08-25 | LX1011 | 13.7 | 186 | 13.7 | 187 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 8136 | 623.9997 | 144.3498
SYL-N.1.RR.826.2 | 24534189152127 | Sylhet, East Zindabazar, Hazi Mosharrof | 2021-11-08 | NQ1007 | 12.2 | 97 | 11.9 | 98 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 8136 | 623.9997 | 125.3841
SYL-N.1.RR.827.1 | 24534239152172 | East Zindabazar, Barutkhana, Beside of Tobarok Ali Masjid, H # 69 | 2019-08-25 | LX1011 | 15.3 | 188 | 15.3 | 189 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 8136 | 623.9997 | 161.2082
SYL-N.1.RR.828.1 | 24534239152172 | East Zindabazar, Barutkhana,Beside of Tobarok Ali Masjid, H # 70 | 2019-08-25 | LX1011 | 36.7 | 190 | 36.7 | 191 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 36.7 | 36.7 | 2.202 | 2.202 | 0.0007168 | 100% | 0% | 2.202 | 2.202 | 0.0011869 | 28 | 0.044143 | 0.044143 |  | 0 | 0 | 8136 | 623.9997 | 386.6889
SYL-N.1.RR.829.1 | 24534119152174 | Barutkhana, Uttaran, H # 73 | 2019-08-25 | LX1011 | 16.4 | 192 | 16.4 | 193 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 16.4 | 16.4 | 0.984 | 0.984 | 0.0007168 | 100% | 0% | 0.984 | 0.984 | 0.0011869 | 28 | 0.019726 | 0.019726 |  | 0 | 0 | 8136 | 623.9997 | 172.7983
SYL-N.1.RR.830.1 | 24534119152174 | Barutkhana, Uttaran, H # 73 | 2019-08-25 | LX1011 | 17 | 194 | 17 | 195 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 17 | 17 | 1.02 | 1.02 | 0.0007168 | 100% | 0% | 1.02 | 1.02 | 0.0011869 | 28 | 0.020448 | 0.020448 |  | 0 | 0 | 8136 | 623.9997 | 179.1202
SYL-N.1.RR.831.1 | 24532309152231 | Bondor Bazar, Mohajon Potti, Parboti | 2019-08-26 | LX1011 | 32.7 | 276 | 32.7 | 277 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 32.7 | 32.7 | 1.962 | 1.962 | 0.0007168 | 100% | 0% | 1.962 | 1.962 | 0.0011869 | 28 | 0.039331 | 0.039331 |  | 0 | 0 | 8256 | 503.9997 | 344.5429
SYL-N.1.RR.832.1 | 24532309152231 | Bondor Bazar, Mohajon Potti, Bolo Ram | 2019-08-26 | LX1011 | 6.6 | 278 | 6.6 | 279 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 8256 | 503.9997 | 69.5408
SYL-N.1.RR.833.1 | 24532309152231 | Bondor Bazar, Mohajon Potti, Dudu Mia | 2019-08-26 | LX1011 | 13.9 | 280 | 13.9 | 281 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 8256 | 503.9997 | 146.4571
SYL-N.1.RR.834.1 | 24532309152231 | Bondor Bazar, Mohajon Potti, Ronjon | 2019-08-26 | LX1011 | 11.7 | 282 | 11.7 | 283 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8256 | 503.9997 | 123.2768
SYL-N.1.RR.835.1 | 24532169152230 | Bondor Bazar, Mohajon Potti, Puzus Bonik | 2019-08-26 | LX1011 | 11.3 | 284 | 10.7 | 285 | 2022-01-01 | [9 empty] | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0
SYL-N.1.RR.836.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 11.5 | 286 | 11.5 | 287 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8184 | 575.9997 | 121.1695
SYL-N.1.RR.837.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 6.3 | 288 | 6.3 | 289 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8184 | 575.9997 | 66.3798
SYL-N.1.RR.838.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 19.4 | 290 | 19.5 | 291 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 19.5 | 19.5 | 1.17 | 1.17 | 0.0007168 | 100% | 0% | 1.17 | 1.17 | 0.0011869 | 28 | 0.023454 | 0.023454 |  | 0 | 0 | 8184 | 575.9997 | 205.4614
SYL-N.1.RR.839.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 16.9 | 292 | 16.9 | 293 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 8184 | 575.9997 | 178.0665
SYL-N.1.RR.840.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 14.7 | 294 | 14.7 | 295 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 8184 | 575.9997 | 154.8863
SYL-N.1.RR.841.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 13.2 | 296 | 13.2 | 297 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 8184 | 575.9997 | 139.0816
SYL-N.1.RR.842.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 18 | 298 | 18.1 | 299 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 18.1 | 18.1 | 1.086 | 1.086 | 0.0007168 | 100% | 0% | 1.086 | 1.086 | 0.0011869 | 28 | 0.021771 | 0.021771 |  | 0 | 0 | 8184 | 575.9997 | 190.7103
SYL-N.1.RR.843.1 | 24532249152406 | Sobhanighat, Chalibondor, Sthapona Nurjahan tower, Somota-7 | 2019-08-26 | LX1011 | 17.6 | 300 | 17.6 | 301 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 17.6 | 17.6 | 1.056 | 1.056 | 0.0007168 | 100% | 0% | 1.056 | 1.056 | 0.0011869 | 28 | 0.021169 | 0.021169 |  | 0 | 0 | 8184 | 575.9997 | 185.4421
SYL-N.1.RR.844.1 | 24531279152322 | Chorarpar, Jame Masjid Goli, Nur Islam | 2019-08-27 | NQ1003 | 15.7 | 440 | 15.7 | 441 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 8256 | 503.9997 | 165.4228
SYL-N.1.RR.845.1 | 24531619152344 | Chorarpar, Jame Masjid Goli, Mintu Mia | 2019-08-27 | NQ1003 | 10.8 | 442 | 10.9 | 443 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 8256 | 503.9997 | 114.8476
SYL-N.1.RR.846.1 | 24531509152361 | Chorarpar, Jame Masjid Goli, Helal Mia | 2019-08-27 | NQ1003 | 21.4 | 446 | 21.4 | 447 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 8256 | 503.9997 | 225.4807
SYL-N.1.RR.847.1 | 24531589152325 | Chorarpar, Jame Masjid Goli, Jony Mia | 2019-08-27 | NQ1003 | 9 | 449 | 9 | 450 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 8256 | 503.9997 | 94.8283
SYL-N.1.RR.848.1 | 24531349152297 | Chorarpar, Amzad Ali Road, Sugandha-67/A | 2019-08-27 | NQ1003 | 10.3 | 451 | 10.3 | 452 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8256 | 503.9997 | 108.5258
SYL-N.1.RR.848.2 | 24531349152297 | Chorarpar, Amzad Ali Road, Sugandha-67/A | 2020-10-27 | NQ1003 | 1.2 | 205 | 1.2 | 206 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 8256 | 503.9997 | 12.6438
SYL-N.1.RR.849.1 | 24531569152250 | Kalighat, Amzad Ali Road, Gows Uddin | 2019-08-27 | NQ1003 | 9.7 | 453 | 9.7 | 454 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8256 | 503.9997 | 102.2039
SYL-N.1.RR.849.2 | 24531569152250 | Kalighat, Amzad Ali Road, Gows Uddin | 2021-11-18 | NQ1007 | 18.6 | 103 | 18.6 | 104 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 8256 | 503.9997 | 195.9786
SYL-N.1.RR.850.1 | 24531569152250 | Kalighat, Amzad Ali Road, Zahid Khan | 2019-08-27 | NQ1003 | 12.5 | 455 | 12.5 | 456 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 8256 | 503.9997 | 131.706
SYL-N.1.RR.851.1 | 24532889151444 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, Ahad Chowdhory | 2019-08-20 | NQ1003 | 29.4 | 133 | 29.4 | 134 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 29.4 | 29.4 | 1.764 | 1.764 | 0.0007168 | 100% | 0% | 1.764 | 1.764 | 0.0011869 | 28 | 0.035362 | 0.035362 |  | 0 | 0 | 8256 | 503.9997 | 309.7725
SYL-N.1.RR.851.2 | 24532889151444 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, Ahad Chowdhory | 2021-11-18 | NQ1007 | 6.3 | 106 | 6.3 | 107 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8256 | 503.9997 | 66.3798
SYL-N.1.RR.852.1 | 24532849151467 | Sylhet Sodor, Khuliatula Road, Nilima, R/A, Md. Gas Mia | 2019-08-20 | NQ1003 | 14.7 | 135 | 14.7 | 136 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 8256 | 503.9997 | 154.8863
SYL-N.1.RR.853.1 | 24535849152233 | Sylhet Sodor, Mirboxtola, Mirboxtola Road, Ajadi, Sha Anuar Chowdhury | 2019-08-24 | LX1011 | 11.3 | 158 | 11.3 | 159 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8256 | 503.9997 | 119.0622
SYL-N.1.RR.854.1 | 24535849152236 | Sylhet Sodor, Mirboxtola, Mirboxtola Road, Ajadi - 65 | 2019-08-24 | LX1011 | 22 | 160 | 22 | 161 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 22 | 22 | 1.32 | 1.32 | 0.0007168 | 100% | 0% | 1.32 | 1.32 | 0.0011869 | 28 | 0.026461 | 0.026461 |  | 0 | 0 | 8256 | 503.9997 | 231.8026
SYL-N.1.RR.855.1 | 24535879152230 | Sylhet Sodor, Mirboxtola, Mirboxtola Road, Ajadi - 66 | 2019-08-24 | LX1011 | 12.7 | 162 | 12.7 | 163 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 8256 | 503.9997 | 133.8133
SYL-N.1.RR.857.1 | 24535969152255 | Sylhet Sodor, Mirboxtola, Mirboxtola Road, Ajadi - 57 | 2019-08-24 | LX1011 | 6 | 166 | 6 | 167 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 8256 | 503.9997 | 63.2189
SYL-N.1.RR.859.1 | 24540279152264 | Sylhet Sodor, Mirboxtola, Mirboxtola Road, Ajadi - 8/4 | 2019-08-24 | LX1011 | 16.2 | 172 | 16.2 | 173 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 8256 | 503.9997 | 170.691
SYL-N.1.RR.860.1 | 24533829152185 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 19/2 | 2019-08-25 | LX1011 | 11.7 | 196 | 11.7 | 197 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 8136 | 623.9997 | 123.2768
SYL-N.1.RR.861.1 | 24533839152172 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 22 | 2019-08-25 | LX1011 | 5.9 | 198 | 5.9 | 199 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 8136 | 623.9997 | 62.1652
SYL-N.1.RR.862.1 | 24533849152164 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 24 | 2019-08-25 | LX1011 | 12.6 | 200 | 12.6 | 201 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 8136 | 623.9997 | 132.7597
SYL-N.1.RR.863.1 | 24533879152152 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 26 | 2019-08-25 | LX1011 | 4.3 | 202 | 4.3 | 203 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 8136 | 623.9997 | 45.3069
SYL-N.1.RR.864.1 | 24533869152139 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 28 | 2019-08-25 | LX1011 | 6.3 | 204 | 6.3 | 205 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8136 | 623.9997 | 66.3798
SYL-N.1.RR.865.1 | 24533729152188 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 17/3 | 2019-08-25 | LX1011 | 4.1 | 206 | 4.1 | 207 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 8136 | 623.9997 | 43.1996
SYL-N.1.RR.866.1 | 24533589152205 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 11/5 | 2019-08-25 | LX1011 | 11.8 | 208 | 12.1 | 209 | 2022-01-01 | [9 empty] | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0
SYL-N.1.RR.867.1 | 24533569152200 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 11/4 | 2019-08-25 | LX1011 | 11.4 | 210 | 11.4 | 211 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 8136 | 623.9997 | 120.1159
SYL-N.1.RR.868.1 | 24533579152199 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 11/2 | 2019-08-25 | LX1011 | 8.9 | 212 | 8.9 | 213 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 8136 | 623.9997 | 93.7747
SYL-N.1.RR.869.1 | 24533529152189 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 12 | 2019-08-25 | LX1011 | 3.3 | 214 | 3.3 | 215 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 8136 | 623.9997 | 34.7704
SYL-N.1.RR.869.2 | 24533529152189 | Sylhet Sodoe, Barutkhana Road, Uttoron R/A, H # 12 | 2022-12-06 | NQ1007 | 6.7 | 259 | 6.7 | 260 | 2022-12-06 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 0 | 623.9997 | 5.0286
SYL-N.1.RR.870.1 | 24533489152206 | Barutkhana, Lal Bazar Road,Uttoron R/A, Allahola Monjil | 2019-08-25 | LX1011 | 13.8 | 216 | 13.8 | 217 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 8136 | 623.9997 | 145.4034
SYL-N.1.RR.871.1 | 24533479152195 | Barutkhana, Lal Bazar Road,Uttoron R/A, Al-Fala Complex | 2019-08-25 | LX1011 | 9.7 | 219 | 9.7 | 220 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 8136 | 623.9997 | 102.2039
SYL-N.1.RR.872.1 | 24533479152195 | Barutkhana, Lal Bazar Road,Uttoron R/A, Al-Fala Complex | 2019-08-25 | LX1011 | 10.1 | 221 | 10.1 | 222 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 8136 | 623.9997 | 106.4185
SYL-N.1.RR.873.1 | 24533479152195 | Barutkhana, Lal Bazar Road,Uttoron R/A, Al-Fala Complex | 2019-08-25 | LX1011 | 14.4 | 226 | 14.4 | 227 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 8136 | 623.9997 | 151.7253
SYL-N.1.RR.874.1 | 24533579152217 | Sylhet Sodoe, Barutkhana,Lal Bazar Road, Uttoron R/A, Puli Cotege | 2019-08-25 | LX1011 | 10.7 | 230 | 10.7 | 231 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8136 | 623.9997 | 112.7403
SYL-N.1.RR.875.1 | 24533239152228 | Sylhet Sodor, Bondor Bazar, Jeil Road, Holy City Dantal Care | 2019-08-26 | LX1011 | 12.6 | 232 | 12.7 | 233 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 8136 | 623.9997 | 133.8133
SYL-N.1.RR.875.2 | 24533239152228 | Sylhet Sodor, Bondor Bazar, Jeil Road, Holy City Dantal Care | 2021-11-08 | NQ1007 | 3.8 | 91 | 3.8 | 92 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8136 | 623.9997 | 40.0386
SYL-N.1.RR.876.1 | 24533359152211 | Sylhet Sodor, Barutkhana Road, Uttron R/A, H # 2 | 2019-08-26 | LX1011 | 9.4 | 234 | 9.5 | 235 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8136 | 623.9997 | 100.0966
SYL-N.1.RR.877.1 | 24533359152211 | Sylhet Sodor, Barutkhana Road, Uttron R/A, H # 3 | 2019-08-26 | LX1011 | 10.8 | 236 | 10.8 | 237 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 8136 | 623.9997 | 113.794
SYL-N.1.RR.878.1 | 24533359152211 | Sylhet Sodor, Barutkhana Road, Uttron R/A, H # 4 | 2019-08-26 | LX1011 | 14.6 | 238 | 14.6 | 239 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 8136 | 623.9997 | 153.8326
SYL-N.1.RR.879.1 | 24533359152211 | Sylhet Sodor, Barutkhana Road, Uttron R/A, Md. Maruf | 2019-08-26 | LX1011 | 11.3 | 240 | 11.3 | 241 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 8136 | 623.9997 | 119.0622
SYL-N.1.RR.879.2 | 24533359152211 | Sylhet Sodor, Barutkhana Road, Uttron R/A, Md. Maruf | 2022-12-06 | NQ1007 | 11.1 | 264 | 11.1 | 265 | 2022-12-06 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 0 | 623.9997 | 8.331
SYL-N.1.RR.880.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 31.8 | 242 | 31.8 | 243 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 31.8 | 31.8 | 1.908 | 1.908 | 0.0007168 | 100% | 0% | 1.908 | 1.908 | 0.0011869 | 28 | 0.038249 | 0.038249 |  | 0 | 0 | 8136 | 623.9997 | 335.0601
SYL-N.1.RR.881.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 11.2 | 244 | 11.2 | 245 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 8136 | 623.9997 | 118.0086
SYL-N.1.RR.882.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 10.4 | 246 | 10.4 | 247 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8136 | 623.9997 | 109.5794
SYL-N.1.RR.882.2 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2021-02-15 | LU1001 | 13.6 | 196 | 13.6 | 197 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 8136 | 623.9997 | 143.2961
SYL-N.1.RR.883.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 11.6 | 248 | 11.5 | 249 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 8136 | 623.9997 | 121.1695
SYL-N.1.RR.884.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 10.4 | 250 | 10.4 | 251 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 8136 | 623.9997 | 109.5794
SYL-N.1.RR.885.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 8.7 | 252 | 8.7 | 253 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 8136 | 623.9997 | 91.6674
SYL-N.1.RR.886.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 8.8 | 254 | 8.8 | 255 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8136 | 623.9997 | 92.721
SYL-N.1.RR.887.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 6.1 | 256 | 6.1 | 257 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8136 | 623.9997 | 64.2725
SYL-N.1.RR.888.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 6.1 | 258 | 6.1 | 259 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 8136 | 623.9997 | 64.2725
SYL-N.1.RR.888.2 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 3.4 | 260 | 3.4 | 261 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 8136 | 623.9997 | 35.824
SYL-N.1.RR.889.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 7.1 | 262 | 7.1 | 263 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 8136 | 623.9997 | 74.809
SYL-N.1.RR.890.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 7.1 | 264 | 7.1 | 265 | 2022-01-01 | 2022-12-06 | NQ1007 | 2.6 | 255 | 2.5 | 256 | 2022-12-06 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8136 | 623.9997
SYL-N.1.RR.891.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 6.3 | 266 | 6.3 | 267 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 8136 | 623.9997 | 66.3798
SYL-N.1.RR.892.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 7 | 268 | 7.1 | 269 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 8136 | 623.9997 | 74.809
SYL-N.1.RR.893.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 8.1 | 270 | 8.4 | 271 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 8136 | 623.9997 | 88.5064
SYL-N.1.RR.894.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 7.9 | 272 | 7.9 | 273 | 2022-01-01 | 2022-12-06 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 8136 | 623.9997 | 83.2382
SYL-N.1.RR.895.1 | 24533959152113 | Sylhet Sodor, Jinda Bazar Road, Al-Marjan Soping Center | 2019-08-26 | LX1011 | 2.4 | 274 | 2.4 | 275 | 2022-01-01 | 2022-12-06 | NQ1007 | 1.2 | 257 | 1.2 | 258 | 2022-12-06 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 8136 | 623.9997
SYL-N.1.RR.896.1 | 24532169152402 | Sylhet Sodor, Chalibandar, Somata R/A, H # 9 | 2019-08-27 | NQ1003 | 14.4 | 410 | 14.4 | 411 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 8184 | 575.9997 | 151.7253
SYL-N.1.RR.897.1 | 24532169152402 | Sylhet Sodor, Chalibandar, Somata R/A, H # 9 | 2019-08-27 | NQ1003 | 33 | 412 | 33 | 413 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 33 | 33 | 1.98 | 1.98 | 0.0007168 | 100% | 0% | 1.98 | 1.98 | 0.0011869 | 28 | 0.039692 | 0.039692 |  | 0 | 0 | 8184 | 575.9997 | 347.7039
SYL-N.1.RR.897.2 | 24532169152402 | Sylhet Sodor, Chalibandar, Somata R/A, H # 9 | 2021-11-11 | NQ1007 | 12.9 | 99 | 12.9 | 100 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 8184 | 575.9997 | 135.9206
SYL-N.1.RR.898.1 | 24532179152436 | Sylhet Sodor, Chalibandar, Somata R/A, H # 41/4 | 2019-08-27 | NQ1003 | 12.8 | 414 | 12.8 | 415 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8184 | 575.9997 | 134.867
SYL-N.1.RR.899.1 | 24531839152409 | Sylhet Sodor, Chalibandar, Somata R/A, H # 37/2 | 2019-08-27 | NQ1003 | 22.7 | 416 | 22.7 | 417 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 22.7 | 22.7 | 1.362 | 1.362 | 0.0007168 | 100% | 0% | 1.362 | 1.362 | 0.0011869 | 28 | 0.027303 | 0.027303 |  | 0 | 0 | 8184 | 575.9997 | 239.1781
SYL-N.1.RR.900.1 | 24531389152366 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 29 | 2019-08-27 | NQ1003 | 16.8 | 418 | 16.8 | 419 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 16.8 | 16.8 | 1.008 | 1.008 | 0.0007168 | 100% | 0% | 1.008 | 1.008 | 0.0011869 | 28 | 0.020207 | 0.020207 |  | 0 | 0 | 8256 | 503.9997 | 177.0129
SYL-N.1.RR.901.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 8.1 | 400 | 8.1 | 401 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 8184 | 575.9997 | 85.3455
SYL-N.1.RR.902.1 | 24530249152413 | Masimpur, Doyel-13 | 2019-08-26 | LU1001 | 3.7 | 64 | 3.8 | 65 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 8256 | 503.9997 | 40.0386
SYL-N.1.RR.903.1 | 24530439152390 | Masimpur, Doyel-10 | 2019-08-26 | LU1001 | 7.2 | 66 | 7.2 | 67 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 8256 | 503.9997 | 75.8627
SYL-N.1.RR.904.1 | 24532759152395 | Shobhanigat, Kastaghar Road, Kastaghar R/A, H # 46/1 | 2019-08-26 | NQ1003 | 11.1 | 402 | 11.1 | 403 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8184 | 575.9997 | 116.9549
SYL-N.1.RR.905.1 | 24530579152381 | Masimpur Sadar, Masimpur R/A, Mohammed Kibria | 2019-08-27 | LX1011 | 4.1 | 304 | 4.1 | 305 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 8256 | 503.9997 | 43.1996
SYL-N.1.RR.906.1 | 24530699152370 | Masimpur Sadar, Masimpur R/A, Md. Mokbul Hossain | 2019-08-27 | LX1011 | 8.1 | 306 | 8 | 307 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 8256 | 503.9997 | 84.2919
SYL-N.1.RR.907.1 | 24530699152370 | Masimpur Sadar, Masimpur R/A, Md. Nuruddin Mia | 2019-08-27 | LX1011 | 10 | 308 | 10.6 | 309 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 8256 | 503.9997 | 111.6867
SYL-N.1.RR.908.1 | 24530699152370 | Masimpur Sadar, Masimpur R/A, Md. Afroz Mia | 2019-08-27 | LX1011 | 8.1 | 310 | 8.1 | 311 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 8256 | 503.9997 | 85.3455
SYL-N.1.RR.908.2 | 24530699152370 | Masimpur Sadar, Masimpur R/A, Md. Afroz Mia | 2019-08-27 | LX1011 | 14.8 | 313 | 14.8 | 314 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 8256 | 503.9997 | 155.9399
SYL-N.1.RR.920.1 | 24531299152371 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 31 | 2019-08-27 | NQ1003 | 3.5 | 420 | 3.6 | 421 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 8256 | 503.9997 | 37.9313
SYL-N.1.RR.921.1 | 24531329152355 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 32 | 2019-08-27 | NQ1003 | 12.4 | 422 | 12.4 | 423 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 8256 | 503.9997 | 130.6524
SYL-N.1.RR.922.1 | 24531339152362 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 35 | 2019-08-27 | NQ1003 | 8.8 | 424 | 8.8 | 425 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 8256 | 503.9997 | 92.721
SYL-N.1.RR.923.1 | 24531309152340 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 14 | 2019-08-27 | NQ1003 | 9.9 | 426 | 9.9 | 427 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8256 | 503.9997 | 104.3112
SYL-N.1.RR.924.1 | 24531299152337 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 37/1 | 2019-08-27 | NQ1003 | 11.6 | 428 | 11.6 | 429 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 8256 | 503.9997 | 122.2232
SYL-N.1.RR.925.1 | 24531379152343 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 13/5 | 2019-08-27 | NQ1003 | 8.2 | 430 | 8.2 | 431 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 8256 | 503.9997 | 86.3991
SYL-N.1.RR.926.1 | 24531379152343 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 13/4 | 2019-08-27 | NQ1003 | 6.2 | 432 | 6.2 | 433 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 8256 | 503.9997 | 65.3262
SYL-N.1.RR.927.1 | 24531379152343 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 13/A | 2019-08-27 | NQ1003 | 12.8 | 434 | 12.8 | 435 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 8256 | 503.9997 | 134.867
SYL-N.1.RR.928.1 | 24531379152343 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 13/A | 2019-08-27 | NQ1003 | 9.9 | 436 | 9.9 | 437 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 8256 | 503.9997 | 104.3112
SYL-N.1.RR.929.1 | 24531349152334 | Sylhet Sodor, Churarpar, Sugondha R/A, H # 37 | 2019-08-27 | NQ1003 | 8.5 | 438 | 8.5 | 439 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 8256 | 503.9997 | 89.5601
SYL-N.1.RR.930.1 | 24531909152315 | Sylhet Sodor, Kalighat, Kamalgor, Ward # 18, H # 118 | 2019-08-28 | LX1011 | 10.3 | 315 | 10.3 | 316 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 8184 | 575.9997 | 108.5258
SYL-N.1.RR.931.1 | 24531909152315 | Sylhet Sodor, Kalighat, Kamalgor, Ward # 18, H # 118 | 2019-08-28 | LX1011 | 12.7 | 317 | 12.7 | 318 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 8184 | 575.9997 | 133.8133
SYL-N.1.RR.932.1 | 24531799152325 | Sylhet Sodor, Kalighat, Kamalgor, Ward # 18, H # 140/D | 2019-08-28 | LX1011 | 5.6 | 319 | 5.6 | 320 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 8184 | 575.9997 | 59.0043
SYL-N.1.RR.933.1 | 24531799152340 | Sylhet Sodor, Kalighat, Kamalgor, Ward # 18, H # 138 | 2019-08-28 | LX1011 | 9.2 | 321 | 9.2 | 322 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8184 | 575.9997 | 96.9356
SYL-N.1.RR.934.1 | 24531799152340 | Sylhet Sodor, Kalighat, Kamalgor, Ward # 18, H # 134 | 2019-08-28 | LX1011 | 6.5 | 323 | 6.5 | 324 | 2022-01-01 | 2022-12-08 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 8184 | 575.9997 | 68.4871
SYL-N.1.RR.935.1 | 24543769151441 | East Sobid Bazar, Fazil Chist R/A, H # 30 | 2019-09-03 | MN1032 | 11.4 | 381 | 11.1 | 382 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 8088 | 671.9997 | 116.9549
SYL-N.1.RR.936.1 | 24543879151446 | East Sobid Bazar, Fazil Chist R/A, Hazi Jonab Ali | 2019-09-03 | MN1032 | 9.2 | 383 | 9.2 | 384 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 8088 | 671.9997 | 96.9356
SYL-N.1.RR.937.1 | 24543879151434 | East Sobid Bazar, Fazil Chist R/A, H # 34/1 | 2019-09-03 | MN1032 | 6.5 | 385 | 6.5 | 386 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 8088 | 671.9997 | 68.4871
SYL-N.1.RR.938.1 | 24543989151428 | East Sobid Bazar, Fazil Chist R/A, H # 34/2 | 2019-09-03 | MN1032 | 10.7 | 387 | 10.7 | 388 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 8088 | 671.9997 | 112.7403
SYL-N.1.RR.939.1 | 24543989151428 | East Sobid Bazar, Fazil Chist R/A, H # 34/3 | 2019-09-03 | MN1032 | 11 | 389 | 11 | 390 | 2022-01-01 | 2022-12-04 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 8088 | 671.9997 | 115.9013
SYL-N.1.RR.946.1 | 24540969152261 | Kazitula, Luharpara, H # 36 | 2019-09-03 | NQ1008 | 3.2 | 309 | 3.2 | 310 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 8256 | 503.9997 | 33.7167
SYL-N.1.RR.947.1 | 24540969152261 | Kazitula, Luharpara, H # 35 | 2019-09-03 | NQ1008 | 11.7 | 311 | 11.4 | 312 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 8256 | 503.9997 | 120.1159
SYL-N.1.RR.948.1 | 24540939152278 | Kazitula, Luharpara, H # 31/1 | 2019-09-03 | NQ1008 | 9.5 | 313 | 9.5 | 314 | 2022-01-01 | 2022-12-11 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 8256 | 503.9997 | 100.0966
SYL-S.1.CR.1.1 | 24530809151583 | South Shurma, Bharthkhola, Station Road, Karnaphuli Mishti Ghar | 2019-07-17 | NQ1011 | 9 | 15 | 9 | 16 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7584 | 1175.9997 | 94.8283
SYL-S.1.CR.2.1 | 24521489153246 | Mugla Bazar, Word # 27, Alampur, Sairunnesha | 2019-08-01 | NQ1008 | 10.5 | 435 | 10.5 | 436 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7512 | 1247.9997 | 110.6331
SYL-S.1.RR.1.1 | 24524359151466 | South Surma, East Khojarkhola, Block # E, Rd # 01, Sopno Neer, H # 510 | 2019-07-17 | NQ1008 | 6.1 | 1 | 6.1 | 2 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7584 | 1175.9997 | 64.2725
SYL-S.1.RR.2.1 | 24524009151462 | South Surma, East Khojarkhola, Block # E, Rd # 01, Chara Pir Bari, A.R Kabir House | 2019-07-17 | NQ1008 | 17.4 | 3 | 17.4 | 4 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 7584 | 1175.9997 | 183.3348
SYL-S.1.RR.3.1 | 24523609151303 | South Surma, Laurai Abashik Alaka, Laurai Road, Porbotpur, Block # C, Rd # 02, H # 04, Azad Mia | 2019-07-17 | NQ1008 | 34.4 | 7 | 34.4 | 8 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 34.4 | 34.4 | 2.064 | 2.064 | 0.0007168 | 100% | 0% | 2.064 | 2.064 | 0.0011869 | 28 | 0.041376 | 0.041376 |  | 0 | 0 | 7584 | 1175.9997 | 362.455
SYL-S.1.RR.4.1 | 24523269151372 | South Surma, Laurai Abashik Alaka, porbotpur, Block # A, Rd # 03, H # 54, Md Saju | 2019-07-17 | NQ1008 | 13.2 | 9 | 13.2 | 10 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7584 | 1175.9997 | 139.0816
SYL-S.1.RR.5.1 | 24523299151380 | South Surma, Laurai Abashik Alaka, porbotpur, Block # A, Rd # 03, H # 52, Ali Monjil | 2019-07-17 | NQ1008 | 6.6 | 11 | 6.6 | 12 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7584 | 1175.9997 | 69.5408
SYL-S.1.RR.6.1 | 24524059151306 | South Surma, Ward # 4, Lawaii (Ummar Kabul), Block-B, Rd # 2/1, H # 58, Abdul Wahab | 2019-07-20 | NQ1008 | 10.2 | 60 | 10.2 | 61 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7584 | 1175.9997 | 107.4721
SYL-S.1.RR.7.1 | 24524059151242 | South Surma, Ward # 2, Lawaii (Ummar Kabul), Block-B, Rd # 2/1, H # 43, Selim Ahmed | 2019-07-20 | NQ1008 | 8.2 | 62 | 8.2 | 63 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7584 | 1175.9997 | 86.3991
SYL-S.1.RR.8.1 | 24523849151260 | South Surma, Ward # 2, Lawaii (Ummar Kabul), Block-B, Rd # 2/1, H # 38, Abdus Samad | 2019-07-20 | NQ1008 | 26.5 | 64 | 25 | 65 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 25 | 25 | 1.5 | 1.5 | 0.0007168 | 100% | 0% | 1.5 | 1.5 | 0.0011869 | 28 | 0.03007 | 0.03007 |  | 0 | 0 | 7584 | 1175.9997 | 263.412
SYL-S.1.RR.9.1 | 24523719151241 | South Surma, Ward # 2, Lawaii (Ummar Kabul), Block-B, Rd # 2/1, H # 18, Faruk Ahmed | 2019-07-20 | NQ1008 | 12.8 | 66 | 12.8 | 67 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7584 | 1175.9997 | 134.867
SYL-S.1.RR.10.1 | 24523719151137 | South Surma, Ward # 3, Lawaii, Raier Gram, Azom Ali | 2019-07-20 | NQ1008 | 14.8 | 68 | 14.8 | 69 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 7584 | 1175.9997 | 155.9399
SYL-S.1.RR.10.2 | 24523719151137 | South Surma, Ward # 3, Lawaii, Raier Gram, Azom Ali | 2019-07-20 | NQ1008 | 10.9 | 70 | 10.9 | 71 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7584 | 1175.9997 | 114.8476
SYL-S.1.RR.11.1 | 24523749151133 | South Surma, Ward # 3, Lawaii, Raier Gram, Shah Alom | 2019-07-20 | NQ1008 | 9.8 | 72 | 9.8 | 73 | 2022-01-01 | 2022-11-13 | MN1018 | 1.3 | 135 | 1.3 | 136 | 2022-11-13 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7584 | 1175.9997
SYL-S.1.RR.11.2 | 24523749151133 | South Surma, Ward # 3, Lawaii, Raier Gram, Shah Alom | 2021-02-28 | LU1001 | 5.3 | 228 | 5.3 | 229 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7584 | 1175.9997 | 55.8434
SYL-S.1.RR.12.1 | 24523569151044 | South Surma, Boroikandi, Ward # 3, Raygram, Rd # 01, Anjali Bhabon | 2019-07-22 | NQ1008 | 26.6 | 89 | 26.6 | 90 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 26.6 | 26.6 | 1.596 | 1.596 | 0.0007168 | 100% | 0% | 1.596 | 1.596 | 0.0011869 | 28 | 0.031994 | 0.031994 |  | 0 | 0 | 7584 | 1175.9997 | 280.2704
SYL-S.1.RR.13.1 | 24523559151076 | South Surma, Boroikandi, Ward # 3, Raygram, Rd # 01, Kajol Sutradhor | 2019-07-22 | NQ1008 | 14.2 | 91 | 14.2 | 92 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7584 | 1175.9997 | 149.618
SYL-S.1.RR.14.1 | 24523539151085 | South Surma, Boroikandi, Ward # 3, Raygram, Rd # 01, Mofiz Mia | 2019-07-22 | NQ1008 | 11.3 | 93 | 11.3 | 94 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7584 | 1175.9997 | 119.0622
SYL-S.1.RR.15.1 | 24523799151013 | South Surma, Boroikandi, Ward # 3, Kamushona, Rd # 01, Abdullah Monjil | 2019-07-22 | NQ1008 | 3.7 | 95 | 3.7 | 96 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7584 | 1175.9997 | 38.985
SYL-S.1.RR.16.1 | 24523769151053 | South Surma, Boroikandi, Ward # 3, Kamushona, Rd # 01, Ashini Kopali | 2019-07-22 | NQ1008 | 21.9 | 97 | 21.9 | 98 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 21.9 | 21.9 | 1.314 | 1.314 | 0.0007168 | 100% | 0% | 1.314 | 1.314 | 0.0011869 | 28 | 0.026341 | 0.026341 |  | 0 | 0 | 7584 | 1175.9997 | 230.7489
SYL-S.1.RR.17.1 | 24523999151056 | South Surma, Boroikandi, Ward # 3, Kamushona, Rd # 01, Ali Akbor | 2019-07-22 | NQ1008 | 1.4 | 100 | 1.4 | 101 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7584 | 1175.9997 | 14.7511
SYL-S.1.RR.18.1 | 24524149151114 | South Surma, Boroikandi, Ward # 3, Raygram, Rd # 01, Pinku Das | 2019-07-22 | NQ1008 | 92.8 | 104 | 92.8 | 105 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 92.8 | 92.8 | 5.568 | 5.568 | 0.0007168 | 100% | 0% | 5.568 | 5.568 | 0.0011869 | 28 | 0.11162 | 0.11162 |  | 0 | 0 | 7584 | 1175.9997 | 977.7855
SYL-S.1.RR.19.1 | 24524599151226 | South Surma, Boroikandi, Lawaii (Ummar Kobul), Moslondor House, Afsar Ali | 2019-07-22 | NQ1008 | 23.8 | 106 | 23.8 | 107 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 23.8 | 23.8 | 1.428 | 1.428 | 0.0007168 | 100% | 0% | 1.428 | 1.428 | 0.0011869 | 28 | 0.028627 | 0.028627 |  | 0 | 0 | 7584 | 1175.9997 | 250.7683
SYL-S.1.RR.19.2 | 24524599151226 | South Surma, Boroikandi, Lawaii (Ummar Kobul), Moslondor House, Afsar Ali | 2021-10-26 | LU1001 | 12.6 | 96 | 12.6 | 97 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7584 | 1175.9997 | 132.7597
SYL-S.1.RR.20.1 | 24524029151145 | South Surma, Boroikandi Union, Ward # 3, Rayergram, Habibur Rahman | 2019-07-23 | NQ1008 | 12.1 | 123 | 12.1 | 124 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7584 | 1175.9997 | 127.4914
SYL-S.1.RR.21.1 | 24524029151145 | South Surma, Boroikandi Union, Ward # 3, Rayergram, Mujibur Rahman | 2019-07-23 | NQ1008 | 15.6 | 125 | 15.6 | 126 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7584 | 1175.9997 | 164.3691
SYL-S.1.RR.22.1 | 24524029151145 | South Surma, Boroikandi Union, Ward # 3, Rayergram, Aatiqur Rahman | 2019-07-23 | NQ1008 | 12.5 | 127 | 12.5 | 128 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7584 | 1175.9997 | 131.706
SYL-S.1.RR.23.1 | 24524069151146 | South Surma, Boroikandi Union, Ward # 3, Rayergram, Kutub Uddin | 2019-07-23 | NQ1008 | 22.4 | 129 | 22.4 | 130 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 22.4 | 22.4 | 1.344 | 1.344 | 0.0007168 | 100% | 0% | 1.344 | 1.344 | 0.0011869 | 28 | 0.026943 | 0.026943 |  | 0 | 0 | 7584 | 1175.9997 | 236.0172
SYL-S.1.RR.24.1 | 24520859151115 | South Surma, Tetli Union, Ward # 1, Dhoradhorpur, Rd # 1, Makhon Mia | 2019-07-23 | NQ1008 | 14.5 | 131 | 14.5 | 132 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7632 | 1127.9997 | 152.779
SYL-S.1.RR.25.1 | 24520859151115 | South Surma, Tetli Union, Ward # 1, Dhoradhorpur, Rd # 1, Showkot Mia | 2019-07-23 | NQ1008 | 31 | 133 | 31 | 134 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 31 | 31 | 1.86 | 1.86 | 0.0007168 | 100% | 0% | 1.86 | 1.86 | 0.0011869 | 28 | 0.037287 | 0.037287 |  | 0 | 0 | 7632 | 1127.9997 | 326.6309
SYL-S.1.RR.26.1 | 24520859151115 | South Surma, Tetli Union, Ward # 1, Dhoradhorpur, Rd # 1, Mojnu Mia | 2019-07-23 | NQ1008 | 12 | 135 | 12 | 136 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7632 | 1127.9997 | 126.4378
SYL-S.1.RR.27.1 | 24520399151135 | South Surma, Tetli Union, Ward # 1, Dhoradhorpur, Rd # 1, H # 1, Gazi Bari | 2019-07-23 | NQ1008 | 16.3 | 137 | 16.3 | 138 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 7632 | 1127.9997 | 171.7446
SYL-S.1.RR.28.1 | 24520399151135 | South Surma, Tetli Union, Ward # 1, Dhoradhorpur, Rd # 1, H # 1, Gazi Bari | 2019-07-23 | NQ1008 | 12.6 | 139 | 12.6 | 140 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7632 | 1127.9997 | 132.7597
SYL-S.1.RR.29.1 | 24511839150539 | South Surma, Boldi R/A, Rd # 01, Ward # 2, Block-A, Soleman Ali | 2019-07-24 | NQ1008 | 5.8 | 141 | 5.8 | 142 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7632 | 1127.9997 | 61.1116
SYL-S.1.RR.30.1 | 24511839150539 | South Surma, Boldi R/A, Rd # 01, Ward # 2, Block-A, Soleman Ali | 2019-07-24 | NQ1008 | 4.2 | 143 | 4.2 | 144 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7632 | 1127.9997 | 44.2532
SYL-S.1.RR.31.1 | 24511889150596 | South Surma, Boldi R/A, Rd # 01, Ward # 2, Block-A, Manik Mia | 2019-07-24 | NQ1008 | 24.5 | 145 | 24.5 | 146 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 7632 | 1127.9997 | 258.1438
SYL-S.1.RR.32.1 | 24512469150578 | South Surma, Boldi R/A, Rd # 02, Block-B, H # 115, Furkan Monjil | 2019-07-24 | NQ1008 | 5.6 | 147 | 5.6 | 148 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7632 | 1127.9997 | 59.0043
SYL-S.1.RR.33.1 | 24512469150578 | South Surma, Boldi R/A, Tetli Union, Ward # 2, Block-B, Rd # 2, Motaleb Mia | 2019-07-24 | NQ1008 | 14.5 | 149 | 14.5 | 150 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7632 | 1127.9997 | 152.779
SYL-S.1.RR.34.1 | 24512339150574 | South Surma, Boldi R/A, Tetli Union, Ward # 2, Block-B, Rd # 2, H # 84, Azmol Ali | 2019-07-24 | NQ1008 | 11 | 151 | 11 | 152 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7632 | 1127.9997 | 115.9013
SYL-S.1.RR.35.1 | 24512329150577 | South Surma, Boldi R/A, Tetli Union, Ward # 2, Block-B, Rd # 2, Harun Mia | 2019-07-24 | NQ1008 | 7.1 | 153 | 7.1 | 154 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7632 | 1127.9997 | 74.809
SYL-S.1.RR.36.1 | 24511649151003 | South Surma, 3No Tetli Union, Ward # 2, Boldi R/A, Block-B, Mokseduil Karim Nuhel | 2019-07-25 | NQ1008 | 7.4 | 171 | 7.5 | 172 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7632 | 1127.9997 | 79.0236
SYL-S.1.RR.37.1 | 24511239150587 | South Surma, 3No Tetli Union, Ward # 2, Boldi R/A, Block-B, H # 172, Abdul Rokib | 2019-07-25 | NQ1008 | 19.7 | 173 | 19.7 | 174 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 19.7 | 19.7 | 1.182 | 1.182 | 0.0007168 | 100% | 0% | 1.182 | 1.182 | 0.0011869 | 28 | 0.023695 | 0.023695 |  | 0 | 0 | 7632 | 1127.9997 | 207.5687
SYL-S.1.RR.38.1 | 24511019150587 | South Surma, 3No Tetli Union, Ward # 2, Boldi R/A, Block-B, Sultan Mia | 2019-07-25 | NQ1008 | 16.7 | 175 | 16.7 | 176 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 7632 | 1127.9997 | 175.9592
SYL-S.1.RR.39.1 | 24505419150353 | South Surma, Banesshorpur, Ward # 3, Road # 1, Block # A, Manik Mia | 2019-07-25 | NQ1008 | 25.8 | 177 | 25.8 | 178 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 25.8 | 25.8 | 1.548 | 1.548 | 0.0007168 | 100% | 0% | 1.548 | 1.548 | 0.0011869 | 28 | 0.031032 | 0.031032 |  | 0 | 0 | 7632 | 1127.9997 | 271.8412
SYL-S.1.RR.40.1 | 24530319150256 | South Surma, Mollargoan, Telirai, Gupshahar, Sadekur Rahman | 2019-07-25 | NQ1011 | 13.1 | 193 | 12.8 | 194 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7680 | 1079.9997 | 134.867
SYL-S.1.RR.41.1 | 24530499150138 | South Surma, Mollargoan, Telirai, Gupshahar, Sadek Ahmad | 2019-07-25 | NQ1011 | 4.6 | 195 | 4.4 | 196 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7680 | 1079.9997 | 46.3605
SYL-S.1.RR.42.1 | 24530709150143 | South Surma, Mollargoan, Telirai, Gupshahar, Mushahid Khan | 2019-07-25 | NQ1011 | 6.1 | 197 | 6.1 | 198 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7680 | 1079.9997 | 64.2725
SYL-S.1.RR.43.1 | 24531329150303 | South Surma, Mollargoan, Mokon Dukan, Kamal Bazar Road, Soleman Khan | 2019-07-25 | NQ1011 | 27 | 199 | 27 | 200 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 27 | 27 | 1.62 | 1.62 | 0.0007168 | 100% | 0% | 1.62 | 1.62 | 0.0011869 | 28 | 0.032475 | 0.032475 |  | 0 | 0 | 7680 | 1079.9997 | 284.485
SYL-S.1.RR.51.1 | 24522699151390 | Pirojpur, Dokkhin Surma, Word # 5, H # 75, Shafiqul Haque | 2019-07-17 | NQ1008 | 24.1 | 13 | 24.1 | 14 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 24.1 | 24.1 | 1.446 | 1.446 | 0.0007168 | 100% | 0% | 1.446 | 1.446 | 0.0011869 | 28 | 0.028987 | 0.028987 |  | 0 | 0 | 7584 | 1175.9997 | 253.9292
SYL-S.1.RR.52.1 | 24522679151396 | Pirojpur, Dokkhin Surma, Word # 5, H # 5, Rd # 3, Tomjid Alli | 2019-07-17 | NQ1008 | 15.8 | 15 | 15.8 | 16 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7584 | 1175.9997 | 166.4764
SYL-S.1.RR.53.1 | 24523289151399 | Dhakkin Surma, Lawai, Word # 3, Nijam Miar Bari, Nijam Uddin | 2019-07-17 | NQ1008 | 8.3 | 17 | 8.3 | 18 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7584 | 1175.9997 | 87.4528
SYL-S.1.RR.53.2 | 24523289151399 | Dhakkin Surma, Lawai, Word # 3, Nijam Miar Bari, Nijam Uddin | 2019-07-17 | NQ1008 | 4.8 | 19 | 4.8 | 20 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7584 | 1175.9997 | 50.5751
SYL-S.1.RR.54.1 | 24522889151348 | Lawai, Porbotpur, Shapla Geat, Road # 4, Block - E, Alongir Mia | 2019-07-17 | NQ1008 | 5.9 | 21 | 5.9 | 22 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7584 | 1175.9997 | 62.1652
SYL-S.1.RR.54.2 | 24522889151348 | Lawai, Porbotpur, Shapla Geat, Road # 4, Block - E, Alongir Mia | 2022-11-13 | MN1018 | 1.6 | 133 | 1.6 | 134 | 2022-11-13 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 0 | 1175.9997 | 2.2632
SYL-S.1.RR.55.1 | 24522889151348 | Lawai, Porbotpur, Shapla Geat, Road # 4, Block - E, H # 12, Khalilur Rahman | 2019-07-17 | NQ1008 | 5.5 | 24 | 5.5 | 25 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7584 | 1175.9997 | 57.9506
SYL-S.1.RR.56.1 | 24522159151331 | Pirojpur, Bonghobir Road, Jubo Unnaon Kendro, Ancholik Manob Shampod Unnaon Kendro | 2019-07-17 | NQ1008 | 3.3 | 26 | 3.3 | 27 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7584 | 1175.9997 | 34.7704
SYL-S.1.RR.57.1 | 24521929151366 | Pirojpur, Bonghobir Road, Khan Bari, Surma Selay Proshikhon Kendro, Sayful Khan | 2019-07-17 | NQ1008 | 11.4 | 30 | 11.4 | 31 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7584 | 1175.9997 | 120.1159
SYL-S.1.RR.58.1 | 24521929151366 | Pirojpur, Bonghobir Road, Khan Bari, Surma Selay Proshikhon Kendro, Sayful Khan | 2019-07-17 | NQ1008 | 8.8 | 32 | 8.8 | 33 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7584 | 1175.9997 | 92.721
SYL-S.1.RR.58.2 | 24521929151366 | Pirojpur, Bonghobir Road, Khan Bari, Surma Selay Proshikhon Kendro, Sayful Khan | 2021-02-28 | LU1001 | 12.3 | 226 | 12.3 | 227 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7584 | 1175.9997 | 129.5987
SYL-S.1.RR.59.1 | 24521929151366 | Pirojpur, Bonghobir Road, Khan Bari, Surma Selay Proshikhon Kendro, Solayman Khan | 2019-07-17 | NQ1008 | 1.4 | 36 | 1.4 | 37 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7584 | 1175.9997 | 14.7511
SYL-S.1.RR.60.1 | 24521929151366 | Pirojpur, Bonghobir Road, Khan Bari, Surma Selay Proshikhon Kendro, Solayman Khan | 2019-07-17 | NQ1008 | 11.3 | 38 | 11 | 39 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7584 | 1175.9997 | 115.9013
SYL-S.1.RR.61.1 | 24520799151339 | South Surma, Pirojpur, Bonghobir Road, Nojir Ahmed Juwil | 2019-07-18 | NQ1008 | 12.9 | 40 | 12.9 | 41 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7656 | 1103.9997 | 135.9206
SYL-S.1.RR.62.1 | 24520889151336 | South Surma, Pirojpur, Bonghobir Road, Moin Uddin | 2019-07-18 | NQ1008 | 9.1 | 42 | 9.1 | 43 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7656 | 1103.9997 | 95.882
SYL-S.1.RR.63.1 | 24520869151413 | South Surma, Pirojpur, Word # 5, Road # 1, China House, Naaf Holiday Cottage | 2019-07-18 | NQ1008 | 11.8 | 44 | 11.8 | 45 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7656 | 1103.9997 | 124.3305
SYL-S.1.RR.64.1 | 24521009151415 | South Surma, Pirojpur, Bonghobir Road, Word # 5, Block-C, Samsul Haque | 2019-07-18 | NQ1008 | 22.4 | 46 | 22 | 47 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 22 | 22 | 1.32 | 1.32 | 0.0007168 | 100% | 0% | 1.32 | 1.32 | 0.0011869 | 28 | 0.026461 | 0.026461 |  | 0 | 0 | 7656 | 1103.9997 | 231.8026
SYL-S.1.RR.65.1 | 24521159151432 | South Surma, Pirojpur, Bonghobir Road, Word # 5, Road # 1, Anam Mia | 2019-07-18 | NQ1008 | 14.6 | 48 | 14.6 | 49 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7656 | 1103.9997 | 153.8326
SYL-S.1.RR.66.1 | 24521179151404 | South Surma, Pirojpur, Bonghobir Road, Word # 5, Road # 1, H # 56, Nokibul Islam | 2019-07-18 | NQ1008 | 10.7 | 52 | 10.7 | 53 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7656 | 1103.9997 | 112.7403
SYL-S.1.RR.67.1 | 24521709151416 | South Surma, Pirojpur, Word # 5, Boro Bari, Sirajul Islam | 2019-07-18 | NQ1008 | 9.1 | 54 | 9.1 | 55 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7656 | 1103.9997 | 95.882
SYL-S.1.RR.68.1 | 24521939151416 | South Surma, Pirojpur, Word # 5, Boro Bari, Noab Mia | 2019-07-18 | NQ1008 | 15.7 | 56 | 15.7 | 57 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0 | 7656 | 1103.9997 | 165.4228
SYL-S.1.RR.69.1 | 24521939151416 | South Surma, Pirojpur, Word # 5, Boro Bari, Noab Mia | 2019-07-18 | NQ1008 | 8.1 | 58 | 8.1 | 59 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7656 | 1103.9997 | 85.3455
SYL-S.1.RR.70.1 | 24522299152080 | South Surma, Mominkhola, Galimpur Road, Moni Villa | 2019-07-21 | NQ1008 | 20.8 | 76 | 20.9 | 77 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 20.9 | 20.9 | 1.254 | 1.254 | 0.0007168 | 100% | 0% | 1.254 | 1.254 | 0.0011869 | 28 | 0.025138 | 0.025138 |  | 0 | 0 | 7656 | 1103.9997 | 220.2125
SYL-S.1.RR.71.1 | 24522809152130 | South Surma, Mominkhola, Word # 25, Ajijul Rahman (Raza) | 2019-07-21 | NQ1008 | 12.2 | 78 | 11.9 | 79 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7656 | 1103.9997 | 125.3841
SYL-S.1.RR.72.1 | 24523199152113 | South Surma, Mominkhola, Word # 25, Sahed Mia | 2019-07-21 | NQ1008 | 12.1 | 80 | 12.1 | 81 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7656 | 1103.9997 | 127.4914
SYL-S.1.RR.72.2 | 24523199152113 | South Surma, Mominkhola, Word # 25, Sahed Mia | 2019-07-21 | NQ1008 | 8.1 | 83 | 8.1 | 84 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7656 | 1103.9997 | 85.3455
SYL-S.1.RR.73.1 | 24523259152110 | South Surma, Mominkhola, Rd #5, Block-B, Nowser Alam | 2019-07-21 | NQ1008 | 3.9 | 85 | 3.9 | 86 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7656 | 1103.9997 | 41.0923
SYL-S.1.RR.74.1 | 24523259152110 | South Surma, Mominkhola, Rd #5, Block-B, Nowser Alam | 2019-07-21 | NQ1008 | 3.5 | 87 | 3.5 | 88 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7656 | 1103.9997 | 36.8777
SYL-S.1.RR.75.1 | 24523329151013 | South Surma, Boraykandi R/A, Rayar Gram Kamusana, Word # 3, Sirajul Islam | 2019-07-23 | NQ1008 | 18.6 | 108 | 18.6 | 109 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 7584 | 1175.9997 | 195.9786
SYL-S.1.RR.76.1 | 24522179150514 | South Surma, Purantetly, Boraykandi Road, Word # 4, Hazi Sofik Mia | 2019-07-23 | NQ1008 | 64.3 | 110 | 64.3 | 111 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 64.3 | 64.3 | 3.858 | 3.858 | 0.0007168 | 100% | 0% | 3.858 | 3.858 | 0.0011869 | 28 | 0.07734 | 0.07734 |  | 0 | 0 | 7608 | 1151.9997 | 677.4957
SYL-S.1.RR.77.1 | 24522319150437 | South Surma, Purantetly, Boraykandi Road, Word # 4, Minara Begom | 2019-07-23 | NQ1008 | 12.3 | 112 | 12 | 113 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7608 | 1151.9997 | 126.4378
SYL-S.1.RR.78.1 | 24522229150405 | South Surma, Purantetly, Boraykandi Road, Word # 4, Nasir Mia | 2019-07-23 | NQ1008 | 14.1 | 114 | 14.1 | 115 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7608 | 1151.9997 | 148.5644
SYL-S.1.RR.79.1 | 24521979150418 | South Surma, Purantetly, Boraykandi Road, Wora # 4, Sohid Mia | 2019-07-23 | NQ1008 | 9.6 | 116 | 9.6 | 117 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7608 | 1151.9997 | 101.1502
SYL-S.1.RR.80.1 | 24521979150418 | South Surma, Purantetly, Boraykandi Road, Wora # 4, Salam | 2019-07-23 | NQ1008 | 6.4 | 119 | 6.4 | 120 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7608 | 1151.9997 | 67.4335
SYL-S.1.RR.81.1 | 24521779150425 | South Surma, Purantetly, Boraykandi Road, Wora # 4, Intaj Alli | 2019-07-23 | NQ1008 | 21.4 | 121 | 21.4 | 122 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 21.4 | 21.4 | 1.284 | 1.284 | 0.0007168 | 100% | 0% | 1.284 | 1.284 | 0.0011869 | 28 | 0.02574 | 0.02574 |  | 0 | 0 | 7608 | 1151.9997 | 225.4807
SYL-S.1.RR.82.1 | 24514809151120 | South Surma, Bodikona, Bodikona Boldia 1.no Road, Word # 2, Abdul Mosabbir | 2019-07-25 | NQ1008 | 47.1 | 155 | 47.1 | 156 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 47.1 | 47.1 | 2.826 | 2.826 | 0.0007168 | 100% | 0% | 2.826 | 2.826 | 0.0011869 | 28 | 0.056652 | 0.056652 |  | 0 | 0 | 7632 | 1127.9997 | 496.2683
SYL-S.1.RR.83.1 | 24514739151112 | South Surma, Bodikona, Bodikona Boldia 1.no Road, Word # 2, Meherun Necha | 2019-07-25 | NQ1008 | 21.2 | 157 | 21.2 | 158 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 21.2 | 21.2 | 1.272 | 1.272 | 0.0007168 | 100% | 0% | 1.272 | 1.272 | 0.0011869 | 28 | 0.025499 | 0.025499 |  | 0 | 0 | 7632 | 1127.9997 | 223.3734
SYL-S.1.RR.84.1 | 24513689151111 | South Surma, Bodikona, Bodikona Boldia 1.no Road, Word # 2, Yealis Mia | 2019-07-25 | NQ1008 | 9.3 | 159 | 9.3 | 160 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7632 | 1127.9997 | 97.9893
SYL-S.1.RR.85.1 | 24512809151110 | South Surma, Boldi, Boldi 1.no Road, Word # 2, Md.Kalu Mia | 2019-07-25 | NQ1008 | 27.3 | 161 | 27.3 | 162 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 27.3 | 27.3 | 1.638 | 1.638 | 0.0007168 | 100% | 0% | 1.638 | 1.638 | 0.0011869 | 28 | 0.032836 | 0.032836 |  | 0 | 0 | 7632 | 1127.9997 | 287.6459
SYL-S.1.RR.86.1 | 24512019151091 | South Surma, Boldi, Boldi 1.no Road, Word # 2, Moynuddin Membor | 2019-07-25 | NQ1008 | 11.2 | 163 | 11 | 164 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7632 | 1127.9997 | 115.9013
SYL-S.1.RR.87.1 | 24512019151091 | South Surma, Boldi, Boldi 1.no Road, Word # 2, Moynuddin Membor | 2019-07-25 | NQ1008 | 5.8 | 165 | 5.8 | 166 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7632 | 1127.9997 | 61.1116
SYL-S.1.RR.88.1 | 24512019151091 | South Surma, Boldi, Boldi 1.no Road, Word # 2, Moynuddin Membor | 2019-07-25 | NQ1008 | 6.6 | 167 | 6.6 | 168 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7632 | 1127.9997 | 69.5408
SYL-S.1.RR.89.1 | 24511479150487 | South Surma, Boldi R/A, Road # 2, Word # 2, Mujibor Rahman | 2019-07-25 | NQ1008 | 4.8 | 169 | 4.7 | 170 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7632 | 1127.9997 | 49.5215
SYL-S.1.RR.101.1 | 24530929152150 | Chadneghat, South Surma, Jalo Para, Abdul Mojid | 2019-07-17 | MN1032 | 7.7 | 1 | 7.6 | 2 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7584 | 1175.9997 | 80.0773
SYL-S.1.RR.101.2 | 24530929152150 | Chadneghat, South Surma, Jalo Para, Abdul Mojid | 2019-07-17 | MN1032 | 10.3 | 5 | 10.3 | 6 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7584 | 1175.9997 | 108.5258
SYL-S.1.RR.102.1 | 24530769152158 | Chadneghat, South Surma, Jalo Para, Md Jilur Rahman | 2019-07-17 | MN1032 | 26.5 | 7 | 26.5 | 8 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 26.5 | 26.5 | 1.59 | 1.59 | 0.0007168 | 100% | 0% | 1.59 | 1.59 | 0.0011869 | 28 | 0.031874 | 0.031874 |  | 0 | 0 | 7584 | 1175.9997 | 279.2168
SYL-S.1.RR.103.1 | 24530839152167 | Chadneghat, South Surma, Jalo Para, Jabed | 2019-07-17 | MN1032 | 12.3 | 9 | 12.3 | 10 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7584 | 1175.9997 | 129.5987
SYL-S.1.RR.104.1 | 24530489152153 | Chadneghat, South Surma, Jalo Para, Anower Hossen | 2019-07-17 | MN1032 | 15.3 | 11 | 15.3 | 12 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 7584 | 1175.9997 | 161.2082
SYL-S.1.RR.105.1 | 24530129152131 | Vartakhala, Sornaly, Block - A, Nuruddin Soudagar | 2019-07-17 | MN1032 | 10.6 | 13 | 10.6 | 14 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7584 | 1175.9997 | 111.6867
SYL-S.1.RR.106.1 | 24530019152144 | Vartakhala, Sornaly, Block - A, Gada Mia | 2019-07-17 | MN1032 | 15.9 | 15 | 16.2 | 16 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 7584 | 1175.9997 | 170.691
SYL-S.1.RR.107.1 | 24530129152124 | Vartakhala, Sornaly, Block - A, Toju Mia | 2019-07-17 | MN1032 | 13.8 | 17 | 13.5 | 18 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7584 | 1175.9997 | 142.2425
SYL-S.1.RR.107.2 | 24530129152124 | Vartakhala, Sornaly, Block - A, Toju Mia | 2022-12-05 | MN1018 | 4.2 | 161 | 4.2 | 162 | 2022-12-05 | 2022-12-05 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 0 | 647.9997 | 3.2735
SYL-S.1.RR.108.1 | 24530739152117 | Chadneghat, South Surma, Jalo Para, Faruk Mia | 2019-07-17 | MN1032 | 12.9 | 19 | 12.9 | 20 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7584 | 1175.9997 | 135.9206
SYL-S.1.RR.109.1 | 24530769152119 | Chadneghat, South Surma, Jalo Para, Mobarak Hossen | 2019-07-17 | MN1032 | 5.8 | 25 | 5.8 | 26 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7584 | 1175.9997 | 61.1116
SYL-S.1.RR.110.1 | 24530909152108 | Chadneghat, South Surma, Jalo Para, Alak Uddin | 2019-07-17 | MN1032 | 7.3 | 27 | 7.3 | 28 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7584 | 1175.9997 | 76.9163
SYL-S.1.RR.111.1 | 24524679151402 | South Khojar Khola R/A, Block - D, H # 429/1, Hazi Jahir Ali | 2019-07-18 | MN1032 | 13.4 | 47 | 13.4 | 48 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7584 | 1175.9997 | 141.1888
SYL-S.1.RR.112.1 | 24524809151417 | South Khojar Khola R/A, Block - D, H # 432, Anower Mia | 2019-07-18 | MN1032 | 10.8 | 49 | 10.8 | 50 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7584 | 1175.9997 | 113.794
SYL-S.1.RR.113.1 | 24524339151384 | South Khojar Khola R/A, Block - D, Moktar Mia | 2019-07-18 | MN1032 | 10.6 | 51 | 10.6 | 52 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7584 | 1175.9997 | 111.6867
SYL-S.1.RR.114.1 | 24524739151363 | South Khojar Khola, Block - D, Abdul Subahan | 2019-07-18 | MN1032 | 8.4 | 53 | 8.4 | 54 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7584 | 1175.9997 | 88.5064
SYL-S.1.RR.115.1 | 24524739151363 | South Khojar Khola, Block - D, Abdul Subahan | 2019-07-18 | MN1032 | 10 | 55 | 10 | 56 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7584 | 1175.9997 | 105.3648
SYL-S.1.RR.115.2 | 24524739151363 | South Khojar Khola, Block - D, Abdul Subahan | 2019-07-18 | MN1032 | 4.8 | 57 | 4.8 | 58 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7584 | 1175.9997 | 50.5751
SYL-S.1.RR.116.1 | 24522799152174 | Monin Khola, South Surma, Block - C, Shahim | 2019-07-22 | MN1032 | 12.6 | 89 | 12.6 | 90 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7656 | 1103.9997 | 132.7597
SYL-S.1.RR.117.1 | 24523099152205 | Monin Khola, South Surma, Sathe Bagum | 2019-07-22 | MN1032 | 3.8 | 93 | 3.8 | 94 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7656 | 1103.9997 | 40.0386
SYL-S.1.RR.118.1 | 24522009152091 | Paschim Momin Khola, Galimpur Road, Ickbal Rosne House | 2019-07-22 | MN1032 | 4.1 | 95 | 4.1 | 96 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7656 | 1103.9997 | 43.1996
SYL-S.1.RR.119.1 | 24521969152092 | Paschim Momin Khola, Galimpur Road, Bappu | 2019-07-22 | MN1032 | 10.8 | 97 | 10.8 | 98 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7656 | 1103.9997 | 113.794
SYL-S.1.RR.120.1 | 24521049152087 | Goinpur, Galaimpur, Road, Sharafat Ali | 2019-07-22 | MN1032 | 1.1 | 101 | 1.1 | 102 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7656 | 1103.9997 | 11.5901
SYL-S.1.RR.121.1 | 24525049151025 | Boroi Kande, Suram Pur, Rd # 1, Md. Oatir Ali | 2019-07-23 | MN1032 | 10.5 | 124 | 10.5 | 125 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7632 | 1127.9997 | 110.6331
SYL-S.1.RR.122.1 | 24525009151041 | Boroi Kande, Suram Pur, Rd # 1, Azmol Ali | 2019-07-23 | MN1032 | 10.1 | 126 | 10.1 | 127 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7632 | 1127.9997 | 106.4185
SYL-S.1.RR.123.1 | 24525009151041 | Boroi Kande, Suram Pur, Rd # 1, Azmol Ali | 2019-07-23 | MN1032 | 9.3 | 128 | 9.3 | 129 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7632 | 1127.9997 | 97.9893
SYL-S.1.RR.124.1 | 24525009151041 | Boroi Kande, Suram Pur, Rd # 1, Azmol Ali | 2019-07-23 | MN1032 | 5.3 | 130 | 5.3 | 131 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7632 | 1127.9997 | 55.8434
SYL-S.1.RR.125.1 | 24515149150513 | Poschim Daradarpur, Arkum Nagur, Block - B, Habib Mia | 2019-07-23 | MN1032 | 12.1 | 132 | 12.1 | 133 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7608 | 1151.9997 | 127.4914
SYL-S.1.RR.125.2 | 24515149150513 | Poschim Daradarpur, Arkum Nagur, Block - B, Habib Mia | 2021-03-01 | NQ1007 | 3.3 | 236 | 3.3 | 237 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7608 | 1151.9997 | 34.7704
SYL-S.1.RR.126.1 | 24515259150515 | Poschim Daradarpur, Arkum Nagur, Block - B, FulJan Bebe | 2019-07-23 | MN1032 | 13 | 134 | 13 | 135 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7608 | 1151.9997 | 136.9743
SYL-S.1.RR.127.1 | 24520479150557 | Poschim Dorador Pur, South Surma, Hazi Md. Nozir Mia | 2019-07-24 | MN1032 | 10.6 | 137 | 10.6 | 138 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7608 | 1151.9997 | 111.6867
SYL-S.1.RR.128.1 | 24515259151100 | South Surma, Bode Khola, Dr. Sofur Ali | 2019-07-25 | MN1032 | 2.5 | 139 | 2.5 | 140 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7632 | 1127.9997 | 26.3412
SYL-S.1.RR.129.1 | 24515259151100 | South Surma, Bode Khola, Dr. Sofur Ali | 2019-07-25 | MN1032 | 2.7 | 141 | 2.7 | 142 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7632 | 1127.9997 | 28.4485
SYL-S.1.RR.130.1 | 24515259151100 | South Surma, Bode Khola, Dr. Sofur Ali | 2019-07-25 | MN1032 | 5.6 | 143 | 5.6 | 144 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7632 | 1127.9997 | 59.0043
SYL-S.1.RR.131.1 | 24515259151100 | South Surma, Bode Khola, Dr. Sofur Ali | 2019-07-25 | MN1032 | 10.6 | 145 | 10.6 | 146 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7632 | 1127.9997 | 111.6867
SYL-S.1.RR.132.1 | 24515259151100 | South Surma, Bode Khola, Dr. Sofur Ali | 2019-07-25 | MN1032 | 2.2 | 147 | 2.2 | 148 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7632 | 1127.9997 | 23.1803
SYL-S.1.RR.133.1 | 24515289151130 | South Surma, Bode Khola, Abdul Bari | 2019-07-25 | MN1032 | 10.8 | 149 | 10.8 | 150 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7632 | 1127.9997 | 113.794
SYL-S.1.RR.134.1 | 24515909151108 | South Surma, Bode Khola, Gias Mia | 2019-07-25 | MN1032 | 59.9 | 151 | 58.4 | 152 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 58.4 | 58.4 | 3.504 | 3.504 | 0.0007168 | 100% | 0% | 3.504 | 3.504 | 0.0011869 | 28 | 0.070243 | 0.070243 |  | 0 | 0 | 7632 | 1127.9997 | 615.3305
SYL-S.1.RR.135.1 | 24515909151108 | South Surma, Bode Khola, Gias Mia | 2019-07-25 | MN1032 | 3.7 | 153 | 3.5 | 154 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7632 | 1127.9997 | 36.8777
SYL-S.1.RR.136.1 | 24521479152418 | South Surma, Pathan Para, Dokkin Khan Bari, Bodrul Khan | 2019-07-25 | MN1032 | 23.1 | 155 | 22.5 | 156 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 22.5 | 22.5 | 1.35 | 1.35 | 0.0007168 | 100% | 0% | 1.35 | 1.35 | 0.0011869 | 28 | 0.027063 | 0.027063 |  | 0 | 0 | 7512 | 1247.9997 | 237.0708
SYL-S.1.RR.137.1 | 24522209152341 | South Surma, Pathan Para, Block - A, Rd # 1, Babul Khan | 2019-07-25 | MN1032 | 13.2 | 157 | 13.2 | 158 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7512 | 1247.9997 | 139.0816
SYL-S.1.RR.138.1 | 24522209152341 | South Surma, Pathan Para, Block - A, Rd # 1, Babul Khan | 2019-07-25 | MN1032 | 12.9 | 159 | 12.1 | 160 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7512 | 1247.9997 | 127.4914
SYL-S.1.RR.139.1 | 24522159152408 | South Surma, Pathan Para, Khan Bari Road, Nurul Islam Khan | 2019-07-25 | MN1032 | 16.6 | 165 | 16.6 | 166 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 16.6 | 16.6 | 0.996 | 0.996 | 0.0007168 | 100% | 0% | 0.996 | 0.996 | 0.0011869 | 28 | 0.019966 | 0.019966 |  | 0 | 0 | 7512 | 1247.9997 | 174.9056
SYL-S.1.RR.140.1 | 24522359152438 | South Surma, Pathan Para, Khan Bari Road, Fozlul Haque Khan | 2019-07-25 | MN1032 | 6.1 | 167 | 6.1 | 168 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7512 | 1247.9997 | 64.2725
SYL-S.1.RR.141.1 | 24522359152438 | South Surma, Pathan Para, Khan Bari Road, Fozlul Haque Khan | 2019-07-25 | MN1032 | 3.8 | 169 | 3.8 | 170 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7512 | 1247.9997 | 40.0386
SYL-S.1.RR.141.2 | 24522359152438 | South Surma, Pathan Para, Khan Bari Road, Fozlul Haque Khan | 2021-02-28 | LX1011 | 3.4 | 165 | 3.4 | 166 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7512 | 1247.9997 | 35.824
SYL-S.1.RR.142.1 | 24522619152471 | South Surma, Pathan Para, Khan Bari Road, Balal Uddin Ahmed | 2019-07-25 | MN1032 | 4.4 | 171 | 4.4 | 172 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7512 | 1247.9997 | 46.3605
SYL-S.1.RR.143.1 | 24522599152476 | South Surma, Pathan Para, Khan Bari Road, Amir Khan | 2019-07-25 | MN1032 | 11.5 | 173 | 11.5 | 174 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7512 | 1247.9997 | 121.1695
SYL-S.1.RR.151.1 | 24530759152188 | Chadneghat, Bharthokola, Shopnonir R/A, Block # D, H # 78 | 2019-07-17 | MN1032 | 9.8 | 31 | 9.8 | 32 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7584 | 1175.9997 | 103.2575
SYL-S.1.RR.152.1 | 24530759152188 | Chadneghat, Bharthokola, Shopnonir R/A, Block # D, H # 78 | 2019-07-17 | MN1032 | 8.6 | 33 | 8.6 | 34 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7584 | 1175.9997 | 90.6137
SYL-S.1.RR.153.1 | 24530759152188 | Chadneghat, Bharthokola, Shopnonir R/A, Block # D, H # 78 | 2019-07-17 | MN1032 | 4.3 | 35 | 4.3 | 36 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7584 | 1175.9997 | 45.3069
SYL-S.1.RR.154.1 | 24530649152214 | Jhalopara, Shopnonir R/A, Block # D, H # 99/1 | 2019-07-17 | MN1032 | 8.9 | 37 | 8.2 | 38 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7584 | 1175.9997 | 86.3991
SYL-S.1.RR.155.1 | 24530649152214 | Jhalopara, Shopnonir R/A, Block # D, H # 99 | 2019-07-17 | MN1032 | 9.2 | 39 | 9.2 | 40 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7584 | 1175.9997 | 96.9356
SYL-S.1.RR.156.1 | 24530649152214 | Jhalopara, Shopnonir R/A, Block # D, H # 99 | 2019-07-17 | MN1032 | 9.3 | 41 | 9 | 42 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7584 | 1175.9997 | 94.8283
SYL-S.1.RR.157.1 | 24530649152214 | Jhalopara, Shopnonir R/A, Block # D, H # 99 | 2019-07-17 | MN1032 | 11 | 43 | 11 | 44 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7584 | 1175.9997 | 115.9013
SYL-S.1.RR.158.1 | 24530649152214 | Jhalopara, Shopnonir R/A, Block # D, H # 99 | 2019-07-17 | MN1032 | 5.9 | 45 | 5.9 | 46 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7584 | 1175.9997 | 62.1652
SYL-S.1.RR.159.1 | 24523709152051 | Kaysthorall, Concord R/A, Block # C, Rd #1, H # 25 | 2019-07-18 | MN1032 | 9.5 | 59 | 9.5 | 60 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7656 | 1103.9997 | 100.0966
SYL-S.1.RR.160.1 | 24523709152051 | Kaysthorall, Concord R/A, Block # C, Rd #1, H # 19 | 2019-07-18 | MN1032 | 6.1 | 61 | 6.1 | 62 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7656 | 1103.9997 | 64.2725
SYL-S.1.RR.161.1 | 24523889152028 | Barkhola, Rupale R/A, Block # C, Lailu Mia | 2019-07-18 | MN1032 | 9.9 | 63 | 9.9 | 64 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7656 | 1103.9997 | 104.3112
SYL-S.1.RR.162.1 | 24523889152028 | Barkhola, Rupale R/A, Block # C, Hasan | 2019-07-18 | MN1032 | 10.4 | 65 | 10.4 | 66 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7656 | 1103.9997 | 109.5794
SYL-S.1.RR.163.1 | 24523719152027 | Barkhola, Rupale R/A, Block # C, H # 24 | 2019-07-18 | MN1032 | 4.2 | 67 | 4.2 | 68 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7656 | 1103.9997 | 44.2532
SYL-S.1.RR.163.2 | 24523719152027 | Barkhola, Rupale R/A, Block # C, H # 24 | 2021-03-02 | NQ1007 | 12.9 | 238 | 13.4 | 239 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7656 | 1103.9997 | 141.1888
SYL-S.1.RR.164.1 | 24522619152004 | Dahudpur Mushargau, Sha Munjur R/A, B # A, Rd # 1, H # 18 | 2019-07-20 | MN1032 | 11.3 | 69 | 11.3 | 70 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7656 | 1103.9997 | 119.0622
SYL-S.1.RR.165.1 | 24522349152005 | Dahudpur Mushargau, Sha Munjur R/A, B # A, Rd # 1, Tara Mia | 2019-07-20 | MN1032 | 7.5 | 71 | 7.5 | 72 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7656 | 1103.9997 | 79.0236
SYL-S.1.RR.166.1 | 24523719151559 | Barkhola, Rupali R/A, B # B, Tonjul Mia | 2019-07-20 | MN1032 | 8.7 | 73 | 8.7 | 74 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7656 | 1103.9997 | 91.6674
SYL-S.1.RR.167.1 | 24523719151559 | Barkhola, Rupali R/A, B # B, Tonjul Mia | 2019-07-20 | MN1032 | 7.3 | 75 | 7.3 | 76 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7656 | 1103.9997 | 76.9163
SYL-S.1.RR.168.1 | 24523719151559 | Barkhola, Rupali R/A, B # B, Golap Khan | 2019-07-20 | MN1032 | 10.9 | 79 | 10.9 | 80 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7656 | 1103.9997 | 114.8476
SYL-S.1.RR.169.1 | 24523719151559 | Barkhola, Rupali R/A, B # B, Dulal Khan | 2019-07-20 | MN1032 | 12.8 | 81 | 12.8 | 82 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7656 | 1103.9997 | 134.867
SYL-S.1.RR.170.1 | 24523409151509 | Kaysthorail, Concord R/A, Rd # 3, H # 40 | 2019-07-20 | MN1032 | 6.3 | 83 | 6.3 | 84 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7656 | 1103.9997 | 66.3798
SYL-S.1.RR.171.1 | 24523409151509 | Kaysthorail, Concord R/A, Rd # 3, H # 40 | 2019-07-20 | MN1032 | 3.6 | 85 | 3.6 | 86 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7656 | 1103.9997 | 37.9313
SYL-S.1.RR.171.2 | 24523409151509 | Kaysthorail, Concord R/A, Rd # 3, H # 40 | 2022-11-16 | MN1018 | 4.3 | 143 | 4.3 | 144 | 2022-11-16 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 0 | 1103.9997 | 5.7099
SYL-S.1.RR.172.1 | 24520289152073 | South Surma, Galim Pur, Joinpur, Mamun | 2019-07-21 | MN1032 | 7.4 | 87 | 7.4 | 88 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7656 | 1103.9997 | 77.97
SYL-S.1.RR.173.1 | 24521069151590 | South Surma, Dhaudpur, Khella Bare | 2019-07-23 | MN1032 | 3.3 | 104 | 3.1 | 105 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7656 | 1103.9997 | 32.6631
SYL-S.1.RR.174.1 | 24521069151590 | South Surma, Dhaudpur, Khella Bare | 2019-07-23 | MN1032 | 4 | 106 | 4 | 107 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7656 | 1103.9997 | 42.1459
SYL-S.1.RR.175.1 | 24521069151590 | South Surma, Dhaudpur, Khella Bare | 2019-07-23 | MN1032 | 11.1 | 108 | 11.1 | 109 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7656 | 1103.9997 | 116.9549
SYL-S.1.RR.176.1 | 24521229152000 | South Surma, Dhaudpur, Nazrul Islam | 2019-07-23 | MN1032 | 5.3 | 110 | 5.3 | 111 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7656 | 1103.9997 | 55.8434
SYL-S.1.RR.176.2 | 24521229152000 | South Surma, Dhaudpur, Nazrul Islam | 2021-10-20 | LU1001 | 1.4 | 74 | 1.4 | 75 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7656 | 1103.9997 | 14.7511
SYL-S.1.RR.177.1 | 24521319152000 | South Surma, Dhaudpur, Hosen Ali | 2019-07-23 | MN1032 | 2 | 112 | 2 | 113 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7656 | 1103.9997 | 21.073
SYL-S.1.RR.178.1 | 24521449151589 | South Surma, Dhaudpur, Tonu Mia | 2019-07-23 | MN1032 | 28.8 | 114 | 28.8 | 115 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 28.8 | 28.8 | 1.728 | 1.728 | 0.0007168 | 100% | 0% | 1.728 | 1.728 | 0.0011869 | 28 | 0.03464 | 0.03464 |  | 0 | 0 | 7656 | 1103.9997 | 303.4507
SYL-S.1.RR.179.1 | 24521489152006 | South Surma, Dhaudpur, Sagel Mia | 2019-07-23 | MN1032 | 8.7 | 116 | 8.7 | 117 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7656 | 1103.9997 | 91.6674
SYL-S.1.RR.180.1 | 24525699151190 | South Surma, Boroikandi, Kazirkhola, Rd # 01, H # 26 | 2019-07-23 | MN1032 | 10.9 | 118 | 10.9 | 119 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7632 | 1127.9997 | 114.8476
SYL-S.1.RR.181.1 | 24525559151192 | South Surma, Boroikandi, Kazirkhola, Rd # 01, H # 32 | 2019-07-23 | MN1032 | 5.3 | 120 | 5.3 | 121 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7632 | 1127.9997 | 55.8434
SYL-S.1.RR.182.1 | 24525569151123 | South Surma, Boroikandi, Kazirkhola, Rd # 01, H # 62 | 2019-07-23 | MN1032 | 16.9 | 122 | 16.9 | 123 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 16.9 | 16.9 | 1.014 | 1.014 | 0.0007168 | 100% | 0% | 1.014 | 1.014 | 0.0011869 | 28 | 0.020327 | 0.020327 |  | 0 | 0 | 7632 | 1127.9997 | 178.0665
SYL-S.1.RR.183.1 | 24522439152369 | Kodomtali, Pathan Para, Shohid Ahmad | 2019-07-25 | MN1032 | 52.5 | 175 | 52.9 | 176 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 52.9 | 52.9 | 3.174 | 3.174 | 0.0007168 | 100% | 0% | 3.174 | 3.174 | 0.0011869 | 28 | 0.063628 | 0.063628 |  | 0 | 0 | 7512 | 1247.9997 | 557.3799
SYL-S.1.RR.184.1 | 24523039152393 | Kodomtali, Pathan Para, Baher Uddin | 2019-07-25 | MN1032 | 12.4 | 177 | 12.4 | 178 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7512 | 1247.9997 | 130.6524
SYL-S.1.RR.185.1 | 24523199152393 | Kodomtali, Pathan Para, Gous Mia | 2019-07-25 | MN1032 | 3.2 | 179 | 3.5 | 180 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7512 | 1247.9997 | 36.8777
SYL-S.1.RR.186.1 | 24523199152393 | Kodomtali, Pathan Para, Shahid Ahmad | 2019-07-25 | MN1032 | 5.5 | 181 | 5.5 | 182 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7512 | 1247.9997 | 57.9506
SYL-S.1.RR.187.1 | 24523729152404 | Kodomtali, Pathan Para, Block # A, H # 118 | 2019-07-25 | MN1032 | 13.3 | 183 | 13.2 | 184 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7512 | 1247.9997 | 139.0816
SYL-S.1.RR.188.1 | 24523789152399 | Kodomtali, Pathan Para, Tunu Mia | 2019-07-25 | MN1032 | 5.7 | 187 | 5.7 | 188 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7512 | 1247.9997 | 60.0579
SYL-S.1.RR.189.1 | 24523789152399 | Kodomtali, Pathan Para, Tunu Mia | 2019-07-25 | MN1032 | 9 | 189 | 9 | 190 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7512 | 1247.9997 | 94.8283
SYL-S.1.RR.190.1 | 24524139152437 | Kodomtali, Mazar Road, H # 150 | 2019-07-25 | MN1032 | 11.6 | 191 | 11.6 | 192 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7512 | 1247.9997 | 122.2232
SYL-S.1.RR.191.1 | 24524139152437 | Kodomtali, Mazar Road, H # 150 | 2019-07-25 | MN1032 | 9.2 | 193 | 8.7 | 194 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7512 | 1247.9997 | 91.6674
SYL-S.1.RR.192.1 | 24524269152441 | Kodomtali, Mazar Road, H # 52 | 2019-07-25 | MN1032 | 2.9 | 195 | 2.9 | 196 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7512 | 1247.9997 | 30.5558
SYL-S.1.RR.193.1 | 24524699152509 | Kodomtali, Ferighat Road, Akmol | 2019-07-25 | MN1032 | 4.9 | 197 | 4.9 | 198 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7512 | 1247.9997 | 51.6288
SYL-S.1.RR.193.2 | 24524699152509 | Kodomtali, Ferighat Road, Akmol | 2020-10-28 | NQ1000 | 3.4 | 191 | 3.4 | 192 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7512 | 1247.9997 | 35.824
SYL-S.1.RR.194.1 | 24524699152509 | Kodomtali, Ferighat Road, Akmol | 2019-07-25 | MN1032 | 9.9 | 199 | 9.9 | 200 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7512 | 1247.9997 | 104.3112
SYL-S.1.RR.201.1 | 24530729152031 | Bharthkhola, Station Road, Shornali R/A, Block # B, Ma Complex | 2019-07-17 | NQ1011 | 12.2 | 1 | 12.2 | 2 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7584 | 1175.9997 | 128.5451
SYL-S.1.RR.202.1 | 24530459152030 | Bharthkhola, Station Road, Shornali R/A, Block # B, H # 21 | 2019-07-17 | NQ1011 | 10.7 | 3 | 10.7 | 4 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7584 | 1175.9997 | 112.7403
SYL-S.1.RR.203.1 | 24530459152030 | Bharthkhola, Station Road, Shornali R/A, Block # B, H # 21 | 2019-07-17 | NQ1011 | 6.9 | 5 | 6.9 | 6 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7584 | 1175.9997 | 72.7017
SYL-S.1.RR.203.2 | 24530459152030 | Bharthkhola, Station Road, Shornali R/A, Block # B, H # 21 | 2019-07-17 | NQ1011 | 3.1 | 9 | 3.1 | 10 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7584 | 1175.9997 | 32.6631
SYL-S.1.RR.204.1 | 24530619152008 | South Shurma, Bharthkhola, Station Road, Shornali R/A, Block # C, H # 6 | 2019-07-17 | NQ1011 | 3.3 | 13 | 3 | 14 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7584 | 1175.9997 | 31.6094
SYL-S.1.RR.205.1 | 24530519151575 | South Shurma, Bharthkhola, Station Road, Shornali R/A, Block # C, Putul Mia | 2019-07-17 | NQ1011 | 13 | 17 | 13 | 18 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7584 | 1175.9997 | 136.9743
SYL-S.1.RR.206.1 | 24530519151575 | South Shurma, Bharthkhola, Station Road, Shornali R/A, Block # C, H # 11, Anowara Villa | 2019-07-17 | NQ1011 | 13.4 | 19 | 13.2 | 20 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7584 | 1175.9997 | 139.0816
SYL-S.1.RR.207.1 | 24530339151564 | South Shurma, Bharthkhola, Station Road, Shornali R/A, Block # C, H # 15, Sikandar Ali | 2019-07-17 | NQ1011 | 19.7 | 21 | 19.7 | 22 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 19.7 | 19.7 | 1.182 | 1.182 | 0.0007168 | 100% | 0% | 1.182 | 1.182 | 0.0011869 | 28 | 0.023695 | 0.023695 |  | 0 | 0 | 7584 | 1175.9997 | 207.5687
SYL-S.1.RR.208.1 | 24530339151564 | South Shurma, Bharthkhola, Station Road, Shornali R/A, Block # C, H # 14, Jafrul | 2019-07-17 | NQ1011 | 55.7 | 23 | 55.7 | 24 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 55.7 | 55.7 | 3.342 | 3.342 | 0.0007168 | 100% | 0% | 3.342 | 3.342 | 0.0011869 | 28 | 0.066996 | 0.066996 |  | 0 | 0 | 7584 | 1175.9997 | 586.882
SYL-S.1.RR.209.1 | 24530139151388 | South Shurma, Khojarkhola R/A, Block-B, Rd # 1, H # 209, Md Ibrahim | 2019-07-18 | NQ1011 | 6.8 | 41 | 6.8 | 42 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7584 | 1175.9997 | 71.6481
SYL-S.1.RR.210.1 | 24530029151323 | South Shurma, Khojarkhola R/A, Block-A, Rd # 1, H # 104, Nehar Begum | 2019-07-18 | NQ1011 | 9.2 | 43 | 9.2 | 44 | 2022-01-01 | 2022-11-13 | MN1018 | 0.7 | 137 | 0.7 | 138 | 2022-11-13 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 0 | 0 | 7584 | 1175.9997
SYL-S.1.RR.210.2 | 24530029151323 | South Shurma, Khojarkhola R/A, Block-A, Rd # 1, H # 104, Nehar Begum | 2021-02-28 | MN1032 | 6.1 | 194 | 6.1 | 195 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7584 | 1175.9997 | 64.2725
SYL-S.1.RR.211.1 | 24525499151318 | South Shurma, Khojarkhola R/A, Block-A, Rd # 1, H # 111, Abdul Haque | 2019-07-18 | NQ1011 | 6.8 | 45 | 6.8 | 46 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7584 | 1175.9997 | 71.6481
SYL-S.1.RR.212.1 | 24525219151293 | South Shurma, Khojarkhola R/A, Block-A, Rd # 1, H # 121, Mokhlesur Rahman | 2019-07-18 | NQ1011 | 2.3 | 47 | 2.3 | 48 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7584 | 1175.9997 | 24.2339
SYL-S.1.RR.214.1 | 24525299151281 | South Shurma, Khojarkhola R/A, Block-A, Rd # 1, H # 121, Kabir Ahmed | 2019-07-18 | NQ1011 | 5.9 | 53 | 6 | 54 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7584 | 1175.9997 | 63.2189
SYL-S.1.RR.215.1 | 24525119151302 | South Shurma, Khojarkhola R/A, Block-A, Rd # 1, H # 122, Kamal | 2019-07-18 | NQ1011 | 11.2 | 55 | 11.2 | 56 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7584 | 1175.9997 | 118.0086
SYL-S.1.RR.216.1 | 24530799150502 | South Shurma, Boroikandi R/A, Rd # 8, Shafiq Uddin | 2019-07-22 | NQ1011 | 12.3 | 111 | 12.3 | 112 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7632 | 1127.9997 | 129.5987
SYL-S.1.RR.217.1 | 24530799150502 | South Shurma, Boroikandi R/A, Rd # 8, Md. Nur Uddin | 2019-07-22 | NQ1011 | 11.8 | 113 | 11.8 | 114 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7632 | 1127.9997 | 124.3305
SYL-S.1.RR.217.2 | 24530799150502 | South Shurma, Boroikandi R/A, Rd # 8, Md. Nur Uddin | 2021-02-28 | NQ1007 | 3.4 | 232 | 3.2 | 233 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7632 | 1127.9997 | 33.7167
SYL-S.1.RR.218.1 | 24530709150500 | South Shurma, Boroikandi R/A, Rd # 8, H # 23, Abul Kalam Azad | 2019-07-22 | NQ1011 | 7.6 | 115 | 7.6 | 116 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7632 | 1127.9997 | 80.0773
SYL-S.1.RR.219.1 | 24531199150469 | South Shurma, Boroikandi R/A, Rd # 9, Sultan Mia | 2019-07-22 | NQ1011 | 3.8 | 117 | 3.8 | 118 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7632 | 1127.9997 | 40.0386
SYL-S.1.RR.219.2 | 24531199150469 | South Shurma, Boroikandi R/A, Rd # 9, Sultan Mia | 2021-02-28 | NQ1007 | 2.2 | 234 | 2.2 | 235 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7632 | 1127.9997 | 23.1803
SYL-S.1.RR.220.1 | 24531109150466 | South Shurma, Boroikandi R/A, Rd # 10, Shamim | 2019-07-22 | NQ1011 | 8.8 | 119 | 8.8 | 120 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7632 | 1127.9997 | 92.721
SYL-S.1.RR.221.1 | 24531109150466 | South Shurma, Boroikandi R/A, Rd # 10, Ahmad Ali | 2019-07-22 | NQ1011 | 11.3 | 121 | 11.3 | 122 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7632 | 1127.9997 | 119.0622
SYL-S.1.RR.222.1 | 24530529150457 | South Shurma, Boroikandi R/A, Rd # 10, H # 46, Hazi Md. Rashid Ali villa | 2019-07-22 | NQ1011 | 8.1 | 123 | 7.7 | 124 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7632 | 1127.9997 | 81.1309
SYL-S.1.RR.223.1 | 24530449150468 | South Shurma, Boroikandi R/A, Rd # 10, Muhibur Rahman | 2019-07-22 | NQ1011 | 7.8 | 125 | 7.8 | 126 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7632 | 1127.9997 | 82.1846
SYL-S.1.RR.224.1 | 24530369150452 | South Shurma, Boroikandi R/A, Rd # 10, H # 52, Jahangir Alam | 2019-07-22 | NQ1011 | 10.1 | 127 | 10.1 | 128 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7632 | 1127.9997 | 106.4185
SYL-S.1.RR.225.1 | 24530369150452 | South Shurma, Boroikandi R/A, Rd # 10, Mamun | 2019-07-22 | NQ1011 | 9.6 | 129 | 9.6 | 130 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7632 | 1127.9997 | 101.1502
SYL-S.1.RR.226.1 | 24530369150452 | South Shurma, Boroikandi R/A, Rd # 10, H # 53, Afroz Mia | 2019-07-23 | NQ1011 | 10.2 | 131 | 10.2 | 132 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7632 | 1127.9997 | 107.4721
SYL-S.1.RR.227.1 | 24525949150501 | South Shurma, Boroikandi R/A, Rd # 10, H # 55/3, Kazi Bari | 2019-07-23 | NQ1011 | 12.4 | 133 | 12.4 | 134 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7680 | 1079.9997 | 130.6524
SYL-S.1.RR.228.1 | 24530069150532 | South Shurma, Boroikandi R/A, Rd # 10, H # 57, Talukdar Bari, Azizur Rahman Moti | 2019-07-23 | NQ1011 | 9.2 | 135 | 9.2 | 136 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7680 | 1079.9997 | 96.9356
SYL-S.1.RR.229.1 | 24530069150532 | South Shurma, Boroikandi R/A, Rd # 10, Abdul Alim | 2019-07-23 | NQ1011 | 6.8 | 137 | 6.2 | 138 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7680 | 1079.9997 | 65.3262
SYL-S.1.RR.230.1 | 24530259150540 | South Shurma, Boroikandi R/A, Rd # 10, Abdul Mumin | 2019-07-23 | NQ1011 | 12.2 | 139 | 12.2 | 140 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7680 | 1079.9997 | 128.5451
SYL-S.1.RR.231.1 | 24530279150538 | South Shurma, Boroikandi R/A, Rd # 10, Dilbar Hossain | 2019-07-23 | NQ1011 | 7.4 | 141 | 7.4 | 142 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7680 | 1079.9997 | 77.97
SYL-S.1.RR.231.2 | 24530279150538 | South Shurma, Boroikandi R/A, Rd # 10, Dilbar Hossain | 2021-02-28 | NQ1003 | 5.9 | 305 | 5.9 | 306 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7680 | 1079.9997 | 62.1652
SYL-S.1.RR.231.3 | 24530279150538 | South Shurma, Boroikandi R/A, Rd # 10, Dilbar Hossain | 2021-02-28 | NQ1003 | 6.9 | 307 | 6.9 | 308 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7680 | 1079.9997 | 72.7017
SYL-S.1.RR.232.1 | 24530109150504 | South Shurma, Boroikandi R/A, Rd # 10, Kazi Shafiqur Rahman | 2019-07-23 | NQ1011 | 4.3 | 143 | 4.3 | 144 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7680 | 1079.9997 | 45.3069
SYL-S.1.RR.233.1 | 24525639150433 | South Shurma, Niyamotpur R/A, Rd # 10/1, Mahbubur Rob | 2019-07-23 | NQ1011 | 5.4 | 145 | 5.4 | 146 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7680 | 1079.9997 | 56.897
SYL-S.1.RR.234.1 | 24525609150433 | South Shurma, Niyamotpur R/A, Rd # 10/1, Shafiq Ahmed | 2019-07-23 | NQ1011 | 12.5 | 147 | 12.2 | 148 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7680 | 1079.9997 | 128.5451
SYL-S.1.RR.235.1 | 24525609150433 | South Shurma, Niyamotpur R/A, Rd # 10/1, Josna Begum | 2019-07-23 | NQ1011 | 8.4 | 149 | 8.4 | 150 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7680 | 1079.9997 | 88.5064
SYL-S.1.RR.236.1 | 24525609150433 | South Shurma, Niyamotpur R/A, Rd # 10/1, Peyara Begum | 2019-07-23 | NQ1011 | 7.3 | 151 | 7.3 | 152 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7680 | 1079.9997 | 76.9163
SYL-S.1.RR.237.1 | 24524989150425 | South Shurma, Niyamotpur R/A, Rd # 10/2, H # 80, Hazi Abdur Razzak | 2019-07-23 | NQ1011 | 5.6 | 155 | 5.6 | 156 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7680 | 1079.9997 | 59.0043
SYL-S.1.RR.238.1 | 24530669150111 | South Shurma, Gopshohor, Shahipara, Hazi Md. Soyful Khan | 2019-07-25 | NQ1011 | 9.1 | 201 | 9.1 | 202 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7680 | 1079.9997 | 95.882
SYL-S.1.RR.239.1 | 24530329150108 | South Shurma, Gopshohor, Shahipara, Showkat Khan | 2019-07-25 | NQ1011 | 1.5 | 205 | 1.5 | 206 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7680 | 1079.9997 | 15.8047
SYL-S.1.RR.240.1 | 24525769150128 | South Shurma, Gopshohor, Pashchim Para, Mollik Mia | 2019-07-25 | NQ1011 | 12 | 207 | 12 | 208 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7680 | 1079.9997 | 126.4378
SYL-S.1.RR.241.1 | 24530019150108 | South Shurma, Gopshohor, Pashchim Para, Alauddin | 2019-07-25 | NQ1011 | 11.4 | 209 | 11.4 | 210 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7680 | 1079.9997 | 120.1159
SYL-S.1.RR.242.1 | 24520629152406 | Sylhet, Shib Bari Bazar, Gotatikor, Shib Mondir Road, Montosh Kumar Dhor | 2019-07-25 | NQ1011 | 10.3 | 213 | 10.3 | 214 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7656 | 1103.9997 | 108.5258
SYL-S.1.RR.243.1 | 24520629152406 | Sylhet, Shib Bari Bazar, Gotatikor, Shib Mondir Road, Manik Lal Dhor | 2019-07-25 | NQ1011 | 15.3 | 215 | 15.3 | 216 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 7656 | 1103.9997 | 161.2082
SYL-S.1.RR.243.2 | 24520629152406 | Sylhet, Shib Bari Bazar, Gotatikor, Shib Mondir Road, Manik Lal Dhor | 2019-07-25 | NQ1011 | 4.9 | 218 | 4.9 | 219 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7656 | 1103.9997 | 51.6288
SYL-S.1.RR.244.1 | 24520779152450 | Sylhet, Shib Bari Bazar, Gotatikor, Shib Mondir Road, Nirmolendu Dey | 2019-07-25 | NQ1011 | 11.9 | 220 | 11.9 | 221 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7656 | 1103.9997 | 125.3841
SYL-S.1.RR.251.1 | 24530459151428 | South Surma, Technical Road By Lane, Khujar Khola, Sylhet Sadar Khadda gudam, Monuar Hossen | 2019-07-17 | NQ1011 | 3.4 | 27 | 3.4 | 28 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7584 | 1175.9997 | 35.824
SYL-S.1.RR.252.1 | 24525819151385 | South Surma, Khujar Khola, Adorshow R/A, Block-B, Rezaur Rahman Rujon | 2019-07-17 | NQ1011 | 6.4 | 29 | 5.9 | 30 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7584 | 1175.9997 | 62.1652
SYL-S.1.RR.253.1 | 24525439151372 | South Surma, Khujar Khola, Adorshow R/A, Block-B, Jamir Uddin | 2019-07-17 | NQ1011 | 3 | 31 | 3 | 32 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7584 | 1175.9997 | 31.6094
SYL-S.1.RR.254.1 | 24525989151424 | South Surma, Khujar Khola, Adorshow R/A, Ismaeel Complex, H # 301/ C-4 | 2019-07-17 | NQ1011 | 3.2 | 33 | 3.2 | 34 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7584 | 1175.9997 | 33.7167
SYL-S.1.RR.255.1 | 24525799151434 | South Surma, Khujar Khola, Adorshow R/A, Block-C, Babul Mia | 2019-07-17 | NQ1011 | 10.5 | 35 | 10.5 | 36 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7584 | 1175.9997 | 110.6331
SYL-S.1.RR.256.1 | 24525749151430 | South Surma, Khujar Khola, Adorshow R/A, Block-C, Goni Mia | 2019-07-17 | NQ1011 | 7.7 | 37 | 7.7 | 38 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7584 | 1175.9997 | 81.1309
SYL-S.1.RR.257.1 | 24525659151428 | South Surma, Khujar Khola, Adorshow R/A, Block-C, H # 308, Nasir Uddin | 2019-07-17 | NQ1011 | 6.4 | 39 | 6.4 | 40 | 2022-01-01 | 2022-11-13 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7584 | 1175.9997 | 67.4335
SYL-S.1.RR.258.1 | 24530819151257 | South Surma, Boroikandi, Technical Road, Jaman Mia | 2019-07-18 | NQ1011 | 3.5 | 57 | 3.5 | 58 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7632 | 1127.9997 | 36.8777
SYL-S.1.RR.259.1 | 24530819151257 | South Surma, Boroikandi, Technical Road, Dar Abu Ahmad | 2019-07-18 | NQ1011 | 4.5 | 59 | 4.5 | 60 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7632 | 1127.9997 | 47.4142
SYL-S.1.RR.260.1 | 24530819151166 | South Surma, Boroikandi R/A, Rd # 01, Khayrul Islam | 2019-07-18 | NQ1011 | 4.4 | 61 | 4.4 | 62 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7632 | 1127.9997 | 46.3605
SYL-S.1.RR.261.1 | 24530789151158 | South Surma, Boroikandi R/A, Rd # 01, Babu Mia | 2019-07-18 | NQ1011 | 7.1 | 63 | 7.1 | 64 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7632 | 1127.9997 | 74.809
SYL-S.1.RR.262.1 | 24530709151158 | South Surma, Boroikandi R/A, Rd # 01, Aftab Ali | 2019-07-18 | NQ1011 | 8.7 | 65 | 8.7 | 66 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7632 | 1127.9997 | 91.6674
SYL-S.1.RR.263.1 | 24530849151136 | South Surma, Boroikandi R/A, Rd # 01, Yusuf Mia | 2019-07-18 | NQ1011 | 11.4 | 67 | 11.4 | 68 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7632 | 1127.9997 | 120.1159
SYL-S.1.RR.264.1 | 24530549151082 | South Surma, Boroikandi R/A, Rd # 02, Akter Hasan | 2019-07-18 | NQ1011 | 9.7 | 69 | 9.7 | 70 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7632 | 1127.9997 | 102.2039
SYL-S.1.RR.265.1 | 24531319151048 | South Surma, Boroikandi R/A, Rd # 03, Selim | 2019-07-20 | NQ1011 | 5.5 | 71 | 5.5 | 72 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7632 | 1127.9997 | 57.9506
SYL-S.1.RR.266.1 | 24531319151048 | South Surma, Boroikandi R/A, Rd # 03, Sona Mia | 2019-07-20 | NQ1011 | 25.5 | 73 | 24.6 | 74 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 24.6 | 24.6 | 1.476 | 1.476 | 0.0007168 | 100% | 0% | 1.476 | 1.476 | 0.0011869 | 28 | 0.029589 | 0.029589 |  | 0 | 0 | 7632 | 1127.9997 | 259.1974
SYL-S.1.RR.267.1 | 24531109151058 | South Surma, Boroikandi R/A, Rd # 03, Hira Mia | 2019-07-20 | NQ1011 | 12.2 | 75 | 12 | 76 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7632 | 1127.9997 | 126.4378
SYL-S.1.RR.268.1 | 24530889151023 | South Surma, Boroikandi R/A, Rd # 03, Ahmod Hossen | 2019-07-20 | NQ1011 | 9.6 | 79 | 9.6 | 80 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7632 | 1127.9997 | 101.1502
SYL-S.1.RR.269.1 | 24530919151006 | South Surma, Boroikandi R/A, Rd # 03, Rofiq | 2019-07-20 | NQ1011 | 2.8 | 81 | 2.8 | 82 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7632 | 1127.9997 | 29.5021
SYL-S.1.RR.270.1 | 24530919151006 | South Surma, Boroikandi R/A, Rd # 03, Boshir Ahmad | 2019-07-20 | NQ1011 | 6.2 | 83 | 6.2 | 84 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7632 | 1127.9997 | 65.3262
SYL-S.1.RR.271.1 | 24530689151027 | South Surma, Boroikandi R/A, Rd # 03, Abdus Samad | 2019-07-20 | NQ1011 | 11.1 | 85 | 11.1 | 86 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7632 | 1127.9997 | 116.9549
SYL-S.1.RR.272.1 | 24530539151001 | South Surma, Boroikandi R/A, Rd # 03, Sujeffor Ali | 2019-07-20 | NQ1011 | 7.6 | 87 | 7 | 88 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7632 | 1127.9997 | 73.7554
SYL-S.1.RR.273.1 | 24530689151050 | South Surma, Boroikandi R/A, Rd # 03, Sabuj | 2019-07-20 | NQ1011 | 3.3 | 99 | 3.2 | 100 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7632 | 1127.9997 | 33.7167
SYL-S.1.RR.274.1 | 24530539151001 | South Surma, Boroikandi R/A, Rd # 03, Ustar Ali | 2019-07-20 | NQ1011 | 11.7 | 89 | 11.7 | 90 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7632 | 1127.9997 | 123.2768
SYL-S.1.RR.275.1 | 24530539151001 | South Surma, Boroikandi R/A, Rd # 03, Yusuf Ali | 2019-07-20 | NQ1011 | 3.9 | 91 | 3.9 | 92 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7632 | 1127.9997 | 41.0923
SYL-S.1.RR.276.1 | 24530539151001 | South Surma, Boroikandi R/A, Rd # 03, Malai Mia | 2019-07-20 | NQ1011 | 7.2 | 93 | 7.2 | 94 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7632 | 1127.9997 | 75.8627
SYL-S.1.RR.277.1 | 24530689151050 | South Surma, Boroikandi R/A, Rd # 03, Monjur Mia | 2019-07-20 | NQ1011 | 4.4 | 95 | 4.4 | 96 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7632 | 1127.9997 | 46.3605
SYL-S.1.RR.278.1 | 24530689151050 | South Surma, Boroikandi R/A, Rd # 03, Gous Mia | 2019-07-20 | NQ1011 | 2.1 | 97 | 2.1 | 98 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7632 | 1127.9997 | 22.1266
SYL-S.1.RR.279.1 | 24530789150578 | South Surma, Boroikandi R/A, Rd # 04, Malik Monzil, Abdul Malek | 2019-07-21 | NQ1011 | 3.5 | 101 | 3.5 | 102 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7632 | 1127.9997 | 36.8777
SYL-S.1.RR.279.2 | 24530789150578 | South Surma, Boroikandi R/A, Rd # 04, Malik Monzil, Abdul Malek | 2021-10-24 | LU1001 | 10.3 | 80 | 10.3 | 81 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7632 | 1127.9997 | 108.5258
SYL-S.1.RR.280.1 | 24530629151165 | South Surma, Boroikandi (Gangu) R/A, Rd # 01, Jasim Ahmod Polash | 2019-07-21 | NQ1011 | 14.1 | 103 | 14.2 | 104 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7632 | 1127.9997 | 149.618
SYL-S.1.RR.281.1 | 24530629151165 | South Surma, Boroikandi (Gangu) R/A, Dudu Mia | 2019-07-21 | NQ1011 | 11.4 | 105 | 11.4 | 106 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7632 | 1127.9997 | 120.1159
SYL-S.1.RR.282.1 | 24530629151165 | South Surma, Boroikandi (Gangu) R/A, Helal Mia | 2019-07-21 | NQ1011 | 3.7 | 107 | 3.7 | 108 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7632 | 1127.9997 | 38.985
SYL-S.1.RR.283.1 | 24530629151165 | South Surma, Boroikandi (Gangu) R/A, Khaled Mia | 2019-07-21 | NQ1011 | 3.7 | 109 | 3.7 | 110 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7632 | 1127.9997 | 38.985
SYL-S.1.RR.284.1 | 24531019150389 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 01, Layek Ahmod | 2019-07-23 | NQ1011 | 15 | 157 | 15 | 158 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 7680 | 1079.9997 | 158.0472
SYL-S.1.RR.285.1 | 24530859150388 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 01, Khasrujjaman | 2019-07-23 | NQ1011 | 5.5 | 159 | 5.5 | 160 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7680 | 1079.9997 | 57.9506
SYL-S.1.RR.286.1 | 24530559150379 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 01, Gedu Mia | 2019-07-23 | NQ1011 | 15.2 | 161 | 15.2 | 162 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7680 | 1079.9997 | 160.1545
SYL-S.1.RR.286.2 | 24530559150379 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 01, Gedu Mia | 2021-02-28 | NQ1003 | 5 | 302 | 5 | 303 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7680 | 1079.9997 | 52.6824
SYL-S.1.RR.287.1 | 24530189150341 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 03, Abdur Rob | 2019-07-23 | NQ1011 | 8.4 | 163 | 8.4 | 164 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7680 | 1079.9997 | 88.5064
SYL-S.1.RR.288.1 | 24530319150352 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 03, Masum Hasan | 2019-07-23 | NQ1011 | 3.1 | 165 | 3.1 | 166 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7680 | 1079.9997 | 32.6631
SYL-S.1.RR.289.1 | 24530869150347 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 03, Showkot Ali | 2019-07-23 | NQ1011 | 5.2 | 167 | 5.2 | 168 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7680 | 1079.9997 | 54.7897
SYL-S.1.RR.290.1 | 24530869150347 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 03, Islam Ali | 2019-07-23 | NQ1011 | 3.8 | 169 | 3.8 | 170 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7680 | 1079.9997 | 40.0386
SYL-S.1.RR.291.1 | 24530869150347 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 03, Masuk Mia | 2019-07-23 | NQ1011 | 6.2 | 171 | 6.2 | 172 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7680 | 1079.9997 | 65.3262
SYL-S.1.RR.292.1 | 24531079150341 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 03, Lukman | 2019-07-23 | NQ1011 | 11 | 173 | 11 | 174 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7680 | 1079.9997 | 115.9013
SYL-S.1.RR.293.1 | 24531199150368 | South Surma, Technical Road, Mollargoan, Telirai, Samol Malakar | 2019-07-24 | NQ1011 | 4.4 | 175 | 4.4 | 176 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7680 | 1079.9997 | 46.3605
SYL-S.1.RR.293.2 | 24531199150368 | South Surma, Technical Road, Mollargoan, Telirai, Samol Malakar | 2019-07-24 | NQ1011 | 4 | 177 | 4 | 178 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7680 | 1079.9997 | 42.1459
SYL-S.1.RR.294.1 | 24525169150370 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 01, Mokhsed Mia | 2019-07-24 | NQ1011 | 10.5 | 179 | 10.5 | 180 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7680 | 1079.9997 | 110.6331
SYL-S.1.RR.295.1 | 24525169150370 | South Surma, Technical Road, Mollargoan, Telirai R/A, Rd # 01, Chaleha Khatun | 2019-07-24 | NQ1011 | 5.8 | 181 | 5.8 | 182 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7680 | 1079.9997 | 61.1116
SYL-S.1.RR.296.1 | 24525489150255 | South Surma, Mollargoan, Telirai, Niamotpur, Doulat Mia | 2019-07-24 | NQ1011 | 6.7 | 183 | 6.3 | 184 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7680 | 1079.9997 | 66.3798
SYL-S.1.RR.297.1 | 24524749150220 | South Surma, Mollargoan, Telirai, Goalgaw, Ilas Mia | 2019-07-24 | NQ1011 | 4.2 | 185 | 4.2 | 186 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7680 | 1079.9997 | 44.2532
SYL-S.1.RR.298.1 | 24524749150220 | South Surma, Mollargoan, Telirai, Goalgaw, Abdal | 2019-07-24 | NQ1011 | 10.4 | 187 | 10.4 | 188 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7680 | 1079.9997 | 109.5794
SYL-S.1.RR.299.1 | 24524749150220 | South Surma, Mollargoan, Telirai, Goalgaw, Jafrul Hoque | 2019-07-24 | NQ1011 | 7.4 | 189 | 7.4 | 190 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7680 | 1079.9997 | 77.97
SYL-S.1.RR.300.1 | 24524749150220 | South Surma, Mollargoan, Telirai, Goalgaw, Azad Mia | 2019-07-24 | NQ1011 | 3.6 | 191 | 3.6 | 192 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7680 | 1079.9997 | 37.9313
SYL-S.1.RR.301.1 | 24532589150166 | Sylhet, Khitta Khalpar, Khalpar Road, Goljar | 2019-07-28 | NQ1008 | 14 | 213 | 14 | 214 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 7488 | 0 | 264 | 1007.9997 | 21.4194
SYL-S.1.RR.301.2 | 24532589150166 | Sylhet, Khitta Khalpar, Khalpar Road, Goljar | 2019-07-28 | NQ1008 | 4.3 | 215 | 4.3 | 216 | 2022-01-01 | 2022-11-20 | MN1018 | 0.9 | 147 | 0.9 | 148 | 2022-11-20 | GS | 0 |  |  |  |  | 0.0007168 | 100% | 0% |  |  | 0.0011869 | 28 |  |  |  | 7488 | 0 | 264 | 1007.9997
SYL-S.1.RR.302.1 | 24532869150159 | Sylhet, Khitta Khalpar, Khalpar Road, Abdus Salam Horu Mia | 2019-07-28 | NQ1008 | 3.3 | 217 | 3.3 | 218 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7752 | 1007.9997 | 34.7704
SYL-S.1.RR.303.1 | 24532909150159 | Sylhet, Khitta Khalpar, Khalpar Road, Kamrul Islam | 2019-07-28 | NQ1008 | 9 | 219 | 8.3 | 220 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7752 | 1007.9997 | 87.4528
SYL-S.1.RR.303.2 | 24532909150159 | Sylhet, Khitta Khalpar, Khalpar Road, Kamrul Islam | 2019-07-28 | NQ1008 | 10.8 | 221 | 10.8 | 222 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7752 | 1007.9997 | 113.794
SYL-S.1.RR.304.1 | 24535069150147 | Sylhet, Sodor Khola, Sourh Surma, Rd # 2, Shibul | 2019-07-28 | NQ1008 | 5.2 | 223 | 5.3 | 224 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7752 | 1007.9997 | 55.8434
SYL-S.1.RR.305.1 | 24534439150075 | Sylhet, South Surma, Sodor Khola, Rd # 2, Chunu Mia | 2019-07-28 | NQ1008 | 3.8 | 225 | 3.8 | 226 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7752 | 1007.9997 | 40.0386
SYL-S.1.RR.306.1 | 24534439150075 | Sylhet, South Surma, Sodor Khola, Rd # 2, Forhad Mia | 2019-07-28 | NQ1008 | 3.9 | 227 | 3.8 | 228 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7752 | 1007.9997 | 40.0386
SYL-S.1.RR.307.1 | 24535479150108 | Sylhet, South Surma, Sodor Khola, Rd # 2, Poresh | 2019-07-28 | NQ1008 | 4.2 | 231 | 4.2 | 232 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7752 | 1007.9997 | 44.2532
SYL-S.1.RR.308.1 | 24540199150003 | Sylhet, South Surma, Kharua, Azharul Islam | 2019-07-28 | NQ1008 | 4.8 | 234 | 4.8 | 235 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7752 | 1007.9997 | 50.5751
SYL-S.1.RR.309.1 | 24540419150041 | Sylhet, South Surma, Kharua, Ruwel | 2019-07-28 | NQ1008 | 11.5 | 236 | 11.5 | 237 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7752 | 1007.9997 | 121.1695
SYL-S.1.RR.310.1 | 24524769148564 | Sylhet, South Surma, Sohidpur, Abdul Hamid | 2019-07-29 | NQ1008 | 5.2 | 273 | 5.2 | 274 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7680 | 1079.9997 | 54.7897
SYL-S.1.RR.310.2 | 24524769148564 | Sylhet, South Surma, Sohidpur, Abdul Hamid | 2019-07-29 | NQ1008 | 10.9 | 275 | 10.9 | 276 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7680 | 1079.9997 | 114.8476
SYL-S.1.RR.311.1 | 24524769148564 | Sylhet, South Surma, Sohidpur, Abdul Hamid | 2019-07-29 | NQ1008 | 11.9 | 277 | 11.7 | 278 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7680 | 1079.9997 | 123.2768
SYL-S.1.RR.311.2 | 24524769148564 | Sylhet, South Surma, Sohidpur, Abdul Hamid | 2019-07-29 | NQ1008 | 3.3 | 279 | 3.3 | 280 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7680 | 1079.9997 | 34.7704
SYL-S.1.RR.312.1 | 24524169149003 | Sylhet, South Surma, Sohidpur, Mukabbir Ali | 2019-07-29 | NQ1008 | 3.8 | 281 | 3.8 | 282 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7680 | 1079.9997 | 40.0386
SYL-S.1.RR.312.2 | 24524169149003 | Sylhet, South Surma, Sohidpur, Mukabbir Ali | 2021-10-25 | LU1001 | 6.5 | 90 | 6.5 | 91 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7680 | 1079.9997 | 68.4871
SYL-S.1.RR.313.1 | 24522839148377 | Sylhet, Bissonatah, Nobabi, Kamal Bazar, Monfor | 2019-07-29 | NQ1008 | 3 | 283 | 3.3 | 284 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7680 | 1079.9997 | 34.7704
SYL-S.1.RR.314.1 | 24522839148377 | Sylhet, Bissonatah, Nobabi, Kamal Bazar, Cherag Ali | 2019-07-29 | NQ1008 | 4.6 | 286 | 4.6 | 287 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7680 | 1079.9997 | 48.4678
SYL-S.1.RR.315.1 | 24522469153398 | Sylhet, Muglabazar, Alompur R/A, Nuru Mia | 2019-07-30 | NQ1008 | 10.7 | 300 | 10.7 | 301 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7488 | 1271.9997 | 112.7403
SYL-S.1.RR.316.1 | 24522249153380 | Sylhet, Muglabazar, Alompur R/A, Lutfor | 2019-07-30 | NQ1008 | 4.5 | 302 | 4.5 | 303 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7488 | 1271.9997 | 47.4142
SYL-S.1.RR.316.2 | 24522249153380 | Sylhet, Muglabazar, Alompur R/A, Lutfor | 2019-07-30 | NQ1008 | 9.4 | 304 | 9.4 | 305 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7488 | 1271.9997 | 99.0429
SYL-S.1.RR.317.1 | 24522249153380 | Sylhet, Muglabazar, Alompur R/A, Lutfor | 2019-07-30 | NQ1008 | 6.6 | 306 | 6.6 | 307 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7488 | 1271.9997 | 69.5408
SYL-S.1.RR.317.2 | 24522249153380 | Sylhet, Muglabazar, Alompur R/A, Lutfor | 2021-02-24 | LX1011 | 1.6 | 155 | 1.6 | 156 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7488 | 1271.9997 | 16.8584
SYL-S.1.RR.318.1 | 24522249153380 | Sylhet, Muglabazar, Alompur R/A, Lutfor | 2019-07-30 | NQ1008 | 9.6 | 308 | 9.6 | 309 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7488 | 1271.9997 | 101.1502
SYL-S.1.RR.319.1 | 24521789153349 | Sylhet, Muglabazar, Alompur R/A, Shah Monjil, Salek Ahmed | 2019-07-30 | NQ1008 | 18.5 | 310 | 18.5 | 311 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 18.5 | 18.5 | 1.11 | 1.11 | 0.0007168 | 100% | 0% | 1.11 | 1.11 | 0.0011869 | 28 | 0.022252 | 0.022252 |  | 0 | 0 | 7488 | 1271.9997 | 194.9249
SYL-S.1.RR.320.1 | 24521789153349 | Sylhet, Muglabazar, Alompur R/A, Shah Monjil, Musa Mia | 2019-07-30 | NQ1008 | 11.7 | 312 | 11.7 | 313 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7488 | 1271.9997 | 123.2768
SYL-S.1.RR.321.1 | 24521789153349 | Sylhet, Muglabazar, Alompur R/A, Shah Monjil, Monohor Ali | 2019-07-30 | NQ1008 | 10.3 | 314 | 10.1 | 315 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7488 | 1271.9997 | 106.4185
SYL-S.1.RR.322.1 | 24521789153349 | Sylhet, Muglabazar, Alompur R/A, Shah Monjil, Selim Ahmed | 2019-07-30 | NQ1008 | 3.6 | 316 | 3.6 | 317 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7488 | 1271.9997 | 37.9313
SYL-S.1.RR.323.1 | 24521789153324 | Sylhet, Muglabazar, Alompur R/A, Amina Begum | 2019-07-30 | NQ1008 | 3.7 | 318 | 3.7 | 319 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7488 | 1271.9997 | 38.985
SYL-S.1.RR.324.1 | 24521429153335 | Sylhet, Muglabazar, Alompur R/A, Nuru Mia | 2019-07-30 | NQ1008 | 10.3 | 320 | 10.3 | 321 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7488 | 1271.9997 | 108.5258
SYL-S.1.RR.325.1 | 24521429153335 | Sylhet, Muglabazar, Alompur R/A, Fajlu Mia | 2019-07-30 | NQ1008 | 1.7 | 322 | 1.7 | 323 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7488 | 1271.9997 | 17.912
SYL-S.1.RR.326.1 | 24521429153335 | Sylhet, Muglabazar, Alompur R/A, Samsu | 2019-07-30 | NQ1008 | 7.8 | 324 | 7.8 | 325 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7488 | 1271.9997 | 82.1846
SYL-S.1.RR.327.1 | 24521749153278 | Sylhet, Muglabazar, Alompur R/A, Sofiqur Rohman | 2019-07-30 | NQ1008 | 1.6 | 326 | 1.6 | 327 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7512 | 1247.9997 | 16.8584
SYL-S.1.RR.328.1 | 24521699153269 | Sylhet, Muglabazar, Alompur R/A, Shahin | 2019-07-30 | NQ1008 | 2 | 328 | 2 | 329 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7512 | 1247.9997 | 21.073
SYL-S.1.RR.328.2 | 24521699153269 | Sylhet, Muglabazar, Alompur R/A, Shahin | 2019-07-30 | NQ1008 | 2.5 | 330 | 2.5 | 331 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7512 | 1247.9997 | 26.3412
SYL-S.1.RR.329.1 | 24521749153394 | Sylhet, Muglabazar, Alompur R/A, Mujibur Rohman | 2019-07-31 | NQ1008 | 6.9 | 362 | 6.9 | 363 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7488 | 1271.9997 | 72.7017
SYL-S.1.RR.330.1 | 24521769153403 | Sylhet, Muglabazar, Alompur R/A, Moinuddin | 2019-07-31 | NQ1008 | 5.2 | 364 | 5.2 | 365 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7488 | 1271.9997 | 54.7897
SYL-S.1.RR.331.1 | 24521709153385 | Sylhet, Muglabazar, Alompur R/A, Hazi Ana Mia | 2019-07-31 | NQ1008 | 10 | 366 | 10 | 367 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7488 | 1271.9997 | 105.3648
SYL-S.1.RR.332.1 | 24521189153384 | Sylhet, Muglabazar, Alompur R/A, Romabosh Sen | 2019-07-31 | NQ1008 | 9.9 | 368 | 9.9 | 369 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7488 | 1271.9997 | 104.3112
SYL-S.1.RR.333.1 | 24520899153376 | Sylhet, Muglabazar, Alompur R/A, Toibur Rohman | 2019-07-31 | NQ1008 | 3.8 | 370 | 3.8 | 371 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7488 | 1271.9997 | 40.0386
SYL-S.1.RR.334.1 | 24520909153378 | Sylhet, Muglabazar, Alompur R/A, Aktarujjaman | 2019-07-31 | NQ1008 | 10.4 | 372 | 10.4 | 373 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7488 | 1271.9997 | 109.5794
SYL-S.1.RR.334.2 | 24520909153378 | Sylhet, Muglabazar, Alompur R/A, Aktarujjaman | 2019-07-31 | NQ1008 | 9.9 | 374 | 9.9 | 375 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7488 | 1271.9997 | 104.3112
SYL-S.1.RR.335.1 | 24520549153362 | Sylhet, Muglabazar, Alompur R/A, Dipok Ronjon Sorkar | 2019-07-31 | NQ1008 | 11.7 | 376 | 11.7 | 377 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7512 | 1247.9997 | 123.2768
SYL-S.1.RR.336.1 | 24520029153371 | Sylhet, Muglabazar, Alompur R/A, Sunil Dey | 2019-07-31 | NQ1008 | 10.7 | 378 | 10.7 | 379 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7512 | 1247.9997 | 112.7403
SYL-S.1.RR.337.1 | 24520049153362 | Sylhet, Muglabazar, Alompur R/A, Ajoy Kumar Deb | 2019-07-31 | NQ1008 | 12.4 | 380 | 12.4 | 381 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7512 | 1247.9997 | 130.6524
SYL-S.1.RR.337.2 | 24520049153362 | Sylhet, Muglabazar, Alompur R/A, Ajoy Kumar Deb | 2021-02-24 | MN1018 | 2.1 | 157 | 2.1 | 158 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7512 | 1247.9997 | 22.1266
SYL-S.1.RR.338.1 | 24520019153349 | Sylhet, Muglabazar, Alompur R/A, Ajoy Kumar Deb | 2019-07-31 | NQ1008 | 9.6 | 382 | 9.6 | 383 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7512 | 1247.9997 | 101.1502
SYL-S.1.RR.339.1 | 24515199153375 | Sylhet, Muglabazar, Gongramer Chokh, Bijoy Nath | 2019-07-31 | NQ1008 | 7.4 | 384 | 7.4 | 385 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 2808 | 0 | 4704 | 1247.9997 | 52.9768
SYL-S.1.RR.340.1 | 24514979153415 | Sylhet, Muglabazar, Gongaramer Chokh, Lelu Mia | 2019-08-01 | NQ1008 | 11.2 | 386 | 11.2 | 387 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7512 | 1247.9997 | 118.0086
SYL-S.1.RR.341.1 | 24520239154416 | Sylhet, Muglabazar, Kusai, Hanif Ahmed | 2019-08-01 | NQ1008 | 10.2 | 390 | 10.2 | 391 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7488 | 1271.9997 | 107.4721
SYL-S.1.RR.342.1 | 24520239154416 | Sylhet, Muglabazar, Kusai, Harun | 2019-08-01 | NQ1008 | 3.2 | 392 | 3.2 | 393 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7488 | 1271.9997 | 33.7167
SYL-S.1.RR.343.1 | 24520019154419 | Sylhet, Muglabazar, Kusai, Bosir Ali | 2019-08-01 | NQ1008 | 2.1 | 394 | 2.1 | 395 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7488 | 1271.9997 | 22.1266
SYL-S.1.RR.343.2 | 24520019154419 | Sylhet, Muglabazar, Kusai, Bosir Ali | 2019-08-01 | NQ1008 | 4.5 | 397 | 4.5 | 398 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7488 | 1271.9997 | 47.4142
SYL-S.1.RR.344.1 | 24515929154417 | Sylhet, Muglabazar, Kusai, Beside Abdul Ohab | 2019-08-01 | NQ1008 | 12.7 | 399 | 12.7 | 400 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7488 | 1271.9997 | 133.8133
SYL-S.1.RR.345.1 | 24515799154414 | Sylhet, Muglabazar, Kusai, Hasan Mia | 2019-08-01 | NQ1008 | 5.5 | 401 | 5.5 | 402 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7488 | 1271.9997 | 57.9506
SYL-S.1.RR.346.1 | 24515799154414 | Sylhet, Muglabazar, Kusai, Manik | 2019-08-01 | NQ1008 | 6.3 | 403 | 6.1 | 404 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7488 | 1271.9997 | 64.2725
SYL-S.1.RR.347.1 | 24515799154414 | Sylhet, Muglabazar, Kusai, Manik | 2019-08-01 | NQ1008 | 4.4 | 405 | 4.4 | 406 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7488 | 1271.9997 | 46.3605
SYL-S.1.RR.348.1 | 24521789154418 | Sylhet, Muglabazar, Sarping, Alamin | 2019-08-01 | NQ1008 | 5.5 | 407 | 5.5 | 408 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7488 | 1271.9997 | 57.9506
SYL-S.1.RR.349.1 | 24521829154384 | Sylhet, Muglabazar, Sarping, Nazmul | 2019-08-01 | NQ1008 | 10.5 | 409 | 10.2 | 410 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7488 | 1271.9997 | 107.4721
SYL-S.1.RR.350.1 | 24522079154427 | Sylhet, Muglabazar, Sarping, Buro Mia | 2019-08-01 | NQ1008 | 7.8 | 411 | 7.8 | 412 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7488 | 1271.9997 | 82.1846
SYL-S.1.RR.351.1 | 24510339150459 | Sylhet, South Boldi, Banessorpur, Muktar Mia | 2019-07-27 | NQ1008 | 8 | 183 | 8 | 184 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7632 | 1127.9997 | 84.2919
SYL-S.1.RR.351.2 | 24510339150459 | Sylhet, South Boldi, Banessorpur, Muktar Mia | 2019-07-27 | NQ1008 | 6.5 | 185 | 6.5 | 186 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7632 | 1127.9997 | 68.4871
SYL-S.1.RR.352.1 | 24510009150355 | Sylhet, South Boldi, Banessorpur, Mostafizur Rahaman | 2019-07-27 | NQ1008 | 6.9 | 187 | 6.9 | 188 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7632 | 1127.9997 | 72.7017
SYL-S.1.RR.353.1 | 24515939152423 | Moglabazar, Bandar Ghat, Word - 27, Azad Mia | 2019-07-27 | NQ1008 | 15.6 | 189 | 15.6 | 190 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 15.6 | 15.6 | 0.936 | 0.936 | 0.0007168 | 100% | 0% | 0.936 | 0.936 | 0.0011869 | 28 | 0.018764 | 0.018764 |  | 0 | 0 | 7656 | 1103.9997 | 164.3691
SYL-S.1.RR.353.2 | 24515939152423 | Moglabazar, Bandar Ghat, Word - 27, Azad Mia | 2019-07-27 | NQ1008 | 5.6 | 191 | 5.6 | 192 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7656 | 1103.9997 | 59.0043
SYL-S.1.RR.354.1 | 24520029152445 | Moglabazar, Bandar Ghat, Word - 27, Zahir Rayhan | 2019-07-27 | NQ1008 | 11.2 | 193 | 10.9 | 194 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7656 | 1103.9997 | 114.8476
SYL-S.1.RR.355.1 | 24520179152478 | Moglabazar, Bandar Ghat, Word - 27, Oshit Dostidhor | 2019-07-27 | NQ1008 | 4.9 | 195 | 4.9 | 196 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7656 | 1103.9997 | 51.6288
SYL-S.1.RR.355.2 | 24520179152478 | Moglabazar, Bandar Ghat, Word - 27, Oshit Dostidhor | 2019-07-27 | NQ1008 | 14.1 | 197 | 14.1 | 198 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7656 | 1103.9997 | 148.5644
SYL-S.1.RR.356.1 | 24520179152478 | Moglabazar, Bandar Ghat, Word - 27, Suronjon Babu | 2019-07-27 | NQ1008 | 8.9 | 201 | 8.9 | 202 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7656 | 1103.9997 | 93.7747
SYL-S.1.RR.357.1 | 24520019152512 | Moglabazar, Bandar Ghat, Word - 27, Nipendro Malakar | 2019-07-27 | NQ1008 | 12 | 203 | 12 | 204 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 840 | 0 | 6816 | 1103.9997 | 114.3136
SYL-S.1.RR.358.1 | 24520069152542 | Moglabazar, Bandar Ghat, Word - 27, Anamul Haque | 2019-07-27 | NQ1008 | 9.9 | 205 | 9.9 | 206 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7656 | 1103.9997 | 104.3112
SYL-S.1.RR.359.1 | 24520509152504 | Moglabazar, Paityapara, Word - 27, Songku Dash | 2019-07-27 | NQ1008 | 9.7 | 207 | 9.7 | 208 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7656 | 1103.9997 | 102.2039
SYL-S.1.RR.360.1 | 24520639152504 | Moglabazar, Paityapara, Word - 27, Shonjit Dey | 2019-07-27 | NQ1008 | 10.6 | 209 | 10.6 | 210 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7656 | 1103.9997 | 111.6867
SYL-S.1.RR.361.1 | 24520639152504 | Moglabazar, Paityapara, Word - 27, Sujit | 2019-07-27 | NQ1008 | 6.9 | 211 | 6.9 | 212 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7656 | 1103.9997 | 72.7017
SYL-S.1.RR.362.1 | 24535909149599 | South Surma, 1 No Mollargaon, Khanoa, Hoji Raza Mia | 2019-07-28 | NQ1008 | 12.1 | 239 | 11.9 | 240 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7752 | 1007.9997 | 125.3841
SYL-S.1.RR.363.1 | 24534749149549 | South Surma, 1 No Mollargaon, Khanoa, Kolomdhor | 2019-07-28 | NQ1008 | 6.6 | 241 | 6.6 | 242 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7752 | 1007.9997 | 69.5408
SYL-S.1.RR.364.1 | 24534889149593 | South Surma, 1 No Mollargaon, Khanoa, Haji Siddek Alir Bari | 2019-07-28 | NQ1008 | 3.6 | 243 | 3.6 | 244 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7752 | 1007.9997 | 37.9313
SYL-S.1.RR.365.1 | 24535589149556 | South Surma, 1 No Mollargaon, Khanoa, Lal Mia | 2019-07-28 | NQ1008 | 11.5 | 245 | 11.5 | 246 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7752 | 1007.9997 | 121.1695
SYL-S.1.RR.365.2 | 24535589149556 | South Surma, 1 No Mollargaon, Khanoa, Lal Mia | 2022-11-20 | MN1018 | 7.5 | 145 | 7.5 | 146 | 2022-11-20 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 0 | 1007.9997 | 9.0931
SYL-S.1.RR.366.1 | 24535589149556 | South Surma, 1 No Mollargaon, Khanoa, Lal Mia | 2019-07-28 | NQ1008 | 4.1 | 247 | 4.1 | 248 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7752 | 1007.9997 | 43.1996
SYL-S.1.RR.367.1 | 24541649149447 | Jalalabad, 8 No Khandigaon, Enatabad, Altaf Hosen | 2019-07-28 | NQ1008 | 7 | 249 | 7 | 250 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7752 | 1007.9997 | 73.7554
SYL-S.1.RR.369.1 | 24541899149373 | Jalalabad, 8 No Khandigaon, Word - 9, Paikargaon, Rashed Ahammed | 2019-07-29 | NQ1008 | 12.2 | 251 | 12.2 | 252 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7752 | 1007.9997 | 128.5451
SYL-S.1.RR.370.1 | 24542479149356 | Jalalabad, 8 No Khandigaon, Word - 9, Paikargaon, Kamrul | 2019-07-29 | NQ1008 | 11.1 | 253 | 11.1 | 254 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7752 | 1007.9997 | 116.9549
SYL-S.1.RR.371.1 | 24542549148576 | Jalalabad, 8 No Khandigaon, Word - 9, Badeali, Masuk Bazar Road, Abid | 2019-07-29 | NQ1008 | 5.1 | 255 | 5.1 | 256 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7752 | 1007.9997 | 53.7361
SYL-S.1.RR.371.2 | 24542549148576 | Jalalabad, 8 No Khandigaon, Word - 9, Badeali, Masuk Bazar Road, Abid | 2021-10-23 | LU1001 | 12.5 | 76 | 12.5 | 77 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7752 | 1007.9997 | 131.706
SYL-S.1.RR.372.1 | 24542459149029 | Jalalabad, 8 No Khandigaon, Badeali, Word - 9, Abdus Salam Chowdhury | 2019-07-29 | NQ1008 | 10.4 | 257 | 10.4 | 258 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7752 | 1007.9997 | 109.5794
SYL-S.1.RR.373.1 | 24542459149029 | Jalalabad, 8 No Khandigaon, Badeali, Word - 9, Abdur Rob | 2019-07-29 | NQ1008 | 5.4 | 259 | 5.4 | 260 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7752 | 1007.9997 | 56.897
SYL-S.1.RR.374.1 | 24542479149158 | Jalalabad, Mollahargaon, Anatapur, Fokru Islam | 2019-07-29 | NQ1008 | 6.7 | 261 | 6.7 | 262 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7752 | 1007.9997 | 70.5944
SYL-S.1.RR.375.1 | 24542479149158 | Jalalabad, Mollahargaon, Anatapur, Johirul Haque | 2019-07-29 | NQ1008 | 7.1 | 265 | 6.6 | 266 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7752 | 1007.9997 | 69.5408
SYL-S.1.RR.376.1 | 24542479149158 | Jalalabad, Mollahargaon, Anatapur, Abbuse Uddin | 2019-07-29 | NQ1008 | 10.5 | 267 | 10.5 | 268 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7752 | 1007.9997 | 110.6331
SYL-S.1.RR.377.1 | 24542479149158 | Jalalabad, Mollahargaon, Anatapur, Forid Ahammed | 2019-07-29 | NQ1008 | 9.1 | 271 | 9.1 | 272 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7752 | 1007.9997 | 95.882
SYL-S.1.RR.378.1 | 24522349148303 | South Surma, Kamal Bazar, Naobagi, jamal mia | 2019-07-30 | NQ1008 | 14.8 | 289 | 14.3 | 290 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7680 | 1079.9997 | 150.6717
SYL-S.1.RR.379.1 | 24522929148317 | South Surma, Kamal Bazar, Naobagi, Chonchal Mia | 2019-07-30 | NQ1008 | 5.3 | 291 | 5.3 | 292 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7680 | 1079.9997 | 55.8434
SYL-S.1.RR.379.2 | 24522929148317 | South Surma, Kamal Bazar, Naobagi, Chonchal Mia | 2019-07-30 | NQ1008 | 3.3 | 294 | 3.3 | 295 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7680 | 1079.9997 | 34.7704
SYL-S.1.RR.380.1 | 24524309152398 | South Surma, Kadamtoli, Word - 26, Sorner Shikha 160/B | 2019-07-30 | NQ1008 | 23.2 | 296 | 23.2 | 297 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 23.2 | 23.2 | 1.392 | 1.392 | 0.0007168 | 100% | 0% | 1.392 | 1.392 | 0.0011869 | 28 | 0.027905 | 0.027905 |  | 0 | 0 | 7512 | 1247.9997 | 244.4464
SYL-S.1.RR.381.1 | 24524309152398 | South Surma, Kadamtoli, Word - 26, Kholilur Rahaman | 2019-07-30 | NQ1008 | 1.9 | 298 | 1.9 | 299 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7512 | 1247.9997 | 20.0193
SYL-S.1.RR.382.1 | 24521129153266 | South Surma, Ward - 27, Alampur R/A, Haji Selim Ahmed | 2019-07-31 | NQ1008 | 6.6 | 332 | 6.7 | 333 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7512 | 1247.9997 | 70.5944
SYL-S.1.RR.383.1 | 24521129153266 | South Surma, Ward - 27, Alampur R/A, Abdul Mumin | 2019-07-31 | NQ1008 | 7.1 | 334 | 7.1 | 335 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7512 | 1247.9997 | 74.809
SYL-S.1.RR.384.1 | 24521069153263 | South Surma, Ward - 27, Alampur R/A, Abdul Hamid | 2019-07-31 | NQ1008 | 6.5 | 336 | 6.5 | 337 | 2022-01-01 | [9 empty] | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 | 2022-05-16 12:00 | 0 | 0
SYL-S.1.RR.385.1 | 24521069153263 | South Surma, Ward - 27, Alampur R/A, Foysal | 2019-07-31 | NQ1008 | 4.1 | 338 | 4.1 | 339 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7512 | 1247.9997 | 43.1996
SYL-S.1.RR.386.1 | 24520889153276 | South Surma, Ward - 27, Alampur R/A, Abdul Karim | 2019-07-31 | NQ1008 | 9.6 | 340 | 9.6 | 341 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7512 | 1247.9997 | 101.1502
SYL-S.1.RR.387.1 | 24520759153297 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Shekhor Kumar | 2019-07-31 | NQ1008 | 4.9 | 342 | 4.9 | 343 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7512 | 1247.9997 | 51.6288
SYL-S.1.RR.388.1 | 24520719153296 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Shudhonsho Ronjon | 2019-07-31 | NQ1008 | 11.4 | 344 | 11.4 | 345 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7512 | 1247.9997 | 120.1159
SYL-S.1.RR.388.2 | 24520719153296 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Shudhonsho Ronjon | 2019-07-31 | NQ1008 | 4 | 346 | 4 | 347 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7512 | 1247.9997 | 42.1459
SYL-S.1.RR.389.1 | 24520549153331 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Panna Dep | 2019-07-31 | NQ1008 | 3.3 | 348 | 3.3 | 349 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7512 | 1247.9997 | 34.7704
SYL-S.1.RR.390.1 | 24520739153340 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Monoj Deb | 2019-07-31 | NQ1008 | 10.3 | 350 | 10.3 | 351 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7512 | 1247.9997 | 108.5258
SYL-S.1.RR.391.1 | 24520689153354 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Sagor Dash | 2019-07-31 | NQ1008 | 8.5 | 352 | 8.5 | 353 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7512 | 1247.9997 | 89.5601
SYL-S.1.RR.392.1 | 24520659153359 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Rahman Villa | 2019-07-31 | NQ1008 | 9.1 | 354 | 9.1 | 355 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7512 | 1247.9997 | 95.882
SYL-S.1.RR.393.1 | 24520889153256 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Motiur Rahman | 2019-07-31 | NQ1008 | 4.3 | 357 | 4.3 | 358 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7512 | 1247.9997 | 45.3069
SYL-S.1.RR.394.1 | 24520989153239 | South Surma, Ward - 9, 4 No Kuchai, Monipur (Alampur), Monipur Road, Moyen Villa | 2019-07-31 | NQ1008 | 11.8 | 359 | 11.8 | 360 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7512 | 1247.9997 | 124.3305
SYL-S.1.RR.395.1 | 24520919153240 | Mugla Bazar, Word # 27, Alampur, Sohena Begum | 2019-08-01 | NQ1008 | 6 | 415 | 6 | 416 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7512 | 1247.9997 | 63.2189
SYL-S.1.RR.396.1 | 24520839153234 | Mugla Bazar, Word # 27, Alampur, Khaled Ahmed | 2019-08-01 | NQ1008 | 12 | 417 | 12 | 418 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7512 | 1247.9997 | 126.4378
SYL-S.1.RR.397.1 | 24520759153233 | Mugla Bazar, Word # 27, Alampur, Shefali | 2019-08-01 | NQ1008 | 12.2 | 419 | 12.2 | 420 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7512 | 1247.9997 | 128.5451
SYL-S.1.RR.398.1 | 24520639153229 | Mugla Bazar, Word # 27, Alampur, Shahin Ahmed | 2019-08-01 | NQ1008 | 7.6 | 421 | 7.7 | 422 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7512 | 1247.9997 | 81.1309
SYL-S.1.RR.399.1 | 24520639153229 | Mugla Bazar, Word # 27, Alampur, Asgar Ali | 2019-08-01 | NQ1008 | 12 | 423 | 12 | 424 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7512 | 1247.9997 | 126.4378
SYL-S.1.RR.400.1 | 24520449153232 | Mugla Bazar, Word # 27, Alampur, Sanu Mia | 2019-08-01 | NQ1008 | 12.9 | 425 | 12.9 | 426 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7512 | 1247.9997 | 135.9206
SYL-S.1.RR.401.1 | 24531309150092 | South Surma, Upper Hazrai, H #1 | 2019-07-27 | MN1032 | 1.5 | 201 | 1.5 | 202 | 2022-01-01 | [9 empty] | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0
SYL-S.1.RR.402.1 | 24531399150103 | South Surma, Upper Hazrai, Md Nahid | 2019-07-27 | MN1032 | 11.5 | 203 | 11.5 | 204 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7680 | 1079.9997 | 121.1695
SYL-S.1.RR.403.1 | 24532169150161 | South Surma, Mondir Khola, Hobibur Rahman | 2019-07-27 | MN1032 | 14.7 | 205 | 14.7 | 206 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7752 | 1007.9997 | 154.8863
SYL-S.1.RR.403.2 | 24532169150161 | South Surma, Mondir Khola, Hobibur Rahman | 2021-02-25 | NQ1007 | 15.3 | 225 | 15.8 | 226 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7752 | 1007.9997 | 166.4764
SYL-S.1.RR.404.1 | 24532169150161 | South Surma, Mondir Khola, Mozibur Rahman | 2019-07-27 | MN1032 | 8.6 | 207 | 7.9 | 208 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7752 | 1007.9997 | 83.2382
SYL-S.1.RR.405.1 | 24532609150133 | South Surma, Mondir Khola, khlopher, Foizur Rahman | 2019-07-27 | MN1032 | 12.1 | 209 | 12.1 | 210 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7752 | 1007.9997 | 127.4914
SYL-S.1.RR.406.1 | 24532509150124 | South Surma, Mondir Khola, khlopher, Md. Khaled Mia | 2019-07-27 | MN1032 | 9.5 | 212 | 9.5 | 213 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7752 | 1007.9997 | 100.0966
SYL-S.1.RR.407.1 | 24532689150109 | South Surma, Khaloper, Abdul Hashem | 2019-07-27 | MN1032 | 11 | 214 | 11 | 215 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7752 | 1007.9997 | 115.9013
SYL-S.1.RR.408.1 | 24532519150111 | South Surma, Khaloper, Khaloper, Imran Hossen | 2019-07-27 | MN1032 | 4.8 | 216 | 4.8 | 217 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7752 | 1007.9997 | 50.5751
SYL-S.1.RR.409.1 | 24532919150067 | South Surma, Khaloper, Khaloper, Iskandar Ali | 2019-07-27 | MN1032 | 2.3 | 218 | 2.3 | 219 | 2022-01-01 | [9 empty] | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0
SYL-S.1.RR.410.1 | 24532919150067 | South Surma, Khaloper, Khaloper, Nurul Islam | 2019-07-27 | MN1032 | 4.3 | 220 | 4.4 | 221 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7752 | 1007.9997 | 46.3605
SYL-S.1.RR.411.1 | 24533119150067 | South Surma, Khaloper, Khaloper, Kaptan Mia | 2019-07-27 | MN1032 | 5.6 | 222 | 5.6 | 223 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7752 | 1007.9997 | 59.0043
SYL-S.1.RR.412.1 | 24533389150066 | South Surma, Khaloper, Khaloper, Abdul Aziz | 2019-07-27 | MN1032 | 18.3 | 224 | 18.4 | 225 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 18.4 | 18.4 | 1.104 | 1.104 | 0.0007168 | 100% | 0% | 1.104 | 1.104 | 0.0011869 | 28 | 0.022131 | 0.022131 |  | 0 | 0 | 7752 | 1007.9997 | 193.8713
SYL-S.1.RR.413.1 | 24533409150014 | South Surma, Mollargaon, Mostofa Mia | 2019-07-27 | MN1032 | 3.9 | 226 | 3.9 | 227 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7752 | 1007.9997 | 41.0923
SYL-S.1.RR.414.1 | 24532819150021 | South Surma, Mullargaw, Md.Zakir Hossen | 2019-07-28 | MN1032 | 15.3 | 228 | 15.3 | 229 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 7752 | 1007.9997 | 161.2082
SYL-S.1.RR.415.1 | 24532679150006 | South Surma, Mullargaw, Md.Nizamuddin | 2019-07-28 | MN1032 | 13.3 | 232 | 13.3 | 233 | 2022-01-01 | [9 empty] | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0
SYL-S.1.RR.416.1 | 24533179149546 | South Surma, Mullargaw, Niazul Alam | 2019-07-28 | MN1032 | 3.9 | 235 | 3.9 | 236 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7752 | 1007.9997 | 41.0923
SYL-S.1.RR.417.1 | 24533179149546 | South Surma, Mullargaw, Abdul Musabbir | 2019-07-28 | MN1032 | 6.5 | 237 | 6.5 | 238 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7752 | 1007.9997 | 68.4871
SYL-S.1.RR.418.1 | 24533039149537 | South Surma, Mullargaw, Dr.Gaus | 2019-07-28 | MN1032 | 9.2 | 239 | 9.2 | 240 | 2022-01-01 | [9 empty] | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0
SYL-S.1.RR.419.1 | 24532869149592 | South Surma, Mullargaw, Salim Ahmed | 2019-07-28 | MN1032 | 16.3 | 241 | 15.7 | 242 | 2022-01-01 | [9 empty] | 15.7 | 15.7 | 0.942 | 0.942 | 0.0007168 | 100% | 0% | 0.942 | 0.942 | 0.0011869 | 28 | 0.018884 | 0.018884 |  | 0 | 0
SYL-S.1.RR.420.1 | 24533019149582 | South Surma, Mullargaw, Md.Paplu | 2019-07-28 | MN1032 | 5.2 | 243 | 5.2 | 244 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7752 | 1007.9997 | 54.7897
SYL-S.1.RR.421.1 | 24533019149582 | South Surma, Mullargaw, Bokul | 2019-07-28 | MN1032 | 3.1 | 245 | 3.1 | 246 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7752 | 1007.9997 | 32.6631
SYL-S.1.RR.422.1 | 24530399149183 | South Surma, Chonupara, Chonupara Road, Hazi Huru Mia | 2019-07-29 | MN1032 | 7.8 | 280 | 7.8 | 281 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7680 | 1079.9997 | 82.1846
SYL-S.1.RR.423.1 | 24532109149177 | South Surma, Chonupara, Chonupara Road, Dr.Bari, Sirazul Islam | 2019-07-29 | MN1032 | 3.9 | 283 | 3.9 | 284 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7680 | 1079.9997 | 41.0923
SYL-S.1.RR.424.1 | 24532099149229 | South Surma, Chonupara, Chonupara Road, Md.Dolil | 2019-07-29 | MN1032 | 4.1 | 285 | 4.1 | 286 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7680 | 1079.9997 | 43.1996
SYL-S.1.RR.424.2 | 24532099149229 | South Surma, Chonupara, Chonupara Road, Md.Dolil | 2021-03-03 | NQ1007 | 9 | 247 | 9 | 248 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7680 | 1079.9997 | 94.8283
SYL-S.1.RR.425.1 | 24532099149229 | South Surma, Chonupara, Chonupara Road, Sumon Ali | 2019-07-29 | MN1032 | 6.7 | 289 | 6.8 | 290 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7680 | 1079.9997 | 71.6481
SYL-S.1.RR.426.1 | 24532379149139 | South Surma, Chonupara, Chonupara Road, Aminul Islam | 2019-07-29 | MN1032 | 6.2 | 291 | 6.2 | 292 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7680 | 1079.9997 | 65.3262
SYL-S.1.RR.427.1 | 24521999153039 | South Surma, Kodomtoli, Gotatikor, Block-B, Road # 3, H # 8/9, Saro Mia | 2019-07-30 | MN1032 | 11.5 | 303 | 11.5 | 304 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7512 | 1247.9997 | 121.1695
SYL-S.1.RR.428.1 | 24522029153058 | South Surma, Kodomtoli, Gotatikor, Block-B, Road # 3, H # 27, Rowson Ali | 2019-07-30 | MN1032 | 10.5 | 305 | 10.5 | 306 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7512 | 1247.9997 | 110.6331
SYL-S.1.RR.429.1 | 24521909153039 | South Surma, Kodomtoli, Gotatikor, Block-B, Road # 3, Afsar Mia | 2019-07-30 | MN1032 | 7.6 | 307 | 7.6 | 308 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7512 | 1247.9997 | 80.0773
SYL-S.1.RR.430.1 | 24521679152578 | South Surma, Kodomtoli, Gotatikor, Block-B, Shahjahan | 2019-07-30 | MN1032 | 11.6 | 309 | 11.6 | 310 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7512 | 1247.9997 | 122.2232
SYL-S.1.RR.431.1 | 24522069153440 | South Surma, Kodomtoli, Habinondi, Babul Ahmed | 2019-07-31 | MN1032 | 9.6 | 333 | 9.6 | 334 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7488 | 1271.9997 | 101.1502
SYL-S.1.RR.432.1 | 24522069153440 | South Surma, Kodomtoli, Habinondi, Abdul Kadir Rana | 2019-07-31 | MN1032 | 11.3 | 335 | 11.3 | 336 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7488 | 1271.9997 | 119.0622
SYL-S.1.RR.433.1 | 24520899153505 | South Surma, Kodomtoli, Ganganagar, Shamal Hasan, Belal Ahmed | 2019-07-31 | MN1032 | 4 | 337 | 4 | 338 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7488 | 1271.9997 | 42.1459
SYL-S.1.RR.434.1 | 24520899153505 | South Surma, Kodomtoli, Ganganagar, Shamal Hasan, Alauddin | 2019-07-31 | MN1032 | 4.9 | 339 | 4.9 | 340 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 1080 | 0 | 6408 | 1271.9997 | 45.2636
SYL-S.1.RR.434.2 | 24520899153505 | South Surma, Kodomtoli, Ganganagar, Shamal Hasan, Alauddin | 2022-05-28 | NQ1007 | 6.1 | 188 | 6.1 | 189 | 2022-05-28 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 3960 | 1271.9997 | 38.3874
SYL-S.1.RR.435.1 | 24520899153505 | South Surma, Kodomtoli, Ganganagar, Shamal Hasan, Rofiq Mia | 2019-07-31 | MN1032 | 8.9 | 341 | 8.9 | 342 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7488 | 1271.9997 | 93.7747
SYL-S.1.RR.436.1 | 24521009153451 | South Surma, Kodomtoli, Ganganagar, Shamal Hasan, Khalik Mia | 2019-07-31 | MN1032 | 11.2 | 343 | 11.2 | 344 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7488 | 1271.9997 | 118.0086
SYL-S.1.RR.437.1 | 24521009153451 | South Surma, Kodomtoli, Ganganagar, Shamal Hasan, Harun Mia | 2019-07-31 | MN1032 | 12 | 345 | 12.1 | 346 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7488 | 1271.9997 | 127.4914
SYL-S.1.RR.438.1 | 24520839153449 | South Surma, Kodomtoli, Ganganagar, Shamal Hasan, Fridge Ali | 2019-07-31 | MN1032 | 8.6 | 347 | 8.4 | 348 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7488 | 1271.9997 | 88.5064
SYL-S.1.RR.439.1 | 24520829154339 | South Surma, Kodomtoli, Kuchai, Middle Para, Md.Tunu Mia | 2019-08-01 | MN1032 | 8.9 | 349 | 8.9 | 350 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7488 | 1271.9997 | 93.7747
SYL-S.1.RR.440.1 | 24520489154332 | South Surma, Kodomtoli, Kuchai, Middle Para, Nesar Ali | 2019-08-01 | MN1032 | 11.2 | 351 | 10.8 | 352 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7488 | 1271.9997 | 113.794
SYL-S.1.RR.441.1 | 24520199154329 | South Surma, Kodomtoli, Kuchai, Middle Para, Akram Ali | 2019-08-01 | MN1032 | 10.5 | 353 | 10.5 | 354 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7488 | 1271.9997 | 110.6331
SYL-S.1.RR.442.1 | 24515779154332 | South Surma, Kodomtoli, Kuchai, Middle Para, Abdul Goffor | 2019-08-01 | MN1032 | 5.4 | 355 | 5.4 | 356 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7488 | 1271.9997 | 56.897
SYL-S.1.RR.443.1 | 24515779154332 | South Surma, Kodomtoli, Kuchai, Middle Para, Abdul Malik | 2019-08-01 | MN1032 | 14 | 357 | 13.2 | 358 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7488 | 1271.9997 | 139.0816
SYL-S.1.RR.444.1 | 24513529154424 | South Surma, Kodomtoli, Kuchai, Poschim Para, Abul Hossen | 2019-08-01 | MN1032 | 11.2 | 363 | 11.2 | 364 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7488 | 1271.9997 | 118.0086
SYL-S.1.RR.445.1 | 24513529154424 | South Surma, Kodomtoli, Kuchai, Poschim Para, Hira Mia | 2019-08-01 | MN1032 | 5.4 | 365 | 5.4 | 366 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7488 | 1271.9997 | 56.897
SYL-S.1.RR.445.2 | 24513529154424 | South Surma, Kodomtoli, Kuchai, Poschim Para, Hira Mia | 2021-10-11 | LU1001 | 14.6 | 49 | 14.6 | 50 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7488 | 1271.9997 | 153.8326
SYL-S.1.RR.446.1 | 24513919154428 | South Surma, Kodomtoli, Kuchai, Poschim Para, Masuk Mia | 2019-08-01 | MN1032 | 9.4 | 367 | 9.4 | 368 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7488 | 1271.9997 | 99.0429
SYL-S.1.RR.447.1 | 24513909154509 | South Surma, Kodomtoli, Kuchai, Poschimbagh, Shafiqul Haque | 2019-08-01 | MN1032 | 10.9 | 369 | 10.9 | 370 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7488 | 1271.9997 | 114.8476
SYL-S.1.RR.448.1 | 24513909154509 | South Surma, Kodomtoli, Kuchai, Poschimbagh, Hazi Iqbal Ahmed | 2019-08-01 | MN1032 | 11.5 | 371 | 11.5 | 372 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7488 | 1271.9997 | 121.1695
SYL-S.1.RR.449.1 | 24513989154594 | South Surma, Kuchai, Sultanpur, Hazi Gulzar Ahmed | 2019-08-01 | MN1032 | 4 | 373 | 4.1 | 374 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7488 | 1271.9997 | 43.1996
SYL-S.1.RR.449.2 | 24513989154594 | South Surma, Kuchai, Sultanpur, Hazi Gulzar Ahmed | 2021-03-01 | LX1011 | 5.7 | 167 | 5.7 | 168 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7488 | 1271.9997 | 60.0579
SYL-S.1.RR.450.1 | 24513989154594 | South Surma, Kuchai, Sultanpur, Hazi Gulzar Ahmed | 2019-08-01 | MN1032 | 9.9 | 375 | 9.9 | 376 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7488 | 1271.9997 | 104.3112
SYL-S.1.RR.451.1 | 24533149149587 | Sylhet, Borobari, Mollargao, Buli Khatun | 2019-07-28 | MN1032 | 5.3 | 247 | 5.3 | 248 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7752 | 1007.9997 | 55.8434
SYL-S.1.RR.452.1 | 24533079149552 | Sylhet, Borobari, Mollargao, Muktar Ali | 2019-07-28 | MN1032 | 7.8 | 249 | 7.8 | 250 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7752 | 1007.9997 | 82.1846
SYL-S.1.RR.453.1 | 24533259149585 | Sylhet, Borobari, Mollargao, Suruz Mia | 2019-07-28 | MN1032 | 8.6 | 251 | 8.6 | 252 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7752 | 1007.9997 | 90.6137
SYL-S.1.RR.454.1 | 24533259149585 | Sylhet, Borobari, Mollargao, Shamim | 2019-07-28 | MN1032 | 7.7 | 253 | 7.7 | 254 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7752 | 1007.9997 | 81.1309
SYL-S.1.RR.455.1 | 24533069149504 | Sylhet, Mollargao, Md.Toyeb Ali | 2019-07-28 | MN1032 | 8.1 | 255 | 8.1 | 256 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7752 | 1007.9997 | 85.3455
SYL-S.1.RR.456.1 | 24533239149493 | Sylhet, Mollargao, Lokman/Makhon | 2019-07-28 | MN1032 | 3.8 | 257 | 3.8 | 258 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7752 | 1007.9997 | 40.0386
SYL-S.1.RR.457.1 | 24533649149522 | Sylhet, Mollargao, West Hati Rd, Moklom | 2019-07-28 | MN1032 | 5.6 | 259 | 5.6 | 260 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7752 | 1007.9997 | 59.0043
SYL-S.1.RR.458.1 | 24533799149539 | Sylhet, Mollargao, West Hati Rd, Enam | 2019-07-28 | MN1032 | 5.7 | 261 | 5.7 | 262 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7752 | 1007.9997 | 60.0579
SYL-S.1.RR.459.1 | 24533909149528 | Sylhet, Mollargao, West Hati Rd, Gias uddin | 2019-07-28 | MN1032 | 8.5 | 263 | 8.5 | 264 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7752 | 1007.9997 | 89.5601
SYL-S.1.RR.460.1 | 24532749149519 | Sylhet, Mollargao, Kabir Ahmed | 2019-07-28 | MN1032 | 12.7 | 265 | 12.7 | 266 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7752 | 1007.9997 | 133.8133
SYL-S.1.RR.461.1 | 24532769149512 | Sylhet, Mollargao, Anowar | 2019-07-29 | MN1032 | 9.9 | 267 | 9.9 | 268 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7752 | 1007.9997 | 104.3112
SYL-S.1.RR.461.2 | 24532769149512 | Sylhet, Mollargao, Anowar | 2021-02-25 | NQ1007 | 4.9 | 229 | 4.9 | 230 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7752 | 1007.9997 | 51.6288
SYL-S.1.RR.462.1 | 24532769149512 | Sylhet, Mollargao, Shofique | 2019-07-29 | MN1032 | 12.8 | 269 | 12.8 | 270 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7752 | 1007.9997 | 134.867
SYL-S.1.RR.463.1 | 24541699149179 | Sylhet, Anontopur, Jahangir Mia | 2019-07-29 | MN1032 | 16.7 | 271 | 16.7 | 272 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 7752 | 1007.9997 | 175.9592
SYL-S.1.RR.464.1 | 24541459149175 | Sylhet, Anontopur, Ward # 9, Lukman | 2019-07-29 | MN1032 | 3.1 | 273 | 3.1 | 274 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7752 | 1007.9997 | 32.6631
SYL-S.1.RR.465.1 | 24541429149176 | Sylhet, Anontopur, Ward # 9, Iskondor Ali | 2019-07-29 | MN1032 | 6.5 | 275 | 6.5 | 276 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7752 | 1007.9997 | 68.4871
SYL-S.1.RR.466.1 | 24541429149176 | Sylhet, Anontopur, Ward # 9, Kholil Mia | 2019-07-29 | MN1032 | 12.1 | 277 | 12.1 | 278 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7752 | 1007.9997 | 127.4914
SYL-S.1.RR.467.1 | 24523409148260 | South Surma, Kamal Bazar, Novag, Beside Asha Branch, Dobir Mia | 2019-07-30 | MN1032 | 5 | 293 | 5 | 294 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7680 | 1079.9997 | 52.6824
SYL-S.1.RR.468.1 | 24522369148179 | South Surma, Ragib Nagar, Afros | 2019-07-30 | MN1032 | 5.4 | 295 | 5.4 | 296 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7680 | 1079.9997 | 56.897
SYL-S.1.RR.469.1 | 24523379152552 | Sylhet, Kadamtali, Block-B, H # 15 | 2019-07-30 | MN1032 | 10.2 | 297 | 10.2 | 298 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7512 | 1247.9997 | 107.4721
SYL-S.1.RR.470.1 | 24523379152552 | Sylhet, Kadamtali, Block-B, H # 15 | 2019-07-30 | MN1032 | 3.5 | 301 | 3.5 | 302 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7512 | 1247.9997 | 36.8777
SYL-S.1.RR.471.1 | 24520889153133 | Sylhet, Gotatikor Purbo Para, Habibur | 2019-07-31 | MN1032 | 7.8 | 311 | 7.7 | 312 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7512 | 1247.9997 | 81.1309
SYL-S.1.RR.472.1 | 24520889153133 | Sylhet, Gotatikor Purbo Para, Alal Mia | 2019-07-31 | MN1032 | 9.2 | 313 | 9.2 | 314 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7512 | 1247.9997 | 96.9356
SYL-S.1.RR.473.1 | 24520819153139 | Sylhet, Gotatikor Purbo Para, Ekbal Mia | 2019-07-31 | MN1032 | 6.8 | 315 | 6.8 | 316 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7512 | 1247.9997 | 71.6481
SYL-S.1.RR.474.1 | 24520779153140 | Sylhet, Gotatikor Purbo Para, Akbor Ali | 2019-07-31 | MN1032 | 11.2 | 317 | 11.3 | 318 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7512 | 1247.9997 | 119.0622
SYL-S.1.RR.475.1 | 24520739153136 | Sylhet, Gotatikor Purbo Para, Forid Mia | 2019-07-31 | MN1032 | 10.9 | 323 | 10.5 | 324 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7512 | 1247.9997 | 110.6331
SYL-S.1.RR.476.1 | 24520689153137 | Sylhet, Gotatikor Purbo Para, Johura | 2019-07-31 | MN1032 | 6 | 325 | 6.2 | 326 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7512 | 1247.9997 | 65.3262
SYL-S.1.RR.477.1 | 24522159153444 | Sylhet, Hobinondi, Ward # 27, Ostar | 2019-07-31 | MN1032 | 16.3 | 327 | 16.3 | 328 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 7488 | 1271.9997 | 171.7446
SYL-S.1.RR.477.2 | 24522159153444 | Sylhet, Hobinondi, Ward # 27, Ostar | 2021-02-24 | LX1011 | 4 | 157 | 4 | 158 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7488 | 1271.9997 | 42.1459
SYL-S.1.RR.478.1 | 24522159153444 | Sylhet, Hobinondi, Ward # 27, Manik Mia | 2019-07-31 | MN1032 | 12.4 | 329 | 12.4 | 330 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7488 | 1271.9997 | 130.6524
SYL-S.1.RR.479.1 | 24522159153444 | Sylhet, Hobinondi, Ward # 27, Chand Mia | 2019-07-31 | MN1032 | 10.7 | 331 | 10.7 | 332 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7488 | 1271.9997 | 112.7403
SYL-S.1.RR.480.1 | 24512479155509 | Sylhet, Panch Mile, Boraya Uttarbugh, Koichor Vila | 2019-08-03 | MN1032 | 11 | 405 | 10.8 | 406 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7464 | 1295.9997 | 113.794
SYL-S.1.RR.481.1 | 24514009155494 | Sylhet, Panch Mile, Boraya Uttarbugh, Kamal Mia | 2019-08-03 | MN1032 | 13.8 | 407 | 13.8 | 408 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7464 | 1295.9997 | 145.4034
SYL-S.1.RR.482.1 | 24514009155494 | Sylhet, Panch Mile, Boraya Uttarbugh, Sayesta Mia | 2019-08-03 | MN1032 | 12.5 | 409 | 12.6 | 410 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7464 | 1295.9997 | 132.7597
SYL-S.1.RR.483.1 | 24514009155494 | Sylhet, Panch Mile, Boraya Uttarbugh, Abdul Malik | 2019-08-03 | MN1032 | 6.1 | 413 | 6.1 | 414 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7464 | 1295.9997 | 64.2725
SYL-S.1.RR.484.1 | 24514009155494 | Sylhet, Panch Mile, Boraya Uttarbugh, Abdur Rashid | 2019-08-03 | MN1032 | 8.4 | 415 | 8.4 | 416 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7464 | 1295.9997 | 88.5064
SYL-S.1.RR.484.2 | 24514009155494 | Sylhet, Panch Mile, Boraya Uttarbugh, Abdur Rashid | 2021-02-25 | MN1032 | 8.6 | 192 | 8.6 | 193 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7464 | 1295.9997 | 90.6137
SYL-S.1.RR.485.1 | 24512289155543 | Sylhet, Panch Mile, Boraya Uttarbugh, Md. Alauddin | 2019-08-03 | MN1032 | 3.6 | 417 | 3.6 | 418 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7464 | 1295.9997 | 37.9313
SYL-S.1.RR.486.1 | 24512289155553 | Sylhet, Panch Mile, Boraya Uttarbugh, Lutfor Rahman | 2019-08-03 | MN1032 | 4.2 | 419 | 4.2 | 420 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7464 | 1295.9997 | 44.2532
SYL-S.1.RR.487.1 | 24512259156039 | Sylhet, Panch Mile, Boraya Uttarbugh, Babul | 2019-08-03 | MN1032 | 3.8 | 421 | 3.8 | 422 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-S.1.RR.488.1 | 24512719156121 | Sylhet, Bagarkhala, Fokrul Islam | 2019-08-04 | MN1032 | 7.7 | 423 | 7.7 | 424 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7464 | 1295.9997 | 81.1309
SYL-S.1.RR.489.1 | 24512719156121 | Sylhet, Bagarkhala, Abdul Koyes | 2019-08-04 | MN1032 | 6 | 425 | 6 | 426 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7464 | 1295.9997 | 63.2189
SYL-S.1.RR.490.1 | 24512879156117 | Sylhet, Bagarkhala, Abdul Malik | 2019-08-04 | MN1032 | 6.2 | 427 | 6.2 | 428 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7464 | 1295.9997 | 65.3262
SYL-S.1.RR.491.1 | 24512779156067 | Sylhet, Bagarkhala, Momota Khatun | 2019-08-04 | MN1032 | 9.5 | 429 | 9.5 | 430 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7464 | 1295.9997 | 100.0966
SYL-S.1.RR.492.1 | 24512669156061 | Sylhet, Bagarkhala, Shahid Mia | 2019-08-04 | MN1032 | 4.3 | 431 | 4.3 | 432 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7464 | 1295.9997 | 45.3069
SYL-S.1.RR.493.1 | 24512669156061 | Sylhet, Bagarkhala, Hazi Chand Mia | 2019-08-04 | MN1032 | 5.3 | 433 | 5.3 | 434 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7464 | 1295.9997 | 55.8434
SYL-S.1.RR.494.1 | 24512589156073 | Sylhet, Bagarkhala, Romiz Uddin | 2019-08-04 | MN1032 | 3.5 | 435 | 3.5 | 436 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7464 | 1295.9997 | 36.8777
SYL-S.1.RR.495.1 | 24504929159425 | Golapganj, Phulbari South Para, Jiauddin | 2019-08-05 | MN1032 | 10.2 | 462 | 10.2 | 463 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7440 | 1319.9997 | 107.4721
SYL-S.1.RR.496.1 | 24504969159414 | Golapganj, Phulbari South Para, Helal | 2019-08-05 | MN1032 | 10.4 | 464 | 10.4 | 465 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7440 | 1319.9997 | 109.5794
SYL-S.1.RR.497.1 | 24505289159375 | Golapganj, Phulbari South Para, Aftab Ali | 2019-08-05 | MN1032 | 4.1 | 466 | 4.1 | 467 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7440 | 1319.9997 | 43.1996
SYL-S.1.RR.498.1 | 24505239159342 | Golapganj, Phulbari South Para, Makmuda | 2019-08-05 | MN1032 | 7.3 | 468 | 7.3 | 469 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7440 | 1319.9997 | 76.9163
SYL-S.1.RR.498.2 | 24505239159342 | Golapganj, Phulbari South Para, Makmuda | 2020-10-28 | MP1006 | 15.1 | 112 | 15.1 | 113 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7440 | 1319.9997 | 159.1009
SYL-S.1.RR.499.1 | 24505239159342 | Golapganj, Phulbari South Para, Sadeka | 2019-08-05 | MN1032 | 11.4 | 470 | 11.2 | 471 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7440 | 1319.9997 | 118.0086
SYL-S.1.RR.500.1 | 24505239159342 | Golapganj, Phulbari South Para, Sorafot | 2019-08-05 | MN1032 | 6.2 | 472 | 6.2 | 473 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7440 | 1319.9997 | 65.3262
SYL-S.1.RR.500.2 | 24505239159342 | Golapganj, Phulbari South Para, Sorafot | 2020-10-28 | MP1006 | 1.2 | 110 | 1.2 | 111 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7440 | 1319.9997 | 12.6438
SYL-S.1.RR.501.1 | 24533219150124 | South Surma, Khalopar, Enamul Islam | 2019-07-28 | NQ1011 | 5.8 | 250 | 5.8 | 251 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7752 | 1007.9997 | 61.1116
SYL-S.1.RR.502.1 | 24533179150095 | South Surma, Khalopar (Kittha), Md. Shofiq Mia | 2019-07-28 | NQ1011 | 6.4 | 252 | 6.4 | 253 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7752 | 1007.9997 | 67.4335
SYL-S.1.RR.503.1 | 24531919150211 | South Surma, Mondir Khola, Habiba Monjil, Eahsanul Haque | 2019-07-28 | NQ1011 | 4.8 | 254 | 4.8 | 255 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7752 | 1007.9997 | 50.5751
SYL-S.1.RR.504.1 | 24531919150211 | South Surma, Mondir Khola, Nasir Ahmed | 2019-07-28 | NQ1011 | 2.6 | 258 | 2.6 | 259 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7752 | 1007.9997 | 27.3949
SYL-S.1.RR.505.1 | 24531899150223 | South Surma, Mondir Khola, Khairul Islam | 2019-07-28 | NQ1011 | 3 | 260 | 3 | 261 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7752 | 1007.9997 | 31.6094
SYL-S.1.RR.506.1 | 24531659150243 | South Surma, Mondir Khola, Abdul Ali | 2019-07-28 | NQ1011 | 6 | 262 | 6 | 263 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7752 | 1007.9997 | 63.2189
SYL-S.1.RR.507.1 | 24531619150242 | South Surma, Mondir Khola, Jomir Ali | 2019-07-28 | NQ1011 | 3.4 | 264 | 3.4 | 265 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7752 | 1007.9997 | 35.824
SYL-S.1.RR.508.1 | 24531619150242 | South Surma, Mondir Khola, Obed Ali | 2019-07-28 | NQ1011 | 2.8 | 268 | 2.8 | 269 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7752 | 1007.9997 | 29.5021
SYL-S.1.RR.509.1 | 24531649150221 | South Surma, Mondir Khola, Abdul Mojid Khan | 2019-07-28 | NQ1011 | 7 | 272 | 6.5 | 273 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7752 | 1007.9997 | 68.4871
SYL-S.1.RR.510.1 | 24531649150221 | South Surma, Mondir Khola, Abdul Motin Khan | 2019-07-28 | NQ1011 | 3.6 | 276 | 3.6 | 277 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7752 | 1007.9997 | 37.9313
SYL-S.1.RR.511.1 | 24524379148429 | South Surma, Mollargaon, Soyedpur, Abdul Ali | 2019-07-29 | NQ1011 | 10 | 317 | 10.5 | 318 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7680 | 1079.9997 | 110.6331
SYL-S.1.RR.512.1 | 24530999148271 | South Surma, Kamal Bazar, Purangaon, Khorshed Ali | 2019-07-29 | NQ1011 | 7.7 | 319 | 8.2 | 320 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7680 | 1079.9997 | 86.3991
SYL-S.1.RR.513.1 | 24530999148271 | South Surma, Kamal Bazar, Purangaon, Sonapor Ali | 2019-07-29 | NQ1011 | 7.9 | 321 | 7.9 | 322 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7680 | 1079.9997 | 83.2382
SYL-S.1.RR.514.1 | 24530999148271 | South Surma, Kamal Bazar, Purangaon, Abdul Aziz | 2019-07-29 | NQ1011 | 8.3 | 323 | 8.6 | 324 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7680 | 1079.9997 | 90.6137
SYL-S.1.RR.515.1 | 24530999148271 | South Surma, Kamal Bazar, Purangaon, Sonaban Begum | 2019-07-29 | NQ1011 | 9.8 | 325 | 9.8 | 326 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7680 | 1079.9997 | 103.2575
SYL-S.1.RR.516.1 | 24532219148320 | South Surma, Kamal Bazar, Purangaon, Sonu Mia | 2019-07-29 | NQ1011 | 10.7 | 327 | 10.7 | 328 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7680 | 1079.9997 | 112.7403
SYL-S.1.RR.517.1 | 24532219148320 | South Surma, Kamal Bazar, Purangaon, Forid Ali | 2019-07-29 | NQ1011 | 5.3 | 329 | 5.3 | 330 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7680 | 1079.9997 | 55.8434
SYL-S.1.RR.518.1 | 24522439153121 | South Surma, Gotatikor R/A, Rd# 3, Block- B, Mokhles | 2019-07-30 | NQ1011 | 5.1 | 339 | 5.2 | 340 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7512 | 1247.9997 | 54.7897
SYL-S.1.RR.519.1 | 24522439153121 | South Surma, Gotatikor R/A, Rd# 3, Block- B, H# 50 | 2019-07-30 | NQ1011 | 4.8 | 343 | 4.8 | 344 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7512 | 1247.9997 | 50.5751
SYL-S.1.RR.520.1 | 24522339153111 | South Surma, Gotatikor R/A, Rd# 3, Block- B, Deb Bari | 2019-07-30 | NQ1011 | 4.7 | 345 | 4.7 | 346 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7512 | 1247.9997 | 49.5215
SYL-S.1.RR.521.1 | 24522039153092 | South Surma, Gotatikor R/A, Rd# 3, Block- B, Nasir | 2019-07-30 | NQ1011 | 9 | 347 | 9 | 348 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7512 | 1247.9997 | 94.8283
SYL-S.1.RR.522.1 | 24522539153179 | South Surma, BSCIC Shilponogori, Gotatikor, Hiron Mia | 2019-07-30 | NQ1011 | 3.3 | 349 | 3.3 | 350 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7512 | 1247.9997 | 34.7704
SYL-S.1.RR.523.1 | 24522399153179 | South Surma, BSCIC Shilponogori, Gotatikor, Sonu Mia | 2019-07-30 | NQ1011 | 6.7 | 351 | 6.7 | 352 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7512 | 1247.9997 | 70.5944
SYL-S.1.RR.524.1 | 24521729153220 | Alampur R/A, Ward# 27, Kazi Salauddin | 2019-07-30 | NQ1011 | 4.9 | 353 | 4.9 | 354 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7512 | 1247.9997 | 51.6288
SYL-S.1.RR.525.1 | 24521329154021 | Sylhet, Palpur R/A, Jamil Ahmed | 2019-07-31 | NQ1011 | 6.2 | 381 | 6.2 | 382 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7488 | 1271.9997 | 65.3262
SYL-S.1.RR.526.1 | 24521329154021 | Sylhet, Palpur R/A, Manna Ahmed | 2019-07-31 | NQ1011 | 9.7 | 383 | 9.7 | 384 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7488 | 1271.9997 | 102.2039
SYL-S.1.RR.527.1 | 24521979154024 | Sylhet, Palpur R/A, Akhtarujjaman | 2019-07-31 | NQ1011 | 8.8 | 385 | 8.8 | 386 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7488 | 1271.9997 | 92.721
SYL-S.1.RR.528.1 | 24521689154028 | Sylhet, Palpur R/A, Munnujan Begum | 2019-07-31 | NQ1011 | 11.7 | 387 | 11.6 | 388 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7488 | 1271.9997 | 122.2232
SYL-S.1.RR.529.1 | 24521559154284 | Sylhet, Kuchai R/A, Tota Mia | 2019-07-31 | NQ1011 | 6.3 | 389 | 6.4 | 390 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7488 | 1271.9997 | 67.4335
SYL-S.1.RR.530.1 | 24521459154269 | Sylhet, Kuchai R/A, Noyon Mia | 2019-07-31 | NQ1011 | 6.4 | 391 | 6.6 | 392 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7488 | 1271.9997 | 69.5408
SYL-S.1.RR.531.1 | 24521459154269 | Sylhet, Kuchai R/A, Shafiq Mia | 2019-07-31 | NQ1011 | 3.9 | 393 | 3.9 | 394 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7488 | 1271.9997 | 41.0923
SYL-S.1.RR.532.1 | 24521459154269 | Sylhet, Kuchai R/A, Rafiq Mia | 2019-07-31 | NQ1011 | 12.5 | 395 | 12.5 | 396 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7488 | 1271.9997 | 131.706
SYL-S.1.RR.532.2 | 24521459154269 | Sylhet, Kuchai R/A, Rafiq Mia | 2021-03-01 | MN1018 | 10.1 | 181 | 10.1 | 182 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7488 | 1271.9997 | 106.4185
SYL-S.1.RR.533.1 | 24521459154269 | Sylhet, Kuchai Rin/A, Alauddin | 2019-07-31 | NQ1011 | 10.4 | 397 | 10.4 | 398 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7488 | 1271.9997 | 109.5794
SYL-S.1.RR.534.1 | 24512959155283 | South Surma, Sreerampur, Giasuddin Ahmed | 2019-08-01 | NQ1011 | 7.1 | 422 | 7.1 | 423 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7464 | 1295.9997 | 74.809
SYL-S.1.RR.535.1 | 24512919155312 | South Surma, Sreerampur, Alamgir | 2019-08-01 | NQ1011 | 7.5 | 426 | 7.5 | 427 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7464 | 1295.9997 | 79.0236
SYL-S.1.RR.535.2 | 24512919155312 | South Surma, Sreerampur, Alamgir | 2021-03-03 | LX1011 | 15 | 173 | 15 | 174 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 7464 | 1295.9997 | 158.0472
SYL-S.1.RR.536.1 | 24512599155296 | South Surma, Sreerampur, Milon Ahmed | 2019-08-01 | NQ1011 | 5 | 428 | 5 | 429 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7464 | 1295.9997 | 52.6824
SYL-S.1.RR.537.1 | 24512439155294 | South Surma, Sreerampur, Golam Akbar Villa | 2019-08-01 | NQ1011 | 7.9 | 430 | 7.8 | 431 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 2904 | 0 | 4560 | 1295.9997 | 54.9398
SYL-S.1.RR.538.1 | 24512229155286 | South Surma, Sreerampur, Habibur Rahman | 2019-08-01 | NQ1011 | 4.2 | 432 | 4.5 | 433 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7464 | 1295.9997 | 47.4142
SYL-S.1.RR.539.1 | 24512229155286 | South Surma, Sreerampur, Seraj Uddin | 2019-08-01 | NQ1011 | 11.3 | 434 | 11.3 | 435 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7464 | 1295.9997 | 119.0622
SYL-S.1.RR.540.1 | 24512229155286 | South Surma, Sreerampur, Abdul Malek | 2019-08-01 | NQ1011 | 8.9 | 436 | 8.9 | 437 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7464 | 1295.9997 | 93.7747
SYL-S.1.RR.541.1 | 24512199155278 | South Surma, Sreerampur, Chunu Mia | 2019-08-01 | NQ1011 | 14.2 | 438 | 13.6 | 439 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7464 | 1295.9997 | 143.2961
SYL-S.1.RR.542.1 | 24511969155317 | South Surma, Sreerampur, Abul Kalam Monsur | 2019-08-01 | NQ1011 | 13.4 | 440 | 13.4 | 441 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7464 | 1295.9997 | 141.1888
SYL-S.1.RR.542.2 | 24511969155317 | South Surma, Sreerampur, Abul Kalam Monsur | 2021-10-12 | LU1001 | 6.8 | 55 | 6.8 | 56 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7464 | 1295.9997 | 71.6481
SYL-S.1.RR.543.1 | 24511909155320 | South Surma, Sreerampur, Abdul Kuddus | 2019-08-01 | NQ1011 | 7.3 | 442 | 7.3 | 443 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7464 | 1295.9997 | 76.9163
SYL-S.1.RR.544.1 | 24511769155316 | South Surma, Sreerampur, Abdur Rahman Ana Mia | 2019-08-01 | NQ1011 | 4.1 | 444 | 4.1 | 445 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7464 | 1295.9997 | 43.1996
SYL-S.1.RR.545.1 | 24511449155286 | South Surma, Sreerampur, Abdul Jalil | 2019-08-01 | NQ1011 | 9.5 | 446 | 9.5 | 447 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7464 | 1295.9997 | 100.0966
SYL-S.1.RR.546.1 | 24511969155265 | South Surma, Sreerampur, Abdul Gaffar | 2019-08-01 | NQ1011 | 9.5 | 448 | 9.5 | 449 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7464 | 1295.9997 | 100.0966
SYL-S.1.RR.547.1 | 24511449155286 | South Surma, Sreerampur, Moynul Islam | 2019-08-01 | NQ1011 | 2.9 | 452 | 2.9 | 453 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7464 | 1295.9997 | 30.5558
SYL-S.1.RR.548.1 | 24511969155265 | South Surma, Sreerampur, Bazlur Rashid | 2019-08-01 | NQ1011 | 8.7 | 454 | 8.7 | 455 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7464 | 1295.9997 | 91.6674
SYL-S.1.RR.549.1 | 24511969155265 | South Surma, Sreerampur, Nejam Uddin | 2019-08-01 | NQ1011 | 1.3 | 458 | 1.3 | 459 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7464 | 1295.9997 | 13.6974
SYL-S.1.RR.550.1 | 24511969155265 | South Surma, Sreerampur, Ataur Rahman | 2019-08-01 | NQ1011 | 2 | 460 | 2 | 461 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7464 | 1295.9997 | 21.073
SYL-S.1.RR.551.1 | 24510549150423 | Sylhet, South Boldi, Banershorpur Road, Motaher Ali | 2019-07-27 | NQ1011 | 14 | 222 | 14 | 223 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14 | 14 | 0.84 | 0.84 | 0.0007168 | 100% | 0% | 0.84 | 0.84 | 0.0011869 | 28 | 0.016839 | 0.016839 |  | 0 | 0 | 7632 | 1127.9997 | 147.5107
SYL-S.1.RR.552.1 | 24510559150408 | Sylhet, South Boldi, Banershorpur Road, Nurun Nesa | 2019-07-27 | NQ1011 | 3.3 | 224 | 3.3 | 225 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7632 | 1127.9997 | 34.7704
SYL-S.1.RR.553.1 | 24510299150263 | Sylhet, South Shurma, Banershorpur, Abdus Salam Master | 2019-07-27 | NQ1011 | 4 | 226 | 4 | 227 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7632 | 1127.9997 | 42.1459
SYL-S.1.RR.554.1 | 24520069152272 | Sylhet, Shib Bari, Jonepur Road, Kazi Villa | 2019-07-27 | NQ1011 | 2 | 228 | 2 | 229 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7656 | 1103.9997 | 21.073
SYL-S.1.RR.555.1 | 24520029152262 | Sylhet, Shib Bari, Jonepur Road, Ronju Mia | 2019-07-27 | NQ1011 | 7.8 | 230 | 7.9 | 231 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7656 | 1103.9997 | 83.2382
SYL-S.1.RR.556.1 | 24520019152264 | Sylhet, Shib Bari, Jonepur Road, Saleh Ahmed | 2019-07-27 | NQ1011 | 3.7 | 232 | 3.7 | 233 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7656 | 1103.9997 | 38.985
SYL-S.1.RR.557.1 | 24515899152257 | Sylhet, Shib Bari, Jonepur Road, Sunu Mia | 2019-07-27 | NQ1011 | 4.8 | 234 | 4.8 | 235 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7656 | 1103.9997 | 50.5751
SYL-S.1.RR.558.1 | 24515859152257 | Sylhet, Shib Bari, Jonepur Road, Abdur Roshid Mia | 2019-07-27 | NQ1011 | 8.8 | 236 | 8.8 | 237 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7656 | 1103.9997 | 92.721
SYL-S.1.RR.559.1 | 24515469152326 | Sylhet, Jonepur, Jonepur Road, Omar Dotto | 2019-07-27 | NQ1011 | 10.5 | 238 | 10.5 | 239 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7656 | 1103.9997 | 110.6331
SYL-S.1.RR.560.1 | 24515229152278 | Sylhet, Jonepur, Jonepur Road, Lieakot Khan | 2019-07-27 | NQ1011 | 11.5 | 240 | 11.5 | 241 | 2022-01-01 | [9 empty] | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0
SYL-S.1.RR.561.1 | 24515229152259 | Sylhet, Jonepur, Jonepur Road, Jhalak Chokroborti | 2019-07-27 | NQ1011 | 5.3 | 242 | 5.3 | 243 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7656 | 1103.9997 | 55.8434
SYL-S.1.RR.562.1 | 24514839152257 | Sylhet, Jonepur, Jonepur Road, Sohel Rana | 2019-07-27 | NQ1011 | 8.5 | 244 | 8.5 | 245 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7656 | 1103.9997 | 89.5601
SYL-S.1.RR.563.1 | 24514979152293 | Sylhet, Jonepur, Jonepur Road, Ismail Mia | 2019-07-27 | NQ1011 | 11 | 246 | 10.5 | 247 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7656 | 1103.9997 | 110.6331
SYL-S.1.RR.564.1 | 24515069152234 | Sylhet, Jonepur, Jonepur Road, Onup Das Gupto | 2019-07-27 | NQ1011 | 10.5 | 248 | 10.5 | 249 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7656 | 1103.9997 | 110.6331
SYL-S.1.RR.565.1 | 24530749150044 | Sylhet, South Surma, Hajrai Chowdhury Gaon, Rd # 2, Bacchu Mia | 2019-07-28 | NQ1011 | 4.4 | 278 | 4.4 | 279 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7680 | 1079.9997 | 46.3605
SYL-S.1.RR.566.1 | 24530449150012 | Sylhet, South Surma, Hajrai Chowdhury Gaon, Rd # 2, Abdul Bari | 2019-07-28 | NQ1011 | 3.6 | 285 | 3.6 | 286 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7680 | 1079.9997 | 37.9313
SYL-S.1.RR.567.1 | 24530449150012 | Sylhet, South Surma, Hajrai Chowdhury Gaon, Rd # 2, Md Foysal | 2019-07-28 | NQ1011 | 5.2 | 287 | 5.2 | 288 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7680 | 1079.9997 | 54.7897
SYL-S.1.RR.568.1 | 24530079150006 | Sylhet, South Surma, Hajrai Chowdhury Gaon, Rd # 2, Sana Mia | 2019-07-28 | NQ1011 | 10.3 | 289 | 10.3 | 290 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7680 | 1079.9997 | 108.5258
SYL-S.1.RR.569.1 | 24530079150006 | Sylhet, South Surma, Hajrai Chowdhury Gaon, Rd # 2, Giyas Mia | 2019-07-28 | NQ1011 | 10.7 | 291 | 10.7 | 292 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7680 | 1079.9997 | 112.7403
SYL-S.1.RR.570.1 | 24530529150012 | Sylhet, South Surma, Hajrai Chowdhury Gaon, Rd # 2, Ajir Uddin | 2019-07-28 | NQ1011 | 4.3 | 293 | 4.7 | 294 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7680 | 1079.9997 | 49.5215
SYL-S.1.RR.571.1 | 24530609150196 | Sylhet, South Surma, Gopshor, Mollar Gaw, Md. Hafizur Rahman | 2019-07-28 | NQ1011 | 186.1 | 295 | 186.1 | 296 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 186.1 | 186.1 | 11.166 | 11.166 | 0.0007168 | 100% | 0% | 11.166 | 11.166 | 0.0011869 | 28 | 0.22384 | 0.22384 |  | 0 | 0 | 7680 | 1079.9997 | 1960.8392
SYL-S.1.RR.572.1 | 24541899149373 | Sylhet, Jalalabad, Mollahar Gaon, Pairkar Gaon Road, Dulal Mia | 2019-07-29 | NQ1011 | 6.9 | 297 | 6.9 | 298 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7752 | 1007.9997 | 72.7017
SYL-S.1.RR.573.1 | 24542389149357 | Sylhet, Jalalabad, Mollahar Gaon, Pairkar Gaon, Abu Saleh | 2019-07-29 | NQ1011 | 13.9 | 299 | 13.9 | 300 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7752 | 1007.9997 | 146.4571
SYL-S.1.RR.574.1 | 24543009149146 | Sylhet, Anantapur, Masuk Bazar Road, Hindu Bari, Sunil Nath | 2019-07-29 | NQ1011 | 10.4 | 301 | 10.4 | 302 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7752 | 1007.9997 | 109.5794
SYL-S.1.RR.575.1 | 24543009149146 | Sylhet, Anantapur, Masuk Bazar Road, Hindu Bari, Subikash Nath | 2019-07-29 | NQ1011 | 3.7 | 303 | 3.7 | 304 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7752 | 1007.9997 | 38.985
SYL-S.1.RR.576.1 | 24542949149148 | Sylhet, Anantapur, Masuk Bazar Road, Hindu Bari, Robindra Den Nath | 2019-07-29 | NQ1011 | 5.2 | 305 | 5.2 | 306 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7752 | 1007.9997 | 54.7897
SYL-S.1.RR.577.1 | 24542959149148 | Sylhet, Anantapur, Masuk Bazar Road, Hindu Bari, Nittananda Nath | 2019-07-29 | NQ1011 | 7.9 | 307 | 7.9 | 308 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7752 | 1007.9997 | 83.2382
SYL-S.1.RR.578.1 | 24542939149148 | Sylhet, Anantapur, Masuk Bazar Road, Hindu Bari, Pronoti Chowdhury | 2019-07-29 | NQ1011 | 8.8 | 309 | 8.7 | 310 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7752 | 1007.9997 | 91.6674
SYL-S.1.RR.579.1 | 24542559149147 | Sylhet, Jalalabad, Mollahar Gaon, Anantapur, Dendo Bari, Khairul Islam | 2019-07-29 | NQ1011 | 6.4 | 311 | 6.4 | 312 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7752 | 1007.9997 | 67.4335
SYL-S.1.RR.580.1 | 24542559149147 | Sylhet, Jalalabad, Mollahar Gaon, Anantapur, Dendo Bari, Tajul Islam | 2019-07-29 | NQ1011 | 11.5 | 315 | 11.5 | 316 | 2022-01-01 | 2022-11-20 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7752 | 1007.9997 | 121.1695
SYL-S.1.RR.581.1 | 24522089148184 | Bisshonath, Kamal Bazar, Talibpur college Road, Haji Bari Mia | 2019-07-30 | NQ1011 | 10.8 | 331 | 10.8 | 332 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7680 | 1079.9997 | 113.794
SYL-S.1.RR.582.1 | 24522089148184 | Bisshonath, Kamal Bazar, Talibpur college Road, Ahsan Mia | 2019-07-30 | NQ1011 | 3 | 333 | 3 | 334 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7680 | 1079.9997 | 31.6094
SYL-S.1.RR.583.1 | 24521729148164 | Bisshonath, Kamal Bazar, Talibpur college Road, Rabea Banu General Hospital | 2019-07-30 | NQ1011 | 10.8 | 335 | 10.8 | 336 | 2022-01-01 | 2022-11-17 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7680 | 1079.9997 | 113.794
SYL-S.1.RR.584.1 | 24523649152461 | Kodomtoli, Shornoshikha, Jokigong Road, Md. Kamal Mia | 2019-07-30 | NQ1011 | 10.4 | 337 | 10.4 | 338 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7512 | 1247.9997 | 109.5794
SYL-S.1.RR.585.1 | 24521279153186 | Gotatikor, Shibbari, Gotatikor Road, Abdus Samat | 2019-07-31 | NQ1011 | 12.3 | 355 | 12.3 | 356 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7512 | 1247.9997 | 129.5987
SYL-S.1.RR.586.1 | 24521279153186 | Gotatikor, Shibbari, Gotatikor Road, Ibrahim House | 2019-07-31 | NQ1011 | 5.2 | 357 | 5.2 | 358 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7512 | 1247.9997 | 54.7897
SYL-S.1.RR.587.1 | 24521259153184 | Gotatikor, Shibbari, Gotatikor Road, Bulu Dev | 2019-07-31 | NQ1011 | 5.8 | 359 | 5.8 | 360 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7512 | 1247.9997 | 61.1116
SYL-S.1.RR.588.1 | 24522399153543 | Moglabazar, Kodomtoli, Hobinondi R/A, Faruk Mia | 2019-07-31 | NQ1011 | 2.1 | 361 | 2.1 | 362 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7488 | 1271.9997 | 22.1266
SYL-S.1.RR.589.1 | 24522319153541 | Moglabazar, Kodomtoli, Hobinondi R/A, Shamim Ahmed | 2019-07-31 | NQ1011 | 10.2 | 363 | 10.2 | 364 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7488 | 1271.9997 | 107.4721
SYL-S.1.RR.590.1 | 24521649153525 | Moglabazar, Kodomtoli, Hobinondi R/A, Anowar Islam | 2019-07-31 | NQ1011 | 11 | 365 | 11 | 366 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7488 | 1271.9997 | 115.9013
SYL-S.1.RR.591.1 | 24521439153474 | Moglabazar, Kodomtoli, Hobinondi R/A, Tohir Mia | 2019-07-31 | NQ1011 | 11 | 367 | 11 | 368 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7488 | 1271.9997 | 115.9013
SYL-S.1.RR.592.1 | 24521559153526 | Moglabazar, Kodomtoli, Hobinondi R/A, Amirul Islam Kamal | 2019-07-31 | NQ1011 | 8.1 | 369 | 8.1 | 370 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7488 | 1271.9997 | 85.3455
SYL-S.1.RR.593.1 | 24521449153551 | Moglabazar, Kodomtoli, Hobinondi R/A, Abdul Kadir | 2019-07-31 | NQ1011 | 8.5 | 371 | 8.5 | 372 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7488 | 1271.9997 | 89.5601
SYL-S.1.RR.594.1 | 24521579153568 | Moglabazar, Kodomtoli, Hobinondi R/A, Dara Mia | 2019-07-31 | NQ1011 | 2.3 | 373 | 2.3 | 374 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7488 | 1271.9997 | 24.2339
SYL-S.1.RR.595.1 | 24521579153568 | Moglabazar, Kodomtoli, Hobinondi R/A, Abdul Malek | 2019-07-31 | NQ1011 | 3.9 | 375 | 3.9 | 376 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7488 | 1271.9997 | 41.0923
SYL-S.1.RR.596.1 | 24521179153561 | Moglabazar, Kodomtoli, Hobinondi R/A, Abul Kashem Farid | 2019-07-31 | NQ1011 | 3.3 | 377 | 3.3 | 378 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7488 | 1271.9997 | 34.7704
SYL-S.1.RR.597.1 | 24520969153561 | Moglabazar, Kodomtoli, Hobinondi R/A, Kola Mia | 2019-07-31 | NQ1011 | 3.4 | 379 | 3.4 | 380 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7488 | 1271.9997 | 35.824
SYL-S.1.RR.598.1 | 24520259154252 | Moglabazar, Kodomtoli, Kuchiya R/A, Md. Mohiuddin | 2019-08-01 | NQ1011 | 9.2 | 399 | 9.2 | 400 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7488 | 1271.9997 | 96.9356
SYL-S.1.RR.599.1 | 24520259154252 | Moglabazar, Kodomtoli, Kuchiya R/A, Abdur Nur | 2019-08-01 | NQ1011 | 7.8 | 401 | 7.8 | 402 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7488 | 1271.9997 | 82.1846
SYL-S.1.RR.600.1 | 24520259154252 | Moglabazar, Kodomtoli, Kuchiya R/A, Md. Musabbir | 2019-08-01 | NQ1011 | 12.2 | 403 | 12.2 | 404 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7488 | 1271.9997 | 128.5451
SYL-S.1.RR.601.1 | 24522029154425 | Sylhet, Muglabazar, Sarping, Joynal Abadin | 2019-08-01 | NQ1008 | 2.9 | 413 | 2.9 | 414 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7488 | 1271.9997 | 30.5558
SYL-S.1.RR.602.1 | 24505949157227 | Sylhet, Golapganj, Hetimganj, Shudhang Shuranjan De | 2019-08-04 | NQ1008 | 14.6 | 538 | 13.7 | 539 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7440 | 1319.9997 | 144.3498
SYL-S.1.RR.603.1 | 24510189157232 | Sylhet, Golapganj, Hetimganj, Hamza Kamil | 2019-08-04 | NQ1008 | 7.2 | 542 | 7.2 | 543 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7440 | 1319.9997 | 75.8627
SYL-S.1.RR.604.1 | 24510349157232 | Sylhet, Golapganj, Hetimganj, Jakaria | 2019-08-04 | NQ1008 | 5.1 | 544 | 5.1 | 545 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7440 | 1319.9997 | 53.7361
SYL-S.1.RR.605.1 | 24510559157235 | Sylhet, Golapganj, Hetimganj, Abdul Hakim | 2019-08-04 | NQ1008 | 2.3 | 546 | 2.3 | 547 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7440 | 1319.9997 | 24.2339
SYL-S.1.RR.606.1 | 24510559157235 | Sylhet, Golapganj, Hetimganj, Bodrul Islam | 2019-08-04 | NQ1008 | 10.7 | 548 | 10.4 | 549 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7440 | 1319.9997 | 109.5794
SYL-S.1.RR.607.1 | 24510659157239 | Sylhet, Golapganj, Hetimganj, Jumma Khan | 2019-08-04 | NQ1008 | 12.1 | 550 | 11.7 | 551 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7440 | 1319.9997 | 123.2768
SYL-S.1.RR.608.1 | 24510729157240 | Sylhet, Golapganj, Hetimganj, Sohid Uddin | 2019-08-04 | NQ1008 | 5.1 | 552 | 5.2 | 553 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7440 | 1319.9997 | 54.7897
SYL-S.1.RR.609.1 | 24510809157206 | Sylhet, Golapganj, Hetimganj, Bahar Uddin Dipu | 2019-08-04 | NQ1008 | 4.3 | 554 | 4.3 | 555 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7440 | 1319.9997 | 45.3069
SYL-S.1.RR.610.1 | 24511109157281 | Sylhet, Golapganj, Hetimganj, Jubaer | 2019-08-05 | NQ1008 | 12.5 | 556 | 12.5 | 557 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7440 | 1319.9997 | 131.706
SYL-S.1.RR.611.1 | 24511579157302 | Sylhet, Golapganj, Hetimganj, Md. Abdul Manik | 2019-08-05 | NQ1008 | 13 | 558 | 13 | 559 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7440 | 1319.9997 | 136.9743
SYL-S.1.RR.611.2 | 24511579157302 | Sylhet, Golapganj, Hetimganj, Md. Abdul Manik | 2019-08-05 | NQ1008 | 7.1 | 562 | 7.1 | 563 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7440 | 1319.9997 | 74.809
SYL-S.1.RR.612.1 | 24512169157302 | Sylhet, Golapganj, Hetimganj, Tota Mia | 2019-08-05 | NQ1008 | 31.5 | 564 | 30.3 | 565 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 30.3 | 30.3 | 1.818 | 1.818 | 0.0007168 | 100% | 0% | 1.818 | 1.818 | 0.0011869 | 28 | 0.036445 | 0.036445 |  | 0 | 0 | 7440 | 1319.9997 | 319.2554
SYL-S.1.RR.613.1 | 24512859157381 | Sylhet, Golapganj, Hetimganj, Shamim | 2019-08-05 | NQ1008 | 5.3 | 566 | 5.3 | 567 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7440 | 1319.9997 | 55.8434
SYL-S.1.RR.614.1 | 24512859157381 | Sylhet, Golapganj, Hetimganj, Foridi Doctor | 2019-08-05 | NQ1008 | 5.4 | 568 | 5.4 | 569 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7440 | 1319.9997 | 56.897
SYL-S.1.RR.615.1 | 24512859157381 | Sylhet, Golapganj, Hetimganj, Juhed Ahmed | 2019-08-05 | NQ1008 | 8 | 570 | 8 | 571 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7440 | 1319.9997 | 84.2919
SYL-S.1.RR.615.2 | 24512859157381 | Sylhet, Golapganj, Hetimganj, Juhed Ahmed | 2021-10-13 | LU1001 | 11.8 | 64 | 11.8 | 65 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7440 | 1319.9997 | 124.3305
SYL-S.1.RR.616.1 | 24513449157579 | Sylhet, Hazipur, Lorypor, Alim Uddin | 2019-08-05 | NQ1008 | 3 | 572 | 3 | 573 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7440 | 1319.9997 | 31.6094
SYL-S.1.RR.617.1 | 24513389158035 | Sylhet, Hazipur, Lorypor, Hazi Khezir Mia | 2019-08-05 | NQ1008 | 14.4 | 576 | 14.4 | 577 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7440 | 1319.9997 | 151.7253
SYL-S.1.RR.617.2 | 24513389158035 | Sylhet, Hazipur, Lorypor, Hazi Khezir Mia | 2021-03-02 | LX1011 | 4.8 | 171 | 4.8 | 172 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7440 | 1319.9997 | 50.5751
SYL-S.1.RR.618.1 | 24512819158075 | Sylhet, Hazipur, Lorypor, Opposite Lorypur Sorkari Primary School | 2019-08-05 | NQ1008 | 3.2 | 582 | 3.2 | 583 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7440 | 1319.9997 | 33.7167
SYL-S.1.RR.619.1 | 24513039158104 | Sylhet, Hazipur, Lorypor, Selim | 2019-08-05 | NQ1008 | 10.2 | 584 | 10.2 | 585 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7440 | 1319.9997 | 107.4721
SYL-S.1.RR.620.1 | 24514319149377 | Sylhet, South Surma, Khedirpur, Abdul Mannan | 2019-08-06 | NQ1008 | 7.1 | 612 | 7.1 | 613 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7608 | 1151.9997 | 74.809
SYL-S.1.RR.621.1 | 24514149149401 | Sylhet, South Surma, Khedirpur, Mobassir Ali | 2019-08-06 | NQ1008 | 5.3 | 614 | 5.3 | 615 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7608 | 1151.9997 | 55.8434
SYL-S.1.RR.622.1 | 24514239149446 | Sylhet, South Surma, Khedirpur, Jamil Ahmed | 2019-08-06 | NQ1008 | 4.5 | 616 | 4.5 | 617 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7608 | 1151.9997 | 47.4142
SYL-S.1.RR.623.1 | 24514309149447 | Sylhet, South Surma, Khedirpur, Abdul Wahid | 2019-08-06 | NQ1008 | 7.8 | 618 | 7.8 | 619 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7608 | 1151.9997 | 82.1846
SYL-S.1.RR.624.1 | 24514329149485 | Sylhet, South Surma, Khedirpur, Islam Mia | 2019-08-06 | NQ1008 | 11.1 | 620 | 11.1 | 621 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7608 | 1151.9997 | 116.9549
SYL-S.1.RR.625.1 | 24514329149485 | Sylhet, South Surma, Khedirpur, Mourtuza | 2019-08-06 | NQ1008 | 10.9 | 622 | 10.9 | 623 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7608 | 1151.9997 | 114.8476
SYL-S.1.RR.626.1 | 24514329149485 | Sylhet, South Surma, Khedirpur, Abdur Rob | 2019-08-06 | NQ1008 | 5.8 | 624 | 5.8 | 625 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7608 | 1151.9997 | 61.1116
SYL-S.1.RR.627.1 | 24514249149499 | Sylhet, South Surma, Khedirpur, Salek Mia | 2019-08-06 | NQ1008 | 3.9 | 626 | 3.9 | 627 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7608 | 1151.9997 | 41.0923
SYL-S.1.RR.628.1 | 24514239149514 | Sylhet, South Surma, Khedirpur, Alkas Mia | 2019-08-06 | NQ1008 | 3.4 | 628 | 3.4 | 629 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7608 | 1151.9997 | 35.824
SYL-S.1.RR.629.1 | 24514419149516 | Sylhet, South Surma, Khedirpur, Samad | 2019-08-06 | NQ1008 | 3.9 | 630 | 3.9 | 631 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7608 | 1151.9997 | 41.0923
SYL-S.1.RR.630.1 | 24514609149516 | Sylhet, South Surma, Khedirpur, Ashik | 2019-08-06 | NQ1008 | 6.1 | 632 | 6.1 | 633 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7608 | 1151.9997 | 64.2725
SYL-S.1.RR.651.1 | 24521069153240 | Mugla Bazar, Word # 27, Alampur, Arif Villa | 2019-08-01 | NQ1008 | 5.4 | 427 | 5.5 | 428 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7512 | 1247.9997 | 57.9506
SYL-S.1.RR.652.1 | 24521079153239 | Mugla Bazar, Word # 27, Alampur, Asgar Ali | 2019-08-01 | NQ1008 | 10.4 | 429 | 10.4 | 430 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7512 | 1247.9997 | 109.5794
SYL-S.1.RR.652.2 | 24521079153239 | Mugla Bazar, Word # 27, Alampur, Asgar Ali | 2019-08-01 | NQ1008 | 5.7 | 433 | 5.7 | 434 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7512 | 1247.9997 | 60.0579
SYL-S.1.RR.653.1 | 24521879154366 | Mugla Bazar, Kuchai, Sadek Mia | 2019-08-01 | NQ1008 | 4.4 | 438 | 4.4 | 439 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7488 | 1271.9997 | 46.3605
SYL-S.1.RR.654.1 | 24522359154444 | Mugla Bazar, Kuchai, Mojammel Ali | 2019-08-01 | NQ1008 | 10.2 | 440 | 10.2 | 441 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7488 | 1271.9997 | 107.4721
SYL-S.1.RR.654.2 | 24522359154444 | Mugla Bazar, Kuchai, Mojammel Ali | 2019-08-01 | NQ1008 | 6.3 | 442 | 6.3 | 443 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7488 | 1271.9997 | 66.3798
SYL-S.1.RR.655.1 | 24522389154450 | Mugla Bazar, Kuchai, Abdus Samad | 2019-08-01 | NQ1008 | 9.9 | 444 | 9.9 | 445 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7488 | 1271.9997 | 104.3112
SYL-S.1.RR.655.2 | 24522389154450 | Mugla Bazar, Kuchai, Abdus Samad | 2021-10-11 | LU1001 | 3.1 | 51 | 3.1 | 52 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7488 | 1271.9997 | 32.6631
SYL-S.1.RR.656.1 | 24522389154450 | Mugla Bazar, Kuchai, Kamal Uddin | 2019-08-01 | NQ1008 | 11 | 446 | 11 | 447 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7488 | 1271.9997 | 115.9013
SYL-S.1.RR.656.2 | 24522389154450 | Mugla Bazar, Kuchai, Kamal Uddin | 2022-11-09 | MN1018 | 5.7 | 129 | 5.7 | 130 | 2022-11-09 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 0 | 1271.9997 | 8.7207
SYL-S.1.RR.657.1 | 24522479154461 | Mugla Bazar, Kuchai, Moyna Mia | 2019-08-01 | NQ1008 | 7.4 | 448 | 7.4 | 449 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7488 | 1271.9997 | 77.97
SYL-S.1.RR.658.1 | 24520429154552 | Monglabazar, 4 No Kuchai, Possimvag R/A, Rusna Begum | 2019-08-03 | NQ1008 | 10 | 450 | 10 | 451 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7464 | 1295.9997 | 105.3648
SYL-S.1.RR.659.1 | 24520559155023 | Monglabazar, 4 No Kuchai, Possimvag R/A, Dilip Kumar Nath | 2019-08-03 | NQ1008 | 11.3 | 452 | 10.9 | 453 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7464 | 1295.9997 | 114.8476
SYL-S.1.RR.659.2 | 24520559155023 | Monglabazar, 4 No Kuchai, Possimvag R/A, Dilip Kumar Nath | 2019-08-03 | NQ1008 | 2.3 | 454 | 2.3 | 455 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7464 | 1295.9997 | 24.2339
SYL-S.1.RR.659.3 | 24520559155023 | Monglabazar, 4 No Kuchai, Possimvag R/A, Dilip Kumar Nath | 2019-08-03 | NQ1008 | 2.4 | 458 | 2.4 | 459 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7464 | 1295.9997 | 25.2876
SYL-S.1.RR.659.4 | 24520559155023 | Monglabazar, 4 No Kuchai, Possimvag R/A, Dilip Kumar Nath | 2019-08-03 | NQ1008 | 7.3 | 460 | 7.3 | 461 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7464 | 1295.9997 | 76.9163
SYL-S.1.RR.660.1 | 24520569155032 | Monglabazar, 4 No Kuchai, Possimvag R/A, Shahin | 2019-08-03 | NQ1008 | 6.9 | 462 | 6.9 | 463 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7464 | 1295.9997 | 72.7017
SYL-S.1.RR.661.1 | 24520569155032 | Monglabazar, 4 No Kuchai, Possimvag R/A, Shahin | 2019-08-03 | NQ1008 | 6.8 | 464 | 6.8 | 465 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7464 | 1295.9997 | 71.6481
SYL-S.1.RR.662.1 | 24520569155032 | Monglabazar, 4 No Kuchai, Possimvag R/A, Shahin | 2019-08-03 | NQ1008 | 4.3 | 466 | 4.3 | 467 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7464 | 1295.9997 | 45.3069
SYL-S.1.RR.662.2 | 24520569155032 | Monglabazar, 4 No Kuchai, Possimvag R/A, Shahin | 2019-08-03 | NQ1008 | 7.8 | 468 | 7.8 | 469 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7464 | 1295.9997 | 82.1846
SYL-S.1.RR.663.1 | 24520699155063 | Monglabazar, 4 No Kuchai, Possimvag R/A, Makhon Mia | 2019-08-03 | NQ1008 | 4.3 | 470 | 4.3 | 471 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7464 | 1295.9997 | 45.3069
SYL-S.1.RR.664.1 | 24520909155066 | Monglabazar, 4 No Kuchai, Possimvag R/A, Kalam Mia | 2019-08-03 | NQ1008 | 9.8 | 472 | 9.9 | 473 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7464 | 1295.9997 | 104.3112
SYL-S.1.RR.665.1 | 24520199155052 | Monglabazar, 4 No Kuchai, Possimvag R/A, Anowar Hosen | 2019-08-03 | NQ1008 | 12.1 | 474 | 12.1 | 475 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7464 | 1295.9997 | 127.4914
SYL-S.1.RR.665.2 | 24520199155052 | Monglabazar, 4 No Kuchai, Possimvag R/A, Anowar Hosen | 2019-08-03 | NQ1008 | 2.4 | 476 | 2.4 | 477 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7464 | 1295.9997 | 25.2876
SYL-S.1.RR.666.1 | 24520029155054 | Monglabazar, 4 No Kuchai, Possimvag R/A, Hiron Mia | 2019-08-03 | NQ1008 | 4 | 478 | 4 | 479 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7464 | 1295.9997 | 42.1459
SYL-S.1.RR.666.2 | 24520029155054 | Monglabazar, 4 No Kuchai, Possimvag R/A, Hiron Mia | 2019-08-03 | NQ1008 | 2.7 | 480 | 2.7 | 481 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7464 | 1295.9997 | 28.4485
SYL-S.1.RR.667.1 | 24515709155047 | Monglabazar, 4 No Kuchai, Possimvag R/A, Firoz Ali | 2019-08-03 | NQ1008 | 12 | 482 | 12 | 483 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7464 | 1295.9997 | 126.4378
SYL-S.1.RR.667.2 | 24515709155047 | Monglabazar, 4 No Kuchai, Possimvag R/A, Firoz Ali | 2019-08-03 | NQ1008 | 6 | 484 | 6 | 485 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7464 | 1295.9997 | 63.2189
SYL-S.1.RR.668.1 | 24520179154593 | Monglabazar, 4 No Kuchai, Possimvag R/A, Nazrul Islam | 2019-08-03 | NQ1008 | 11.4 | 486 | 11.4 | 487 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7464 | 1295.9997 | 120.1159
SYL-S.1.RR.668.2 | 24520179154593 | Monglabazar, 4 No Kuchai, Possimvag R/A, Nazrul Islam | 2019-08-03 | NQ1008 | 6.1 | 488 | 6.1 | 489 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7464 | 1295.9997 | 64.2725
SYL-S.1.RR.669.1 | 24520129154594 | Monglabazar, 4 No Kuchai, Possimvag R/A, Salim Ahammed | 2019-08-03 | NQ1008 | 5 | 490 | 5 | 491 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7464 | 1295.9997 | 52.6824
SYL-S.1.RR.670.1 | 24520189154585 | Monglabazar, 4 No Kuchai, Possimvag R/A, Naznin Begum | 2019-08-03 | NQ1008 | 11.2 | 492 | 11.2 | 493 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7464 | 1295.9997 | 118.0086
SYL-S.1.RR.671.1 | 24520679154594 | Monglabazar, 4 No Kuchai, Possimvag R/A, Mukhlesur Rahman | 2019-08-03 | NQ1008 | 2.4 | 494 | 2.4 | 495 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7464 | 1295.9997 | 25.2876
SYL-S.1.RR.672.1 | 24520829154596 | Monglabazar, 4 No Kuchai, Possimvag R/A, Mon Mohon Nath | 2019-08-03 | NQ1008 | 10.6 | 496 | 10.6 | 497 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7464 | 1295.9997 | 111.6867
SYL-S.1.RR.673.1 | 24521319155005 | Monglabazar, 4 No Kuchai, Possimvag R/A, Hosen Ahammed | 2019-08-03 | NQ1008 | 3.9 | 500 | 3.9 | 501 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7464 | 1295.9997 | 41.0923
SYL-S.1.RR.674.1 | 24521319155005 | Monglabazar, 4 No Kuchai, Possimvag R/A, Abdul Alim | 2019-08-03 | NQ1008 | 5.2 | 502 | 5.2 | 503 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7464 | 1295.9997 | 54.7897
SYL-S.1.RR.674.2 | 24521319155005 | Monglabazar, 4 No Kuchai, Possimvag R/A, Abdul Alim | 2019-08-03 | NQ1008 | 2.4 | 504 | 2.4 | 505 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7464 | 1295.9997 | 25.2876
SYL-S.1.RR.675.1 | 24521329155064 | Monglabazar, 4 No Kuchai, Possimvag R/A, Block - A, Rd # 4, Moznu Mia | 2019-08-03 | NQ1008 | 3.8 | 506 | 3.8 | 507 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-S.1.RR.676.1 | 24521329155064 | Monglabazar, 4 No Kuchai, Possimvag R/A, Block - A, Rd # 4, Abdus Samad | 2019-08-03 | NQ1008 | 4 | 508 | 4 | 509 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7464 | 1295.9997 | 42.1459
SYL-S.1.RR.677.1 | 24521599155018 | Monglabazar, 4 No Kuchai, Possimvag R/A, Abdul Hamid | 2019-08-03 | NQ1008 | 9.9 | 510 | 9.9 | 511 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7464 | 1295.9997 | 104.3112
SYL-S.1.RR.678.1 | 24521979155003 | Monglabazar, 4 No Kuchai, Possimvag R/A, Dulal Ahammed | 2019-08-03 | NQ1008 | 6.2 | 512 | 6.2 | 513 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7464 | 1295.9997 | 65.3262
SYL-S.1.RR.679.1 | 24522889154554 | Monglabazar, 4 No Kuchai, Word - 8, Sarpin, Haji Abdur Rahman | 2019-08-04 | NQ1008 | 12.1 | 514 | 11.9 | 515 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7488 | 1271.9997 | 125.3841
SYL-S.1.RR.680.1 | 24522759154538 | Monglabazar, 4 No Kuchai, Word - 8, Sarpin, Soyed Ullah | 2019-08-04 | NQ1008 | 6 | 516 | 6 | 517 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7488 | 1271.9997 | 63.2189
SYL-S.1.RR.681.1 | 24522709154528 | Monglabazar, 4 No Kuchai, Word - 8, Sarpin, Kholil Mia | 2019-08-04 | NQ1008 | 5.3 | 518 | 5.3 | 519 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7488 | 1271.9997 | 55.8434
SYL-S.1.RR.682.1 | 24521669155106 | Monglabazar, 4 No Kuchai, Word - 6, Possimvag R/A, Sekendar Ali | 2019-08-04 | NQ1008 | 11.5 | 520 | 11.5 | 521 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7464 | 1295.9997 | 121.1695
SYL-S.1.RR.682.2 | 24521669155106 | Monglabazar, 4 No Kuchai, Word - 6, Possimvag R/A, Sekendar Ali | 2019-08-04 | NQ1008 | 7 | 522 | 7 | 523 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7464 | 1295.9997 | 73.7554
SYL-S.1.RR.683.1 | 24521669155106 | Monglabazar, 4 No Kuchai, Word - 6, Possimvag R/A, Shochib Ali | 2019-08-04 | NQ1008 | 3 | 526 | 3 | 527 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7464 | 1295.9997 | 31.6094
SYL-S.1.RR.683.2 | 24521669155106 | Monglabazar, 4 No Kuchai, Word - 6, Possimvag R/A, Shochib Ali | 2019-08-04 | NQ1008 | 15.9 | 528 | 15.9 | 529 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 15.9 | 15.9 | 0.954 | 0.954 | 0.0007168 | 100% | 0% | 0.954 | 0.954 | 0.0011869 | 28 | 0.019124 | 0.019124 |  | 0 | 0 | 7464 | 1295.9997 | 167.5301
SYL-S.1.RR.683.3 | 24521669155106 | Monglabazar, 4 No Kuchai, Word - 6, Possimvag R/A, Shochib Ali | 2019-08-04 | NQ1008 | 7.1 | 532 | 7.1 | 533 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7464 | 1295.9997 | 74.809
SYL-S.1.RR.684.1 | 24521419155104 | Monglabazar, 4 No Kuchai, Word - 6, Possimvag R/A, Anowar Hosen | 2019-08-04 | NQ1008 | 11.7 | 534 | 11.7 | 535 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7464 | 1295.9997 | 123.2768
SYL-S.1.RR.685.1 | 24520019155124 | Monglabazar, 4 No Kuchai, Word - 6, Possimvag R/A, Emran Ahammed | 2019-08-04 | NQ1008 | 9.1 | 536 | 8.8 | 537 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7464 | 1295.9997 | 92.721
SYL-S.1.RR.686.1 | 24505639159360 | Golapgong, 3 No Fulbari, Word - 8, Fulbari South Para, Mukta Mia | 2019-08-05 | NQ1008 | 2.7 | 586 | 2.7 | 587 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7440 | 1319.9997 | 28.4485
SYL-S.1.RR.687.1 | 24505639159360 | Golapgong, 3 No Fulbari, Word - 8, Fulbari South Para, Mukta Mia | 2019-08-05 | NQ1008 | 4.2 | 588 | 4.2 | 589 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7440 | 1319.9997 | 44.2532
SYL-S.1.RR.688.1 | 24505639159360 | Golapgong, 3 No Fulbari, Word - 8, Fulbari South Para, Mukta Mia | 2019-08-05 | NQ1008 | 7.9 | 592 | 7.9 | 593 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7440 | 1319.9997 | 83.2382
SYL-S.1.RR.689.1 | 24505739159369 | Golapgong, 3 No Fulbari, Word - 8, Fulbari South Para, Ansar Mia | 2019-08-05 | NQ1008 | 5.2 | 594 | 5.2 | 595 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7440 | 1319.9997 | 54.7897
SYL-S.1.RR.690.1 | 24505739159369 | Golapgong, 3 No Fulbari, Word - 8, Fulbari South Para, Shahed Mia | 2019-08-05 | NQ1008 | 4.4 | 596 | 4.4 | 597 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7440 | 1319.9997 | 46.3605
SYL-S.1.RR.691.1 | 24505749159379 | Golapgong, 3 No Fulbari, Word - 8, Fulbari South Para, Moshiur Rahman | 2019-08-05 | NQ1008 | 10.7 | 598 | 10.7 | 599 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7440 | 1319.9997 | 112.7403
SYL-S.1.RR.692.1 | 24505789159390 | Golapgong, 3 No Fulbari, Word - 8, Fulbari South Para, Sakhawat Hosen | 2019-08-05 | NQ1008 | 16.3 | 600 | 16.3 | 601 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 7440 | 1319.9997 | 171.7446
SYL-S.1.RR.693.1 | 24505829159350 | Golapgong, 3 No Fulbari, Word - 9, Fulbari South Para, Nazrul Ali | 2019-08-05 | NQ1008 | 23.6 | 602 | 23.6 | 603 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 23.6 | 23.6 | 1.416 | 1.416 | 0.0007168 | 100% | 0% | 1.416 | 1.416 | 0.0011869 | 28 | 0.028386 | 0.028386 |  | 0 | 0 | 7440 | 1319.9997 | 248.661
SYL-S.1.RR.694.1 | 24510319159379 | Golapgong, 3 No Fulbari, Word - 9, Fulbari North Para, Somir Uddin | 2019-08-05 | NQ1008 | 3.1 | 604 | 3.1 | 605 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7440 | 1319.9997 | 32.6631
SYL-S.1.RR.694.2 | 24510319159379 | Golapgong, 3 No Fulbari, Word - 9, Fulbari North Para, Somir Uddin | 2019-08-05 | NQ1008 | 2.2 | 606 | 2.2 | 607 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7440 | 1319.9997 | 23.1803
SYL-S.1.RR.695.1 | 24510319159379 | Golapgong, 3 No Fulbari, Word - 9, Fulbari North Para, Somir Uddin | 2019-08-05 | NQ1008 | 3.9 | 608 | 3.9 | 609 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7440 | 1319.9997 | 41.0923
SYL-S.1.RR.695.2 | 24510319159379 | Golapgong, 3 No Fulbari, Word - 9, Fulbari North Para, Somir Uddin | 2019-08-05 | NQ1008 | 10.1 | 610 | 10.1 | 611 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7440 | 1319.9997 | 106.4185
SYL-S.1.RR.696.1 | 24515149151094 | South Surma, 3 No Tetli, Word - 2, Bodikona, Razna Begum | 2019-08-06 | NQ1008 | 6.5 | 636 | 6.5 | 637 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7632 | 1127.9997 | 68.4871
SYL-S.1.RR.696.2 | 24515149151094 | South Surma, 3 No Tetli, Word - 2, Bodikona, Razna Begum | 2019-08-06 | NQ1008 | 2.4 | 638 | 2.4 | 639 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7632 | 1127.9997 | 25.2876
SYL-S.1.RR.697.1 | 24520219152403 | Monglabazar, Word - 27, Bandar Ghat, Gotatikar, Jamal Uddin | 2019-08-06 | NQ1008 | 5.5 | 640 | 5.5 | 641 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7656 | 1103.9997 | 57.9506
SYL-S.1.RR.698.1 | 24520759152461 | Monglabazar, Word - 27, Gotatikar, Shib Bari, Poytta Para, Pintu Babu | 2019-08-06 | NQ1008 | 8.2 | 642 | 8.2 | 643 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7656 | 1103.9997 | 86.3991
SYL-S.1.RR.699.1 | 24521299152503 | Monglabazar, Word - 27, Gotatikar, Pathan Para R/A, Abdul Malik | 2019-08-06 | NQ1008 | 19.8 | 644 | 19.8 | 645 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 19.8 | 19.8 | 1.188 | 1.188 | 0.0007168 | 100% | 0% | 1.188 | 1.188 | 0.0011869 | 28 | 0.023815 | 0.023815 |  | 0 | 0 | 7512 | 1247.9997 | 208.6223
SYL-S.1.RR.700.1 | 24521299152503 | Monglabazar, Word - 27, Gotatikar, Pathan Para R/A, Abdul Malik | 2019-08-06 | NQ1008 | 8.2 | 646 | 8.2 | 647 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7512 | 1247.9997 | 86.3991
SYL-S.1.RR.701.1 | 24514069155039 | South Surma, Kuchai, Sultanpur, Abul Kalam Chairman | 2019-08-01 | MN1032 | 7.5 | 379 | 7.5 | 380 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7488 | 1271.9997 | 79.0236
SYL-S.1.RR.701.2 | 24514069155039 | South Surma, Kuchai, Sultanpur, Abul Kalam Chairman | 2020-10-28 | NQ1000 | 0.6 | 193 | 0.6 | 194 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 0.6 | 0.6 | 0.036 | 0.036 | 0.0007168 | 100% | 0% | 0.036 | 0.036 | 0.0011869 | 28 | 0.00072168 | 0.00072168 |  | 0 | 0 | 7488 | 1271.9997 | 6.3219
SYL-S.1.RR.702.1 | 24514259155032 | South Surma, Kuchai, Sultanpur, Abdur Razzak | 2019-08-01 | MN1032 | 26.4 | 381 | 26.4 | 382 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 26.4 | 26.4 | 1.584 | 1.584 | 0.0007168 | 100% | 0% | 1.584 | 1.584 | 0.0011869 | 28 | 0.031754 | 0.031754 |  | 0 | 0 | 7488 | 1271.9997 | 278.1631
SYL-S.1.RR.703.1 | 24512759155342 | South Surma, Sreerampur, Uttar Para, Bacchu Mia | 2019-08-01 | MN1032 | 10.8 | 383 | 10.8 | 384 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7464 | 1295.9997 | 113.794
SYL-S.1.RR.704.1 | 24514249155358 | South Surma, Sreerampur, Sheikh Para, Md. Showkot Mia | 2019-08-01 | MN1032 | 5.6 | 385 | 5.6 | 386 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7464 | 1295.9997 | 59.0043
SYL-S.1.RR.705.1 | 24514249155358 | South Surma, Sreerampur, Sheikh Para, Rokib Ali | 2019-08-01 | MN1032 | 10.9 | 387 | 10.9 | 388 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7464 | 1295.9997 | 114.8476
SYL-S.1.RR.706.1 | 24514719155368 | South Surma, Sreerampur, Sheikh Para, Azizur Rahman | 2019-08-03 | MN1032 | 11.5 | 389 | 11.5 | 390 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7464 | 1295.9997 | 121.1695
SYL-S.1.RR.707.1 | 24514929155268 | South Surma, Sreerampur, Toyab Kamal R/A, Md.Bodrul Alam | 2019-08-03 | MN1032 | 7.3 | 391 | 7.3 | 392 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7464 | 1295.9997 | 76.9163
SYL-S.1.RR.708.1 | 24514929155268 | South Surma, Sreerampur, Toyab Kamal R/A, Shah Nizamuddin | 2019-08-03 | MN1032 | 7.4 | 393 | 7.4 | 394 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7464 | 1295.9997 | 77.97
SYL-S.1.RR.709.1 | 24515359155257 | South Surma, Sreerampur, Toyab Kamal R/A, Tareak | 2019-08-03 | MN1032 | 12.5 | 395 | 12.5 | 396 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7464 | 1295.9997 | 131.706
SYL-S.1.RR.710.1 | 24514819155198 | South Surma, Sreerampur, Toyab Kamal Pirbari, Nazimuddin | 2019-08-03 | MN1032 | 12.6 | 397 | 12.6 | 398 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7464 | 1295.9997 | 132.7597
SYL-S.1.RR.711.1 | 24514819155198 | South Surma, Sreerampur, Toyab Kamal Pirbari, Gousuddin | 2019-08-03 | MN1032 | 8.6 | 399 | 8.6 | 400 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7464 | 1295.9997 | 90.6137
SYL-S.1.RR.712.1 | 24515399155196 | South Surma, Sreerampur, Toyab Kamal, Abdur Sottor Sikder | 2019-08-03 | MN1032 | 3.2 | 401 | 3.2 | 402 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7464 | 1295.9997 | 33.7167
SYL-S.1.RR.713.1 | 24515399155196 | South Surma, Sreerampur, Toyab Kamal, Abdur Sottor Sikder | 2019-08-03 | MN1032 | 30.8 | 403 | 29.7 | 404 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 29.7 | 29.7 | 1.782 | 1.782 | 0.0007168 | 100% | 0% | 1.782 | 1.782 | 0.0011869 | 28 | 0.035723 | 0.035723 |  | 0 | 0 | 7464 | 1295.9997 | 312.9335
SYL-S.1.RR.714.1 | 24503839157144 | Golapganj, Moskapur, Dewan Road, Abdur Rab | 2019-08-04 | MN1032 | 12.3 | 437 | 12.3 | 438 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7440 | 1319.9997 | 129.5987
SYL-S.1.RR.715.1 | 24502609157200 | Golapganj, Moskapur, Jamtola, Azizur Rahman Khan | 2019-08-04 | MN1032 | 8.8 | 439 | 8.8 | 440 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7440 | 1319.9997 | 92.721
SYL-S.1.RR.716.1 | 24502639157264 | Golapganj, Moskapur, Nearest Moskapur Jame Mosjid, Jalaluddin | 2019-08-04 | MN1032 | 30.7 | 441 | 30.4 | 442 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 30.4 | 30.4 | 1.824 | 1.824 | 0.0007168 | 100% | 0% | 1.824 | 1.824 | 0.0011869 | 28 | 0.036565 | 0.036565 |  | 0 | 0 | 7440 | 1319.9997 | 320.309
SYL-S.1.RR.716.2 | 24502639157264 | Golapganj, Moskapur, Nearest Moskapur Jame Mosjid, Jalaluddin | 2021-03-02 | MN1018 | 10 | 185 | 10.1 | 186 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7440 | 1319.9997 | 106.4185
SYL-S.1.RR.717.1 | 24502639157264 | Golapganj, Moskapur, Nearest Moskapur Jame Mosjid, Md.Mokul | 2019-08-04 | MN1032 | 8 | 443 | 8 | 444 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7440 | 1319.9997 | 84.2919
SYL-S.1.RR.718.1 | 24501179157330 | Golapganj, Nistofa, Kazi bari, Md.Mohiuudin | 2019-08-05 | MN1032 | 11.1 | 447 | 11.1 | 448 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7440 | 1319.9997 | 116.9549
SYL-S.1.RR.719.1 | 24501179157330 | Golapganj, Nistofa, Kazi bari, Abdul Muhit Chowdhuory | 2019-08-05 | MN1032 | 3.9 | 449 | 3.9 | 450 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7440 | 1319.9997 | 41.0923
SYL-S.1.RR.720.1 | 24495699157492 | Golapganj, Kotalpur, Kazi bari, Sebeka Sultana | 2019-08-05 | MN1032 | 11.7 | 452 | 11.7 | 453 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7440 | 1319.9997 | 123.2768
SYL-S.1.RR.721.1 | 24495699157492 | Golapganj, Kotalpur, Kazi bari, Kazi Anam Ahmed | 2019-08-05 | MN1032 | 4 | 454 | 4 | 455 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7440 | 1319.9997 | 42.1459
SYL-S.1.RR.722.1 | 24495699157492 | Golapganj, Kotalpur, Kazi bari, Abdul Lotif | 2019-08-05 | MN1032 | 7.2 | 456 | 7.2 | 457 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7440 | 1319.9997 | 75.8627
SYL-S.1.RR.722.2 | 24495699157492 | Golapganj, Kotalpur, Kazi bari, Abdul Lotif | 2021-10-13 | LU1001 | 14.4 | 66 | 14.4 | 67 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7440 | 1319.9997 | 151.7253
SYL-S.1.RR.723.1 | 24501839157489 | Golapganj, Nistofa, Dewan Road, Kola Mia | 2019-08-05 | MN1032 | 10.3 | 458 | 10.3 | 459 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7440 | 1319.9997 | 108.5258
SYL-S.1.RR.724.1 | 24501839157489 | Golapganj, Nistofa, Dewan Road, Hazi Manik Mia | 2019-08-05 | MN1032 | 6.2 | 460 | 6.2 | 461 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7440 | 1319.9997 | 65.3262
SYL-S.1.RR.725.1 | 24514059149324 | South Surma, Lokkipur, Kutubuddin | 2019-08-06 | MN1032 | 10.2 | 480 | 10.2 | 481 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7608 | 1151.9997 | 107.4721
SYL-S.1.RR.726.1 | 24514009149400 | South Surma, Betuarpur, Hasan Ali | 2019-08-06 | MN1032 | 3.4 | 484 | 3.4 | 485 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7608 | 1151.9997 | 35.824
SYL-S.1.RR.727.1 | 24514009149400 | South Surma, Betuarpur, Md.Arosh Ali | 2019-08-06 | MN1032 | 3.2 | 486 | 3.2 | 487 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7608 | 1151.9997 | 33.7167
SYL-S.1.RR.728.1 | 24513819149442 | South Surma, Betuarpur, Eleyas Mia | 2019-08-06 | MN1032 | 10.2 | 488 | 10.2 | 489 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7608 | 1151.9997 | 107.4721
SYL-S.1.RR.729.1 | 24513339149438 | South Surma, Betuarpur, Rubel | 2019-08-06 | MN1032 | 10.3 | 492 | 10.3 | 493 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7608 | 1151.9997 | 108.5258
SYL-S.1.RR.730.1 | 24513339149438 | South Surma, Betuarpur, Sofiq Mia | 2019-08-06 | MN1032 | 10.9 | 494 | 11 | 495 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7608 | 1151.9997 | 115.9013
SYL-S.1.RR.731.1 | 24514169150248 | South Surma, Tetli, Tilabari, Chomok Ali | 2019-08-06 | MN1032 | 11.1 | 496 | 10.4 | 497 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7608 | 1151.9997 | 109.5794
SYL-S.1.RR.751.1 | 24505129159369 | Golapganj, Phulbari South Para, Abul Hosen | 2019-08-05 | MN1032 | 9.1 | 474 | 9.1 | 475 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7440 | 1319.9997 | 95.882
SYL-S.1.RR.752.1 | 24504839159399 | Golapganj, Phulbari South Para, Mokit | 2019-08-05 | MN1032 | 4.7 | 476 | 4.7 | 477 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7440 | 1319.9997 | 49.5215
SYL-S.1.RR.753.1 | 24505149159446 | Golapganj, Phulbari Purbopara, Mosnu | 2019-08-05 | MN1032 | 10.7 | 478 | 10.7 | 479 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7440 | 1319.9997 | 112.7403
SYL-S.1.RR.754.1 | 24515129151088 | South Surma, 3 No Tetli, Ward-2, Bodikona, Md. Ashique Ahmed | 2019-08-06 | MN1032 | 9.2 | 498 | 9.2 | 499 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7632 | 1127.9997 | 96.9356
SYL-S.1.RR.755.1 | 24515209152321 | South Surma, Jonpur, Chandai Road, Patan Mia | 2019-08-06 | MN1032 | 4.1 | 500 | 4.1 | 501 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7656 | 1103.9997 | 43.1996
SYL-S.1.RR.756.1 | 24514949152321 | South Surma, Jonpur, Chandai Road, Romzan Ali | 2019-08-06 | MN1032 | 14.1 | 502 | 14.1 | 503 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7656 | 1103.9997 | 148.5644
SYL-S.1.RR.757.1 | 24514839152309 | South Surma, Jonpur, Chandai Road, Mostak | 2019-08-06 | MN1032 | 4.9 | 504 | 4.9 | 505 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7656 | 1103.9997 | 51.6288
SYL-S.1.RR.758.1 | 24514689152313 | South Surma, Jonpur, Chandai Road, Ohab Mia | 2019-08-06 | MN1032 | 10.4 | 506 | 10.4 | 507 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7656 | 1103.9997 | 109.5794
SYL-S.1.RR.759.1 | 24514499152289 | South Surma, Jonpur, Chandai Road, Junaid Hosen | 2019-08-06 | MN1032 | 10.4 | 508 | 10.1 | 509 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7656 | 1103.9997 | 106.4185
SYL-S.1.RR.801.1 | 24512479155226 | South Surma, Sreerampur, Wathier Ali | 2019-08-03 | NQ1011 | 6.4 | 487 | 6 | 488 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7464 | 1295.9997 | 63.2189
SYL-S.1.RR.802.1 | 24512479155226 | South Surma, Sreerampur, Abdus Shahid | 2019-08-03 | NQ1011 | 4.7 | 491 | 4.7 | 492 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7464 | 1295.9997 | 49.5215
SYL-S.1.RR.803.1 | 24512249155233 | South Surma, Sreerampur, Sakibur Rahman | 2019-08-03 | NQ1011 | 6.4 | 493 | 6.4 | 494 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7464 | 1295.9997 | 67.4335
SYL-S.1.RR.804.1 | 24511319155186 | South Surma, Sreerampur, Akmal Ali | 2019-08-03 | NQ1011 | 11.9 | 495 | 11.9 | 496 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7464 | 1295.9997 | 125.3841
SYL-S.1.RR.805.1 | 24511319155186 | South Surma, Sreerampur, Shafiq Mia | 2019-08-03 | NQ1011 | 6.1 | 497 | 6.1 | 498 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7464 | 1295.9997 | 64.2725
SYL-S.1.RR.806.1 | 24511799155106 | South Surma, Sreerampur, Akhter Hossain | 2019-08-03 | NQ1011 | 10.6 | 499 | 10.6 | 500 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7464 | 1295.9997 | 111.6867
SYL-S.1.RR.807.1 | 24511799155106 | South Surma, Sreerampur, Abdul Khalek | 2019-08-03 | NQ1011 | 8.5 | 501 | 8.5 | 502 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7464 | 1295.9997 | 89.5601
SYL-S.1.RR.808.1 | 24511799155106 | South Surma, Sreerampur, Sharif Uddin | 2019-08-03 | NQ1011 | 8.2 | 503 | 7.7 | 504 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7464 | 1295.9997 | 81.1309
SYL-S.1.RR.809.1 | 24511599155132 | South Surma, Sreerampur, Rezwan Ahamed | 2019-08-03 | NQ1011 | 4.6 | 505 | 4.3 | 506 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7464 | 1295.9997 | 45.3069
SYL-S.1.RR.810.1 | 24511519155104 | South Surma, Sreerampur, Azadur Rahman | 2019-08-03 | NQ1011 | 11.2 | 507 | 11.3 | 508 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7464 | 1295.9997 | 119.0622
SYL-S.1.RR.811.1 | 24511289155150 | South Surma, Sreerampur, Bashir Mia | 2019-08-03 | NQ1011 | 3.8 | 509 | 3.8 | 510 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7464 | 1295.9997 | 40.0386
SYL-S.1.RR.812.1 | 24511289155150 | South Surma, Sreerampur, Hafiz Khan | 2019-08-03 | NQ1011 | 7.7 | 511 | 7.2 | 512 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7464 | 1295.9997 | 75.8627
SYL-S.1.RR.813.1 | 24511289155150 | South Surma, Sreerampur, Kazol Ahmed | 2019-08-03 | NQ1011 | 8.1 | 513 | 8.1 | 514 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7464 | 1295.9997 | 85.3455
SYL-S.1.RR.814.1 | 24511289200110 | Golapganj, Fulbari, Purbo Para, Abdul Matin | 2019-08-04 | NQ1011 | 11.3 | 538 | 11.3 | 539 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7440 | 1319.9997 | 119.0622
SYL-S.1.RR.815.1 | 24510989200098 | Golapganj, Fulbari, Purbo Para, Mojahidul Islam | 2019-08-04 | NQ1011 | 3.4 | 540 | 3.4 | 541 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7440 | 1319.9997 | 35.824
SYL-S.1.RR.815.2 | 24510989200098 | Golapganj, Fulbari, Purbo Para, Mojahidul Islam | 2019-08-04 | NQ1011 | 6.3 | 542 | 6.3 | 543 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7440 | 1319.9997 | 66.3798
SYL-S.1.RR.816.1 | 24510689200078 | Golapganj, Fulbari, Purbo Para, Askir Ali | 2019-08-04 | NQ1011 | 9.1 | 545 | 9.1 | 546 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7440 | 1319.9997 | 95.882
SYL-S.1.RR.817.1 | 24510129200074 | Golapganj, Fulbari, Purbo Para, Nur Islam | 2019-08-04 | NQ1011 | 6.5 | 547 | 6.5 | 548 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7440 | 1319.9997 | 68.4871
SYL-S.1.RR.818.1 | 24510049200076 | Golapganj, Fulbari, Purbo Para, Abdul Khalek | 2019-08-04 | NQ1011 | 6 | 551 | 6 | 552 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7440 | 1319.9997 | 63.2189
SYL-S.1.RR.819.1 | 24504739200107 | Golapganj, Fulbari, Purbo Para, Najrul Islam | 2019-08-04 | NQ1011 | 11.7 | 553 | 11.7 | 554 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7440 | 1319.9997 | 123.2768
SYL-S.1.RR.820.1 | 24504739200107 | Golapganj, Fulbari, Purbo Para, Najrul Islam | 2019-08-04 | NQ1011 | 4.7 | 555 | 4.7 | 556 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7440 | 1319.9997 | 49.5215
SYL-S.1.RR.821.1 | 24511299200310 | Golapganj, Kodomtoli, Ghoshgaon, Dada Vai Building | 2019-08-05 | NQ1011 | 7.3 | 557 | 7.3 | 558 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7440 | 1319.9997 | 76.9163
SYL-S.1.RR.822.1 | 24511249200307 | Golapganj, Kodomtoli, Ghoshgaon, Sardar Kutir | 2019-08-05 | NQ1011 | 10.2 | 559 | 10.2 | 560 | 2022-01-01 | [9 empty] | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0
SYL-S.1.RR.823.1 | 24510869200289 | Golapganj, Kodomtoli, Ghoshgaon Road, Sacheton, H# 23/0 | 2019-08-05 | NQ1011 | 4.7 | 561 | 4.7 | 562 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7440 | 1319.9997 | 49.5215
SYL-S.1.RR.824.1 | 24510569200273 | Golapganj, Kodomtoli, Ghoshgaon Road, Sornali R/A, Joynal Abedin | 2019-08-05 | NQ1011 | 12.2 | 563 | 12.2 | 564 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7440 | 1319.9997 | 128.5451
SYL-S.1.RR.825.1 | 24510569200273 | Golapganj, Kodomtoli, Ghoshgaon Road, Sornali R/A, Halima Begum | 2019-08-05 | NQ1011 | 4.5 | 565 | 4.5 | 566 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7440 | 1319.9997 | 47.4142
SYL-S.1.RR.826.1 | 24510339200241 | Golapganj, Kodomtoli, Ghoshgaon Road, Ahmed Ali | 2019-08-05 | NQ1011 | 12.5 | 571 | 12.5 | 572 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7440 | 1319.9997 | 131.706
SYL-S.1.RR.827.1 | 24510339200241 | Golapganj, Kodomtoli, Ghoshgaon, Mokhles Ali | 2019-08-05 | NQ1011 | 2 | 573 | 1.8 | 574 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7440 | 1319.9997 | 18.9657
SYL-S.1.RR.828.1 | 24504889200231 | Golapganj, Kodomtoli, Ghoshgaon, Rehana Khanom | 2019-08-05 | NQ1011 | 7.8 | 575 | 7.8 | 576 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7440 | 1319.9997 | 82.1846
SYL-S.1.RR.829.1 | 24513719149590 | South Surma, Tetli Majhpara, Talukdar Bari | 2019-08-06 | NQ1011 | 5.2 | 595 | 5.2 | 596 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7608 | 1151.9997 | 54.7897
SYL-S.1.RR.830.1 | 24513209149569 | South Surma, Tetli Cheragi, Abdul Jalil | 2019-08-06 | NQ1011 | 3.7 | 597 | 3.7 | 598 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7608 | 1151.9997 | 38.985
SYL-S.1.RR.831.1 | 24513219149575 | South Surma, Tetli Cheragi, Raju Mia | 2019-08-06 | NQ1011 | 9.3 | 599 | 9.3 | 600 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7608 | 1151.9997 | 97.9893
SYL-S.1.RR.832.1 | 24513219149575 | South Surma, Tetli Cheragi, Mokbul Mia | 2019-08-06 | NQ1011 | 7.4 | 601 | 7.1 | 602 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7608 | 1151.9997 | 74.809
SYL-S.1.RR.833.1 | 24513219149575 | South Surma, Tetli Cheragi, Monjur Mia | 2019-08-06 | NQ1011 | 6.3 | 603 | 6.3 | 604 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7608 | 1151.9997 | 66.3798
SYL-S.1.RR.834.1 | 24513219149575 | South Surma, Tetli Cheragi, Md. Gojonfor Ali | 2019-08-06 | NQ1011 | 4.3 | 605 | 4.3 | 606 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7608 | 1151.9997 | 45.3069
SYL-S.1.RR.835.1 | 24513199149600 | South Surma, Tetli Cheragi, Aminul Islam | 2019-08-06 | NQ1011 | 2.4 | 607 | 2.5 | 608 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7608 | 1151.9997 | 26.3412
SYL-S.1.RR.836.1 | 24513199149600 | South Surma, Tetli Cheragi, Moinul Islam | 2019-08-06 | NQ1011 | 3.2 | 609 | 3.2 | 610 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7608 | 1151.9997 | 33.7167
SYL-S.1.RR.837.1 | 24513439150030 | South Surma, Tetli Majhpara, Motassir | 2019-08-06 | NQ1011 | 7 | 611 | 7 | 612 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7608 | 1151.9997 | 73.7554
SYL-S.1.RR.837.2 | 24513439150030 | South Surma, Tetli Majhpara, Motassir | 2020-10-25 | NQ1000 | 10.3 | 152 | 10.1 | 153 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7608 | 1151.9997 | 106.4185
SYL-S.1.RR.838.1 | 24513439150030 | South Surma, Tetli Majhpara, Zinab Ali | 2019-08-06 | NQ1011 | 12.2 | 613 | 12.2 | 614 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7608 | 1151.9997 | 128.5451
SYL-S.1.RR.839.1 | 24514029150057 | South Surma, Tetli Majhpara, Formuj Ali | 2019-08-06 | NQ1011 | 7.7 | 615 | 7.7 | 616 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7608 | 1151.9997 | 81.1309
SYL-S.1.RR.840.1 | 24514199150056 | South Surma, Tetli Majhpara, Liton Mia | 2019-08-06 | NQ1011 | 3.1 | 617 | 3.1 | 618 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7608 | 1151.9997 | 32.6631
SYL-S.1.RR.841.1 | 24512409150022 | South Surma, Tetli, Tajul Islam | 2019-08-06 | NQ1011 | 4.6 | 619 | 4.6 | 620 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7608 | 1151.9997 | 48.4678
SYL-S.1.RR.842.1 | 24514299149538 | South Surma, Latifpur, Boro Betuar Par, Amir Ali | 2019-08-06 | NQ1011 | 25.1 | 621 | 25.1 | 622 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 25.1 | 25.1 | 1.506 | 1.506 | 0.0007168 | 100% | 0% | 1.506 | 1.506 | 0.0011869 | 28 | 0.03019 | 0.03019 |  | 0 | 0 | 7608 | 1151.9997 | 264.4657
SYL-S.1.RR.843.1 | 24514719149542 | South Surma, Latifpur, Boro Betuar Par, Lokman | 2019-08-06 | NQ1011 | 9.7 | 623 | 10 | 624 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7608 | 1151.9997 | 105.3648
SYL-S.1.RR.844.1 | 24514719149542 | South Surma, Latifpur, Boro Betuar Par, Salek Uddin | 2019-08-06 | NQ1011 | 8.8 | 625 | 8.8 | 626 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7608 | 1151.9997 | 92.721
SYL-S.1.RR.845.1 | 24514719149542 | South Surma, Latifpur, Boro Betuar Par, Abdur Rob | 2019-08-06 | NQ1011 | 3.2 | 633 | 3.2 | 634 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7608 | 1151.9997 | 33.7167
SYL-S.1.RR.846.1 | 24514719149542 | South Surma, Latifpur, Boro Betuar Par, Abdul Kalam | 2019-08-06 | NQ1011 | 4.2 | 635 | 4 | 636 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7608 | 1151.9997 | 42.1459
SYL-S.1.RR.851.1 | 24520259154252 | Moglabazar, Kodomtoli, Kuchiya R/A, Abdur Rouf (Dara) | 2019-08-01 | NQ1011 | 2.1 | 405 | 2.1 | 406 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7488 | 1271.9997 | 22.1266
SYL-S.1.RR.852.1 | 24520009154249 | Moglabazar, Kodomtoli, Kuchiya R/A, Jamal Uddin | 2019-08-01 | NQ1011 | 7.4 | 407 | 7.4 | 408 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7488 | 1271.9997 | 77.97
SYL-S.1.RR.853.1 | 24520009154249 | Moglabazar, Kodomtoli, Kuchiya R/A, Haris Ali | 2019-08-01 | NQ1011 | 16.1 | 409 | 16.1 | 410 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 16.1 | 16.1 | 0.966 | 0.966 | 0.0007168 | 100% | 0% | 0.966 | 0.966 | 0.0011869 | 28 | 0.019365 | 0.019365 |  | 0 | 0 | 7488 | 1271.9997 | 169.6373
SYL-S.1.RR.854.1 | 24515899154246 | Moglabazar, Kodomtoli, Kuchiya R/A, Abdul Mujib | 2019-08-01 | NQ1011 | 8.7 | 411 | 8.7 | 412 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7488 | 1271.9997 | 91.6674
SYL-S.1.RR.855.1 | 24515549154584 | Moglabazar, Sreerampur, Poshchim Vag - 1, Babul Mia | 2019-08-01 | NQ1011 | 10.4 | 414 | 10.4 | 415 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7488 | 1271.9997 | 109.5794
SYL-S.1.RR.856.1 | 24515399154579 | Moglabazar, Sreerampur, Poshchim Vag - 1, Abdul Halim | 2019-08-01 | NQ1011 | 2.9 | 416 | 2.9 | 417 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7488 | 1271.9997 | 30.5558
SYL-S.1.RR.857.1 | 24515259154531 | Moglabazar, Sreerampur, Poshchim Vag - 1, Saleh Ahmed | 2019-08-01 | NQ1011 | 10.9 | 420 | 10.6 | 421 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7488 | 1271.9997 | 111.6867
SYL-S.1.RR.858.1 | 24511239155220 | Moglabazar, Sreerampur, Sreerampur Road, Shahabuddin | 2019-08-03 | NQ1011 | 2.5 | 464 | 2.5 | 465 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7464 | 1295.9997 | 26.3412
SYL-S.1.RR.858.2 | 24511239155220 | Moglabazar, Sreerampur, Sreerampur Road, Shahabuddin | 2021-10-12 | LU1001 | 9.4 | 53 | 9.4 | 54 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7464 | 1295.9997 | 99.0429
SYL-S.1.RR.859.1 | 24511239155220 | Moglabazar, Sreerampur, Sreerampur Road, Md. Burhanuddin | 2019-08-03 | NQ1011 | 2.6 | 466 | 2.6 | 467 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7464 | 1295.9997 | 27.3949
SYL-S.1.RR.860.1 | 24512689155093 | Moglabazar, South Sultanpur, Kusai, Uttar Bari, Md. Ansar Mia | 2019-08-03 | NQ1011 | 7.1 | 468 | 6.9 | 469 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7464 | 1295.9997 | 72.7017
SYL-S.1.RR.861.1 | 24512769155092 | Moglabazar, South Sultanpur, Kusai, Uttar Bari, Md. Razu | 2019-08-03 | NQ1011 | 6.7 | 471 | 6.7 | 472 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7464 | 1295.9997 | 70.5944
SYL-S.1.RR.862.1 | 24512769155092 | Moglabazar, South Sultanpur, Kusai, Uttar Bari, Nazrul Islam | 2019-08-03 | NQ1011 | 12.6 | 473 | 12.6 | 474 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7464 | 1295.9997 | 132.7597
SYL-S.1.RR.863.1 | 24512769155092 | Moglabazar, South Sultanpur, Kusai, Uttar Bari, Md. Chan Mia | 2019-08-03 | NQ1011 | 10.4 | 475 | 10.4 | 476 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7464 | 1295.9997 | 109.5794
SYL-S.1.RR.864.1 | 24512619155026 | Moglabazar, South Sultanpur, Kusai, Danai Bari, Moin Uddin | 2019-08-03 | NQ1011 | 10.7 | 477 | 10.7 | 478 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7464 | 1295.9997 | 112.7403
SYL-S.1.RR.865.1 | 24512619155026 | Moglabazar, South Sultanpur, Kusai, Danai Bari, Md. Juwel | 2019-08-03 | NQ1011 | 15 | 479 | 15 | 480 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 15 | 15 | 0.9 | 0.9 | 0.0007168 | 100% | 0% | 0.9 | 0.9 | 0.0011869 | 28 | 0.018042 | 0.018042 |  | 0 | 0 | 7464 | 1295.9997 | 158.0472
SYL-S.1.RR.866.1 | 24512619155026 | Moglabazar, South Sultanpur, Kusai, Danai Bari, Hazi Asab Mia | 2019-08-03 | NQ1011 | 8.2 | 481 | 8.2 | 482 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7464 | 1295.9997 | 86.3991
SYL-S.1.RR.867.1 | 24512089155057 | Moglabazar, South Sultanpur, Alhajj Eliyas Khan | 2019-08-03 | NQ1011 | 11 | 483 | 11 | 484 | 2022-01-01 | 2022-11-08 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7464 | 1295.9997 | 115.9013
SYL-S.1.RR.868.1 | 24510539156478 | Golapganj, Hatimganj, Surma Daik, Abdul Ahad | 2019-08-04 | NQ1011 | 5.2 | 518 | 5.2 | 519 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7440 | 1319.9997 | 54.7897
SYL-S.1.RR.869.1 | 24510319156487 | Golapganj, Hatimganj, Surma Daik, Moyna Mia | 2019-08-04 | NQ1011 | 6.3 | 520 | 6.3 | 521 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7440 | 1319.9997 | 66.3798
SYL-S.1.RR.870.1 | 24510319156487 | Golapganj, Hatimganj, Surma Daik, Aabdul Motaleb | 2019-08-04 | NQ1011 | 7.8 | 522 | 7.8 | 523 | 2022-01-01 | [9 empty] | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0
SYL-S.1.RR.871.1 | 24505319156403 | Golapganj, Hatimganj, Surma Daik, Insan Ali | 2019-08-04 | NQ1011 | 10.7 | 524 | 10.7 | 525 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7440 | 1319.9997 | 112.7403
SYL-S.1.RR.872.1 | 24505319156403 | Golapganj, Hatimganj, Surma Daik, Insan Ali | 2019-08-04 | NQ1011 | 3.3 | 526 | 3.3 | 527 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7440 | 1319.9997 | 34.7704
SYL-S.1.RR.873.1 | 24510049156525 | Golapganj, Hatimganj, Mollahar Gaon, Salim Member | 2019-08-04 | NQ1011 | 10.8 | 528 | 10.9 | 529 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7440 | 1319.9997 | 114.8476
SYL-S.1.RR.874.1 | 24510049156525 | Golapganj, Hatimganj, Mollahar Gaon, Mannan Mia | 2019-08-04 | NQ1011 | 11.5 | 530 | 11.2 | 531 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7440 | 1319.9997 | 118.0086
SYL-S.1.RR.875.1 | 24505869156518 | Golapganj, Hatimganj, Mollahar Gaon, Gieas Uddin | 2019-08-04 | NQ1011 | 6.1 | 532 | 6.1 | 533 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7440 | 1319.9997 | 64.2725
SYL-S.1.RR.876.1 | 24505469156525 | Golapganj, Hatimganj, Mollahar Gaon, Md. Mustak | 2019-08-04 | NQ1011 | 9.3 | 534 | 9.3 | 535 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7440 | 1319.9997 | 97.9893
SYL-S.1.RR.877.1 | 24510619157040 | Golapganj, Hatimganj, Mollahar Gaon, Abdul Kuddus | 2019-08-04 | NQ1011 | 11.6 | 536 | 11.6 | 537 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7440 | 1319.9997 | 122.2232
SYL-S.1.RR.877.2 | 24510619157040 | Golapganj, Hatimganj, Mollahar Gaon, Abdul Kuddus | 2021-10-13 | LU1001 | 3.2 | 62 | 3.3 | 63 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7440 | 1319.9997 | 34.7704
SYL-S.1.RR.878.1 | 24504929200084 | Golapganj, Fulbari, Purbopara, Purbopara Road, Arshedur Rahman | 2019-08-05 | NQ1011 | 3.9 | 577 | 3.9 | 578 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7440 | 1319.9997 | 41.0923
SYL-S.1.RR.879.1 | 24505099200078 | Golapganj, Fulbari, Purbopara, Purbopara Road, Chunu Mia | 2019-08-05 | NQ1011 | 6.3 | 579 | 6.3 | 580 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7440 | 1319.9997 | 66.3798
SYL-S.1.RR.880.1 | 24505129200007 | Golapganj, Fulbari, Purbopara, Purbopara Road, Md. Mohin | 2019-08-05 | NQ1011 | 10.6 | 581 | 10.7 | 582 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7440 | 1319.9997 | 112.7403
SYL-S.1.RR.881.1 | 24504959200007 | Golapganj, Fulbari, Purbopara, Purbopara Road, Arifa Jahir Chowdhury | 2019-08-05 | NQ1011 | 9.8 | 583 | 9.8 | 584 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7440 | 1319.9997 | 103.2575
SYL-S.1.RR.882.1 | 24504919159594 | Golapganj, Fulbari, Purbopara, Purbopara Road, Tofayel Ahmed | 2019-08-05 | NQ1011 | 7.5 | 585 | 7.5 | 586 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7440 | 1319.9997 | 79.0236
SYL-S.1.RR.883.1 | 24504879159543 | Golapganj, Fulbari, Purbopara, Purbopara Road, Jahingir Alom | 2019-08-05 | NQ1011 | 8.1 | 588 | 8.1 | 589 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7440 | 1319.9997 | 85.3455
SYL-S.1.RR.884.1 | 24504879159543 | Golapganj, Fulbari, Purbopara, Purbopara Road, Enamul Hai | 2019-08-05 | NQ1011 | 7.8 | 590 | 7.8 | 591 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7440 | 1319.9997 | 82.1846
SYL-S.1.RR.885.1 | 24505579159529 | Golapganj, Fulbari, Purbopara, Purbopara Road, Mustak Ahmed | 2019-08-05 | NQ1011 | 8.7 | 592 | 8.7 | 593 | 2022-01-01 | 2022-11-07 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7440 | 1319.9997 | 91.6674
SYL-S.1.RR.886.1 | 24515079151099 | South Surma, 3 No. Tetli, Word # 2, Md. Monai Mia | 2019-08-06 | NQ1011 | 6 | 637 | 6 | 638 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7632 | 1127.9997 | 63.2189
SYL-S.1.RR.887.1 | 24515089152212 | Sylhet, Jynepur, Jynepur Road, Mosaddor Ali | 2019-08-06 | NQ1011 | 3.3 | 639 | 3.3 | 640 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7656 | 1103.9997 | 34.7704
SYL-S.1.RR.888.1 | 24514959152182 | Sylhet, Jynepur, Jynepur Road, Fokir Para, Nafisa House | 2019-08-06 | NQ1011 | 14.7 | 641 | 14.7 | 642 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7656 | 1103.9997 | 154.8863
SYL-S.1.RR.889.1 | 24514629152182 | Sylhet, Jynepur, Jynepur Road, Fokir Para, Md. Helal | 2019-08-06 | NQ1011 | 2.7 | 643 | 2.7 | 644 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7656 | 1103.9997 | 28.4485
SYL-S.1.RR.890.1 | 24521429153335 | Sylhet, Muglabazar, Alompur R/A, A.Gofur Golap Mia | 2019-08-27 | MP1006 | 1.5 | 280 | 1.5 | 281 | 2022-01-01 | 2022-11-09 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7488 | 1271.9997 | 15.8047
SYL-S.1.RR.891.1 | 24511689151347 | Sylhet, South Surma, Silam, Dhalipara, Abdul Haque | 2019-09-07 | NQ1008 | 6.4 | 69 | 6.4 | 70 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7608 | 1151.9997 | 67.4335
SYL-S.1.RR.892.1 | 24511229151268 | Sylhet, South Surma, Silam, Dhalipara, Gias Uddin | 2019-09-07 | NQ1008 | 4.4 | 71 | 4.4 | 72 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7608 | 1151.9997 | 46.3605
SYL-S.1.RR.892.2 | 24511229151268 | Sylhet, South Surma, Silam, Dhalipara, Gias Uddin | 2021-03-03 | NQ1007 | 7.9 | 245 | 7.9 | 246 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7608 | 1151.9997 | 83.2382
SYL-S.1.RR.893.1 | 24511229151268 | Sylhet, South Surma, Silam, Dhalipara, Gias Uddin | 2019-09-07 | NQ1008 | 6.2 | 73 | 6.2 | 74 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7608 | 1151.9997 | 65.3262
SYL-S.1.RR.894.1 | 24511159151243 | Sylhet, South Surma, Silam, Dhalipara, Aziruddin | 2019-09-07 | NQ1008 | 4.5 | 75 | 4.5 | 76 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7608 | 1151.9997 | 47.4142
SYL-S.1.RR.895.1 | 24510949151237 | Sylhet, South Surma, Silam, Dhalipara, Mohiuddin | 2019-09-07 | NQ1008 | 11.8 | 77 | 11.1 | 78 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7608 | 1151.9997 | 116.9549
SYL-S.1.RR.896.1 | 24510849151229 | Sylhet, South Surma, Silam, Dhalipara, Alom Mia | 2019-09-07 | NQ1008 | 6.7 | 79 | 6.7 | 80 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7608 | 1151.9997 | 70.5944
SYL-S.1.RR.897.1 | 24495639151450 | Sylhet, South Surma, Hazipur, Dhola Mia | 2019-09-07 | NQ1008 | 11.8 | 81 | 11.7 | 82 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7608 | 1151.9997 | 123.2768
SYL-S.1.RR.898.1 | 24513809152140 | Sylhet, Chandai, Majpara, Baharuddin | 2019-09-08 | NQ1008 | 11.1 | 93 | 11.1 | 94 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7656 | 1103.9997 | 116.9549
SYL-S.1.RR.899.1 | 24513499152225 | Sylhet, Chandai, Telipara, Rd # 1, Selim Khan | 2019-09-08 | NQ1008 | 6.4 | 95 | 5.9 | 96 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7656 | 1103.9997 | 62.1652
SYL-S.1.RR.900.1 | 24512429152178 | Sylhet, Chandai, Talukdarpara, Rd # 1, Shamim | 2019-09-08 | NQ1008 | 5.3 | 97 | 5.3 | 98 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7656 | 1103.9997 | 55.8434
SYL-S.1.RR.901.1 | 24511799152164 | Sylhet, Chandai, Talukdarpara, Rd # 1, Somraj Mia | 2019-09-08 | NQ1008 | 4.1 | 99 | 4.1 | 100 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7656 | 1103.9997 | 43.1996
SYL-S.1.RR.931.1 | 24500259151039 | Silam, Rustompur, Turon Ali | 2019-09-07 | NQ1008 | 32.2 | 83 | 30.9 | 84 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 30.9 | 30.9 | 1.854 | 1.854 | 0.0007168 | 100% | 0% | 1.854 | 1.854 | 0.0011869 | 28 | 0.037166 | 0.037166 |  | 0 | 0 | 7608 | 1151.9997 | 325.5773
SYL-S.1.RR.932.1 | 24500259151039 | Silam, Rustompur, Turon Ali | 2019-09-07 | NQ1008 | 9.7 | 85 | 9.7 | 86 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7608 | 1151.9997 | 102.2039
SYL-S.1.RR.933.1 | 24500259151039 | Silam, Rustompur, Mashuk Mia | 2019-09-07 | NQ1008 | 13.4 | 87 | 13.2 | 88 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7608 | 1151.9997 | 139.0816
SYL-S.1.RR.934.1 | 24495869151107 | Silam, East Rustompur, Nurul Amin Chowdhury | 2019-09-07 | NQ1008 | 8 | 89 | 8 | 90 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7608 | 1151.9997 | 84.2919
SYL-S.1.RR.935.1 | 24495869151107 | Silam, East Rustompur, Md. Ahmodul Islam Chowdhury | 2019-09-07 | NQ1008 | 8.7 | 91 | 8.7 | 92 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7608 | 1151.9997 | 91.6674
SYL-S.1.RR.935.2 | 24495869151107 | Silam, East Rustompur, Md. Ahmodul Islam Chowdhury | 2022-05-31 | LU1001 | 12.1 | 193 | 12.1 | 194 | 2022-05-31 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 4008 | 1151.9997 | 75.0977
SYL-S.1.RR.936.1 | 24521869152487 | Shibbari, Pathanpara R/A, Faruk Mia | 2019-09-09 | NQ1008 | 11.5 | 101 | 11.5 | 102 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7512 | 1247.9997 | 121.1695
SYL-S.1.RR.937.1 | 24521869152487 | Shibbari, Pathanpara R/A, H # 31, Monju | 2019-09-09 | NQ1008 | 14.5 | 103 | 14.5 | 104 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 14.5 | 14.5 | 0.87 | 0.87 | 0.0007168 | 100% | 0% | 0.87 | 0.87 | 0.0011869 | 28 | 0.017441 | 0.017441 |  | 0 | 0 | 7512 | 1247.9997 | 152.779
SYL-S.1.RR.971.1 | 24510759151344 | South Surma, Silam, Sheikh Para, Mozibur Rahman Aslam | 2019-09-07 | MN1032 | 5.4 | 39 | 5.8 | 40 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7608 | 1151.9997 | 61.1116
SYL-S.1.RR.972.1 | 24510759151344 | South Surma, Silam, Sheikh Para, Md.Somsu Mia | 2019-09-07 | MN1032 | 12.3 | 41 | 12.3 | 42 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7608 | 1151.9997 | 129.5987
SYL-S.1.RR.973.1 | 24510839151269 | South Surma, Silam, Dhali Para, Md.Namor Ali | 2019-09-07 | MN1032 | 5.2 | 43 | 5.2 | 44 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7608 | 1151.9997 | 54.7897
SYL-S.1.RR.974.1 | 24510349151325 | South Surma, Silam, Tila Para, Md.Habibur Rahman | 2019-09-07 | MN1032 | 10.3 | 45 | 10.3 | 46 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7608 | 1151.9997 | 108.5258
SYL-S.1.RR.974.2 | 24510349151325 | South Surma, Silam, Tila Para, Md.Habibur Rahman | 2022-11-14 | MN1018 | 7.9 | 141 | 7.9 | 142 | 2022-11-14 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 0 | 1151.9997 | 10.9464
SYL-S.1.RR.975.1 | 24505899151405 | South Surma, Silam, Tila Para, Abdur Rashid | 2019-09-07 | MN1032 | 13.4 | 47 | 13.4 | 48 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7608 | 1151.9997 | 141.1888
SYL-S.1.RR.976.1 | 24502279151406 | South Surma, Silam, Teli para, Md.Aziruddin | 2019-09-08 | MN1032 | 9.4 | 57 | 9.4 | 58 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7608 | 1151.9997 | 99.0429
SYL-S.1.RR.977.1 | 24501289151447 | South Surma, Silam, Teli para, Noya Bazar, Md.Osman | 2019-09-08 | MN1032 | 6.8 | 61 | 6.8 | 62 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7608 | 1151.9997 | 71.6481
SYL-S.1.RR.978.1 | 24501289151447 | South Surma, Silam, Teli para, Noya Bazar, Abdul Hamid | 2019-09-08 | MN1032 | 10.1 | 63 | 10.1 | 64 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7608 | 1151.9997 | 106.4185
SYL-S.1.RR.979.1 | 24501039151441 | South Surma, Silam, Teli para, Noya Bazar, Hazi Monfor Ali | 2019-09-08 | MN1032 | 13.7 | 65 | 13.7 | 66 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.7 | 13.7 | 0.822 | 0.822 | 0.0007168 | 100% | 0% | 0.822 | 0.822 | 0.0011869 | 28 | 0.016478 | 0.016478 |  | 0 | 0 | 7608 | 1151.9997 | 144.3498
SYL-S.1.RR.980.1 | 24500269151440 | South Surma, Silam, Hazipur, Bozlu Mia | 2019-09-08 | MN1032 | 20.6 | 67 | 20.6 | 68 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 20.6 | 20.6 | 1.236 | 1.236 | 0.0007168 | 100% | 0% | 1.236 | 1.236 | 0.0011869 | 28 | 0.024778 | 0.024778 |  | 0 | 0 | 7608 | 1151.9997 | 217.0515
SYL-S.1.RR.1011.1 | 24501379151013 | Silam, Mohammadpur East Side, Abdur Rab | 2019-09-07 | MN1032 | 21.7 | 49 | 21.7 | 50 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 21.7 | 21.7 | 1.302 | 1.302 | 0.0007168 | 100% | 0% | 1.302 | 1.302 | 0.0011869 | 28 | 0.026101 | 0.026101 |  | 0 | 0 | 7608 | 1151.9997 | 228.6416
SYL-S.1.RR.1012.1 | 24501379151013 | Silam, Mohammadpur East Side, Abdul Haque | 2019-09-07 | MN1032 | 18.9 | 51 | 18.9 | 52 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 18.9 | 18.9 | 1.134 | 1.134 | 0.0007168 | 100% | 0% | 1.134 | 1.134 | 0.0011869 | 28 | 0.022733 | 0.022733 |  | 0 | 0 | 7608 | 1151.9997 | 199.1395
SYL-S.1.RR.1013.1 | 24501539150516 | Silam, Mohammadpur East Side, Giyash Miah | 2019-09-07 | MN1032 | 13.2 | 53 | 13.2 | 54 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7608 | 1151.9997 | 139.0816
SYL-S.1.RR.1014.1 | 24501459150502 | Silam, Mohammadpur East Side, Sharif Uddin | 2019-09-07 | MN1032 | 10.2 | 55 | 10.2 | 56 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7608 | 1151.9997 | 107.4721
SYL-S.1.RR.1015.1 | 24513129150434 | Islam Nagar, Baldi, South Sorma, Md. Monir Ali | 2019-09-09 | MN1032 | 14.9 | 69 | 14.7 | 70 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7632 | 1127.9997 | 154.8863
SYL-S.1.RR.1016.1 | 24513859150520 | South Surma, Telibazar, Bolda, Masum | 2019-09-11 | MN1032 | 21.6 | 73 | 21.6 | 74 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 21.6 | 21.6 | 1.296 | 1.296 | 0.0007168 | 100% | 0% | 1.296 | 1.296 | 0.0011869 | 28 | 0.02598 | 0.02598 |  | 0 | 0 | 7632 | 1127.9997 | 227.588
SYL-S.1.RR.1017.1 | 24513339150539 | South Surma, Telibazar, Bolda, Babor Ali | 2019-09-11 | MN1032 | 23.2 | 75 | 23.4 | 76 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 23.4 | 23.4 | 1.404 | 1.404 | 0.0007168 | 100% | 0% | 1.404 | 1.404 | 0.0011869 | 28 | 0.028145 | 0.028145 |  | 0 | 0 | 7632 | 1127.9997 | 246.5537
SYL-S.1.RR.1018.1 | 24521699151565 | South Surma, Musargao, Jihar | 2019-09-11 | MN1032 | 11.9 | 79 | 11.9 | 80 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7656 | 1103.9997 | 125.3841
SYL-S.1.RR.1051.1 | 24505549151368 | Silam, Tilapara, Chokerbazar, Azijur Rahman | 2019-09-07 | LX1011 | 9.9 | 41 | 9.9 | 42 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7608 | 1151.9997 | 104.3112
SYL-S.1.RR.1052.1 | 24505039151341 | Silam, Chokerbazar, Majpara, Akhrom Ali | 2019-09-07 | LX1011 | 34.2 | 43 | 34.2 | 44 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 34.2 | 34.2 | 2.052 | 2.052 | 0.0007168 | 100% | 0% | 2.052 | 2.052 | 0.0011869 | 28 | 0.041136 | 0.041136 |  | 0 | 0 | 7608 | 1151.9997 | 360.3477
SYL-S.1.RR.1053.1 | 24505379151558 | Silam, Chokerbazar, Tikorpara, Faruk Ahmod | 2019-09-07 | LX1011 | 13.3 | 45 | 13.3 | 46 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7608 | 1151.9997 | 140.1352
SYL-S.1.RR.1054.1 | 24505009151515 | Silam, Chokerbazar, Tikorpara, Dependro Taron | 2019-09-07 | LX1011 | 12.3 | 47 | 12.3 | 48 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7608 | 1151.9997 | 129.5987
SYL-S.1.RR.1055.1 | 24513459152106 | South Surma, Boroikandi, Chandai Majpara, Md. Sohel | 2019-09-08 | LX1011 | 2.2 | 68 | 2.2 | 69 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7656 | 1103.9997 | 23.1803
SYL-S.1.RR.1056.1 | 24513459152106 | South Surma, Boroikandi, Chandai Majpara, Anower Hossen | 2019-09-08 | LX1011 | 19 | 70 | 19 | 71 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 7656 | 1103.9997 | 200.1931
SYL-S.1.RR.1056.2 | 24513459152106 | South Surma, Boroikandi, Chandai Majpara, Anower Hossen | 2021-03-02 | LU1001 | 2.4 | 231 | 2.4 | 232 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7656 | 1103.9997 | 25.2876
SYL-S.1.RR.1057.1 | 24513349152112 | South Surma, Boroikandi, Chandai Majpara, Maruf Vai | 2019-09-08 | LX1011 | 13 | 72 | 13 | 73 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7656 | 1103.9997 | 136.9743
SYL-S.1.RR.1058.1 | 24512269152078 | South Surma, Boroikandi, Chandai, Tior Gaon, Azmol Ali | 2019-09-08 | LX1011 | 17.9 | 74 | 17.9 | 75 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 7656 | 1103.9997 | 188.603
SYL-S.1.RR.1059.1 | 24512139152077 | South Surma, Boroikandi, Chandai, Tior Gaon, Ali Akther Mashuk | 2019-09-08 | LX1011 | 9.5 | 76 | 9.5 | 77 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7656 | 1103.9997 | 100.0966
SYL-S.1.RR.1060.1 | 24512109151581 | South Surma, Boroikandi, Chandai, Tior Gaon, Puran Bari, Abdul Karim | 2019-09-08 | LX1011 | 2.6 | 78 | 2.6 | 79 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7656 | 1103.9997 | 27.3949
SYL-S.1.RR.1061.1 | 24512109151581 | South Surma, Boroikandi, Chandai, Tior Gaon, Puran Bari, Abdul Mumit | 2019-09-08 | LX1011 | 12.4 | 82 | 11.9 | 83 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7656 | 1103.9997 | 125.3841
SYL-S.1.RR.1062.1 | 24511719151536 | South Surma, Boroikandi, Chandai, Porchim Para, Mahamudur Rahman | 2019-09-08 | LX1011 | 6.9 | 84 | 6.6 | 85 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7656 | 1103.9997 | 69.5408
SYL-S.1.RR.1062.2 | 24511719151536 | South Surma, Boroikandi, Chandai, Porchim Para, Mahamudur Rahman | 2021-10-20 | LU1001 | 7.5 | 68 | 7.5 | 69 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7656 | 1103.9997 | 79.0236
SYL-S.1.RR.1091.1 | 24504539151248 | South Surma, Silam West Para, Udioman R/A, Block - A, H # 67 | 2019-09-07 | LX1011 | 11.6 | 49 | 11.6 | 50 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7608 | 1151.9997 | 122.2232
SYL-S.1.RR.1092.1 | 24504749151245 | South Surma, Silam West Para, Udioman R/A, Afsaruddin | 2019-09-07 | LX1011 | 6.1 | 51 | 6.1 | 52 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7608 | 1151.9997 | 64.2725
SYL-S.1.RR.1093.1 | 24504839151218 | South Surma, Silam West Para, Fulbibi Begum | 2019-09-07 | LX1011 | 4 | 53 | 4 | 54 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7608 | 1151.9997 | 42.1459
SYL-S.1.RR.1094.1 | 24503929151175 | South Surma, Silam West Para, Udioman R/A, Mahbub Alom | 2019-09-07 | LX1011 | 4.5 | 55 | 4.5 | 56 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7608 | 1151.9997 | 47.4142
SYL-S.1.RR.1095.1 | 24503889151176 | South Surma, Silam West Para, Udioman R/A, Ucha Bari, Rahad | 2019-09-07 | LX1011 | 5 | 57 | 5 | 58 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7608 | 1151.9997 | 52.6824
SYL-S.1.RR.1096.1 | 24503889151176 | South Surma, Silam West Para, Udioman R/A, Ucha Bari, Saad | 2019-09-07 | LX1011 | 3.2 | 59 | 3.2 | 60 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7608 | 1151.9997 | 33.7167
SYL-S.1.RR.1097.1 | 24503889151176 | South Surma, Silam West Para, Udioman R/A, Ucha Bari, Giasuddin | 2019-09-07 | LX1011 | 5.9 | 61 | 5.9 | 62 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7608 | 1151.9997 | 62.1652
SYL-S.1.RR.1098.1 | 24504259151180 | South Surma, Silam West Para, Sadek Member | 2019-09-07 | LX1011 | 12.2 | 64 | 12.2 | 65 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7608 | 1151.9997 | 128.5451
SYL-S.1.RR.1098.2 | 24504259151180 | South Surma, Silam West Para, Sadek Member | 2022-11-14 | MN1018 | 6.8 | 139 | 6.8 | 140 | 2022-11-14 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 0 | 1151.9997 | 9.4222
SYL-S.1.RR.1099.1 | 24504209151165 | South Surma, Silam West Para, Sadek Member | 2019-09-07 | LX1011 | 16.5 | 66 | 16.5 | 67 | 2022-01-01 | 2022-11-14 | GS |  |  | 0 |  |  |  |  | 16.5 | 16.5 | 0.99 | 0.99 | 0.0007168 | 100% | 0% | 0.99 | 0.99 | 0.0011869 | 28 | 0.019846 | 0.019846 |  | 0 | 0 | 7608 | 1151.9997 | 173.8519
SYL-S.1.RR.1100.1 | 24521889152535 | Gotatikor, Pathanpara, Acharjo Para, Sunil Achajo | 2019-09-09 | LX1011 | 19.2 | 86 | 18.7 | 87 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 18.7 | 18.7 | 1.122 | 1.122 | 0.0007168 | 100% | 0% | 1.122 | 1.122 | 0.0011869 | 28 | 0.022492 | 0.022492 |  | 0 | 0 | 7512 | 1247.9997 | 197.0322
SYL-S.1.RR.1101.1 | 24522349152542 | Gotatikor, Pathanpara, Acharjo Para, Gonesh Achajo | 2019-09-09 | LX1011 | 12.6 | 88 | 12.6 | 89 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7512 | 1247.9997 | 132.7597
SYL-S.1.RR.1102.1 | 24522269152555 | Gotatikor, Pathanpara, Acharjo Para, Bot Acharjo | 2019-09-09 | LX1011 | 7.2 | 90 | 7.2 | 91 | 2022-01-01 | 2022-11-10 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7512 | 1247.9997 | 75.8627
SYL-S.1.RR.1103.1 | 24513809150494 | South Surma, Telibazar, Bolda,Nurul Hossain | 2019-09-11 | MN1032 | 17.2 | 71 | 17.8 | 72 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 17.8 | 17.8 | 1.068 | 1.068 | 0.0007168 | 100% | 0% | 1.068 | 1.068 | 0.0011869 | 28 | 0.02141 | 0.02141 |  | 0 | 0 | 7632 | 1127.9997 | 187.5494
SYL-S.1.RR.1104.1 | 24513129150545 | South Surma, Telibazar, Mizanur Rahman | 2019-09-11 | MN1032 | 27.6 | 77 | 26.4 | 78 | 2022-01-01 | 2022-11-15 | GS |  |  | 0 |  |  |  |  | 26.4 | 26.4 | 1.584 | 1.584 | 0.0007168 | 100% | 0% | 1.584 | 1.584 | 0.0011869 | 28 | 0.031754 | 0.031754 |  | 0 | 0 | 7632 | 1127.9997 | 278.1631
SYL-S.1.RR.1105.1 | 24521729151557 | South Surma, Musargaon, Ifat Villa | 2019-09-11 | MN1032 | 4.7 | 81 | 4.7 | 82 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7656 | 1103.9997 | 49.5215
SYL-S.1.RR.1105.2 | 24521729151557 | South Surma, Musargaon, Ifat Villa | 2021-03-02 | NQ1007 | 6.1 | 240 | 6.1 | 241 | 2022-01-01 | 2022-11-16 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7656 | 1103.9997 | 64.2725
SYL-W.1.CR.1.1 | 24534409151012 | South Kajolshah, Nobab Road, Kafe Taj Restaurant | 2019-08-21 | NQ1011 | 12.5 | 169 | 12.5 | 170 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7992 | 767.9997 | 131.706
SYL-W.1.RR.1.1 | 24544389149524 | Sylhet, Akhalia, University Gate, Saha Sekendar Abashik Elaka, Ishan Villa, H# 53 | 2019-01-23 | NQ1002 | 19 | 78 | 19 | 79 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 0 | 0 | 8280 | 479.9997 | 200.1931
SYL-W.1.RR.2.1 | 24544359150372 | Sylhet, Akhalia, Nawapara, B.G.B School Road, Md. Borhan Uddin, | 2019-01-23 | NQ1002 | 30 | 80 | 30 | 81 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 30 | 30 | 1.8 | 1.8 | 0.0007168 | 100% | 0% | 1.8 | 1.8 | 0.0011869 | 28 | 0.036084 | 0.036084 |  | 0 | 0 | 7800 | 959.9997 | 316.0944
SYL-W.1.RR.2.2 | 24544359150372 | Sylhet, Akhalia, Nawapara, B.G.B School Road, Md. Borhan Uddin, | 2021-10-20 | NQ1007 | 6.6 | 60 | 6.6 | 61 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7800 | 959.9997 | 69.5408
SYL-W.1.RR.3.1 | 24544539150380 | Sylhet, Akhalia, Nawapara, Block-A, Momo Villa, Hazi Abdul Manaf | 2019-01-23 | NQ1002 | 3.4 | 82 | 3.4 | 83 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7800 | 959.9997 | 35.824
SYL-W.1.RR.4.1 | 24545239150387 | Sylhet, Akhalia, Nawapara, Haque Palace, Momin | 2019-01-23 | NQ1002 | 7.9 | 84 | 7.9 | 85 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7800 | 959.9997 | 83.2382
SYL-W.1.RR.5.1 | 24545079150383 | Sylhet, Akhalia, Nawapara, Mohammad Khokon | 2019-01-23 | NQ1002 | 1.8 | 86 | 1.7 | 87 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7800 | 959.9997 | 17.912
SYL-W.1.RR.6.1 | 24545159150396 | Sylhet, Akhalia, Nawapara, Hazi Villa, Masuk Mia | 2019-01-23 | NQ1002 | 9.9 | 88 | 9.9 | 89 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7800 | 959.9997 | 104.3112
SYL-W.1.RR.7.1 | 24545269150409 | Sylhet, Akhalia, Nawapara, Jogrul | 2019-01-23 | NQ1002 | 2.4 | 90 | 2.4 | 91 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7800 | 959.9997 | 25.2876
SYL-W.1.RR.8.1 | 24545349150416 | Sylhet, Akhalia, Nawapara, City Model School | 2019-01-23 | NQ1002 | 9.7 | 92 | 9.5 | 93 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7800 | 959.9997 | 100.0966
SYL-W.1.RR.9.1 | 24545379150419 | Sylhet, Akhalia, Nawapara, Kholil Mia | 2019-01-23 | NQ1002 | 2.1 | 96 | 2.1 | 97 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7800 | 959.9997 | 22.1266
SYL-W.1.RR.10.1 | 24545469150429 | Sylhet, Akhalia, Nawapara, Azom Ali | 2019-01-23 | NQ1002 | 3 | 98 | 3 | 99 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7800 | 959.9997 | 31.6094
SYL-W.1.RR.11.1 | 24543669151122 | Sylhet, Pathantola, Al-amin Road, Touhid Mia | 2019-08-07 | NQ1008 | 5 | 648 | 5 | 649 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7848 | 911.9997 | 52.6824
SYL-W.1.RR.12.1 | 24543609151127 | Sylhet, Pathantola, Al-amin Road, Shamsuzzaman Loskor | 2019-08-07 | NQ1008 | 6.1 | 650 | 6.1 | 651 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7848 | 911.9997 | 64.2725
SYL-W.1.RR.13.1 | 24543549151130 | Sylhet, Pathantola, Al-amin Road, Rois Mia | 2019-08-07 | NQ1008 | 3.1 | 652 | 3.2 | 653 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7848 | 911.9997 | 33.7167
SYL-W.1.RR.14.1 | 24543239151211 | Sylhet, West Subid Bazar, Nirjor Lovely Road, Mirza Caretaker | 2019-08-07 | NQ1008 | 12 | 654 | 12 | 655 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7848 | 911.9997 | 126.4378
SYL-W.1.RR.15.1 | 24543179151209 | Sylhet, West Subid Bazar, Nirjor Lovely Road, Beside Abid Complex | 2019-08-07 | NQ1008 | 6 | 656 | 6 | 657 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7848 | 911.9997 | 63.2189
SYL-W.1.RR.16.1 | 24542129151113 | Sylhet, Uttor Bagbari, Toiobur Rohman | 2019-08-08 | NQ1008 | 10.7 | 680 | 10.7 | 681 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7920 | 839.9997 | 112.7403
SYL-W.1.RR.17.1 | 24542359151118 | Sylhet, Uttor Bagbari, Billal Ahmed Chowdhury | 2019-08-08 | NQ1008 | 8.5 | 682 | 8.5 | 683 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7920 | 839.9997 | 89.5601
SYL-W.1.RR.18.1 | 24542599151036 | Sylhet, Uttor Bagbari, Promukto Akota, Nurunnasa Hasan | 2019-08-08 | NQ1008 | 11.6 | 684 | 11.6 | 685 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7824 | 935.9997 | 122.2232
SYL-W.1.RR.19.1 | 24542819151043 | Sylhet, Uttor Bagbari, Promukto Akota, Mina Vila | 2019-08-08 | NQ1008 | 3 | 686 | 3 | 687 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7824 | 935.9997 | 31.6094
SYL-W.1.RR.20.1 | 24542649151034 | Sylhet, Uttor Bagbari, Promukto Akota, Abdul Motin Chowdhury | 2019-08-08 | NQ1008 | 13.7 | 688 | 13.3 | 689 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7824 | 935.9997 | 140.1352
SYL-W.1.RR.21.1 | 24542589150133 | Sylhet, Akhalia, Surma R/A, Block-A, Road # 2, Renesha, H # 15, Somoti Chowdrory | 2019-01-23 | NQ1009 | 3.2 | 38 | 3 | 39 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7824 | 935.9997 | 31.6094
SYL-W.1.RR.22.1 | 24542559150227 | Sylhet, Akhalia, Surma R/A, Block-B, Road # 2, Renesha, H # 23, Abdus Jabbar | 2019-01-23 | NQ1009 | 1.6 | 40 | 1.6 | 41 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7824 | 935.9997 | 16.8584
SYL-W.1.RR.23.1 | 24542559150234 | Sylhet, Akhalia, Surma R/A, Block-B, Road # 2, Renesha, H # 22, Mohibur Rahman | 2019-01-23 | NQ1009 | 8 | 42 | 7.9 | 43 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7824 | 935.9997 | 83.2382
SYL-W.1.RR.24.1 | 24542599150239 | Sylhet, Akhalia, Surma R/A, Block-B, Road # 2, Renesha, H # 18, Md. Akmol Hossen | 2019-01-23 | NQ1009 | 1.2 | 44 | 1.1 | 45 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7824 | 935.9997 | 11.5901
SYL-W.1.RR.25.1 | 24542479150173 | Sylhet, Akhalia, Surma R/A, Block-A, Road # 3, Renesha, H # 98, Sumon Vila | 2019-01-23 | NQ1009 | 1.2 | 46 | 1.2 | 47 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7824 | 935.9997 | 12.6438
SYL-W.1.RR.26.1 | 24542339150145 | Sylhet, Akhalia, Surma R/A, Block-A, Road # 4, Nurul Haque Siddik | 2019-01-23 | NQ1009 | 11.5 | 48 | 11.5 | 49 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7824 | 935.9997 | 121.1695
SYL-W.1.RR.27.1 | 24542759151020 | Akota North Bog Bari, Sudip Ronjon Roy | 2019-08-07 | NQ1008 | 9.7 | 658 | 9.8 | 659 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7824 | 935.9997 | 103.2575
SYL-W.1.RR.28.1 | 24542799151032 | Akota North Bog Bari, Chentu | 2019-08-07 | NQ1008 | 10.1 | 660 | 10.1 | 661 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7824 | 935.9997 | 106.4185
SYL-W.1.RR.28.2 | 24542799151032 | Akota North Bog Bari, Chentu | 2019-08-07 | NQ1008 | 5.3 | 662 | 5.3 | 663 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7824 | 935.9997 | 55.8434
SYL-W.1.RR.29.1 | 24542919151027 | Akota North Bog Bari, Madina Tawor | 2019-08-07 | NQ1008 | 5.2 | 664 | 5.2 | 665 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7824 | 935.9997 | 54.7897
SYL-W.1.RR.30.1 | 24542819151012 | Akota North Bog Bari, Bissojit Dash | 2019-08-07 | NQ1008 | 2.3 | 666 | 2.3 | 667 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7824 | 935.9997 | 24.2339
SYL-W.1.RR.31.1 | 24543119150585 | Akota North Bog Bari, Garden Goli, H # 377/9 | 2019-08-07 | NQ1008 | 11.9 | 668 | 11.9 | 669 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7824 | 935.9997 | 125.3841
SYL-W.1.RR.32.1 | 24541679151060 | Akota North Bog Bari, Haji Lokman Ali Road, Syeda Mira Begum | 2019-08-07 | NQ1008 | 9.2 | 670 | 9.2 | 671 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7848 | 911.9997 | 96.9356
SYL-W.1.RR.33.1 | 24541449151034 | Akota North Bog Bari, Norsin Tilla, Monipuri Para, Khirsing | 2019-08-07 | NQ1008 | 11.3 | 672 | 11.3 | 673 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7848 | 911.9997 | 119.0622
SYL-W.1.RR.34.1 | 24541449151034 | Akota North Bog Bari, Norsin Tilla, Monipuri Para, Babu Shana | 2019-08-07 | NQ1008 | 3.6 | 674 | 3.6 | 675 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7848 | 911.9997 | 37.9313
SYL-W.1.RR.35.1 | 24541449151034 | Akota North Bog Bari, Norsin Tilla, Monipuri Para, Orjun Shing | 2019-08-07 | NQ1008 | 1.7 | 676 | 1.7 | 677 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7848 | 911.9997 | 17.912
SYL-W.1.RR.35.2 | 24541449151034 | Akota North Bog Bari, Norsin Tilla, Monipuri Para, Orjun Shing | 2019-08-07 | NQ1008 | 8.8 | 678 | 8.8 | 679 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7848 | 911.9997 | 92.721
SYL-W.1.RR.36.1 | 24541029150597 | Bagbari, Norshing, Tila Road, Promukto Akota, H # 136, M. A. Mannan | 2019-08-08 | NQ1008 | 2.6 | 690 | 2.6 | 691 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7848 | 911.9997 | 27.3949
SYL-W.1.RR.37.1 | 24541169150571 | Bagbari, Norshing, Tila Para, Promukto Akota, Khan Villa, H # 112 | 2019-08-08 | NQ1008 | 11.6 | 692 | 11.6 | 693 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7848 | 911.9997 | 122.2232
SYL-W.1.RR.38.1 | 24540479150548 | Bagbari, Atim School Road, Talukdar Manjil | 2019-08-17 | NQ1008 | 17.2 | 694 | 17.2 | 695 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 17.2 | 17.2 | 1.032 | 1.032 | 0.0007168 | 100% | 0% | 1.032 | 1.032 | 0.0011869 | 28 | 0.020688 | 0.020688 |  | 0 | 0 | 7848 | 911.9997 | 181.2275
SYL-W.1.RR.39.1 | 24540469150510 | Bagbari, Atim School Road, Motin Nibash | 2019-08-17 | NQ1008 | 12.2 | 696 | 12.2 | 697 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7848 | 911.9997 | 128.5451
SYL-W.1.RR.40.1 | 24540399150508 | Bagbari, Atim School Road, Haji Sabazuddin | 2019-08-17 | NQ1008 | 5.9 | 699 | 5.9 | 700 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7848 | 911.9997 | 62.1652
SYL-W.1.RR.40.2 | 24540399150508 | Bagbari, Atim School Road, Haji Sabazuddin | 2019-08-17 | NQ1008 | 12.6 | 701 | 12.6 | 702 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7848 | 911.9997 | 132.7597
SYL-W.1.RR.41.1 | 24543879150536 | Sylhet, West Pathantula, Haziyakub Ali Road, Mohammad Ali | 2019-01-23 | NQ1000 | 26.7 | 180 | 26.7 | 181 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 26.7 | 26.7 | 1.602 | 1.602 | 0.0007168 | 100% | 0% | 1.602 | 1.602 | 0.0011869 | 28 | 0.032115 | 0.032115 |  | 0 | 0 | 7848 | 911.9997 | 281.324
SYL-W.1.RR.42.1 | 24543879150536 | Sylhet, West Pathantula, Haziyakub Ali Road, Aris mia | 2019-01-23 | NQ1000 | 3.2 | 182 | 3.2 | 183 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7848 | 911.9997 | 33.7167
SYL-W.1.RR.43.1 | 24544089150571 | Sylhet, West Pathantula, Pallabi Road, A.Sattar | 2019-01-23 | NQ1000 | 12.7 | 184 | 12.7 | 185 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7848 | 911.9997 | 133.8133
SYL-W.1.RR.43.2 | 24544089150571 | Sylhet, West Pathantula, Pallabi Road, A.Sattar | 2019-01-23 | NQ1000 | 2.6 | 186 | 2.6 | 187 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7848 | 911.9997 | 27.3949
SYL-W.1.RR.44.1 | 24544279150591 | Sylhet, West Pathantula, Pallabi Road, Saheda Khatun | 2019-01-23 | NQ1000 | 1.4 | 190 | 1.4 | 191 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7848 | 911.9997 | 14.7511
SYL-W.1.RR.45.1 | 24544349151000 | Sylhet, West Pathantula, Pallabi Road, Mintu | 2019-01-23 | NQ1000 | 3.7 | 192 | 3.7 | 193 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7848 | 911.9997 | 38.985
SYL-W.1.RR.46.1 | 24544349151000 | Sylhet, West Pathantula, Pallabi Road, Moniruzzaman | 2019-01-23 | NQ1000 | 9.6 | 194 | 9.6 | 195 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7848 | 911.9997 | 101.1502
SYL-W.1.RR.47.1 | 24544499151008 | Sylhet, West Pathantula, Pallabi Road, Md. Abu Taher | 2019-01-23 | NQ1000 | 2.2 | 196 | 2.2 | 197 | 2022-01-01 | 2022-12-12 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 8280 | 479.9997 | 23.1803
SYL-W.1.RR.48.1 | 24544469151028 | Sylhet, West Pathantula, Pallabi Road, Zillur Rahman | 2019-01-23 | NQ1000 | 1.4 | 198 | 1.4 | 199 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7848 | 911.9997 | 14.7511
SYL-W.1.RR.49.1 | 24544859150588 | Sylhet, West Pathantula, Pallabi Road, Ador varities Store | 2019-01-23 | NQ1000 | 2 | 200 | 2 | 201 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7848 | 911.9997 | 21.073
SYL-W.1.RR.50.1 | 24543589151098 | West Surma, Pathantula, Sraboni R/A, Golap Khan | 2019-08-07 | MN1032 | 11.1 | 1 | 11.1 | 2 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7848 | 911.9997 | 116.9549
SYL-W.1.RR.51.1 | 24543459151101 | West Surma, Pathantula, Sraboni R/A, Abdul Hamid Chowdhuory | 2019-08-07 | MN1032 | 4.7 | 3 | 4.7 | 4 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7848 | 911.9997 | 49.5215
SYL-W.1.RR.52.1 | 24543239151100 | West Surma, Pathantula, Sraboni R/A, Md. Moyna Mia | 2019-08-07 | MN1032 | 3.8 | 5 | 3.8 | 6 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7848 | 911.9997 | 40.0386
SYL-W.1.RR.53.1 | 24543029151100 | West Surma, Pathantula, Sraboni R/A, Golam Shahadat Jewel | 2019-08-07 | MN1032 | 11 | 7 | 11 | 8 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7848 | 911.9997 | 115.9013
SYL-W.1.RR.54.1 | 24543029151100 | West Surma, Pathantula, Sraboni R/A, Monjur Mahmud | 2019-08-07 | MN1032 | 4.1 | 9 | 4.1 | 10 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7848 | 911.9997 | 43.1996
SYL-W.1.RR.55.1 | 24542899151121 | West Surma, Pathantula, Sraboni R/A, H # F-3, Md. Junayed | 2019-08-07 | MN1032 | 5.1 | 11 | 5.1 | 12 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7848 | 911.9997 | 53.7361
SYL-W.1.RR.56.1 | 24542739151094 | West Surma, Pathantula, Sraboni R/A, H # F-17, Abdul Mannan | 2019-08-07 | MN1032 | 1.9 | 13 | 1.9 | 14 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7848 | 911.9997 | 20.0193
SYL-W.1.RR.57.1 | 24543449151058 | West Surma, Pathantula, Nikunjo R/A, Road # 1, H # 2, Akbor Ali | 2019-08-08 | MN1032 | 8.2 | 29 | 7.6 | 30 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7848 | 911.9997 | 80.0773
SYL-W.1.RR.58.1 | 24543039151061 | West Surma, Pathantula, Nikunjo R/A, Road # 1, H # 13, Nayeem | 2019-08-08 | MN1032 | 10.9 | 33 | 10.9 | 34 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7848 | 911.9997 | 114.8476
SYL-W.1.RR.59.1 | 24542939151067 | West Surma, Pathantula, Nikunjo R/A, Road # 1, Asia Monjil | 2019-08-08 | MN1032 | 13.3 | 35 | 13.3 | 36 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7848 | 911.9997 | 140.1352
SYL-W.1.RR.60.1 | 24534909151243 | Bhatalia, Bhatalia Road, H # 27/B, Abdul High | 2019-08-19 | MN1032 | 5.6 | 95 | 5.6 | 96 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7944 | 815.9997 | 59.0043
SYL-W.1.RR.61.1 | 24543459150543 | Sylhet, Uttor Bagbari, Modina Market, Alise Lodge, Sazzad, H # 110 | 2019-01-23 | NQ1005 | 3 | 57 | 3.1 | 58 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 2064 | 0 | 5760 | 935.9997 | 24.9671
SYL-W.1.RR.61.2 | 24543459150541 | Sylhet, Uttor Bagbari, Modina Market, Alise Lodge, Sazzad, H # 110 | 2019-01-23 | NQ1005 | 2 | 59 | 2 | 60 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 2064 | 0 | 5760 | 935.9997 | 16.1078
SYL-W.1.RR.62.1 | 24543099150530 | Sylhet, Uttor Bagbari, Modina Residential Area, Kamal Ahmed | 2019-01-23 | NQ1005 | 3.2 | 61 | 3.2 | 62 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7824 | 935.9997 | 33.7167
SYL-W.1.RR.63.1 | 24543069150529 | Sylhet, Uttor Bagbari, Modina Residential Area, Abdul Mumin | 2019-01-23 | NQ1005 | 4.1 | 63 | 4.1 | 64 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7824 | 935.9997 | 43.1996
SYL-W.1.RR.64.1 | 24543199150522 | Sylhet, Uttor Bagbari, Modina Residential Area, Jajira Cattage, H # 42 | 2019-01-23 | NQ1005 | 12.2 | 67 | 12 | 68 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7824 | 935.9997 | 126.4378
SYL-W.1.RR.65.1 | 24543339150454 | Sylhet, Uttor Bagbari, Al-Modina Residential Area, Fazlul, H # 30 | 2019-01-23 | NQ1005 | 10 | 69 | 10 | 70 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7824 | 935.9997 | 105.3648
SYL-W.1.RR.66.1 | 24542429150510 | Sylhet, Uttor Bagbari, Akhra Goli, Abdur Rob Mia, H # 355 | 2019-01-23 | NQ1005 | 2.4 | 71 | 2.4 | 72 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7848 | 911.9997 | 25.2876
SYL-W.1.RR.66.2 | 24542429150510 | Sylhet, Uttor Bagbari, Akhra Goli, Abdur Rob Mia, H # 355 | 2019-01-23 | NQ1005 | 1.3 | 73 | 1.3 | 74 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 1.3 | 1.3 | 0.078 | 0.078 | 0.0007168 | 100% | 0% | 0.078 | 0.078 | 0.0011869 | 28 | 0.0015636 | 0.0015636 |  | 0 | 0 | 7848 | 911.9997 | 13.6974
SYL-W.1.RR.67.1 | 24543299151019 | Sylhet, West Pathantula, Nibas-B, H # 14, Hazi Mosharrof | 2019-08-07 | MN1032 | 4.3 | 17 | 4.3 | 18 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7848 | 911.9997 | 45.3069
SYL-W.1.RR.68.1 | 24543299151019 | Sylhet, West Pathantula, Nibas-B, Mayakunjo | 2019-08-07 | MN1032 | 6.8 | 19 | 6.8 | 20 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7848 | 911.9997 | 71.6481
SYL-W.1.RR.68.2 | 24543299151019 | Sylhet, West Pathantula, Nibas-B, Mayakunjo | 2021-02-23 | LU1001 | 4.9 | 217 | 4.9 | 218 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7848 | 911.9997 | 51.6288
SYL-W.1.RR.69.1 | 24543309151046 | Sylhet, West Pathantula, Nibas-B, Saleh | 2019-08-07 | MN1032 | 3.9 | 21 | 4 | 22 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7848 | 911.9997 | 42.1459
SYL-W.1.RR.70.1 | 24543679150560 | Sylhet, West Pathantula, Madina Market, Surmila | 2019-08-07 | MN1032 | 4.7 | 23 | 4.7 | 24 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7848 | 911.9997 | 49.5215
SYL-W.1.RR.71.1 | 24543679150560 | Sylhet, West Pathantula, Madina Market, Iqbal | 2019-08-07 | MN1032 | 6.1 | 25 | 6.1 | 26 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7848 | 911.9997 | 64.2725
SYL-W.1.RR.72.1 | 24543559150591 | Sylhet, Madina Market, Nibas-B, Aktar Ahmed, H # 20/2 | 2019-08-08 | MN1032 | 9.8 | 37 | 9.8 | 38 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7848 | 911.9997 | 103.2575
SYL-W.1.RR.73.1 | 24541219151081 | West Kajolshah, Sonar Bangla R/A, Khalek Chowdhury | 2019-08-08 | MN1032 | 6.8 | 39 | 6.8 | 40 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7848 | 911.9997 | 71.6481
SYL-W.1.RR.74.1 | 24540699151042 | West Kajolshah, Sonar Bangla R/A, Md.Sattar | 2019-08-17 | MN1032 | 42.9 | 41 | 42.9 | 42 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 42.9 | 42.9 | 2.574 | 2.574 | 0.0007168 | 100% | 0% | 2.574 | 2.574 | 0.0011869 | 28 | 0.0516 | 0.0516 |  | 0 | 0 | 7848 | 911.9997 | 452.015
SYL-W.1.RR.75.1 | 24540689151036 | West Kajolshah, Sonar Bangla R/A, Masuk | 2019-08-17 | MN1032 | 3.7 | 43 | 3.7 | 44 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7848 | 911.9997 | 38.985
SYL-W.1.RR.76.1 | 24540769151046 | West Kajolshah, Sonar Bangla R/A, Md.Ashok Mia | 2019-08-17 | MN1032 | 2.9 | 45 | 2.9 | 46 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7848 | 911.9997 | 30.5558
SYL-W.1.RR.77.1 | 24540799151039 | West Kajolshah, Sonar Bangla R/A, H # 38, Mojid | 2019-08-17 | MN1032 | 12.3 | 47 | 12.3 | 48 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7848 | 911.9997 | 129.5987
SYL-W.1.RR.78.1 | 24542809151164 | Subid Bazar, Sagordighir Par, H # 65 | 2019-08-07 | NQ1011 | 2.4 | 1 | 2.4 | 2 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7920 | 839.9997 | 25.2876
SYL-W.1.RR.79.1 | 24542659151190 | Subid Bazar, Sagordighir Par, Kader Villa | 2019-08-07 | NQ1011 | 11.5 | 3 | 11.5 | 4 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7920 | 839.9997 | 121.1695
SYL-W.1.RR.80.1 | 24542679151154 | Subid Bazar, Sagordighir Par, H # 67 | 2019-08-07 | NQ1011 | 4.1 | 5 | 4.1 | 6 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7920 | 839.9997 | 43.1996
SYL-W.1.RR.81.1 | 24542419151151 | Subid Bazar, Sagordighir Par, Somindro | 2019-08-07 | NQ1011 | 2 | 7 | 2 | 8 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7920 | 839.9997 | 21.073
SYL-W.1.RR.82.1 | 24542189151131 | Subid Bazar, Sagordighir Par, H # 85 | 2019-08-07 | NQ1011 | 6.3 | 9 | 5.9 | 10 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7920 | 839.9997 | 62.1652
SYL-W.1.RR.83.1 | 24541799151170 | Subid Bazar, Sagordighir Par, Sadik | 2019-08-07 | NQ1011 | 7.7 | 11 | 7.7 | 12 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7920 | 839.9997 | 81.1309
SYL-W.1.RR.84.1 | 24542639150582 | Sylhet, North Baghbari, H # 224 | 2019-08-07 | NQ1011 | 3.9 | 13 | 3.9 | 14 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7824 | 935.9997 | 41.0923
SYL-W.1.RR.85.1 | 24542309150577 | Sylhet, North Baghbari, Okil Dhar | 2019-08-07 | NQ1011 | 5.7 | 15 | 5.7 | 16 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7824 | 935.9997 | 60.0579
SYL-W.1.RR.86.1 | 24542239150582 | Sylhet, North Baghbari, Sotto Ranjan | 2019-08-07 | NQ1011 | 8.3 | 17 | 8.3 | 18 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7824 | 935.9997 | 87.4528
SYL-W.1.RR.87.1 | 24542249150571 | Sylhet, North Baghbari, Ashish | 2019-08-07 | NQ1011 | 3.6 | 19 | 3.6 | 20 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7824 | 935.9997 | 37.9313
SYL-W.1.RR.87.2 | 24542249150571 | Sylhet, North Baghbari, Ashish | 2021-10-23 | NQ1007 | 10.3 | 65 | 10.3 | 66 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7824 | 935.9997 | 108.5258
SYL-W.1.RR.88.1 | 24542189150591 | Sylhet, North Baghbari, Jitendro Kumar Roy | 2019-08-07 | NQ1011 | 2.6 | 21 | 2.6 | 22 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7824 | 935.9997 | 27.3949
SYL-W.1.RR.89.1 | 24541619151004 | Sylhet, Bagbari, Norshing Tila, Promukto Akota, H # 270 | 2019-08-08 | NQ1011 | 4.2 | 33 | 4.2 | 34 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7848 | 911.9997 | 44.2532
SYL-W.1.RR.90.1 | 24541279151036 | Sylhet, Bagbari, Promukto Akota, H # 61/A | 2019-08-08 | NQ1011 | 67.2 | 35 | 65.9 | 36 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 65.9 | 65.9 | 3.954 | 3.954 | 0.0007168 | 100% | 0% | 3.954 | 3.954 | 0.0011869 | 28 | 0.079264 | 0.079264 |  | 0 | 0 | 7848 | 911.9997 | 694.3541
SYL-W.1.RR.91.1 | 24541399151015 | Sylhet, Bagbari, Promukto Akota, H # 60/3 | 2019-08-08 | NQ1011 | 8.8 | 37 | 8.9 | 38 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7848 | 911.9997 | 93.7747
SYL-W.1.RR.92.1 | 24540069150479 | South Bagbari, Shamimabadh R/A, Rd # 2, Holiview - 13 | 2019-08-18 | NQ1011 | 10.5 | 73 | 10.5 | 74 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7968 | 791.9997 | 110.6331
SYL-W.1.RR.93.1 | 24540069150479 | South Bagbari, Shamimabadh R/A, Rd # 2, Holiview - 14 | 2019-08-18 | NQ1011 | 6.8 | 75 | 6.8 | 76 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7968 | 791.9997 | 71.6481
SYL-W.1.RR.94.1 | 24535909150493 | South Bagbari, Shamimabadh R/A, Moin Uddin College Road, Md, Yaor Miah | 2019-08-18 | NQ1011 | 8.1 | 77 | 8.1 | 78 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7968 | 791.9997 | 85.3455
SYL-W.1.RR.95.1 | 24535949150473 | South Bagbari, Shamimabadh R/A, Hazi Abdul Mojid Road, Holiview - 28 | 2019-08-18 | NQ1011 | 5.2 | 79 | 5.2 | 80 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7968 | 791.9997 | 54.7897
SYL-W.1.RR.96.1 | 24535789150485 | Bagbari, Shamimabadh, Kutub Uddin Road, H # 1 | 2019-08-18 | NQ1011 | 6.7 | 81 | 6.7 | 82 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7968 | 791.9997 | 70.5944
SYL-W.1.RR.96.2 | 24535789150485 | Bagbari, Shamimabadh, Kutub Uddin Road, H # 1 | 2021-02-23 | NQ1007 | 5.3 | 216 | 5.3 | 217 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7968 | 791.9997 | 55.8434
SYL-W.1.RR.97.1 | 24535529150479 | South Bagbari, Shamimabadh R/A, Mohila College Road, Rashid Monjil | 2019-08-19 | NQ1011 | 9.8 | 83 | 9.8 | 84 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7968 | 791.9997 | 103.2575
SYL-W.1.RR.98.1 | 24535399150480 | South Bagbari, Shamimabadh R/A, Mohila College Road, Ashiyan Monjil | 2019-08-19 | NQ1011 | 11.3 | 85 | 11.3 | 86 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7968 | 791.9997 | 119.0622
SYL-W.1.RR.99.1 | 24540159150456 | South Bagbari, Shamimabadh R/A, Rd # 2, H # 116, Ishak Villa | 2019-08-19 | NQ1011 | 6.8 | 87 | 6.8 | 88 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7968 | 791.9997 | 71.6481
SYL-W.1.RR.100.1 | 24535599150432 | South Bagbari, Shamimabadh R/A, Rd # 2, H # 134, Khadija Nir | 2019-08-19 | NQ1011 | 8.7 | 89 | 8.8 | 90 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7968 | 791.9997 | 92.721
SYL-W.1.RR.101.1 | 24541189150554 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Monu Ahmed | 2019-08-17 | NQ1011 | 4 | 39 | 4.1 | 40 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7848 | 911.9997 | 43.1996
SYL-W.1.RR.102.1 | 24541189150554 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Eskendar Ali | 2019-08-17 | NQ1011 | 10.8 | 41 | 10.8 | 42 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7848 | 911.9997 | 113.794
SYL-W.1.RR.103.1 | 24541319150547 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Johirul Islam Afsar | 2019-08-17 | NQ1011 | 9.6 | 43 | 9.6 | 44 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7848 | 911.9997 | 101.1502
SYL-W.1.RR.104.1 | 24541269150589 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Hazi Mojammel Ali | 2019-08-17 | NQ1011 | 4 | 45 | 4 | 46 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7848 | 911.9997 | 42.1459
SYL-W.1.RR.105.1 | 24541399150587 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Sunil Kanto Das | 2019-08-17 | NQ1011 | 3.8 | 47 | 3.8 | 48 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7848 | 911.9997 | 40.0386
SYL-W.1.RR.106.1 | 24541509150565 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Kollan Broto Pranto Das | 2019-08-17 | NQ1011 | 6 | 49 | 6 | 50 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7848 | 911.9997 | 63.2189
SYL-W.1.RR.107.1 | 24541569150565 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Beside H # 183/44 | 2019-08-17 | NQ1011 | 10.3 | 51 | 10.3 | 52 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7848 | 911.9997 | 108.5258
SYL-W.1.RR.108.1 | 24541659150542 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Kajol Chokroborty | 2019-08-17 | NQ1011 | 10.5 | 53 | 10.5 | 54 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7848 | 911.9997 | 110.6331
SYL-W.1.RR.109.1 | 24541789150546 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Goli # 12, Shofiqur Rohman | 2019-08-18 | NQ1008 | 11.4 | 704 | 11.4 | 705 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7848 | 911.9997 | 120.1159
SYL-W.1.RR.110.1 | 24541789150549 | Sylhet, Norsingtila, Bagbari, Promukto Akota, Goli # 12, Hrishy Keshdhar | 2019-08-18 | NQ1008 | 13.5 | 706 | 13.5 | 707 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7848 | 911.9997 | 142.2425
SYL-W.1.RR.111.1 | 24541109150540 | Sylhet, Norsingtila, West Bagbari, Promukto Akota, Anwar Hosen | 2019-08-18 | NQ1008 | 4 | 708 | 4 | 709 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7848 | 911.9997 | 42.1459
SYL-W.1.RR.112.1 | 24541149150528 | Sylhet, Norsingtila, West Bagbari, Promukto Akota, Kholilur Rohman | 2019-08-18 | NQ1008 | 8 | 710 | 8 | 711 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7848 | 911.9997 | 84.2919
SYL-W.1.RR.113.1 | 24541589150511 | Sylhet, Norsingtila, West Bagbari, Promukto Akota, Samsul Islam | 2019-08-18 | NQ1008 | 9.7 | 712 | 9.7 | 713 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7848 | 911.9997 | 102.2039
SYL-W.1.RR.114.1 | 24541879150525 | Sylhet, Norsingtila, West Bagbari, Promukto Akota, Dilluba | 2019-08-18 | NQ1008 | 11.8 | 714 | 11.8 | 715 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7848 | 911.9997 | 124.3305
SYL-W.1.RR.114.2 | 24541879150525 | Sylhet, Norsingtila, West Bagbari, Promukto Akota, Dilluba | 2019-08-18 | NQ1008 | 7.5 | 716 | 7.5 | 717 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7848 | 911.9997 | 79.0236
SYL-W.1.RR.115.1 | 24541769150486 | Sylhet, Norsingtila, West Bagbari, Promukto Akota, Shawon Das | 2019-08-18 | NQ1008 | 13.1 | 718 | 13.1 | 719 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7848 | 911.9997 | 138.0279
SYL-W.1.RR.116.1 | 24534379151094 | Sylhet, Laladeghir West Par, Kolo Kakoli R/A, Md. Ahbab Mia | 2019-08-19 | NQ1008 | 14.7 | 740 | 14.7 | 741 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7992 | 767.9997 | 154.8863
SYL-W.1.RR.117.1 | 24534489151058 | Sylhet, Laladeghir West Par, Kolo Kakoli R/A, Abdur Rob | 2019-08-19 | NQ1008 | 11 | 744 | 11 | 745 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7992 | 767.9997 | 115.9013
SYL-W.1.RR.117.2 | 24534489151058 | Sylhet, Laladeghir West Par, Kolo Kakoli R/A, Abdur Rob | 2021-10-28 | NQ1007 | 10.1 | 71 | 10.1 | 72 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7992 | 767.9997 | 106.4185
SYL-W.1.RR.118.1 | 24534399151052 | Sylhet, Laladeghir West Par, Kolo Kakoli R/A, Abdur Rob | 2019-08-19 | NQ1008 | 2.1 | 746 | 2.1 | 747 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7992 | 767.9997 | 22.1266
SYL-W.1.RR.119.1 | 24534489151156 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Azizur Rohman | 2019-08-19 | NQ1008 | 18.5 | 748 | 17.3 | 749 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 17.3 | 17.3 | 1.038 | 1.038 | 0.0007168 | 100% | 0% | 1.038 | 1.038 | 0.0011869 | 28 | 0.020808 | 0.020808 |  | 0 | 0 | 7944 | 815.9997 | 182.2811
SYL-W.1.RR.120.1 | 24534679151158 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Hazi Siddique | 2019-08-19 | NQ1008 | 11.8 | 750 | 11.8 | 751 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7944 | 815.9997 | 124.3305
SYL-W.1.RR.121.1 | 24534739151135 | Sylhet, Laladeghir North Par, Kolo Kakoli R/A, Nihar Ronjon Deb | 2019-08-19 | NQ1008 | 9.8 | 752 | 9.2 | 753 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7944 | 815.9997 | 96.9356
SYL-W.1.RR.122.1 | 24534939151144 | Sylhet, Laladeghir North Par, Kolo Kakoli R/A, Mojammel Ali | 2019-08-19 | NQ1008 | 8.5 | 754 | 8.5 | 755 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7944 | 815.9997 | 89.5601
SYL-W.1.RR.123.1 | 24534939151144 | Sylhet, Laladeghir North Par, Kolo Kakoli R/A, Mojammel Ali | 2019-08-19 | NQ1008 | 9 | 756 | 9 | 757 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7944 | 815.9997 | 94.8283
SYL-W.1.RR.124.1 | 24534159151157 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Otul Mia | 2019-08-19 | NQ1008 | 11.9 | 758 | 11.9 | 759 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7944 | 815.9997 | 125.3841
SYL-W.1.RR.125.1 | 24534159151157 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Batil Mia | 2019-08-19 | NQ1008 | 3.9 | 760 | 3.9 | 761 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7944 | 815.9997 | 41.0923
SYL-W.1.RR.126.1 | 24534119151179 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Abdul Jobbar Minu Mia | 2019-08-19 | NQ1008 | 5.3 | 762 | 5.3 | 763 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7944 | 815.9997 | 55.8434
SYL-W.1.RR.127.1 | 24534119151179 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Abdul Rohman | 2019-08-19 | NQ1008 | 2.8 | 764 | 2.8 | 765 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7944 | 815.9997 | 29.5021
SYL-W.1.RR.128.1 | 24534059151206 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Monir Mia | 2019-08-19 | NQ1008 | 4.7 | 766 | 4.7 | 767 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7944 | 815.9997 | 49.5215
SYL-W.1.RR.128.2 | 24534059151206 | Sylhet, Laladeghir East Par, Kolo Kakoli R/A, Monir Mia | 2021-02-24 | LU1001 | 6.9 | 222 | 6.9 | 223 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7944 | 815.9997 | 72.7017
SYL-W.1.RR.129.1 | 24534299151222 | Sylhet, Quarpar R/A, Abdul Khalek | 2019-08-19 | NQ1008 | 9.8 | 768 | 9.8 | 769 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.8 | 9.8 | 0.588 | 0.588 | 0.0007168 | 100% | 0% | 0.588 | 0.588 | 0.0011869 | 28 | 0.011787 | 0.011787 |  | 0 | 0 | 7944 | 815.9997 | 103.2575
SYL-W.1.RR.130.1 | 24534299151222 | Sylhet, Quarpar R/A, Abdul Khalek | 2019-08-19 | NQ1008 | 5.7 | 770 | 5.7 | 771 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7944 | 815.9997 | 60.0579
SYL-W.1.RR.131.1 | 24533599151259 | Sylhet, Kuarpar, Samad | 2019-08-20 | NQ1008 | 9.6 | 788 | 8.8 | 789 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7992 | 767.9997 | 92.721
SYL-W.1.RR.132.1 | 24533659151267 | Sylhet, Kuarpar, Juel Mia | 2019-08-20 | NQ1008 | 8.6 | 790 | 8.1 | 791 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7992 | 767.9997 | 85.3455
SYL-W.1.RR.133.1 | 24533679151278 | Sylhet, Kuarpar, Joglu Mia | 2019-08-20 | NQ1008 | 8.1 | 792 | 8.1 | 793 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7992 | 767.9997 | 85.3455
SYL-W.1.RR.133.2 | 24533679151278 | Sylhet, Kuarpar, Joglu Mia | 2019-08-20 | NQ1008 | 7 | 794 | 7 | 795 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7992 | 767.9997 | 73.7554
SYL-W.1.RR.134.1 | 24533329151259 | Sylhet, Kuarpar, Engulal Road, Forida | 2019-08-20 | NQ1008 | 10.9 | 796 | 10.5 | 797 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7992 | 767.9997 | 110.6331
SYL-W.1.RR.135.1 | 24533079151245 | Sylhet, Kuarpar, Engulal Road, Emdadul Haque | 2019-08-20 | NQ1008 | 5.8 | 798 | 5.3 | 799 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7992 | 767.9997 | 55.8434
SYL-W.1.RR.136.1 | 24533279151280 | Sylhet, Kuarpar, Engulal Road, Abdul Mannan | 2019-08-20 | NQ1008 | 8.6 | 800 | 8 | 801 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7992 | 767.9997 | 84.2919
SYL-W.1.RR.137.1 | 24533249151282 | Sylhet, Kuarpar, Engulal Road, Abdur Rouf Lal Mia | 2019-08-20 | NQ1008 | 8.8 | 802 | 8.5 | 803 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7992 | 767.9997 | 89.5601
SYL-W.1.RR.138.1 | 24533099151291 | Sylhet, Kuarpar, Engulal Road, Lokman Hosen | 2019-08-20 | NQ1008 | 6 | 804 | 6 | 805 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7992 | 767.9997 | 63.2189
SYL-W.1.RR.138.2 | 24533099151291 | Sylhet, Kuarpar, Engulal Road, Lokman Hosen | 2019-08-20 | NQ1008 | 4.2 | 808 | 4.2 | 809 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7992 | 767.9997 | 44.2532
SYL-W.1.RR.139.1 | 24533819151325 | Sylhet, Kuarpar, Hazi Montazur Rohman | 2019-08-21 | NQ1008 | 2.8 | 839 | 2.8 | 840 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7992 | 767.9997 | 29.5021
SYL-W.1.RR.140.1 | 24533589151339 | Sylhet, Kuarpar, Salma Masud | 2019-08-21 | NQ1008 | 11.2 | 843 | 11.2 | 844 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7992 | 767.9997 | 118.0086
SYL-W.1.RR.141.1 | 24533939151343 | Sylhet, Lamabazar, Chayatoru, Moinuddin Ahmed | 2019-08-21 | NQ1008 | 4.8 | 846 | 4.8 | 847 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7992 | 767.9997 | 50.5751
SYL-W.1.RR.142.1 | 24533969151333 | Sylhet, Lamabazar, Chayatoru, H # 56/1 | 2019-08-21 | NQ1008 | 2.9 | 848 | 2.9 | 849 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7992 | 767.9997 | 30.5558
SYL-W.1.RR.144.1 | 24533139151157 | Sylhet, Sheikhghat, Vangatikorpara, Mohitosh Rojon Das | 2019-08-21 | NQ1008 | 2.8 | 851 | 2.8 | 852 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7944 | 815.9997 | 29.5021
SYL-W.1.RR.145.1 | 24533149151146 | Sylhet, Sheikhghat, Vangatikorpara, Ojid Kumar Deb | 2019-08-21 | NQ1008 | 11 | 853 | 11 | 854 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7944 | 815.9997 | 115.9013
SYL-W.1.RR.146.1 | 24532959151175 | Sylhet, Sheikhghat, Suvessa, Block - E, Rd # 16, Forsal Ahmed Fojlu | 2019-08-21 | NQ1008 | 2.9 | 855 | 2.9 | 856 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7944 | 815.9997 | 30.5558
SYL-W.1.RR.147.1 | 24532879151179 | Sylhet, Sheikhghat, Suvessa, Block - E, Rd # 16, Birut Comissoner | 2019-08-21 | NQ1008 | 9.4 | 857 | 9.4 | 858 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7944 | 815.9997 | 99.0429
SYL-W.1.RR.148.1 | 24532989151050 | Sylhet, West Sheikhghat, Nobab Road, H # 196 | 2019-08-22 | NQ1008 | 2.2 | 886 | 2.2 | 887 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7992 | 767.9997 | 23.1803
SYL-W.1.RR.149.1 | 24533949151022 | Sylhet, West Sheikhghat, Nobab Road, Mosjid Quarter | 2019-08-22 | NQ1008 | 10.3 | 888 | 10.3 | 889 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7992 | 767.9997 | 108.5258
SYL-W.1.RR.149.2 | 24533949151022 | Sylhet, West Sheikhghat, Nobab Road, Mosjid Quarter | 2019-08-22 | NQ1008 | 9.7 | 890 | 9.7 | 891 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7992 | 767.9997 | 102.2039
SYL-W.1.RR.150.1 | 24533959151041 | Sylhet, West Sheikhghat, Nobab Road, Seraj Mia | 2019-08-22 | NQ1008 | 3.8 | 892 | 3.8 | 893 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7992 | 767.9997 | 40.0386
SYL-W.1.RR.151.1 | 24541659150481 | Bagbari, Promukto R/A, Rd # 5, H # 174/4 | 2019-08-18 | NQ1008 | 13.4 | 720 | 13.1 | 721 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 13.1 | 13.1 | 0.786 | 0.786 | 0.0007168 | 100% | 0% | 0.786 | 0.786 | 0.0011869 | 28 | 0.015757 | 0.015757 |  | 0 | 0 | 7848 | 911.9997 | 138.0279
SYL-W.1.RR.151.2 | 24541659150481 | Bagbari, Promukto R/A, Rd # 5, H # 174/4 | 2019-08-18 | NQ1008 | 7.8 | 722 | 7.3 | 723 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7848 | 911.9997 | 76.9163
SYL-W.1.RR.152.1 | 24541689150473 | Bagbari, Promukto R/A, Rd # 5, Onil Dash | 2019-08-18 | NQ1008 | 5.1 | 728 | 5.1 | 729 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7848 | 911.9997 | 53.7361
SYL-W.1.RR.153.1 | 24535469151089 | Bagbari, South Kajolshaha R/A, Rd # 4, H # 170 | 2019-08-19 | NQ1008 | 32.1 | 730 | 32.1 | 731 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 32.1 | 32.1 | 1.926 | 1.926 | 0.0007168 | 100% | 0% | 1.926 | 1.926 | 0.0011869 | 28 | 0.03861 | 0.03861 |  | 0 | 0 | 7920 | 839.9997 | 338.221
SYL-W.1.RR.153.2 | 24535469151089 | Bagbari, South Kajolshaha R/A, Rd # 4, H # 170 | 2019-08-19 | NQ1008 | 11.9 | 732 | 11.9 | 733 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7920 | 839.9997 | 125.3841
SYL-W.1.RR.154.1 | 24535189151080 | Bagbari, South Kajolshaha R/A, Rd # 4, H # 166/3 | 2019-08-19 | NQ1008 | 3.5 | 734 | 3.5 | 735 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7920 | 839.9997 | 36.8777
SYL-W.1.RR.155.1 | 24534969151047 | Bagbari, Kajolshaha R/A, Nobab Road, Moynul Isalm | 2019-08-19 | NQ1008 | 11.4 | 736 | 11.4 | 737 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7992 | 767.9997 | 120.1159
SYL-W.1.RR.156.1 | 24534969151047 | Bagbari, Kajolshaha R/A, Nobab Road, Riadul Islam | 2019-08-19 | NQ1008 | 12.8 | 738 | 12.8 | 739 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7992 | 767.9997 | 134.867
SYL-W.1.RR.157.1 | 24533519151193 | Vatatikar, Kuarpar, Rojonigondha R/A, H # 10 | 2019-08-20 | NQ1008 | 12 | 772 | 12.1 | 773 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7944 | 815.9997 | 127.4914
SYL-W.1.RR.157.2 | 24533519151193 | Vatatikar, Kuarpar, Rojonigondha R/A, H # 10 | 2019-08-20 | NQ1008 | 2.7 | 774 | 2.7 | 775 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7944 | 815.9997 | 28.4485
SYL-W.1.RR.157.3 | 24533519151193 | Vatatikar, Kuarpar, Rojonigondha R/A, H # 10 | 2019-08-20 | NQ1008 | 7.5 | 776 | 7.5 | 777 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7944 | 815.9997 | 79.0236
SYL-W.1.RR.158.1 | 24533559151183 | Vatatikar, Sriti R/A, Fokrul Ahammed | 2019-08-20 | NQ1008 | 12.3 | 778 | 12.3 | 779 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7944 | 815.9997 | 129.5987
SYL-W.1.RR.159.1 | 24533589151175 | Vatatikar, Sriti R/A, Somseruddin | 2019-08-20 | NQ1008 | 4.5 | 780 | 4.5 | 781 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7944 | 815.9997 | 47.4142
SYL-W.1.RR.160.1 | 24533689151161 | Vatatikar, Sriti R/A, Nurul Haque Gong | 2019-08-20 | NQ1008 | 13.4 | 782 | 13.5 | 783 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.5 | 13.5 | 0.81 | 0.81 | 0.0007168 | 100% | 0% | 0.81 | 0.81 | 0.0011869 | 28 | 0.016238 | 0.016238 |  | 0 | 0 | 7944 | 815.9997 | 142.2425
SYL-W.1.RR.161.1 | 24533609151152 | Vatatikar, Sriti R/A, Samsul Haque | 2019-08-20 | NQ1008 | 13.7 | 784 | 13.4 | 785 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7944 | 815.9997 | 141.1888
SYL-W.1.RR.162.1 | 24533639151146 | Vatatikar, Sriti R/A, H # 13 | 2019-08-20 | NQ1008 | 7.7 | 786 | 7.7 | 787 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7944 | 815.9997 | 81.1309
SYL-W.1.RR.163.1 | 24535379150337 | Sabuj Sena Mojumdar Para R/A, Block - E, Rd # 5, Shahin Ahammed | 2019-08-21 | NQ1008 | 10.8 | 810 | 10.8 | 811 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7968 | 791.9997 | 113.794
SYL-W.1.RR.164.1 | 24535319150343 | Sabuj Sena Mojumdar Para R/A, Block - E, Rd # 5, H # 71/4 | 2019-08-21 | NQ1008 | 7.4 | 814 | 7.4 | 815 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7968 | 791.9997 | 77.97
SYL-W.1.RR.165.1 | 24535269150347 | Sabuj Sena Mojumdar Para R/A, Block - E, Rd # 5, H # 72 | 2019-08-21 | NQ1008 | 9.6 | 816 | 9.6 | 817 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7968 | 791.9997 | 101.1502
SYL-W.1.RR.165.2 | 24535269150347 | Sabuj Sena Mojumdar Para R/A, Block - E, Rd # 5, H # 72 | 2019-08-21 | NQ1008 | 10.8 | 818 | 10.8 | 819 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7968 | 791.9997 | 113.794
SYL-W.1.RR.166.1 | 24535639150316 | Sabuj Sena Mojumdar Para R/A, Block - E, Rd # 7, Md. Anowar Hosen | 2019-08-21 | NQ1008 | 6.7 | 820 | 6.7 | 821 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7968 | 791.9997 | 70.5944
SYL-W.1.RR.167.1 | 24535739150347 | Sabuj Sena Mojumdar Para R/A, Block - E, Rd # 7, Yeasin Villa | 2019-08-21 | NQ1008 | 11.7 | 822 | 11.7 | 823 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7968 | 791.9997 | 123.2768
SYL-W.1.RR.168.1 | 24540349150284 | Kanishail, Rd # 1, Prottosha, H # 170 | 2019-08-21 | NQ1008 | 10.7 | 824 | 10.7 | 825 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7968 | 791.9997 | 112.7403
SYL-W.1.RR.169.1 | 24540349150284 | Kanishail, Rd # 1, Prottosha, Haji Azizur Rahman | 2019-08-21 | NQ1008 | 12.9 | 826 | 12.9 | 827 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7968 | 791.9997 | 135.9206
SYL-W.1.RR.170.1 | 24540679150236 | Kanishail, Rd # 1, Prottosha, Shovo | 2019-08-21 | NQ1008 | 10.3 | 831 | 10.3 | 832 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7968 | 791.9997 | 108.5258
SYL-W.1.RR.171.1 | 24533319151204 | Vangatikar Para, Rojonigondha R/A, H # 16 | 2019-08-21 | NQ1008 | 1.8 | 835 | 1.8 | 836 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7944 | 815.9997 | 18.9657
SYL-W.1.RR.172.1 | 24533129151193 | Vangatikar Para, Rojonigondha R/A, H # 2 | 2019-08-21 | NQ1008 | 14.6 | 837 | 14.6 | 838 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7944 | 815.9997 | 153.8326
SYL-W.1.RR.173.1 | 24533009151069 | West Shekghat, Word - 12, Uttoron - 32 | 2019-08-22 | NQ1008 | 13 | 859 | 13 | 860 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7992 | 767.9997 | 136.9743
SYL-W.1.RR.173.2 | 24533009151069 | West Shekghat, Word - 12, Uttoron - 32 | 2021-02-24 | LU1001 | 4.2 | 220 | 4.2 | 221 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7992 | 767.9997 | 44.2532
SYL-W.1.RR.174.1 | 24533129151066 | West Shekghat, Word - 12, Shafikur Rahman | 2019-08-22 | NQ1008 | 7.5 | 861 | 7.5 | 862 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7992 | 767.9997 | 79.0236
SYL-W.1.RR.175.1 | 24533179151064 | West Shekghat, Word - 12, Uttoron - 50 | 2019-08-22 | NQ1008 | 3.5 | 863 | 3.5 | 864 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7992 | 767.9997 | 36.8777
SYL-W.1.RR.176.1 | 24533229151064 | West Shekghat, Word - 12, Uttoron - 39 | 2019-08-22 | NQ1008 | 4.1 | 865 | 4.1 | 866 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7992 | 767.9997 | 43.1996
SYL-W.1.RR.177.1 | 24533009151069 | West Shekghat, Word - 12, Uttoron - 29 | 2019-08-22 | NQ1008 | 3.3 | 869 | 3.3 | 870 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7992 | 767.9997 | 34.7704
SYL-W.1.RR.178.1 | 24532569151179 | Shekghat, Word - 12, Suvessa - 261 | 2019-08-22 | NQ1008 | 4.7 | 871 | 4.7 | 872 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7944 | 815.9997 | 49.5215
SYL-W.1.RR.179.1 | 24532569151179 | Shekghat, Word - 12, Suvessa - 262 | 2019-08-22 | NQ1008 | 9.6 | 873 | 9.6 | 874 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7944 | 815.9997 | 101.1502
SYL-W.1.RR.179.2 | 24532569151179 | Shekghat, Word - 12, Suvessa - 262 | 2019-08-22 | NQ1008 | 2.4 | 875 | 2.4 | 876 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7944 | 815.9997 | 25.2876
SYL-W.1.RR.180.1 | 24532669151198 | Shekghat, Word - 12, Suvessa - 269 | 2019-08-22 | NQ1008 | 11.9 | 877 | 12 | 878 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7944 | 815.9997 | 126.4378
SYL-W.1.RR.181.1 | 24532669151198 | Shekghat, Word - 12, Suvessa - 269 | 2019-08-22 | NQ1008 | 6.5 | 879 | 6.5 | 880 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7944 | 815.9997 | 68.4871
SYL-W.1.RR.182.1 | 24532429151205 | Shekghat, Word - 12, Suvessa - 275 | 2019-08-22 | NQ1008 | 10.2 | 881 | 10.2 | 882 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7944 | 815.9997 | 107.4721
SYL-W.1.RR.183.1 | 24532429151199 | Shekghat, Word - 12, Suvessa - 276 | 2019-08-22 | NQ1008 | 9.8 | 883 | 9.7 | 884 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.7 | 9.7 | 0.582 | 0.582 | 0.0007168 | 100% | 0% | 0.582 | 0.582 | 0.0011869 | 28 | 0.011667 | 0.011667 |  | 0 | 0 | 7944 | 815.9997 | 102.2039
SYL-W.1.RR.184.1 | 24532469151206 | Shekghat, Word - 12, Suvessa - 272 | 2019-08-24 | NQ1008 | 4.7 | 1 | 4.7 | 2 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7944 | 815.9997 | 49.5215
SYL-W.1.RR.185.1 | 24532599151214 | Shekghat, Word - 12, Suvessa - 237 | 2019-08-24 | NQ1008 | 10.9 | 3 | 11 | 4 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7944 | 815.9997 | 115.9013
SYL-W.1.RR.186.1 | 24532829151228 | Shekghat, Word - 12, Suvessa - 246 | 2019-08-24 | NQ1008 | 7.2 | 5 | 7.2 | 6 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7944 | 815.9997 | 75.8627
SYL-W.1.RR.187.1 | 24532229151204 | Shekghat, Word - 12, Suvessa - 284 | 2019-08-24 | NQ1008 | 7.2 | 8 | 7.2 | 9 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7944 | 815.9997 | 75.8627
SYL-W.1.RR.188.1 | 24532329151257 | Shekghat, Word - 12, Suvessa - 267 | 2019-08-24 | NQ1008 | 14.4 | 10 | 14.4 | 11 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 14.4 | 14.4 | 0.864 | 0.864 | 0.0007168 | 100% | 0% | 0.864 | 0.864 | 0.0011869 | 28 | 0.01732 | 0.01732 |  | 0 | 0 | 7992 | 767.9997 | 151.7253
SYL-W.1.RR.189.1 | 24532329151257 | Shekghat, Word - 12, Suvessa - 267 | 2019-08-24 | NQ1008 | 5.9 | 12 | 5.9 | 13 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7992 | 767.9997 | 62.1652
SYL-W.1.RR.190.1 | 24532419151265 | Shekghat, Word - 12, Suvessa - 118, Masum Ahammed | 2019-08-24 | NQ1008 | 11.9 | 14 | 11.9 | 15 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7992 | 767.9997 | 125.3841
SYL-W.1.RR.191.1 | 24532409151282 | Shekghat, Word - 12, Suvessa - 116 | 2019-08-24 | NQ1008 | 3.1 | 16 | 3.1 | 17 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7992 | 767.9997 | 32.6631
SYL-W.1.RR.192.1 | 24532159151285 | Shekghat, Word - 12, Suvessa - 351 | 2019-08-24 | NQ1008 | 3 | 18 | 3 | 19 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7992 | 767.9997 | 31.6094
SYL-W.1.RR.192.2 | 24532159151285 | Shekghat, Word - 12, Suvessa - 351 | 2019-08-24 | NQ1008 | 11 | 20 | 10.8 | 21 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7992 | 767.9997 | 113.794
SYL-W.1.RR.193.1 | 24532709151293 | Shekghat, Word - 12, Suvessa - 90 | 2019-08-24 | NQ1008 | 7.2 | 22 | 7.2 | 23 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7992 | 767.9997 | 75.8627
SYL-W.1.RR.194.1 | 24532529151312 | Shekghat, Word - 12, Suvessa - 82 | 2019-08-24 | NQ1008 | 11.6 | 24 | 11.6 | 25 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7992 | 767.9997 | 122.2232
SYL-W.1.RR.195.1 | 24532219151190 | Shekghat, Word - 12, Haji Chan Mia | 2019-08-25 | NQ1008 | 3.4 | 43 | 3.4 | 44 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7944 | 815.9997 | 35.824
SYL-W.1.RR.195.2 | 24532219151190 | Shekghat, Word - 12, Haji Chan Mia | 2020-10-25 | MN1032 | 10.6 | 727 | 10.6 | 728 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7944 | 815.9997 | 111.6867
SYL-W.1.RR.196.1 | 24532369151187 | Shekghat, Word - 12, Suvessa - 291 | 2019-08-25 | NQ1008 | 4.1 | 45 | 4.1 | 46 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7944 | 815.9997 | 43.1996
SYL-W.1.RR.197.1 | 24532459151185 | Shekghat, Word - 12, Suvessa - 296 | 2019-08-25 | NQ1008 | 4.8 | 47 | 4.8 | 48 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7944 | 815.9997 | 50.5751
SYL-W.1.RR.198.1 | 24532459151185 | Shekghat, Word - 12, Suvessa - 295 | 2019-08-25 | NQ1008 | 3.1 | 49 | 3.1 | 50 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7944 | 815.9997 | 32.6631
SYL-W.1.RR.199.1 | 24532229151171 | Shekghat, Word - 12, Sumon | 2019-08-25 | NQ1008 | 11.8 | 51 | 11.8 | 52 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7944 | 815.9997 | 124.3305
SYL-W.1.RR.199.2 | 24532229151171 | Shekghat, Word - 12, Sumon | 2021-10-24 | NQ1007 | 1.9 | 67 | 1.9 | 68 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7944 | 815.9997 | 20.0193
SYL-W.1.RR.200.1 | 24532539151092 | Shekghat, Word - 12, Forest Colony | 2019-08-25 | NQ1008 | 10.9 | 53 | 10.9 | 54 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7992 | 767.9997 | 114.8476
SYL-W.1.RR.201.1 | 24535109151253 | Madhau Shahid, H # 90, Md.Faruk Ahmed | 2019-08-19 | MN1032 | 16 | 97 | 16 | 98 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 16 | 16 | 0.96 | 0.96 | 0.0007168 | 100% | 0% | 0.96 | 0.96 | 0.0011869 | 28 | 0.019245 | 0.019245 |  | 0 | 0 | 7944 | 815.9997 | 168.5837
SYL-W.1.RR.202.1 | 24535389151267 | Madhau Shahid, H # 60, Sadek | 2019-08-19 | MN1032 | 14.2 | 99 | 14.2 | 100 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 14.2 | 14.2 | 0.852 | 0.852 | 0.0007168 | 100% | 0% | 0.852 | 0.852 | 0.0011869 | 28 | 0.01708 | 0.01708 |  | 0 | 0 | 7944 | 815.9997 | 149.618
SYL-W.1.RR.203.1 | 24535379151250 | Madhau Shahid, H # 118/1, Md.Juber Ahmed | 2019-08-19 | MN1032 | 11.9 | 101 | 11.9 | 102 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7944 | 815.9997 | 125.3841
SYL-W.1.RR.204.1 | 24535019151279 | Madhau Shahid, H # 9, Hazi Ancharuddin | 2019-08-19 | MN1032 | 15.2 | 103 | 15.2 | 104 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 15.2 | 15.2 | 0.912 | 0.912 | 0.0007168 | 100% | 0% | 0.912 | 0.912 | 0.0011869 | 28 | 0.018282 | 0.018282 |  | 0 | 0 | 7944 | 815.9997 | 160.1545
SYL-W.1.RR.205.1 | 24534789151302 | Noya Para, Bithika R/A, H # B/21 | 2019-08-19 | MN1032 | 11.2 | 105 | 11.2 | 106 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7944 | 815.9997 | 118.0086
SYL-W.1.RR.206.1 | 24534909151318 | Lamabazar, Noya Para, Bithika R/A, H # A/34, Suvas Datta | 2019-08-19 | MN1032 | 15.3 | 107 | 15.3 | 108 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 15.3 | 15.3 | 0.918 | 0.918 | 0.0007168 | 100% | 0% | 0.918 | 0.918 | 0.0011869 | 28 | 0.018403 | 0.018403 |  | 0 | 0 | 7944 | 815.9997 | 161.2082
SYL-W.1.RR.207.1 | 24534679151393 | Lamabazar, Noya para, Bithika R/A, H # B/3, Biddut Kumar | 2019-08-20 | MP1006 | 16.7 | 45 | 16.7 | 46 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 16.7 | 16.7 | 1.002 | 1.002 | 0.0007168 | 100% | 0% | 1.002 | 1.002 | 0.0011869 | 28 | 0.020087 | 0.020087 |  | 0 | 0 | 7944 | 815.9997 | 175.9592
SYL-W.1.RR.208.1 | 24534679151393 | Lamabazar, Noya para, Bithika R/A, H # A/1/1, Samsur Rahman | 2019-08-20 | MP1006 | 12 | 47 | 12 | 48 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7944 | 815.9997 | 126.4378
SYL-W.1.RR.209.1 | 24534679151393 | Lamabazar, Noya para, Bithika R/A, H # A/1/1, Samsur Rahman | 2019-08-20 | MP1006 | 12.3 | 49 | 12.3 | 50 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7944 | 815.9997 | 129.5987
SYL-W.1.RR.210.1 | 24534409151346 | Lamabazar, Nasirbad Bilpar, H # 32, Bahar Loskor | 2019-08-20 | MP1006 | 11.8 | 51 | 11.6 | 52 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7944 | 815.9997 | 122.2232
SYL-W.1.RR.211.1 | 24534469151330 | Lamabazar, Nasirbad Bilpar, H # 37, Md.Badsa Mia | 2019-08-20 | MP1006 | 6.2 | 55 | 6.2 | 56 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7944 | 815.9997 | 65.3262
SYL-W.1.RR.212.1 | 24534469151330 | Lamabazar, Nasirbad Bilpar, H # 41, Imdadul Hossen | 2019-08-20 | MP1006 | 6.9 | 57 | 6.9 | 58 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7944 | 815.9997 | 72.7017
SYL-W.1.RR.213.1 | 24534519151310 | Lamabazar, Nasirbad Bilpar, H # 58, Salim Ahmed | 2019-08-20 | MP1006 | 13.1 | 59 | 13.2 | 60 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7944 | 815.9997 | 139.0816
SYL-W.1.RR.214.1 | 24534629151299 | Lamabazar, Nasirbad Bilpar, H # 71, Khaled Ahmed | 2019-08-20 | MP1006 | 11.3 | 61 | 11.3 | 62 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7944 | 815.9997 | 119.0622
SYL-W.1.RR.215.1 | 24534629151299 | Lamabazar, Nasirbad Bilpar, H # 71, Koyes Ahmed | 2019-08-20 | MP1006 | 14.7 | 63 | 14.7 | 64 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7944 | 815.9997 | 154.8863
SYL-W.1.RR.216.1 | 24532939150548 | Kolapara, Kolapara Point, H # 147, Tobarok Ali | 2019-08-21 | MP1006 | 4.5 | 79 | 4.5 | 80 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7992 | 767.9997 | 47.4142
SYL-W.1.RR.217.1 | 24533399150533 | Lamapara, Nearest Jalalabad Model School and College, Makhon Mia | 2019-08-21 | MP1006 | 6.3 | 81 | 6.3 | 82 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7992 | 767.9997 | 66.3798
SYL-W.1.RR.218.1 | 24533389150522 | Lamapara, Gasitula, Nurjahan Begum | 2019-08-21 | MP1006 | 7.5 | 83 | 7.5 | 84 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7992 | 767.9997 | 79.0236
SYL-W.1.RR.219.1 | 24533229150449 | Lamapara, Gasitula, Block # C, H # 19, Abdul Malek Maya | 2019-08-21 | MP1006 | 15.8 | 85 | 15.8 | 86 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7992 | 767.9997 | 166.4764
SYL-W.1.RR.220.1 | 24532349150370 | Kola para, Dahar, Nurul Islam | 2019-08-22 | MP1006 | 11.4 | 105 | 11.4 | 106 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7968 | 791.9997 | 120.1159
SYL-W.1.RR.221.1 | 24532389150386 | Kola para, Dahar, H # 57, Kutubuddin | 2019-08-22 | MP1006 | 13 | 109 | 13 | 110 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7968 | 791.9997 | 136.9743
SYL-W.1.RR.221.2 | 24532389150386 | Kola para, Dahar, H # 57, Kutubuddin | 2021-10-28 | NQ1007 | 11.6 | 73 | 11.6 | 74 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7968 | 791.9997 | 122.2232
SYL-W.1.RR.222.1 | 24532529150439 | Kola para, Dahar, H # 30, Mokbul Hossen | 2019-08-22 | MP1006 | 11.4 | 111 | 11.4 | 112 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7992 | 767.9997 | 120.1159
SYL-W.1.RR.223.1 | 24532529150439 | Kola para, Dahar, H # 26, Aklesur Rahman | 2019-08-22 | MP1006 | 12 | 113 | 12 | 114 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7992 | 767.9997 | 126.4378
SYL-W.1.RR.224.1 | 24532519150464 | Kola para, Dahar, Abdur Rob | 2019-08-22 | MP1006 | 13.4 | 115 | 13.4 | 116 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7992 | 767.9997 | 141.1888
SYL-W.1.RR.225.1 | 24532269150487 | Kola para, Durbor R/A, Baitun Nur Jame Mosjid | 2019-08-22 | MP1006 | 4 | 117 | 4 | 118 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7992 | 767.9997 | 42.1459
SYL-W.1.RR.226.1 | 24535539151282 | Madhu Sohid, H # 48/1, Atiqur Rahman | 2019-08-24 | MN1032 | 6.5 | 145 | 6.5 | 146 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7944 | 815.9997 | 68.4871
SYL-W.1.RR.227.1 | 24535539151282 | Madhu Sohid, H # 48/1, Sofiqur Rahman | 2019-08-24 | MN1032 | 6.8 | 148 | 6.7 | 149 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7944 | 815.9997 | 70.5944
SYL-W.1.RR.228.1 | 24535279151302 | Madhu Sohid, H # 38, Md. Sayedur | 2019-08-24 | MN1032 | 12.4 | 150 | 12.4 | 151 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7944 | 815.9997 | 130.6524
SYL-W.1.RR.229.1 | 24535279151302 | Madhu Sohid, H # 40, Rohimuddin | 2019-08-24 | MN1032 | 13.4 | 154 | 13.2 | 155 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.2 | 13.2 | 0.792 | 0.792 | 0.0007168 | 100% | 0% | 0.792 | 0.792 | 0.0011869 | 28 | 0.015877 | 0.015877 |  | 0 | 0 | 7944 | 815.9997 | 139.0816
SYL-W.1.RR.230.1 | 24535279151302 | Madhu Sohid, H # 35, Bacchu | 2019-08-24 | MN1032 | 7.1 | 156 | 7.1 | 157 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7944 | 815.9997 | 74.809
SYL-W.1.RR.231.1 | 24535259151392 | Madhu Sohid, H # 16/6, Aklakul Islam | 2019-08-24 | MN1032 | 12.5 | 158 | 12.5 | 159 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7944 | 815.9997 | 131.706
SYL-W.1.RR.232.1 | 24542699150365 | Akhaliya, Nehari Para, Block-C, H # 19, Abdur Sattar | 2019-08-25 | MN1032 | 9 | 172 | 9 | 173 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7824 | 935.9997 | 94.8283
SYL-W.1.RR.233.1 | 24542859150391 | Akhaliya, Nehari Para, Block-C, H # 55 | 2019-08-25 | MN1032 | 3.4 | 176 | 3.4 | 177 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7824 | 935.9997 | 35.824
SYL-W.1.RR.234.1 | 24542609150389 | Akhaliya, Nehari Para, Block-C, H # 75, Jahangir Alam | 2019-08-25 | MN1032 | 12.7 | 178 | 12.7 | 179 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7824 | 935.9997 | 133.8133
SYL-W.1.RR.235.1 | 24542439150394 | Akhaliya, Nehari Para, Block-A, Lake City R/A, H # 6, Siraz | 2019-08-25 | MN1032 | 4.4 | 182 | 4.4 | 183 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7824 | 935.9997 | 46.3605
SYL-W.1.RR.236.1 | 24541899150402 | Akhaliya, Nehari Para, Lake City R/A, Block-E, H # 92, Shilu | 2019-08-25 | MN1032 | 7.1 | 184 | 7.1 | 185 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7824 | 935.9997 | 74.809
SYL-W.1.RR.237.1 | 24541829150379 | Akhaliya, Nehari Para, Lake City R/A, Block-F, H # 105, Musafir Mahol | 2019-08-25 | MN1032 | 3.6 | 186 | 3.6 | 187 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7824 | 935.9997 | 37.9313
SYL-W.1.RR.238.1 | 24550689146442 | Bolauara, Boro bari Road, Md. Shofiq Mia | 2019-08-27 | MN1032 | 8.8 | 192 | 8.8 | 193 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7776 | 983.9997 | 92.721
SYL-W.1.RR.239.1 | 24545879146445 | Bolauara, Boro bari Road, Md. Junayed | 2019-08-27 | MN1032 | 8.2 | 194 | 8.2 | 195 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7776 | 983.9997 | 86.3991
SYL-W.1.RR.240.1 | 24545879146445 | Bolauara, Boro bari Road, Md. Shah Nur | 2019-08-27 | MN1032 | 2.1 | 196 | 2.1 | 197 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7776 | 983.9997 | 22.1266
SYL-W.1.RR.241.1 | 24544929147597 | Gopal, Monohorpur, Md. Rafiq | 2019-08-27 | MN1032 | 4.2 | 198 | 4.2 | 199 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7776 | 983.9997 | 44.2532
SYL-W.1.RR.242.1 | 24544769149061 | Haydorpur, 2nd Goli, Jakaria | 2019-08-28 | MN1032 | 5.7 | 230 | 5.7 | 231 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7776 | 983.9997 | 60.0579
SYL-W.1.RR.243.1 | 24544769149061 | Haydorpur, 2nd Goli, Kutubuddin | 2019-08-28 | MN1032 | 3.1 | 232 | 3.1 | 233 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7776 | 983.9997 | 32.6631
SYL-W.1.RR.244.1 | 24545059149100 | Haydorpur, 1st Goli, Sifatullah | 2019-08-28 | MN1032 | 11 | 234 | 11 | 235 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11 | 11 | 0.66 | 0.66 | 0.0007168 | 100% | 0% | 0.66 | 0.66 | 0.0011869 | 28 | 0.013231 | 0.013231 |  | 0 | 0 | 7776 | 983.9997 | 115.9013
SYL-W.1.RR.245.1 | 24544739149100 | Haydorpur, 1st Goli, Amir Hossen | 2019-08-28 | MN1032 | 10 | 236 | 10 | 237 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7776 | 983.9997 | 105.3648
SYL-W.1.RR.246.1 | 24544669149104 | Haydorpur, 1st Goli, Moyen Mia | 2019-08-28 | MN1032 | 9 | 238 | 9 | 239 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7776 | 983.9997 | 94.8283
SYL-W.1.RR.247.1 | 24544669149104 | Haydorpur, 1st Goli, Aftabuddin | 2019-08-28 | MN1032 | 10.1 | 240 | 10.1 | 241 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7776 | 983.9997 | 106.4185
SYL-W.1.RR.248.1 | 24544609149109 | Haydorpur, 1st Goli, Sirajul Islam | 2019-08-28 | MN1032 | 3.7 | 242 | 3.7 | 243 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7776 | 983.9997 | 38.985
SYL-W.1.RR.249.1 | 24544629149146 | Kumargaon, Churugaon,Sadoruddin | 2019-08-28 | MN1032 | 14.7 | 246 | 14.7 | 247 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7776 | 983.9997 | 154.8863
SYL-W.1.RR.250.1 | 24544629149146 | Kumargaon, Churugaon,Farukuddin | 2019-08-28 | MN1032 | 9 | 248 | 9 | 249 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7776 | 983.9997 | 94.8283
SYL-W.1.RR.251.1 | 24540799151039 | West Kajolshah, Sonar Bangla R/A, H # 388, Malek | 2019-08-17 | MN1032 | 9.5 | 49 | 9.5 | 50 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7848 | 911.9997 | 100.0966
SYL-W.1.RR.252.1 | 24540799151039 | West Kajolshah, Sonar Bangla R/A, H # 388, Almas | 2019-08-17 | MN1032 | 4.6 | 51 | 4.6 | 52 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7848 | 911.9997 | 48.4678
SYL-W.1.RR.253.1 | 24540289151013 | South Kajolshah, Madical Road, H # 117 | 2019-08-18 | MN1032 | 9.3 | 53 | 8.6 | 54 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7848 | 911.9997 | 90.6137
SYL-W.1.RR.254.1 | 24540029151019 | West Kajolshah, Madical Road, Shofiur | 2019-08-18 | MN1032 | 9.5 | 55 | 8.9 | 56 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7848 | 911.9997 | 93.7747
SYL-W.1.RR.255.1 | 24535979151059 | West Kajolshah, Madical Road, Mohamaya Center | 2019-08-18 | MN1032 | 10.4 | 57 | 10.4 | 58 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7920 | 839.9997 | 109.5794
SYL-W.1.RR.256.1 | 24535839151123 | South Kajolshah R/A, Rd # 3, H # 36 | 2019-08-18 | MN1032 | 9 | 59 | 9 | 60 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9 | 9 | 0.54 | 0.54 | 0.0007168 | 100% | 0% | 0.54 | 0.54 | 0.0011869 | 28 | 0.010825 | 0.010825 |  | 0 | 0 | 7920 | 839.9997 | 94.8283
SYL-W.1.RR.257.1 | 24535249151155 | South Kajolshah R/A, Selim Mia | 2019-08-18 | MN1032 | 8.4 | 61 | 8.5 | 62 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7944 | 815.9997 | 89.5601
SYL-W.1.RR.258.1 | 24535569151139 | South Kajolshah R/A, H # 183 | 2019-08-18 | MN1032 | 4.9 | 63 | 4.9 | 64 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7944 | 815.9997 | 51.6288
SYL-W.1.RR.259.1 | 24535389151167 | Vataliya R/A, Mahmuda, H # 156 | 2019-08-18 | MN1032 | 7.2 | 65 | 7.2 | 66 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7944 | 815.9997 | 75.8627
SYL-W.1.RR.260.1 | 24535299151167 | Vataliya R/A, Faruk Mia, H # 155 | 2019-08-18 | MN1032 | 17.4 | 67 | 17.4 | 68 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 17.4 | 17.4 | 1.044 | 1.044 | 0.0007168 | 100% | 0% | 1.044 | 1.044 | 0.0011869 | 28 | 0.020929 | 0.020929 |  | 0 | 0 | 7944 | 815.9997 | 183.3348
SYL-W.1.RR.261.1 | 24535579151234 | Vataliya, Vataliya Rd, Hazi Abul | 2019-08-18 | MN1032 | 4.8 | 69 | 4.8 | 70 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7944 | 815.9997 | 50.5751
SYL-W.1.RR.262.1 | 24535169151218 | Vataliya, Vataliya Rd, Kayom Jalali | 2019-08-18 | MN1032 | 11.8 | 71 | 11.8 | 72 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7944 | 815.9997 | 124.3305
SYL-W.1.RR.263.1 | 24535099151207 | Vataliya, Vataliya Rd, Kutub | 2019-08-18 | MN1032 | 12.3 | 73 | 12.3 | 74 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7944 | 815.9997 | 129.5987
SYL-W.1.RR.264.1 | 24535199151202 | Vataliya, Vataliya Rd, Siddik | 2019-08-18 | MN1032 | 7.2 | 75 | 7.2 | 76 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7944 | 815.9997 | 75.8627
SYL-W.1.RR.265.1 | 24534969151226 | Vataliya, Vataliya Rd, Sazzad | 2019-08-18 | MN1032 | 32.1 | 79 | 32.1 | 80 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 32.1 | 32.1 | 1.926 | 1.926 | 0.0007168 | 100% | 0% | 1.926 | 1.926 | 0.0011869 | 28 | 0.03861 | 0.03861 |  | 0 | 0 | 7944 | 815.9997 | 338.221
SYL-W.1.RR.266.1 | 24534989151199 | Vataliya R/A, H # 87, Rofique Mia | 2019-08-19 | MN1032 | 5.5 | 81 | 5.5 | 82 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7944 | 815.9997 | 57.9506
SYL-W.1.RR.267.1 | 24535039151155 | Vataliya R/A, H # 79, Hazi Najir | 2019-08-19 | MN1032 | 4.9 | 83 | 4.9 | 84 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7944 | 815.9997 | 51.6288
SYL-W.1.RR.268.1 | 24534789151207 | Vataliya R/A, Pukurpar, Rohim Box | 2019-08-19 | MN1032 | 9.6 | 85 | 9.1 | 86 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7944 | 815.9997 | 95.882
SYL-W.1.RR.269.1 | 24534649151218 | Vataliya R/A, Pukurpar, Shah Jahan | 2019-08-19 | MN1032 | 13.4 | 87 | 13.4 | 88 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7944 | 815.9997 | 141.1888
SYL-W.1.RR.270.1 | 24534509151274 | Nasirabad Bilpara, Anowara Begum | 2019-08-19 | MN1032 | 10.5 | 89 | 10.5 | 90 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7944 | 815.9997 | 110.6331
SYL-W.1.RR.271.1 | 24534429151269 | Nasirabad Bilpara, Rofiqul Islam | 2019-08-19 | MN1032 | 11.6 | 91 | 11.7 | 92 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7944 | 815.9997 | 123.2768
SYL-W.1.RR.272.1 | 24534429151269 | Nasirabad Bilpara, Anowar Hosen | 2019-08-19 | MN1032 | 6.3 | 93 | 6.3 | 94 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7944 | 815.9997 | 66.3798
SYL-W.1.RR.273.1 | 24534939151333 | Lamabazar, Noyapara, Bithika R/A, Rahman Vila | 2019-08-20 | MP1006 | 14.6 | 33 | 14.7 | 34 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7944 | 815.9997 | 154.8863
SYL-W.1.RR.273.2 | 24534939151333 | Lamabazar, Noyapara, Bithika R/A, Rahman Vila | 2019-08-20 | MP1006 | 16.4 | 35 | 16.2 | 36 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 7944 | 815.9997 | 170.691
SYL-W.1.RR.274.1 | 24534959151348 | Lamabazar, Noyapara, Bithika R/A, Nurul | 2019-08-20 | MP1006 | 18.6 | 37 | 18.6 | 38 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 18.6 | 18.6 | 1.116 | 1.116 | 0.0007168 | 100% | 0% | 1.116 | 1.116 | 0.0011869 | 28 | 0.022372 | 0.022372 |  | 0 | 0 | 7944 | 815.9997 | 195.9786
SYL-W.1.RR.275.1 | 24535029151352 | Lamabazar, Noyapara, Bithika R/A, H # 21/A | 2019-08-20 | MP1006 | 4.6 | 39 | 4.6 | 40 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7944 | 815.9997 | 48.4678
SYL-W.1.RR.275.2 | 24535029151352 | Lamabazar, Noyapara, Bithika R/A, H # 21/A | 2019-08-20 | MP1006 | 7.8 | 41 | 8 | 42 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 8 | 8 | 0.48 | 0.48 | 0.0007168 | 100% | 0% | 0.48 | 0.48 | 0.0011869 | 28 | 0.0096224 | 0.0096224 |  | 0 | 0 | 7944 | 815.9997 | 84.2919
SYL-W.1.RR.276.1 | 24535089151338 | Lamabazar, Noyapara, Bithika R/A, H # A/27 | 2019-08-20 | MP1006 | 10.7 | 43 | 10.7 | 44 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7944 | 815.9997 | 112.7403
SYL-W.1.RR.277.1 | 24532389151066 | Sheikhghat, Kolapara, Bengle House, H # 02 | 2019-08-21 | MP1006 | 5.7 | 65 | 5.7 | 66 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7992 | 767.9997 | 60.0579
SYL-W.1.RR.278.1 | 24532619150552 | Sheikhghat, Kolapara, Rd # 2, Monoara Griho | 2019-08-21 | MP1006 | 13.3 | 67 | 13.3 | 68 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7992 | 767.9997 | 140.1352
SYL-W.1.RR.279.1 | 24532629150540 | Sheikhghat, Kolapara, Rd # 2, Rahman Monjil | 2019-08-21 | MP1006 | 9.3 | 69 | 9.3 | 70 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7992 | 767.9997 | 97.9893
SYL-W.1.RR.280.1 | 24533079150569 | Sheikhghat, Kolapara Point, Shah Jalal Model School Goli, Abdul Jalil | 2019-08-21 | MP1006 | 4.7 | 71 | 4.7 | 72 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7992 | 767.9997 | 49.5215
SYL-W.1.RR.281.1 | 24532739150565 | Sheikhghat, Kolapara Point, Near by Kolapara Kazi Office, Raj Mohol | 2019-08-21 | MP1006 | 12.6 | 73 | 12.6 | 74 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7992 | 767.9997 | 132.7597
SYL-W.1.RR.282.1 | 24532789150578 | Sheikhghat, Kolapara, Durbar-164, Hassan Villa | 2019-08-21 | MP1006 | 14.8 | 75 | 14.8 | 76 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 7992 | 767.9997 | 155.9399
SYL-W.1.RR.283.1 | 24532859150588 | Sheikhghat, Kolapara, Durbar-186, Manik House | 2019-08-21 | MP1006 | 17.9 | 77 | 17.9 | 78 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 17.9 | 17.9 | 1.074 | 1.074 | 0.0007168 | 100% | 0% | 1.074 | 1.074 | 0.0011869 | 28 | 0.02153 | 0.02153 |  | 0 | 0 | 7992 | 767.9997 | 188.603
SYL-W.1.RR.284.1 | 24532739150336 | Hiraboron Mollapara, Block-D, Rejia Begom | 2019-08-22 | MP1006 | 4.6 | 87 | 4.6 | 88 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7968 | 791.9997 | 48.4678
SYL-W.1.RR.285.1 | 24532599150319 | Hiraboron Mollapara, Block-D, Menai Mia | 2019-08-22 | MP1006 | 6.7 | 91 | 6.7 | 92 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7968 | 791.9997 | 70.5944
SYL-W.1.RR.286.1 | 24532789150333 | Hiraboron Mollapara, Block-D, Sumon Mia | 2019-08-22 | MP1006 | 5.7 | 93 | 5.7 | 94 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7968 | 791.9997 | 60.0579
SYL-W.1.RR.287.1 | 24532479150362 | Hiraboron Mollapara, Block-D, Hajera Monjil | 2019-08-22 | MP1006 | 12.4 | 95 | 12.4 | 96 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7968 | 791.9997 | 130.6524
SYL-W.1.RR.288.1 | 24532479150362 | Hiraboron Mollapara, Block-D, Kala Mia | 2019-08-22 | MP1006 | 7.9 | 97 | 7.9 | 98 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.9 | 7.9 | 0.474 | 0.474 | 0.0007168 | 100% | 0% | 0.474 | 0.474 | 0.0011869 | 28 | 0.0095021 | 0.0095021 |  | 0 | 0 | 7968 | 791.9997 | 83.2382
SYL-W.1.RR.289.1 | 24532629150366 | Hiraboron Mollapara, Block-D, Sukur Ali | 2019-08-22 | MP1006 | 11.5 | 99 | 11.8 | 100 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7968 | 791.9997 | 124.3305
SYL-W.1.RR.290.1 | 24532629150366 | Hiraboron Mollapara, Block-D, Taj Uddin | 2019-08-22 | MP1006 | 4.4 | 101 | 4.4 | 102 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7968 | 791.9997 | 46.3605
SYL-W.1.RR.291.1 | 24532679150377 | Hiraboron Mollapara, Block-D, H # 88, Aleya Vila | 2019-08-22 | MP1006 | 4.1 | 103 | 4.1 | 104 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7968 | 791.9997 | 43.1996
SYL-W.1.RR.291.2 | 24532679150377 | Hiraboron Mollapara, Block-D, H # 88, Aleya Vila | 2020-10-29 | MP1032 | 7.6 | 607 | 7.6 | 608 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7968 | 791.9997 | 80.0773
SYL-W.1.RR.292.1 | 24533389150299 | Ghasitula, Betbazar, Nur Mia | 2019-08-24 | MN1032 | 8.7 | 124 | 8.7 | 125 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.7 | 8.7 | 0.522 | 0.522 | 0.0007168 | 100% | 0% | 0.522 | 0.522 | 0.0011869 | 28 | 0.010464 | 0.010464 |  | 0 | 0 | 7968 | 791.9997 | 91.6674
SYL-W.1.RR.293.1 | 24533389150299 | Ghasitula, Betbazar, Abul Bashar | 2019-08-24 | MN1032 | 4.4 | 126 | 4.2 | 127 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7968 | 791.9997 | 44.2532
SYL-W.1.RR.294.1 | 24533469150313 | Ghasitula, Betbazar, Md. Ashique | 2019-08-24 | MN1032 | 8.4 | 128 | 8.4 | 129 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7968 | 791.9997 | 88.5064
SYL-W.1.RR.295.1 | 24533169150300 | Ghasitula, Betbazar, Babul | 2019-08-24 | MN1032 | 7.3 | 131 | 7.3 | 132 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7968 | 791.9997 | 76.9163
SYL-W.1.RR.296.1 | 24533029150244 | Ghasitula, Betbazar, Belal | 2019-08-24 | MN1032 | 8.9 | 133 | 8.9 | 134 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7968 | 791.9997 | 93.7747
SYL-W.1.RR.297.1 | 24532679150290 | Ghasitula, Betbazar, Rehena | 2019-08-24 | MN1032 | 10.6 | 135 | 10.6 | 136 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7968 | 791.9997 | 111.6867
SYL-W.1.RR.298.1 | 24532649150303 | Ghasitula, Betbazar, Nurul Islam | 2019-08-24 | MN1032 | 4.7 | 137 | 4.7 | 138 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7968 | 791.9997 | 49.5215
SYL-W.1.RR.299.1 | 24532579150296 | Ghasitula, Betbazar, Saru Mia | 2019-08-24 | MN1032 | 1.7 | 139 | 1.7 | 140 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7968 | 791.9997 | 17.912
SYL-W.1.RR.300.1 | 24532669150316 | Ghasitula, Betbazar, Fotik Mia | 2019-08-24 | MN1032 | 6.5 | 143 | 6 | 144 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7968 | 791.9997 | 63.2189
SYL-W.1.RR.300.2 | 24532669150316 | Ghasitula, Betbazar, Fotik Mia | 2020-10-28 | MP1032 | 11.4 | 599 | 11.4 | 600 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7968 | 791.9997 | 120.1159
SYL-W.1.RR.301.1 | 24542159150575 | Sylhet, North Baghbari, Ridoy Tailors, Nipendro Kapali | 2019-08-07 | NQ1011 | 6 | 23 | 6 | 24 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7824 | 935.9997 | 63.2189
SYL-W.1.RR.302.1 | 24542079150583 | Sylhet, North Baghbari, H # 249/10 | 2019-08-07 | NQ1011 | 4.3 | 25 | 4.3 | 26 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 |  | 0 | 0 | 7824 | 935.9997 | 45.3069
SYL-W.1.RR.303.1 | 24541859151210 | Sylhet, Sagordighir Par, Shantibag | 2019-08-08 | NQ1011 | 12 | 27 | 12 | 28 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7920 | 839.9997 | 126.4378
SYL-W.1.RR.304.1 | 24542199151182 | Sylhet, Sagordighir Par, H# 74/7 | 2019-08-08 | NQ1011 | 4.3 | 29 | 4.3 | 30 | 2022-01-01 | [9 empty] | 4.3 | 4.3 | 0.258 | 0.258 | 0.0007168 | 100% | 0% | 0.258 | 0.258 | 0.0011869 | 28 | 0.005172 | 0.005172 | 2022-01-01 12:00 | 0 | 0
SYL-W.1.RR.305.1 | 24540669150470 | Bagbari, Etimkhana Road, Somir Mia | 2019-08-18 | NQ1011 | 6.5 | 55 | 6.2 | 56 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7848 | 911.9997 | 65.3262
SYL-W.1.RR.306.1 | 24540669150442 | Bagbari, Etimkhana Road, Nahar Bag, H# 25/1 | 2019-08-18 | NQ1011 | 14.8 | 57 | 14.8 | 58 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 14.8 | 14.8 | 0.888 | 0.888 | 0.0007168 | 100% | 0% | 0.888 | 0.888 | 0.0011869 | 28 | 0.017801 | 0.017801 |  | 0 | 0 | 7848 | 911.9997 | 155.9399
SYL-W.1.RR.307.1 | 24541119150490 | Bagbar, Road # 3, H# 71 | 2019-08-18 | NQ1011 | 4.6 | 59 | 4.6 | 60 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 2952 | 0 | 4896 | 911.9997 | 32.1348
SYL-W.1.RR.308.1 | 24541139150367 | Bagbari, Etimkhana Road, Nur Mahol | 2019-08-18 | NQ1011 | 8.3 | 61 | 8.3 | 62 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 8.3 | 8.3 | 0.498 | 0.498 | 0.0007168 | 100% | 0% | 0.498 | 0.498 | 0.0011869 | 28 | 0.0099832 | 0.0099832 |  | 0 | 0 | 7848 | 911.9997 | 87.4528
SYL-W.1.RR.309.1 | 24541319150346 | Bagbari, Etimkhana Road, Rofiqul Islam Fenu | 2019-08-18 | NQ1011 | 9.4 | 63 | 9.5 | 64 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7848 | 911.9997 | 100.0966
SYL-W.1.RR.310.1 | 24541159150349 | Bagbari, Etimkhana Road, H# 156 | 2019-08-18 | NQ1011 | 6.1 | 65 | 6.1 | 66 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7848 | 911.9997 | 64.2725
SYL-W.1.RR.311.1 | 24541319150305 | Bagbari, Etimkhana Road, H# 173 | 2019-08-18 | NQ1011 | 2.2 | 67 | 2.2 | 68 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7848 | 911.9997 | 23.1803
SYL-W.1.RR.312.1 | 24541319150305 | Bagbari, Etimkhana Road, H# 172 | 2019-08-18 | NQ1011 | 5.4 | 69 | 5.4 | 70 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7848 | 911.9997 | 56.897
SYL-W.1.RR.313.1 | 24535859150424 | South Bagbari, Shamimabad R/A, Rd # 4, H # 189 | 2019-08-19 | NQ1011 | 3.3 | 97 | 3.2 | 98 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7968 | 791.9997 | 33.7167
SYL-W.1.RR.314.1 | 24535859150424 | South Bagbari, Shamimabad R/A, Rd # 4, Shamim | 2019-08-19 | NQ1011 | 5 | 99 | 5 | 100 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7968 | 791.9997 | 52.6824
SYL-W.1.RR.315.1 | 24540159150410 | South Bagbari, Shamimabad R/A, Rd # 5, Monjur | 2019-08-19 | NQ1011 | 8.1 | 101 | 8.1 | 102 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7968 | 791.9997 | 85.3455
SYL-W.1.RR.316.1 | 24540059150408 | South Bagbari, Shamimabad R/A, Rd # 5, H # 213 | 2019-08-19 | NQ1011 | 6 | 103 | 6.5 | 104 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7968 | 791.9997 | 68.4871
SYL-W.1.RR.317.1 | 24535759150398 | South Bagbari, Shamimabad R/A, Rd # 5, H # 224 | 2019-08-19 | NQ1011 | 4.5 | 105 | 4.5 | 106 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7968 | 791.9997 | 47.4142
SYL-W.1.RR.318.1 | 24535589150352 | South Bagbari, Shamimabad R/A, Rd # 5, Bodrul | 2019-08-19 | NQ1011 | 5 | 107 | 5 | 108 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7968 | 791.9997 | 52.6824
SYL-W.1.RR.319.1 | 24540229150378 | South Bagbari, Shamimabad R/A, Rd # 8, Billal | 2019-08-19 | NQ1011 | 6.6 | 111 | 6.4 | 112 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7968 | 791.9997 | 67.4335
SYL-W.1.RR.320.1 | 24540249150349 | South Bagbari, Kanishail Road, Moinuddin State | 2019-08-19 | NQ1011 | 10.5 | 113 | 10.5 | 114 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7968 | 791.9997 | 110.6331
SYL-W.1.RR.321.1 | 24535179150360 | Ghasitula, Majumdarpara, R/A, H# 67 | 2019-08-20 | NQ1011 | 10.4 | 129 | 10.4 | 130 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7968 | 791.9997 | 109.5794
SYL-W.1.RR.322.1 | 24535179150360 | Ghasitula, Majumdarpara, R/A, Front of H# 69/5 | 2019-08-20 | NQ1011 | 1.9 | 133 | 1.9 | 134 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7968 | 791.9997 | 20.0193
SYL-W.1.RR.323.1 | 24535069150346 | Ghasitula, Majumdarpara, Rakib | 2019-08-20 | NQ1011 | 3.2 | 135 | 3.2 | 136 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7968 | 791.9997 | 33.7167
SYL-W.1.RR.324.1 | 24535069150346 | Ghasitula, Majumdarpara, Shamim | 2019-08-20 | NQ1011 | 10.4 | 137 | 10.4 | 138 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7968 | 791.9997 | 109.5794
SYL-W.1.RR.325.1 | 24535069150346 | Ghasitula, Majumdarpara, Abul Mia | 2019-08-20 | NQ1011 | 2.2 | 139 | 2.2 | 140 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7968 | 791.9997 | 23.1803
SYL-W.1.RR.326.1 | 24535069150346 | Ghasitula, Majumdarpara, Manik Mia | 2019-08-20 | NQ1011 | 7.3 | 143 | 7.3 | 144 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7968 | 791.9997 | 76.9163
SYL-W.1.RR.327.1 | 24534649150350 | Ghasitula, Majumdarpara, Sobuj Sena R/A, Aysha Mahal | 2019-08-20 | NQ1011 | 10 | 147 | 10 | 148 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7968 | 791.9997 | 105.3648
SYL-W.1.RR.328.1 | 24534649150350 | Ghasitula, Majumdarpara, Sobuj Sena R/A, Siraj Mia | 2019-08-20 | NQ1011 | 5 | 149 | 5 | 150 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7968 | 791.9997 | 52.6824
SYL-W.1.RR.329.1 | 24534469150335 | Ghasitula, Majumdarpara, Masuk Mia | 2019-08-20 | NQ1011 | 10 | 151 | 10 | 152 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7968 | 791.9997 | 105.3648
SYL-W.1.RR.329.2 | 24534469150335 | Ghasitula, Majumdarpara, Masuk Mia | 2021-02-23 | NQ1003 | 4.4 | 284 | 4.4 | 285 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4.4 | 4.4 | 0.264 | 0.264 | 0.0007168 | 100% | 0% | 0.264 | 0.264 | 0.0011869 | 28 | 0.0052923 | 0.0052923 |  | 0 | 0 | 7968 | 791.9997 | 46.3605
SYL-W.1.RR.330.1 | 24534469150335 | Ghasitula, Majumdarpara, Ana Mia | 2019-08-20 | NQ1011 | 6.3 | 155 | 6.3 | 156 | 2022-01-01 | [9 empty] | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 | 2022-01-01 12:00 | 0 | 0
SYL-W.1.RR.331.1 | 24534319150342 | Ghasitula, Majumdarpara R/A, Rd# 1, Nirmol Das | 2019-08-20 | NQ1011 | 24.5 | 159 | 24.5 | 160 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 24.5 | 24.5 | 1.47 | 1.47 | 0.0007168 | 100% | 0% | 1.47 | 1.47 | 0.0011869 | 28 | 0.029468 | 0.029468 |  | 0 | 0 | 7968 | 791.9997 | 258.1438
SYL-W.1.RR.332.1 | 24534439150352 | Ghasitula, Majumdarpara R/A, Rd # 2, Masuk Mia | 2019-08-21 | NQ1011 | 7.6 | 175 | 7.6 | 176 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7968 | 791.9997 | 80.0773
SYL-W.1.RR.333.1 | 24534439150355 | Ghasitula, Majumdarpara R/A, Rd # 2, Jalal Uddin | 2019-08-21 | NQ1011 | 5 | 177 | 5 | 178 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7968 | 791.9997 | 52.6824
SYL-W.1.RR.334.1 | 24534439150355 | Ghasitula, Majumdarpara R/A, Rd # 2, Farid Mia | 2019-08-21 | NQ1011 | 10.7 | 179 | 10.7 | 180 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7968 | 791.9997 | 112.7403
SYL-W.1.RR.335.1 | 24534389150325 | Ghasitula, Majumdarpara R/A, Rd # 1, Abdul Hamid | 2019-08-21 | NQ1011 | 16.1 | 181 | 15.4 | 182 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 15.4 | 15.4 | 0.924 | 0.924 | 0.0007168 | 100% | 0% | 0.924 | 0.924 | 0.0011869 | 28 | 0.018523 | 0.018523 |  | 0 | 0 | 7968 | 791.9997 | 162.2618
SYL-W.1.RR.336.1 | 24534279150315 | Ghasitula, Majumdarpara R/A, Abdul Hamid | 2019-08-21 | NQ1011 | 8.9 | 183 | 8.4 | 184 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7968 | 791.9997 | 88.5064
SYL-W.1.RR.336.2 | 24534279150315 | Ghasitula, Majumdarpara R/A, Abdul Hamid | 2021-02-23 | NQ1003 | 3.1 | 282 | 3.1 | 283 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7968 | 791.9997 | 32.6631
SYL-W.1.RR.337.1 | 24534279150315 | Ghasitula, Majumdarpara R/A, Abdul Kadir | 2019-08-21 | NQ1011 | 6.2 | 185 | 6.2 | 186 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7968 | 791.9997 | 65.3262
SYL-W.1.RR.338.1 | 24533979150486 | Ghasitula, Lamapara, Sobuj Sena, Shahin | 2019-08-21 | NQ1011 | 9.6 | 189 | 9.6 | 190 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7992 | 767.9997 | 101.1502
SYL-W.1.RR.339.1 | 24533899150478 | Ghasitula, Lamapara, Sobuj Sena, H # 45/1 | 2019-08-21 | NQ1011 | 4.8 | 191 | 4.6 | 192 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.6 | 4.6 | 0.276 | 0.276 | 0.0007168 | 100% | 0% | 0.276 | 0.276 | 0.0011869 | 28 | 0.0055329 | 0.0055329 |  | 0 | 0 | 7992 | 767.9997 | 48.4678
SYL-W.1.RR.340.1 | 24533929150461 | Ghasitula, Lamapara, Sobuj Sena, Junaid Ahamed | 2019-08-21 | NQ1011 | 8.8 | 193 | 8.8 | 194 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7992 | 767.9997 | 92.721
SYL-W.1.RR.341.1 | 24534019150367 | Ghasitula, Lamapara, Sobuj Sena, H # 88 | 2019-08-21 | NQ1011 | 9.8 | 195 | 9.5 | 196 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.5 | 9.5 | 0.57 | 0.57 | 0.0007168 | 100% | 0% | 0.57 | 0.57 | 0.0011869 | 28 | 0.011427 | 0.011427 |  | 0 | 0 | 7968 | 791.9997 | 100.0966
SYL-W.1.RR.342.1 | 24534019150367 | Ghasitula, Lamapara, Sobuj Sena, Beside H # 88 | 2019-08-21 | NQ1011 | 5.1 | 197 | 5.1 | 198 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7968 | 791.9997 | 53.7361
SYL-W.1.RR.343.1 | 24533389150399 | Ghasitula, Sobuj Sena, Block-C, H # 39 | 2019-08-22 | NQ1011 | 2.5 | 219 | 2.5 | 220 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7992 | 767.9997 | 26.3412
SYL-W.1.RR.344.1 | 24533399150414 | Ghasitula, Sobuj Sena, Block-C, H # 32/2, H # 32/2, Jahed Ahmed | 2019-08-22 | NQ1011 | 5.3 | 221 | 5.3 | 222 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 1464 | 0 | 6528 | 767.9997 | 46.5106
SYL-W.1.RR.345.1 | 24533629150392 | Ghasitula, Sobuj Sena, Block-A, H # A/51 | 2019-08-22 | NQ1011 | 10.9 | 223 | 10.6 | 224 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7992 | 767.9997 | 111.6867
SYL-W.1.RR.346.1 | 24540119151206 | Kazalshah, Medical College Road, Doctor's Garden | 2019-08-22 | NQ1011 | 7.6 | 225 | 7.6 | 226 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7920 | 839.9997 | 80.0773
SYL-W.1.RR.347.1 | 24540119151206 | Kazalshah, Medical College Road, Doctor's Garden | 2019-08-22 | NQ1011 | 2.6 | 227 | 2.6 | 228 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7920 | 839.9997 | 27.3949
SYL-W.1.RR.348.1 | 24540119151206 | Kazalshah, Medical College Road, Doctor's Garden | 2019-08-22 | NQ1011 | 4.7 | 229 | 4.7 | 230 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7920 | 839.9997 | 49.5215
SYL-W.1.RR.349.1 | 24540119151206 | Kazalshah, Medical College Road, Doctor's Garden | 2019-08-22 | NQ1011 | 4.1 | 231 | 4.1 | 232 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7920 | 839.9997 | 43.1996
SYL-W.1.RR.350.1 | 24540119151206 | Kazalshah, Medical College Road, Doctor's Garden | 2019-08-22 | NQ1011 | 5.4 | 233 | 5.4 | 234 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7920 | 839.9997 | 56.897
SYL-W.1.RR.351.1 | 24535839150428 | South Bagbari, Shamimabadh R/A, Rd # 3, H # 158, Md. Suruk Mia | 2019-08-19 | NQ1011 | 3.4 | 93 | 3.4 | 94 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7968 | 791.9997 | 35.824
SYL-W.1.RR.352.1 | 24540019150419 | South Bagbari, Shamimabadh R/A, Rd # 4, Kajol Mondol | 2019-08-19 | NQ1011 | 16.3 | 95 | 16.3 | 96 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 16.3 | 16.3 | 0.978 | 0.978 | 0.0007168 | 100% | 0% | 0.978 | 0.978 | 0.0011869 | 28 | 0.019606 | 0.019606 |  | 0 | 0 | 7968 | 791.9997 | 171.7446
SYL-W.1.RR.353.1 | 24540879150275 | Bagbari, Kanishail R/A, Rd # 2, Prottasha - 283, Talukdar Bari | 2019-08-20 | NQ1011 | 7.8 | 115 | 7.8 | 116 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7968 | 791.9997 | 82.1846
SYL-W.1.RR.354.1 | 24540829150273 | Bagbari, Kanishail R/A, Rd # 2, Prottasha - 280 | 2019-08-20 | NQ1011 | 10.5 | 117 | 10.5 | 118 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7968 | 791.9997 | 110.6331
SYL-W.1.RR.355.1 | 24540829150273 | Bagbari, Kanishail R/A, Rd # 2, H # 78 | 2019-08-20 | NQ1011 | 4 | 119 | 4 | 120 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7968 | 791.9997 | 42.1459
SYL-W.1.RR.356.1 | 24534969150459 | Bagbari, Mojumdarpara Housing, Md. Habibur Rahman | 2019-08-20 | NQ1011 | 2.3 | 121 | 2.3 | 122 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7968 | 791.9997 | 24.2339
SYL-W.1.RR.357.1 | 24534819150455 | Bagbari, Mojumdarpara Housing, Abdul Alim Babu Mia | 2019-08-20 | NQ1011 | 6.8 | 123 | 6.8 | 124 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7968 | 791.9997 | 71.6481
SYL-W.1.RR.358.1 | 24534699150455 | Bagbari, Mojumdarpara, H # 67/8, Rahima Cottage | 2019-08-20 | NQ1011 | 8.5 | 125 | 8.5 | 126 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7968 | 791.9997 | 89.5601
SYL-W.1.RR.359.1 | 24534569150455 | Bagbari, Mojumdarpara, H # 11, Rimon Villa | 2019-08-20 | NQ1011 | 2.7 | 127 | 2.7 | 128 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7968 | 791.9997 | 28.4485
SYL-W.1.RR.360.1 | 24541949150569 | Sylhet, North Bagbari, Bijoy Krisno Dey | 2019-08-08 | NQ1011 | 12.6 | 31 | 12.6 | 32 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7824 | 935.9997 | 132.7597
SYL-W.1.RR.361.1 | 24534509151006 | South Kajolshah, Nobab Road, Mia Bari, Rahman Tower | 2019-08-21 | NQ1011 | 9.2 | 163 | 9.2 | 164 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7992 | 767.9997 | 96.9356
SYL-W.1.RR.362.1 | 24534509151006 | South Kajolshah, Nobab Road, H # 9, Md. Humayun Reza | 2019-08-21 | NQ1011 | 6.3 | 165 | 6.3 | 166 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7992 | 767.9997 | 66.3798
SYL-W.1.RR.363.1 | 24534169151019 | South Kajolshah, Nobab Road, Hazi Ahmed Hossen | 2019-08-21 | NQ1011 | 8.8 | 167 | 8.8 | 168 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7992 | 767.9997 | 92.721
SYL-W.1.RR.364.1 | 24533999150512 | Kotowali, Lamapara Road, Ghashitula Lamapara, Shahabuddin | 2019-08-21 | NQ1011 | 5.1 | 171 | 5.1 | 172 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7992 | 767.9997 | 53.7361
SYL-W.1.RR.365.1 | 24533879150505 | Kotowali, Lamapara Road, Ghashitula Lamapara, Amir Hossen | 2019-08-21 | NQ1011 | 8.6 | 173 | 8.6 | 174 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7992 | 767.9997 | 90.6137
SYL-W.1.RR.365.2 | 24533879150505 | Kotowali, Lamapara Road, Ghashitula Lamapara, Amir Hossen | 2021-02-24 | NQ1003 | 1.9 | 293 | 1.9 | 294 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7992 | 767.9997 | 20.0193
SYL-W.1.RR.366.1 | 24535019151006 | South Kajolshah, Nobab Road, H # 138/1 | 2019-08-21 | NQ1011 | 5 | 161 | 5 | 162 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7992 | 767.9997 | 52.6824
SYL-W.1.RR.367.1 | 24533969150320 | Kotwali, West Ghashitula, Boro Mosjid Road, Altar Mia | 2019-08-22 | NQ1011 | 10.5 | 199 | 10.5 | 200 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7968 | 791.9997 | 110.6331
SYL-W.1.RR.368.1 | 24533969150302 | Kotwali, West Ghashitula, Boro Mosjid Road, Abdur Rouf | 2019-08-22 | NQ1011 | 9.1 | 201 | 9.1 | 202 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7968 | 791.9997 | 95.882
SYL-W.1.RR.369.1 | 24533969150302 | Kotwali, West Ghashitula, Boro Mosjid Road, Abdur Rouf | 2019-08-22 | NQ1011 | 3.8 | 203 | 3.8 | 204 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7968 | 791.9997 | 40.0386
SYL-W.1.RR.370.1 | 24533879150305 | Kotwali, West Ghashitula, Boro Mosjid Road, Md. Jamal Uddin | 2019-08-22 | NQ1011 | 5.6 | 205 | 5.6 | 206 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7968 | 791.9997 | 59.0043
SYL-W.1.RR.371.1 | 24533659150283 | Kotwali, West Ghashitula, Boro Mosjid Road, Sazzad Mia | 2019-08-22 | NQ1011 | 9.3 | 207 | 9.3 | 208 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7968 | 791.9997 | 97.9893
SYL-W.1.RR.372.1 | 24533539150338 | Kotwali, East Khashitula, Block - A, Mukam Bari Road, Md. Raju | 2019-08-22 | NQ1011 | 10.8 | 209 | 10.8 | 210 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7968 | 791.9997 | 113.794
SYL-W.1.RR.373.1 | 24533739150348 | Kotwali, East Khashitula, Block - A, Mukam Bari Road, Safiullah | 2019-08-22 | NQ1011 | 6.4 | 211 | 6.4 | 212 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7968 | 791.9997 | 67.4335
SYL-W.1.RR.374.1 | 24533839150339 | Kotwali, East Khashitula, Block - A, Mukam Bari Road, Beside Khashitula School, Moin Uddin | 2019-08-22 | NQ1011 | 8.8 | 213 | 8.8 | 214 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7968 | 791.9997 | 92.721
SYL-W.1.RR.375.1 | 24533559150361 | Kotwali, East Khashitula, Block - A, Mukam Bari, Mollapara Road, Alauddin Khala Mia | 2019-08-22 | NQ1011 | 9.9 | 215 | 9.9 | 216 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7968 | 791.9997 | 104.3112
SYL-W.1.RR.376.1 | 24533559150361 | Kotwali, East Khashitula, Block - A, Mukam Bari, Mollapara Road, Md. Minhaz | 2019-08-22 | NQ1011 | 7 | 217 | 7 | 218 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7968 | 791.9997 | 73.7554
SYL-W.1.RR.377.1 | 24541029151213 | Kotowali, Kajolshah R/A, Block- D, Hazi Siddik Ali | 2019-08-24 | NQ1011 | 3.3 | 241 | 3.3 | 242 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7920 | 839.9997 | 34.7704
SYL-W.1.RR.378.1 | 24540199151239 | Kotowali, Kajolshah R/A, Block- D, H # 49/1 | 2019-08-24 | NQ1011 | 4.1 | 243 | 4.1 | 244 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7920 | 839.9997 | 43.1996
SYL-W.1.RR.378.2 | 24540199151239 | Kotowali, Kajolshah R/A, Block- D, H # 49/1 | 2021-02-24 | NQ1007 | 2.2 | 220 | 2.2 | 221 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7920 | 839.9997 | 23.1803
SYL-W.1.RR.379.1 | 24540199151239 | Kotowali, Kajolshah R/A, Block- D, H # 48 | 2019-08-24 | NQ1011 | 6.7 | 245 | 6.7 | 246 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7920 | 839.9997 | 70.5944
SYL-W.1.RR.380.1 | 24540199151239 | Kotowali, Kajolshah R/A, Block- D, H # 47 | 2019-08-24 | NQ1011 | 8.4 | 247 | 8.4 | 248 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7920 | 839.9997 | 88.5064
SYL-W.1.RR.381.1 | 24540119151217 | Kotowali, Kajolshah R/A, Block- D, H # 43/1 | 2019-08-24 | NQ1011 | 2.7 | 249 | 2.7 | 250 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7920 | 839.9997 | 28.4485
SYL-W.1.RR.382.1 | 24540119151217 | Kotowali, Kajolshah R/A, Block- D, H # 43 | 2019-08-24 | NQ1011 | 4.8 | 251 | 4.8 | 252 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7920 | 839.9997 | 50.5751
SYL-W.1.RR.383.1 | 24535879151221 | Kotowali, Kajolshah R/A, Block- B, H # 30 | 2019-08-24 | NQ1011 | 3 | 253 | 2.9 | 254 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7920 | 839.9997 | 30.5558
SYL-W.1.RR.384.1 | 24535989151234 | Kotowali, Kajolshah R/A, Block- B, H # 24/3 | 2019-08-24 | NQ1011 | 7 | 255 | 6.6 | 256 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7920 | 839.9997 | 69.5408
SYL-W.1.RR.385.1 | 24535739151251 | Kotowali, Kajolshah R/A, Block- A, H # 10 | 2019-08-24 | NQ1011 | 3.7 | 257 | 3.7 | 258 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7920 | 839.9997 | 38.985
SYL-W.1.RR.386.1 | 24540639151303 | Kotwali, Munshipara R/A, Mosjid Road, Ronju Mia | 2019-08-25 | LU1001 | 2.8 | 1 | 2.8 | 2 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7920 | 839.9997 | 29.5021
SYL-W.1.RR.386.2 | 24540639151303 | Kotwali, Munshipara R/A, Mosjid Road, Ronju Mia | 2020-10-27 | MN1032 | 0.9 | 879 | 0.9 | 880 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 0.9 | 0.9 | 0.054 | 0.054 | 0.0007168 | 100% | 0% | 0.054 | 0.054 | 0.0011869 | 28 | 0.0010825 | 0.0010825 |  | 0 | 0 | 7920 | 839.9997 | 9.4828
SYL-W.1.RR.387.1 | 24540639151303 | Kotwali, Munshipara R/A, Mosjid Road, H # 50/A, Hazi Khalilur Rahman | 2019-08-25 | LU1001 | 5.4 | 3 | 5.4 | 4 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7920 | 839.9997 | 56.897
SYL-W.1.RR.388.1 | 24540719151285 | Kotwali, Munshipara R/A, Majhar Road, Rais Mia | 2019-08-25 | LU1001 | 5 | 5 | 5 | 6 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7920 | 839.9997 | 52.6824
SYL-W.1.RR.389.1 | 24540809151281 | Kotwali, Munshipara R/A, Majhar Road, H # 65 | 2019-08-25 | LU1001 | 3 | 7 | 3 | 8 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7920 | 839.9997 | 31.6094
SYL-W.1.RR.390.1 | 24540839151278 | Kotwali, Munshipara R/A, Majhar Road, H # 66/A | 2019-08-25 | LU1001 | 3.5 | 9 | 3.6 | 10 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7920 | 839.9997 | 37.9313
SYL-W.1.RR.391.1 | 24540879151266 | Kotwali, Munshipara R/A, Majhar Road, H # 34/A | 2019-08-25 | LU1001 | 5.1 | 11 | 5.1 | 12 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7920 | 839.9997 | 53.7361
SYL-W.1.RR.392.1 | 24540949151234 | Kotwali, Munshipara R/A, Majhar Road, H # 68/D | 2019-08-25 | LU1001 | 11.9 | 13 | 11.9 | 14 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7920 | 839.9997 | 125.3841
SYL-W.1.RR.393.1 | 24540949151234 | Kotwali, Munshipara R/A, Majhar Road, H # 68/C | 2019-08-25 | LU1001 | 3 | 15 | 3 | 16 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7920 | 839.9997 | 31.6094
SYL-W.1.RR.394.1 | 24540779151311 | Kotwali, Munshipara R/A, Majhar Road, H # 70 | 2019-08-25 | LU1001 | 5.3 | 19 | 5.3 | 20 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7920 | 839.9997 | 55.8434
SYL-W.1.RR.395.1 | 24540909151337 | Kotwali, Munshipara R/A, Majhar Road, H # 72/9 | 2019-08-25 | LU1001 | 2.1 | 21 | 2.1 | 22 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 7416 | 0 | 504 | 839.9997 | 3.3948
SYL-W.1.RR.396.1 | 24540909151337 | Kotwali, Munshipara R/A, Majhar Road, H # 72/5 | 2019-08-25 | LU1001 | 7.7 | 23 | 7.7 | 24 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.7 | 7.7 | 0.462 | 0.462 | 0.0007168 | 100% | 0% | 0.462 | 0.462 | 0.0011869 | 28 | 0.0092615 | 0.0092615 |  | 0 | 0 | 7920 | 839.9997 | 81.1309
SYL-W.1.RR.397.1 | 24541089151319 | Kotwali, Munshipara R/A, Majhar Road, H # 76 | 2019-08-25 | LU1001 | 4.8 | 25 | 4.8 | 26 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7920 | 839.9997 | 50.5751
SYL-W.1.RR.397.2 | 24541089151319 | Kotwali, Munshipara R/A, Majhar Road, H # 76 | 2021-02-24 | NQ1007 | 3.4 | 223 | 3.4 | 224 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7920 | 839.9997 | 35.824
SYL-W.1.RR.398.1 | 24541139151289 | Kotwali, Munshipara R/A, Majhar Road, H # 79/B | 2019-08-25 | LU1001 | 5.8 | 27 | 5.8 | 28 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7920 | 839.9997 | 61.1116
SYL-W.1.RR.399.1 | 24542039151309 | Kotwali,Sagor Digheer Par, Rd # 3, H # 13/A | 2019-08-27 | NQ1011 | 13.9 | 303 | 13.9 | 304 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 13.9 | 13.9 | 0.834 | 0.834 | 0.0007168 | 100% | 0% | 0.834 | 0.834 | 0.0011869 | 28 | 0.016719 | 0.016719 |  | 0 | 0 | 7920 | 839.9997 | 146.4571
SYL-W.1.RR.400.1 | 24542179151307 | Kotwali,Sagor Digheer Par, Rd # 3, H # 9 | 2019-08-27 | NQ1011 | 6.1 | 305 | 6.1 | 306 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7920 | 839.9997 | 64.2725
SYL-W.1.RR.401.1 | 24532419151230 | Sylhet, Sheikhghat, Suvessa, Samsuddin | 2019-08-22 | NQ1008 | 11.1 | 894 | 11.2 | 895 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7992 | 767.9997 | 118.0086
SYL-W.1.RR.402.1 | 24532419151230 | Sylhet, Sheikhghat, Suvessa, Borhanuddin | 2019-08-22 | NQ1008 | 14.1 | 896 | 14.1 | 897 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7992 | 767.9997 | 148.5644
SYL-W.1.RR.403.1 | 24532419151230 | Sylhet, Sheikhghat, Suvessa, Mostak Ahmed | 2019-08-22 | NQ1008 | 7.6 | 898 | 7.6 | 899 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7992 | 767.9997 | 80.0773
SYL-W.1.RR.404.1 | 24532419151230 | Sylhet, Sheikhghat, Suvessa, Koes Ahmed | 2019-08-22 | NQ1008 | 7.3 | 902 | 7.3 | 903 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 7.3 | 7.3 | 0.438 | 0.438 | 0.0007168 | 100% | 0% | 0.438 | 0.438 | 0.0011869 | 28 | 0.0087804 | 0.0087804 |  | 0 | 0 | 7992 | 767.9997 | 76.9163
SYL-W.1.RR.405.1 | 24532509151257 | Sylhet, Sheikhghat, Suvessa, Laik Mia | 2019-08-22 | NQ1008 | 13.6 | 904 | 13.6 | 905 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 13.6 | 13.6 | 0.816 | 0.816 | 0.0007168 | 100% | 0% | 0.816 | 0.816 | 0.0011869 | 28 | 0.016358 | 0.016358 |  | 0 | 0 | 7992 | 767.9997 | 143.2961
SYL-W.1.RR.406.1 | 24532579151267 | Sylhet, Sheikhghat, Suvessa, Rasel Ahmed | 2019-08-22 | NQ1008 | 12.7 | 906 | 12.7 | 907 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7992 | 767.9997 | 133.8133
SYL-W.1.RR.407.1 | 24532659151252 | Sylhet, Sheikhghat, Suvessa, Josiruddin | 2019-08-22 | NQ1008 | 17.7 | 908 | 17.7 | 909 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 17.7 | 17.7 | 1.062 | 1.062 | 0.0007168 | 100% | 0% | 1.062 | 1.062 | 0.0011869 | 28 | 0.021289 | 0.021289 |  | 0 | 0 | 7992 | 767.9997 | 186.4957
SYL-W.1.RR.408.1 | 24532769151248 | Sylhet, Sheikhghat, Suvessa, Ataur Rohman | 2019-08-22 | NQ1008 | 3.4 | 910 | 3.4 | 911 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7992 | 767.9997 | 35.824
SYL-W.1.RR.409.1 | 24532739151273 | Sylhet, Sheikhghat, Suvessa, Israk Uddin | 2019-08-22 | NQ1008 | 12.5 | 912 | 12.7 | 913 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7992 | 767.9997 | 133.8133
SYL-W.1.RR.410.1 | 24532839151270 | Sylhet, Sheikhghat, Suvessa, parves | 2019-08-22 | NQ1008 | 4.5 | 914 | 4.5 | 915 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7992 | 767.9997 | 47.4142
SYL-W.1.RR.411.1 | 24532769151279 | Sylhet, Sheikhghat, Suvessa, Ali Hosen | 2019-08-22 | NQ1008 | 9.2 | 916 | 9.2 | 917 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7992 | 767.9997 | 96.9356
SYL-W.1.RR.412.1 | 24532809151283 | Sylhet, Sheikhghat, Suvessa, Surap Mia | 2019-08-22 | NQ1008 | 9.1 | 918 | 9.1 | 919 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 9.1 | 9.1 | 0.546 | 0.546 | 0.0007168 | 100% | 0% | 0.546 | 0.546 | 0.0011869 | 28 | 0.010945 | 0.010945 |  | 0 | 0 | 7992 | 767.9997 | 95.882
SYL-W.1.RR.413.1 | 24532089151309 | Sylhet, Sheikhghat, Nondi Para, Suvessa, Bikash Chowdhury | 2019-08-24 | NQ1008 | 6.4 | 26 | 6.4 | 27 | 2022-01-01 | [9 empty] | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 | 2022-03-22 12:00 | 0 | 0
SYL-W.1.RR.414.1 | 24532059151307 | Sylhet, Sheikhghat, Nondi Para, Suvessa, Olok Gupto | 2019-08-24 | NQ1008 | 10.8 | 28 | 10.2 | 29 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7992 | 767.9997 | 107.4721
SYL-W.1.RR.415.1 | 24532059151309 | Sylhet, Sheikhghat, Nondi Para, Suvessa, Bikash Chowdhury | 2019-08-24 | NQ1008 | 8.8 | 31 | 8.4 | 32 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7992 | 767.9997 | 88.5064
SYL-W.1.RR.416.1 | 24531989151305 | Sylhet, Sheikhghat, Nondi Para, Suvessa, Hafiz Foizur Rohman | 2019-08-24 | NQ1008 | 3.4 | 33 | 3.3 | 34 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7992 | 767.9997 | 34.7704
SYL-W.1.RR.417.1 | 24532739151319 | Sylhet, Sheikhghat, Suvessa, Monuessa School Road, Abdul Gofur | 2019-08-24 | NQ1008 | 3.9 | 35 | 3.9 | 36 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7992 | 767.9997 | 41.0923
SYL-W.1.RR.417.2 | 24532739151319 | Sylhet, Sheikhghat, Suvessa, Monuessa School Road, Abdul Gofur | 2019-08-24 | NQ1008 | 3.3 | 37 | 3.3 | 38 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7992 | 767.9997 | 34.7704
SYL-W.1.RR.418.1 | 24532709151315 | Sylhet, Sheikhghat, Suvessa, Monuessa School Road, Aktar Hosen Khaled | 2019-08-24 | NQ1008 | 3.9 | 39 | 3.7 | 40 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7992 | 767.9997 | 38.985
SYL-W.1.RR.419.1 | 24533329151348 | Sylhet, Sheikhghat, Suvessa, Munir Mia | 2019-08-24 | NQ1008 | 11.9 | 41 | 11.6 | 42 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7992 | 767.9997 | 122.2232
SYL-W.1.RR.420.1 | 24543399150344 | Sylhet, Akhalia, Niharipara, Block-D, Shakil Ahmed, H # 9/2 | 2019-08-25 | NQ1008 | 4.2 | 76 | 4.2 | 77 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7824 | 935.9997 | 44.2532
SYL-W.1.RR.421.1 | 24543279150337 | Sylhet, Akhalia, Niharipara, Block-D, Abdul Hannan, H # 9/1 | 2019-08-25 | NQ1008 | 3.7 | 78 | 3.7 | 79 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7968 | 791.9997 | 38.985
SYL-W.1.RR.422.1 | 24543189150345 | Sylhet, Akhalia, Niharipara, Block-D, Abdur Rohim, H # 16 | 2019-08-25 | NQ1008 | 4.2 | 80 | 4.2 | 81 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 4.2 | 4.2 | 0.252 | 0.252 | 0.0007168 | 100% | 0% | 0.252 | 0.252 | 0.0011869 | 28 | 0.0050517 | 0.0050517 |  | 0 | 0 | 7824 | 935.9997 | 44.2532
SYL-W.1.RR.423.1 | 24542979150350 | Sylhet, Akhalia, Niharipara, Block-D, Beside H # 28 | 2019-08-25 | NQ1008 | 9.1 | 82 | 9.2 | 83 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7824 | 935.9997 | 96.9356
SYL-W.1.RR.424.1 | 24542509150328 | Sylhet, Akhalia, Niharipara, Block-D, Fazlul Korim | 2019-08-25 | NQ1008 | 3.8 | 84 | 3.8 | 85 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7824 | 935.9997 | 40.0386
SYL-W.1.RR.425.1 | 24542379150325 | Sylhet, Akhalia, Niharipara, Block-D, Abdul Alim | 2019-08-25 | NQ1008 | 5.7 | 86 | 5.7 | 87 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7824 | 935.9997 | 60.0579
SYL-W.1.RR.426.1 | 24542599150370 | Sylhet, Akhalia, Niharipara, Block-D, Munna | 2019-08-25 | NQ1008 | 14.7 | 88 | 14.7 | 89 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 14.7 | 14.7 | 0.882 | 0.882 | 0.0007168 | 100% | 0% | 0.882 | 0.882 | 0.0011869 | 28 | 0.017681 | 0.017681 |  | 0 | 0 | 7824 | 935.9997 | 154.8863
SYL-W.1.RR.427.1 | 24543069150314 | Sylhet, Akhalia, Niharipara, Block-D, Abdul Hamid | 2019-08-25 | NQ1008 | 6.9 | 90 | 6.9 | 91 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7824 | 935.9997 | 72.7017
SYL-W.1.RR.428.1 | 24541779151523 | Sylhet, Mia Fajil Chisti, Suvessa, Soiad Chomok Ali | 2019-08-26 | NQ1008 | 11.5 | 92 | 11.5 | 93 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7920 | 839.9997 | 121.1695
SYL-W.1.RR.429.1 | 24541779151523 | Sylhet, Mia Fajil Chisti, Suvessa, Abul Kalam Azad | 2019-08-26 | NQ1008 | 8.2 | 94 | 8.2 | 95 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7920 | 839.9997 | 86.3991
SYL-W.1.RR.430.1 | 24541729151535 | Sylhet, Mia Fajil Chisti, East Subid Bazar, Suvessa, Tokul Rana | 2019-08-26 | NQ1008 | 6 | 96 | 6 | 97 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7920 | 839.9997 | 63.2189
SYL-W.1.RR.431.1 | 24541529151499 | Sylhet, Mia Fajil Chisti, Subid Bazar, Suvessa, Samsul Haque | 2019-08-26 | NQ1008 | 12.1 | 98 | 12.1 | 99 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7920 | 839.9997 | 127.4914
SYL-W.1.RR.432.1 | 24541469151457 | Sylhet, Mia Fajil Chisti, Subid Bazar, Suvessa, H # 167 | 2019-08-26 | NQ1008 | 5.2 | 100 | 5.2 | 101 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7920 | 839.9997 | 54.7897
SYL-W.1.RR.433.1 | 24541729151452 | Sylhet, Mia Fajil Chisti, Subid Bazar, Suvessa, Jamal | 2019-08-26 | NQ1008 | 3.8 | 104 | 3.8 | 105 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7920 | 839.9997 | 40.0386
SYL-W.1.RR.434.1 | 24544159148363 | Sylhet, Sunamganj Road, Tukergau, Jaher | 2019-08-27 | NQ1008 | 6 | 144 | 6 | 145 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7776 | 983.9997 | 63.2189
SYL-W.1.RR.435.1 | 24544309148383 | Sylhet, Sunamganj Road, Tukergau, Ruhul Amin | 2019-08-27 | NQ1008 | 3.8 | 148 | 3.8 | 149 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7776 | 983.9997 | 40.0386
SYL-W.1.RR.436.1 | 24544909148362 | Sylhet, Jalalabad, Tukergau, Jabed Mia | 2019-08-27 | NQ1008 | 7 | 150 | 7 | 151 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7776 | 983.9997 | 73.7554
SYL-W.1.RR.436.2 | 24544909148362 | Sylhet, Jalalabad, Tukergau, Jabed Mia | 2021-10-21 | NQ1007 | 9.3 | 63 | 9.3 | 64 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.3 | 9.3 | 0.558 | 0.558 | 0.0007168 | 100% | 0% | 0.558 | 0.558 | 0.0011869 | 28 | 0.011186 | 0.011186 |  | 0 | 0 | 7776 | 983.9997 | 97.9893
SYL-W.1.RR.437.1 | 24544909148362 | Sylhet, Jalalabad, Tukergau, Abdullah | 2019-08-27 | NQ1008 | 1.9 | 152 | 1.9 | 153 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7776 | 983.9997 | 20.0193
SYL-W.1.RR.438.1 | 24545079148351 | Sylhet, Jalalabad, Tukergau, Musabbir | 2019-08-27 | NQ1008 | 3.7 | 154 | 3.7 | 155 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7776 | 983.9997 | 38.985
SYL-W.1.RR.439.1 | 24545079148351 | Sylhet, Jalalabad, Tukergau, Shaesta Mia | 2019-08-27 | NQ1008 | 10.6 | 156 | 10.6 | 157 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7776 | 983.9997 | 111.6867
SYL-W.1.RR.440.1 | 24545109148345 | Sylhet, Jalalabad, Tukergau, Samsul Haque | 2019-08-27 | NQ1008 | 5.4 | 159 | 5.4 | 160 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7776 | 983.9997 | 56.897
SYL-W.1.RR.441.1 | 24545219148365 | Sylhet, Jalalabad, Tukergau, Samszzaman | 2019-08-27 | NQ1008 | 6.8 | 161 | 6.4 | 162 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7776 | 983.9997 | 67.4335
SYL-W.1.RR.442.1 | 24545219148365 | Sylhet, Jalalabad, Tukergau, Murad Mia | 2019-08-27 | NQ1008 | 6.5 | 163 | 6.5 | 164 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7776 | 983.9997 | 68.4871
SYL-W.1.RR.443.1 | 24544409148409 | Sylhet, Jalalabad, Tukergau, Laik Ahmed | 2019-08-28 | NQ1008 | 3.5 | 165 | 3.5 | 166 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7776 | 983.9997 | 36.8777
SYL-W.1.RR.444.1 | 24545659148454 | Sylhet, Shahpur, Khurumkhola, Tukerbazar, Jalal Uddin | 2019-08-28 | NQ1008 | 11.9 | 167 | 11.9 | 168 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7776 | 983.9997 | 125.3841
SYL-W.1.RR.445.1 | 24545709148488 | Sylhet, Shahpur, Khurumkhola, Tukerbazar, Samu | 2019-08-28 | NQ1008 | 10.6 | 169 | 10.6 | 170 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7776 | 983.9997 | 111.6867
SYL-W.1.RR.446.1 | 24545709148488 | Sylhet, Shahpur, Khurumkhola, Tukerbazar, Bilal Mia | 2019-08-28 | NQ1008 | 7.3 | 171 | 6.8 | 172 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7776 | 983.9997 | 71.6481
SYL-W.1.RR.447.1 | 24545529148495 | Sylhet, Shahpur, Khurumkhola, Tukerbazar, Baharuddin | 2019-08-28 | NQ1008 | 3.5 | 175 | 3.5 | 176 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7776 | 983.9997 | 36.8777
SYL-W.1.RR.448.1 | 24545419148498 | Sylhet, Shahpur, Khurumkhola, Tukerbazar, Nazimuddin | 2019-08-28 | NQ1008 | 7.4 | 181 | 7.4 | 182 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7776 | 983.9997 | 77.97
SYL-W.1.RR.449.1 | 24545459148530 | Sylhet, Khurumkhola, Pirpur, Abdul Aziz | 2019-08-28 | NQ1008 | 1.9 | 183 | 1.9 | 184 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7776 | 983.9997 | 20.0193
SYL-W.1.RR.450.1 | 24545809148533 | Sylhet, Khurumkhola, Shahpur, Tukerbazar, Mazar Road, Lokman Chowdhury | 2019-08-28 | NQ1008 | 3.4 | 185 | 3.4 | 186 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7776 | 983.9997 | 35.824
SYL-W.1.RR.451.1 | 24532569151092 | Shekghat, Word - 12, Forest Colony | 2019-08-25 | NQ1008 | 4.7 | 55 | 4.7 | 56 | 2022-01-01 | 2022-11-30 | GS |  |  | 0 |  |  |  |  | 4.7 | 4.7 | 0.282 | 0.282 | 0.0007168 | 100% | 0% | 0.282 | 0.282 | 0.0011869 | 28 | 0.0056531 | 0.0056531 |  | 0 | 0 | 7992 | 767.9997 | 49.5215
SYL-W.1.RR.452.1 | 24541229150172 | Kanishail R/A, Rd # 1, Shofiqur Rahman | 2019-08-25 | NQ1008 | 12.6 | 57 | 12.6 | 58 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7968 | 791.9997 | 132.7597
SYL-W.1.RR.452.2 | 24541229150172 | Kanishail R/A, Rd # 1, Shofiqur Rahman | 2019-08-25 | NQ1008 | 6.7 | 59 | 6.2 | 60 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 6.2 | 6.2 | 0.372 | 0.372 | 0.0007168 | 100% | 0% | 0.372 | 0.372 | 0.0011869 | 28 | 0.0074573 | 0.0074573 |  | 0 | 0 | 7968 | 791.9997 | 65.3262
SYL-W.1.RR.453.1 | 24541229150172 | Kanishail R/A, Rd # 1, Mahmudur Rahman | 2019-08-25 | NQ1008 | 10.5 | 61 | 10.5 | 62 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7968 | 791.9997 | 110.6331
SYL-W.1.RR.454.1 | 24541329150162 | Kanishail R/A, Rd # 1, Kamal Ahammed | 2019-08-25 | NQ1008 | 3.1 | 63 | 3.1 | 64 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7968 | 791.9997 | 32.6631
SYL-W.1.RR.455.1 | 24541349150152 | Kanishail R/A, Rd # 1, Prottasha - 46 | 2019-08-25 | NQ1008 | 11.8 | 65 | 11.8 | 66 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7968 | 791.9997 | 124.3305
SYL-W.1.RR.456.1 | 24541379150150 | Kanishail R/A, Rd # 1, Prottasha - 43 | 2019-08-25 | NQ1008 | 3.5 | 67 | 3.5 | 68 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7968 | 791.9997 | 36.8777
SYL-W.1.RR.457.1 | 24541649150164 | Kanishail R/A, Rd # 1, Prottasha - 27 | 2019-08-25 | NQ1008 | 11.4 | 69 | 11.4 | 70 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7968 | 791.9997 | 120.1159
SYL-W.1.RR.457.2 | 24541649150164 | Kanishail R/A, Rd # 1, Prottasha - 27 | 2022-11-29 | MN1018 | 7 | 149 | 7 | 150 | 2022-11-29 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 0 | 791.9997 | 6.6683
SYL-W.1.RR.458.1 | 24541739150160 | Kanishail R/A, Rd # 1, Prottasha - 13 | 2019-08-25 | NQ1008 | 10.6 | 71 | 10.6 | 72 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7968 | 791.9997 | 111.6867
SYL-W.1.RR.458.2 | 24541739150160 | Kanishail R/A, Rd # 1, Prottasha - 13 | 2019-08-25 | NQ1008 | 1.9 | 74 | 1.9 | 75 | 2022-01-01 | 2022-11-29 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7968 | 791.9997 | 20.0193
SYL-W.1.RR.459.1 | 24542169151461 | East Subid Bazar, Fazil Chisti, Suvessa - 137/1 | 2019-08-26 | NQ1008 | 8.5 | 106 | 8.5 | 107 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7920 | 839.9997 | 89.5601
SYL-W.1.RR.460.1 | 24542169151461 | East Subid Bazar, Fazil Chisti, Suvessa - 137/1 | 2019-08-26 | NQ1008 | 4.8 | 108 | 4.8 | 109 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7920 | 839.9997 | 50.5751
SYL-W.1.RR.461.1 | 24541989151468 | East Subid Bazar, Fazil Chisti, Suvessa -139/4 | 2019-08-26 | NQ1008 | 2.1 | 110 | 2.1 | 111 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7920 | 839.9997 | 22.1266
SYL-W.1.RR.462.1 | 24541979151429 | East Subid Bazar, Fazil Chisti, Prantik - 45 | 2019-08-26 | NQ1008 | 5.3 | 112 | 5.3 | 113 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 |  | 0 | 0 | 7920 | 839.9997 | 55.8434
SYL-W.1.RR.463.1 | 24541869151428 | East Subid Bazar, Fazil Chisti, Prantik - 47/6 | 2019-08-26 | NQ1008 | 3.5 | 114 | 3.4 | 115 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7920 | 839.9997 | 35.824
SYL-W.1.RR.464.1 | 24541839151430 | East Subid Bazar, Fazil Chisti, Prantik - 47/1 | 2019-08-26 | NQ1008 | 3 | 117 | 3.1 | 118 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7920 | 839.9997 | 32.6631
SYL-W.1.RR.465.1 | 24541859151421 | East Subid Bazar, Fazil Chisti, Prantik - 47/11 | 2019-08-26 | NQ1008 | 11.7 | 119 | 11.7 | 120 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7920 | 839.9997 | 123.2768
SYL-W.1.RR.466.1 | 24542459151410 | Subid Bazar, Excel Tawor | 2019-08-26 | NQ1008 | 9.2 | 121 | 9.2 | 122 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 9.2 | 9.2 | 0.552 | 0.552 | 0.0007168 | 100% | 0% | 0.552 | 0.552 | 0.0011869 | 28 | 0.011066 | 0.011066 |  | 0 | 0 | 7920 | 839.9997 | 96.9356
SYL-W.1.RR.467.1 | 24542459151410 | Subid Bazar, Excel Tawor | 2019-08-26 | NQ1008 | 12.6 | 123 | 12.6 | 124 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7920 | 839.9997 | 132.7597
SYL-W.1.RR.468.1 | 24542459151410 | Subid Bazar, Excel Tawor | 2019-08-26 | NQ1008 | 6.4 | 127 | 5.9 | 128 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7920 | 839.9997 | 62.1652
SYL-W.1.RR.469.1 | 24542459151410 | Subid Bazar, Excel Tawor | 2019-08-26 | NQ1008 | 10.1 | 129 | 10.1 | 130 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.1 | 10.1 | 0.606 | 0.606 | 0.0007168 | 100% | 0% | 0.606 | 0.606 | 0.0011869 | 28 | 0.012148 | 0.012148 |  | 0 | 0 | 7920 | 839.9997 | 106.4185
SYL-W.1.RR.470.1 | 24542459151410 | Subid Bazar, Excel Tawor | 2019-08-26 | NQ1008 | 2.3 | 132 | 2.3 | 133 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7920 | 839.9997 | 24.2339
SYL-W.1.RR.471.1 | 24550549146557 | Jalalabad, 8 No Kandigaon, Word - 5, Koskalika, Anamul Haque | 2019-08-27 | NQ1008 | 3 | 136 | 3 | 137 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7776 | 983.9997 | 31.6094
SYL-W.1.RR.472.1 | 24550509146579 | Jalalabad, 8 No Kandigaon, Word - 5, Koskalika, Nurul Kibria | 2019-08-27 | NQ1008 | 8.2 | 138 | 8.2 | 139 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7776 | 983.9997 | 86.3991
SYL-W.1.RR.473.1 | 24550509146579 | Jalalabad, 8 No Kandigaon, Word - 5, Koskalika, Ali Nur Rahman | 2019-08-27 | NQ1008 | 10.8 | 140 | 10.8 | 141 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.8 | 10.8 | 0.648 | 0.648 | 0.0007168 | 100% | 0% | 0.648 | 0.648 | 0.0011869 | 28 | 0.01299 | 0.01299 |  | 0 | 0 | 7776 | 983.9997 | 113.794
SYL-W.1.RR.474.1 | 24550109146565 | Jalalabad, 8 No Kandigaon, Word - 5, Koskalika, Ostar ali | 2019-08-27 | NQ1008 | 13.3 | 142 | 13.3 | 143 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7776 | 983.9997 | 140.1352
SYL-W.1.RR.475.1 | 24545419149043 | Haydarpur, Tuker Bazar, Giyasuddin | 2019-08-28 | NQ1008 | 5.1 | 189 | 5.1 | 190 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7776 | 983.9997 | 53.7361
SYL-W.1.RR.476.1 | 24545399149105 | Haligaon, Tuker Bazar, Kobir | 2019-08-28 | NQ1008 | 2.8 | 191 | 2.6 | 192 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7776 | 983.9997 | 27.3949
SYL-W.1.RR.477.1 | 24545719149101 | Haligaon, Tuker Bazar, Jomshid | 2019-08-28 | NQ1008 | 11.6 | 193 | 11.6 | 194 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7776 | 983.9997 | 122.2232
SYL-W.1.RR.478.1 | 24545989149114 | Haligaon, Tuker Bazar, Somuj Mia | 2019-08-28 | NQ1008 | 10.9 | 195 | 10.5 | 196 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7776 | 983.9997 | 110.6331
SYL-W.1.RR.479.1 | 24545349149226 | Jalalabad, Kumargaon R/A, Badaghat Road, H # 1 | 2019-08-28 | NQ1008 | 11.3 | 197 | 11.3 | 198 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7776 | 983.9997 | 119.0622
SYL-W.1.RR.480.1 | 24545519149220 | Jalalabad, Kumargaon R/A, Badaghat Road, Kamran | 2019-08-28 | NQ1008 | 2.7 | 199 | 2.7 | 200 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.7 | 2.7 | 0.162 | 0.162 | 0.0007168 | 100% | 0% | 0.162 | 0.162 | 0.0011869 | 28 | 0.0032475 | 0.0032475 |  | 0 | 0 | 7776 | 983.9997 | 28.4485
SYL-W.1.RR.481.1 | 24545409149242 | Jalalabad, Kumargaon R/A, Badaghat Road, Nur Islam | 2019-08-28 | NQ1008 | 8.6 | 201 | 8.6 | 202 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.6 | 8.6 | 0.516 | 0.516 | 0.0007168 | 100% | 0% | 0.516 | 0.516 | 0.0011869 | 28 | 0.010344 | 0.010344 |  | 0 | 0 | 7776 | 983.9997 | 90.6137
SYL-W.1.RR.481.2 | 24545409149242 | Jalalabad, Kumargaon R/A, Badaghat Road, Nur Islam | 2019-08-28 | NQ1008 | 13 | 203 | 12.8 | 204 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.8 | 12.8 | 0.768 | 0.768 | 0.0007168 | 100% | 0% | 0.768 | 0.768 | 0.0011869 | 28 | 0.015396 | 0.015396 |  | 0 | 0 | 7776 | 983.9997 | 134.867
SYL-W.1.RR.482.1 | 24545439149252 | Jalalabad, Kumargaon R/A, Badaghat Road, Green Garden House | 2019-08-28 | NQ1008 | 4.8 | 205 | 4.8 | 206 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7776 | 983.9997 | 50.5751
SYL-W.1.RR.482.2 | 24545439149252 | Jalalabad, Kumargaon R/A, Badaghat Road, Green Garden House | 2019-08-28 | NQ1008 | 3.3 | 207 | 3.3 | 208 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7776 | 983.9997 | 34.7704
SYL-W.1.RR.483.1 | 24543069150019 | Akhalia Ghat, Hannan, | 2019-08-29 | NQ1008 | 6.7 | 227 | 6.7 | 228 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7824 | 935.9997 | 70.5944
SYL-W.1.RR.484.1 | 24542879150028 | Akhalia Ghat,H #51, Abdul Lotif | 2019-08-29 | NQ1008 | 3.4 | 229 | 3.4 | 230 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7824 | 935.9997 | 35.824
SYL-W.1.RR.485.1 | 24542649149593 | Akhalia Ghat,Aftab Hosen | 2019-08-29 | NQ1008 | 6.6 | 231 | 6.6 | 232 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7824 | 935.9997 | 69.5408
SYL-W.1.RR.486.1 | 24542689149569 | Akhalia Ghat,,Masuk Mia | 2019-08-29 | NQ1008 | 11.5 | 233 | 11.5 | 234 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7824 | 935.9997 | 121.1695
SYL-W.1.RR.487.1 | 24542729150032 | Akhalia Ghat,,Shafat | 2019-08-29 | NQ1008 | 10.6 | 235 | 10.6 | 236 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7824 | 935.9997 | 111.6867
SYL-W.1.RR.488.1 | 24542429150046 | Akhalia Ghat,,Ana Mia | 2019-08-29 | NQ1008 | 11.6 | 237 | 11.3 | 238 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7824 | 935.9997 | 119.0622
SYL-W.1.RR.489.1 | 24543079150085 | Akhalia Ghat,,Topobon R/A, H #12 | 2019-08-29 | NQ1008 | 8.9 | 239 | 8.9 | 240 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7824 | 935.9997 | 93.7747
SYL-W.1.RR.551.1 | 24534889151408 | Lamabazar, Uddom R/A, Suraiya Begom | 2019-08-25 | MN1032 | 12.2 | 160 | 12.2 | 161 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7944 | 815.9997 | 128.5451
SYL-W.1.RR.552.1 | 24534789151412 | Lamabazar, Uddom R/A,Uddom-27, Pollob Kumar | 2019-08-25 | MN1032 | 5.6 | 164 | 5.6 | 165 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7944 | 815.9997 | 59.0043
SYL-W.1.RR.553.1 | 24535019151389 | Lamabazar, Uddom R/A, Rita Rani | 2019-08-25 | MN1032 | 3.3 | 166 | 3.3 | 167 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7944 | 815.9997 | 34.7704
SYL-W.1.RR.554.1 | 24535589151410 | Modhushahid, Rikabi Bazar, Abul kalam | 2019-08-25 | MN1032 | 11.6 | 168 | 11.6 | 169 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7944 | 815.9997 | 122.2232
SYL-W.1.RR.555.1 | 24535519151370 | Modhushahid, New Madical Rd, Soiyod Monjil | 2019-08-25 | MN1032 | 9.6 | 170 | 9.6 | 171 | 2022-01-01 | 2022-11-28 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7944 | 815.9997 | 101.1502
SYL-W.1.RR.556.1 | 24543029150189 | Akhaliya, Khuliyapara, Surma R/A, Alahi-15, Samsuddoha | 2019-08-26 | LU1001 | 7.4 | 68 | 7.4 | 69 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7824 | 935.9997 | 77.97
SYL-W.1.RR.557.1 | 24543039150152 | Akhaliya, Khuliyapara, Surma R/A Rd, Alahi-B/16 | 2019-08-26 | LU1001 | 7.8 | 71 | 7.8 | 72 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.8 | 7.8 | 0.468 | 0.468 | 0.0007168 | 100% | 0% | 0.468 | 0.468 | 0.0011869 | 28 | 0.0093818 | 0.0093818 |  | 0 | 0 | 7824 | 935.9997 | 82.1846
SYL-W.1.RR.558.1 | 24543039150152 | Akhaliya, Khuliyapara, Surma R/A Rd, Alahi-B/16 | 2019-08-26 | LU1001 | 3.5 | 74 | 3.5 | 75 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7824 | 935.9997 | 36.8777
SYL-W.1.RR.559.1 | 24542919150202 | Akhaliya, Khuliyapara, Surma R/A Rd, Akhabur | 2019-08-26 | LU1001 | 3.9 | 76 | 3.9 | 77 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7824 | 935.9997 | 41.0923
SYL-W.1.RR.560.1 | 24542629150174 | Akhaliya, Surma R/A, Rd # 2, Block-A, Syed Shonahor Ali | 2019-08-26 | LU1001 | 2.6 | 78 | 2.6 | 79 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7824 | 935.9997 | 27.3949
SYL-W.1.RR.561.1 | 24545079148122 | Tuker Bazar, Gopal Uttar, Ali Hosen | 2019-08-27 | MN1032 | 11.3 | 200 | 11.3 | 201 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7776 | 983.9997 | 119.0622
SYL-W.1.RR.562.1 | 24544499148120 | Tuker Bazar, Gopal Uttar, Barek | 2019-08-27 | MN1032 | 8.8 | 202 | 8.8 | 203 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7776 | 983.9997 | 92.721
SYL-W.1.RR.563.1 | 24544499148120 | Tuker Bazar, Gopal Uttar, Rouf | 2019-08-27 | MN1032 | 6.9 | 204 | 6.9 | 205 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7776 | 983.9997 | 72.7017
SYL-W.1.RR.564.1 | 24544459148169 | Tuker Bazar, Gopal Uttar, Rehan Uddin | 2019-08-27 | MN1032 | 11.8 | 206 | 11.8 | 207 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.8 | 11.8 | 0.708 | 0.708 | 0.0007168 | 100% | 0% | 0.708 | 0.708 | 0.0011869 | 28 | 0.014193 | 0.014193 |  | 0 | 0 | 7776 | 983.9997 | 124.3305
SYL-W.1.RR.565.1 | 24544229148165 | Tuker Bazar, Gopal Uttar, Nesar Ahmed | 2019-08-27 | MN1032 | 12.5 | 208 | 12.5 | 209 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.5 | 12.5 | 0.75 | 0.75 | 0.0007168 | 100% | 0% | 0.75 | 0.75 | 0.0011869 | 28 | 0.015035 | 0.015035 |  | 0 | 0 | 7776 | 983.9997 | 131.706
SYL-W.1.RR.566.1 | 24544239148171 | Tuker Bazar, Gopal Uttar, Tushar Ahmed | 2019-08-27 | MN1032 | 13.4 | 210 | 13.4 | 211 | 2022-01-01 | [9 empty] | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0
SYL-W.1.RR.567.1 | 24544549148235 | Tuker Bazar, Sunamgonj Road, Abdul Malek Member | 2019-08-27 | MN1032 | 11.3 | 214 | 11.4 | 215 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7776 | 983.9997 | 120.1159
SYL-W.1.RR.568.1 | 24544909148596 | Jalalabad, Pirpur R/A, Block-B, Md. Monir Uddin | 2019-08-28 | MN1032 | 1.5 | 216 | 1.5 | 217 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7776 | 983.9997 | 15.8047
SYL-W.1.RR.569.1 | 24545049148595 | Jalalabad, Pirpur R/A, Block-B, Meher | 2019-08-28 | MN1032 | 2.5 | 218 | 2.5 | 219 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.5 | 2.5 | 0.15 | 0.15 | 0.0007168 | 100% | 0% | 0.15 | 0.15 | 0.0011869 | 28 | 0.003007 | 0.003007 |  | 0 | 0 | 7776 | 983.9997 | 26.3412
SYL-W.1.RR.570.1 | 24545099148579 | Jalalabad, Pirpur R/A, Block-A, Alim | 2019-08-28 | MN1032 | 1.1 | 220 | 1.1 | 221 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7776 | 983.9997 | 11.5901
SYL-W.1.RR.571.1 | 24544989148579 | Jalalabad, Pirpur R/A, Block-A, Islam | 2019-08-28 | MN1032 | 2.2 | 222 | 2.2 | 223 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7776 | 983.9997 | 23.1803
SYL-W.1.RR.572.1 | 24544859149018 | Jalalabad, Pirpur R/A, Block-B, Abdul Musaddir | 2019-08-28 | MN1032 | 2.2 | 224 | 2.2 | 225 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7776 | 983.9997 | 23.1803
SYL-W.1.RR.573.1 | 24545229149042 | Tuker Bazar, Haidarpur, Mamun | 2019-08-28 | MN1032 | 1.4 | 226 | 1.4 | 227 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.4 | 1.4 | 0.084 | 0.084 | 0.0007168 | 100% | 0% | 0.084 | 0.084 | 0.0011869 | 28 | 0.0016839 | 0.0016839 |  | 0 | 0 | 7776 | 983.9997 | 14.7511
SYL-W.1.RR.573.2 | 24545229149042 | Tuker Bazar, Haidarpur, Mamun | 2019-08-28 | MN1032 | 1.1 | 228 | 1.1 | 229 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.1 | 1.1 | 0.066 | 0.066 | 0.0007168 | 100% | 0% | 0.066 | 0.066 | 0.0011869 | 28 | 0.0013231 | 0.0013231 |  | 0 | 0 | 7776 | 983.9997 | 11.5901
SYL-W.1.RR.574.1 | 24543689149338 | Tuker Bazar, Sheikpara, Abdur Nur | 2019-08-29 | MN1032 | 5.5 | 276 | 5.5 | 277 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7824 | 935.9997 | 57.9506
SYL-W.1.RR.575.1 | 24543579149327 | Tuker Bazar, Sheikpara, Amtur Nesa | 2019-08-29 | MN1032 | 11.4 | 278 | 11.5 | 279 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.5 | 11.5 | 0.69 | 0.69 | 0.0007168 | 100% | 0% | 0.69 | 0.69 | 0.0011869 | 28 | 0.013832 | 0.013832 |  | 0 | 0 | 7824 | 935.9997 | 121.1695
SYL-W.1.RR.576.1 | 24544219149339 | Tuker Bazar, Sheikpara, Jahed Villa | 2019-08-29 | MN1032 | 14.3 | 280 | 14.1 | 281 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7824 | 935.9997 | 148.5644
SYL-W.1.RR.577.1 | 24544219149339 | Tuker Bazar, Sheikpara, Foyjur | 2019-08-29 | MN1032 | 10.3 | 282 | 10.3 | 283 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7824 | 935.9997 | 108.5258
SYL-W.1.RR.578.1 | 24543669149350 | Tuker Bazar, Sheikpara, Nasiruddin | 2019-08-29 | MN1032 | 10 | 284 | 10 | 285 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7824 | 935.9997 | 105.3648
SYL-W.1.RR.579.1 | 24543649149349 | Tuker Bazar, Sheikpara, Kamal | 2019-08-29 | MN1032 | 13.4 | 286 | 13.4 | 287 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 13.4 | 13.4 | 0.804 | 0.804 | 0.0007168 | 100% | 0% | 0.804 | 0.804 | 0.0011869 | 28 | 0.016117 | 0.016117 |  | 0 | 0 | 7824 | 935.9997 | 141.1888
SYL-W.1.RR.580.1 | 24543689149401 | Tuker Bazar, Sheikpara, Nurul | 2019-08-29 | MN1032 | 6 | 288 | 6 | 289 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7824 | 935.9997 | 63.2189
SYL-W.1.RR.581.1 | 24543659149404 | Tuker Bazar, Sheikpara, Fokrul | 2019-08-29 | MN1032 | 12.3 | 290 | 12.3 | 291 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 12.3 | 12.3 | 0.738 | 0.738 | 0.0007168 | 100% | 0% | 0.738 | 0.738 | 0.0011869 | 28 | 0.014794 | 0.014794 |  | 0 | 0 | 7824 | 935.9997 | 129.5987
SYL-W.1.RR.582.1 | 24543829149401 | Tuker Bazar, Sheikpara, Ataur Rahman | 2019-08-29 | MN1032 | 7.1 | 292 | 7.1 | 293 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7824 | 935.9997 | 74.809
SYL-W.1.RR.583.1 | 24543929149428 | Tuker Bazar, Sheikpara, Abdullah Siddik | 2019-08-29 | MN1032 | 7 | 294 | 7 | 295 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7824 | 935.9997 | 73.7554
SYL-W.1.RR.601.1 | 24540119151206 | Kazalshah, Medical College Road, Doctor's Garden | 2019-08-22 | NQ1011 | 3.2 | 235 | 3.2 | 236 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7920 | 839.9997 | 33.7167
SYL-W.1.RR.602.1 | 24540119151206 | Kazalshah, Medical College Road, Doctor's Garden | 2019-08-22 | NQ1011 | 7.2 | 237 | 7.2 | 238 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7920 | 839.9997 | 75.8627
SYL-W.1.RR.603.1 | 24535829151221 | Kazalshah, New Medical Road, Comfort Medical Services | 2019-08-24 | NQ1011 | 3.7 | 259 | 3.7 | 260 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7920 | 839.9997 | 38.985
SYL-W.1.RR.604.1 | 24540019151299 | Munshipara R/A, Osmani Medical Road, Mukit Lodge | 2019-08-24 | NQ1011 | 4.1 | 261 | 4.1 | 262 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7920 | 839.9997 | 43.1996
SYL-W.1.RR.605.1 | 24540019151299 | Munshipara R/A, Osmani Medical Road, Md. Badsha Mia | 2019-08-24 | NQ1011 | 10.2 | 263 | 10.3 | 264 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7920 | 839.9997 | 108.5258
SYL-W.1.RR.606.1 | 24540399151277 | Munshipara R/A, Osmani Medical Road, H # 15/2 | 2019-08-24 | NQ1011 | 3.5 | 265 | 3.5 | 266 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7920 | 839.9997 | 36.8777
SYL-W.1.RR.607.1 | 24540519151250 | Munshipara R/A, Osmani Medical Road, Rejoan | 2019-08-24 | NQ1011 | 5 | 267 | 5 | 268 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7920 | 839.9997 | 52.6824
SYL-W.1.RR.608.1 | 24540499151295 | Munshipara R/A, Osmani Medical Road, H # 20 | 2019-08-24 | NQ1011 | 3.2 | 269 | 3.2 | 270 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7920 | 839.9997 | 33.7167
SYL-W.1.RR.609.1 | 24540499151295 | Munshipara R/A, Osmani Medical Road, H # 16/B | 2019-08-24 | NQ1011 | 10.9 | 271 | 10.9 | 272 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7920 | 839.9997 | 114.8476
SYL-W.1.RR.610.1 | 24540789151236 | Munshipara R/A, Osmani Medical Road, H # 37/A | 2019-08-24 | NQ1011 | 8.5 | 273 | 8.5 | 274 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 8.5 | 8.5 | 0.51 | 0.51 | 0.0007168 | 100% | 0% | 0.51 | 0.51 | 0.0011869 | 28 | 0.010224 | 0.010224 |  | 0 | 0 | 7920 | 839.9997 | 89.5601
SYL-W.1.RR.611.1 | 24541059151328 | Munshipara R/A, Kewapara, Rd # 1, 122 Porshi | 2019-08-25 | LU1001 | 3.3 | 31 | 3.3 | 32 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7920 | 839.9997 | 34.7704
SYL-W.1.RR.612.1 | 24541309151327 | Kewapara, Mirer Moidan, Rd # 2, 213 Porshi | 2019-08-25 | LU1001 | 11.3 | 33 | 11.3 | 34 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7920 | 839.9997 | 119.0622
SYL-W.1.RR.613.1 | 24541269151309 | Kewapara, Mirer Moidan, Rd # 2, 217 Porshi | 2019-08-25 | LU1001 | 6.8 | 35 | 6.8 | 36 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.8 | 6.8 | 0.408 | 0.408 | 0.0007168 | 100% | 0% | 0.408 | 0.408 | 0.0011869 | 28 | 0.008179 | 0.008179 |  | 0 | 0 | 7920 | 839.9997 | 71.6481
SYL-W.1.RR.614.1 | 24541489151300 | Kewapara, Mirer Moidan, Rd # 2, 222 Porshi | 2019-08-25 | LU1001 | 10.7 | 37 | 10.7 | 38 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 10.7 | 10.7 | 0.642 | 0.642 | 0.0007168 | 100% | 0% | 0.642 | 0.642 | 0.0011869 | 28 | 0.01287 | 0.01287 |  | 0 | 0 | 7920 | 839.9997 | 112.7403
SYL-W.1.RR.615.1 | 24541799151351 | Sagordghir Par Road, Western Complex | 2019-08-25 | LU1001 | 1.8 | 39 | 1.8 | 40 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7920 | 839.9997 | 18.9657
SYL-W.1.RR.616.1 | 24541939151335 | Sylhet, Sagordighir Par, H # 3/1 | 2019-08-25 | LU1001 | 11.3 | 42 | 11.3 | 43 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7920 | 839.9997 | 119.0622
SYL-W.1.RR.617.1 | 24541809151330 | Sylhet, Sagordighir Par, Apon White House | 2019-08-25 | LU1001 | 4.5 | 44 | 4.5 | 45 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7920 | 839.9997 | 47.4142
SYL-W.1.RR.618.1 | 24541809151330 | Sylhet, Sagordighir Par, Apon White House | 2019-08-25 | LU1001 | 3.6 | 50 | 3.6 | 51 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7920 | 839.9997 | 37.9313
SYL-W.1.RR.619.1 | 24541809151330 | Sylhet, Sagordighir Par, Apon White House | 2019-08-25 | LU1001 | 2.6 | 52 | 2.6 | 53 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.6 | 2.6 | 0.156 | 0.156 | 0.0007168 | 100% | 0% | 0.156 | 0.156 | 0.0011869 | 28 | 0.0031273 | 0.0031273 |  | 0 | 0 | 7920 | 839.9997 | 27.3949
SYL-W.1.RR.620.1 | 24541809151330 | Sylhet, Sagordighir Par, Apon White House | 2019-08-25 | LU1001 | 1.9 | 54 | 1.9 | 55 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 1.9 | 1.9 | 0.114 | 0.114 | 0.0007168 | 100% | 0% | 0.114 | 0.114 | 0.0011869 | 28 | 0.0022853 | 0.0022853 |  | 0 | 0 | 7920 | 839.9997 | 20.0193
SYL-W.1.RR.621.1 | 24541809151330 | Sylhet, Sagordighir Par, Apon White House | 2019-08-25 | LU1001 | 6.6 | 56 | 6.7 | 57 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7920 | 839.9997 | 70.5944
SYL-W.1.RR.622.1 | 24544389146598 | Jalalabad, Jangail, Shahjahan Ahmed | 2019-08-27 | NQ1011 | 8.9 | 275 | 8.8 | 276 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7776 | 983.9997 | 92.721
SYL-W.1.RR.623.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 4 | 277 | 4 | 278 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7920 | 839.9997 | 42.1459
SYL-W.1.RR.624.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 7 | 279 | 7 | 280 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0 | 7920 | 839.9997 | 73.7554
SYL-W.1.RR.625.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 4.1 | 281 | 4.1 | 282 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7920 | 839.9997 | 43.1996
SYL-W.1.RR.626.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 2.1 | 283 | 2.1 | 284 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7920 | 839.9997 | 22.1266
SYL-W.1.RR.627.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 7.5 | 285 | 7.5 | 286 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7920 | 839.9997 | 79.0236
SYL-W.1.RR.628.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 3.5 | 287 | 3.5 | 288 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7920 | 839.9997 | 36.8777
SYL-W.1.RR.629.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 2 | 289 | 2 | 290 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7920 | 839.9997 | 21.073
SYL-W.1.RR.630.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 1.8 | 291 | 1.8 | 292 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 1.8 | 1.8 | 0.108 | 0.108 | 0.0007168 | 100% | 0% | 0.108 | 0.108 | 0.0011869 | 28 | 0.002165 | 0.002165 |  | 0 | 0 | 7920 | 839.9997 | 18.9657
SYL-W.1.RR.631.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 4.1 | 293 | 4.1 | 294 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7920 | 839.9997 | 43.1996
SYL-W.1.RR.632.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 2.1 | 295 | 2.1 | 296 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7920 | 839.9997 | 22.1266
SYL-W.1.RR.633.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 2.3 | 297 | 2.3 | 298 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7920 | 839.9997 | 24.2339
SYL-W.1.RR.634.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 7.5 | 299 | 7.5 | 300 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.5 | 7.5 | 0.45 | 0.45 | 0.0007168 | 100% | 0% | 0.45 | 0.45 | 0.0011869 | 28 | 0.009021 | 0.009021 |  | 0 | 0 | 7920 | 839.9997 | 79.0236
SYL-W.1.RR.635.1 | 24541919151316 | Sylhet, Sagordighir Par, Apon Blue Tower | 2019-08-27 | NQ1011 | 2.1 | 301 | 2.1 | 302 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7920 | 839.9997 | 22.1266
SYL-W.1.RR.636.1 | 24551609148574 | Noya Khurrum Khola, Badaghat Road, Abdus Sattar | 2019-08-28 | NQ1011 | 10.9 | 351 | 10.6 | 352 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7776 | 983.9997 | 111.6867
SYL-W.1.RR.637.1 | 24551609148574 | Noya Khurrum Khola, Badaghat Road, Omor Ali | 2019-08-28 | NQ1011 | 2.4 | 353 | 2.4 | 354 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7776 | 983.9997 | 25.2876
SYL-W.1.RR.638.1 | 24551999148554 | Jalalabad, Tukarbazar, Moyerchor, Muzibur Rahman | 2019-08-28 | NQ1011 | 11.6 | 357 | 11.6 | 358 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7776 | 983.9997 | 122.2232
SYL-W.1.RR.639.1 | 24552239148525 | Jalalabad, Tukarbazar, Moyerchor, Mohiuddin Ahamed | 2019-08-28 | NQ1011 | 5.8 | 359 | 5.6 | 360 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7776 | 983.9997 | 59.0043
SYL-W.1.RR.640.1 | 24552239148525 | Jalalabad, Tukarbazar, Moyerchor, Front of Sanzida Monjil | 2019-08-28 | NQ1011 | 27.9 | 361 | 27.9 | 362 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 27.9 | 27.9 | 1.674 | 1.674 | 0.0007168 | 100% | 0% | 1.674 | 1.674 | 0.0011869 | 28 | 0.033558 | 0.033558 |  | 0 | 0 | 7776 | 983.9997 | 293.9678
SYL-W.1.RR.641.1 | 24554029149086 | Chatlibond, Airport Road, Kalim Ullah | 2019-08-29 | NQ1011 | 10.9 | 363 | 10.9 | 364 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7776 | 983.9997 | 114.8476
SYL-W.1.RR.651.1 | 24541959151282 | Kotwali,Sagor Digheer Par, H # 14/4 | 2019-08-27 | NQ1011 | 1.6 | 307 | 1.6 | 308 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7920 | 839.9997 | 16.8584
SYL-W.1.RR.652.1 | 24541959151282 | Kotwali,Sagor Digheer Par, H # 14/7 | 2019-08-27 | NQ1011 | 3.5 | 309 | 3.5 | 310 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7920 | 839.9997 | 36.8777
SYL-W.1.RR.653.1 | 24542059151264 | Kotwali,Surma R/A, Sagor Digheer Par, Front of H # 18 | 2019-08-27 | NQ1011 | 6 | 311 | 6 | 312 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7920 | 839.9997 | 63.2189
SYL-W.1.RR.654.1 | 24542209151276 | Kotwali,Surma R/A, Sagor Digheer Par, H # 19/2 | 2019-08-27 | NQ1011 | 3.2 | 313 | 3.2 | 314 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7920 | 839.9997 | 33.7167
SYL-W.1.RR.655.1 | 24542209151276 | Kotwali,Surma R/A, Sagor Digheer Par, H # 19/5 | 2019-08-27 | NQ1011 | 2.8 | 317 | 2.8 | 318 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7920 | 839.9997 | 29.5021
SYL-W.1.RR.656.1 | 24542379151272 | Kotwali,Surma R/A, Sagor Digheer Par, H # 20/1 | 2019-08-27 | NQ1011 | 7.4 | 319 | 7.4 | 320 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7920 | 839.9997 | 77.97
SYL-W.1.RR.657.1 | 24542379151272 | Kotwali,Surma R/A, Sagor Digheer Par, H # 23 | 2019-08-27 | NQ1011 | 3.1 | 322 | 3.1 | 323 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 3.1 | 3.1 | 0.186 | 0.186 | 0.0007168 | 100% | 0% | 0.186 | 0.186 | 0.0011869 | 28 | 0.0037287 | 0.0037287 |  | 0 | 0 | 7920 | 839.9997 | 32.6631
SYL-W.1.RR.658.1 | 24542629151272 | Kotwali,Surma R/A, Sagor Digheer Par, H # 28/1 | 2019-08-27 | NQ1011 | 12 | 324 | 12 | 325 | 2022-01-01 | 2022-11-27 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7920 | 839.9997 | 126.4378
SYL-W.1.RR.659.1 | 24545739149032 | Jalalabad, Pirpur, Monir Complex Road, Pirpur R/A, H # 4 | 2019-08-28 | NQ1011 | 4.1 | 326 | 3.9 | 327 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7776 | 983.9997 | 41.0923
SYL-W.1.RR.660.1 | 24545839149034 | Jalalabad, Pirpur, Monir Complex Road, Pirpur R/A, H # 16 | 2019-08-28 | NQ1011 | 2.4 | 328 | 2.4 | 329 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.4 | 2.4 | 0.144 | 0.144 | 0.0007168 | 100% | 0% | 0.144 | 0.144 | 0.0011869 | 28 | 0.0028867 | 0.0028867 |  | 0 | 0 | 7776 | 983.9997 | 25.2876
SYL-W.1.RR.661.1 | 24550209149042 | Jalalabad, Pirpur, Monir Complex Road, Pirpur R/A, Shahin Ahmed | 2019-08-28 | NQ1011 | 2.2 | 330 | 2.2 | 331 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.2 | 2.2 | 0.132 | 0.132 | 0.0007168 | 100% | 0% | 0.132 | 0.132 | 0.0011869 | 28 | 0.0026461 | 0.0026461 |  | 0 | 0 | 7776 | 983.9997 | 23.1803
SYL-W.1.RR.662.1 | 24550209149042 | Jalalabad, Pirpur, Monir Complex Road, Pirpur R/A, Ansar Ali | 2019-08-28 | NQ1011 | 11.4 | 332 | 11.4 | 333 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 11.4 | 11.4 | 0.684 | 0.684 | 0.0007168 | 100% | 0% | 0.684 | 0.684 | 0.0011869 | 28 | 0.013712 | 0.013712 |  | 0 | 0 | 7776 | 983.9997 | 120.1159
SYL-W.1.RR.663.1 | 24550439149044 | Jalalabad, Pirpur, Monir Complex Road, Pirpur R/A, H # 59 | 2019-08-28 | NQ1011 | 2.1 | 334 | 2.1 | 335 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.1 | 2.1 | 0.126 | 0.126 | 0.0007168 | 100% | 0% | 0.126 | 0.126 | 0.0011869 | 28 | 0.0025259 | 0.0025259 |  | 0 | 0 | 7776 | 983.9997 | 22.1266
SYL-W.1.RR.664.1 | 24550579149045 | Jalalabad, Pirpur, Monir Complex Road, Pirpur R/A, Mokaddos Mia | 2019-08-28 | NQ1011 | 22.4 | 336 | 22.4 | 337 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 22.4 | 22.4 | 1.344 | 1.344 | 0.0007168 | 100% | 0% | 1.344 | 1.344 | 0.0011869 | 28 | 0.026943 | 0.026943 |  | 0 | 0 | 7776 | 983.9997 | 236.0172
SYL-W.1.RR.665.1 | 24550769149046 | Jalalabad, Noya Kurum Khula, Manik Khan | 2019-08-28 | NQ1011 | 12.6 | 339 | 12.6 | 340 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 12.6 | 12.6 | 0.756 | 0.756 | 0.0007168 | 100% | 0% | 0.756 | 0.756 | 0.0011869 | 28 | 0.015155 | 0.015155 |  | 0 | 0 | 7776 | 983.9997 | 132.7597
SYL-W.1.RR.666.1 | 24550779149045 | Jalalabad, Noya Kurum Khula, Nurul Islam | 2019-08-28 | NQ1011 | 2.2 | 341 | 2 | 342 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2 | 2 | 0.12 | 0.12 | 0.0007168 | 100% | 0% | 0.12 | 0.12 | 0.0011869 | 28 | 0.0024056 | 0.0024056 |  | 0 | 0 | 7776 | 983.9997 | 21.073
SYL-W.1.RR.667.1 | 24551219149000 | Jalalabad, Noya Kurum Khula, Md. Sazzad Mia | 2019-08-28 | NQ1011 | 1.7 | 343 | 1.7 | 344 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.7 | 1.7 | 0.102 | 0.102 | 0.0007168 | 100% | 0% | 0.102 | 0.102 | 0.0011869 | 28 | 0.0020448 | 0.0020448 |  | 0 | 0 | 7776 | 983.9997 | 17.912
SYL-W.1.RR.668.1 | 24551009149006 | Jalalabad, Noya Kurum Khula, Khorshed Alom | 2019-08-28 | NQ1011 | 3 | 345 | 3 | 346 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7776 | 983.9997 | 31.6094
SYL-W.1.RR.669.1 | 24551399149004 | Jalalabad, Noya Kurum Khula, Kuchir Ali | 2019-08-28 | NQ1011 | 9.6 | 347 | 9.6 | 348 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7776 | 983.9997 | 101.1502
SYL-W.1.RR.670.1 | 24551109148555 | Jalalabad, Noya Kurum Khula, Faruk Ahmed Khan | 2019-08-28 | NQ1011 | 14.6 | 349 | 14.6 | 350 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 14.6 | 14.6 | 0.876 | 0.876 | 0.0007168 | 100% | 0% | 0.876 | 0.876 | 0.0011869 | 28 | 0.017561 | 0.017561 |  | 0 | 0 | 7776 | 983.9997 | 153.8326
SYL-W.1.RR.671.1 | 24550599150329 | Akhaliya, Karipara, Block-A, Beside of Sanonda Varieties Store, Masud Mia | 2019-08-29 | NQ1011 | 20.1 | 365 | 20.1 | 366 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 20.1 | 20.1 | 1.206 | 1.206 | 0.0007168 | 100% | 0% | 1.206 | 1.206 | 0.0011869 | 28 | 0.024176 | 0.024176 |  | 0 | 0 | 7800 | 959.9997 | 211.7833
SYL-W.1.RR.672.1 | 24550649150304 | Akhaliya, Karipara, Block-A, Beside of Sanonda Varieties Store, Nur Mohammad | 2019-08-29 | NQ1011 | 3.7 | 367 | 3.7 | 368 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7800 | 959.9997 | 38.985
SYL-W.1.RR.673.1 | 24550059150347 | Akhaliya, Noapara, Block-B, H # 82, Sadek Villa | 2019-08-29 | NQ1011 | 1.5 | 369 | 1.5 | 370 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7800 | 959.9997 | 15.8047
SYL-W.1.RR.673.2 | 24550059150347 | Akhaliya, Noapara, Block-B, H # 82, Sadek Villa | 2021-02-22 | NQ1007 | 3.8 | 210 | 3.8 | 211 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7800 | 959.9997 | 40.0386
SYL-W.1.RR.674.1 | 24545869150344 | Akhaliya, Noapara, Block-B, Abdul Aziz | 2019-08-29 | NQ1011 | 9.4 | 371 | 9.4 | 372 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.4 | 9.4 | 0.564 | 0.564 | 0.0007168 | 100% | 0% | 0.564 | 0.564 | 0.0011869 | 28 | 0.011306 | 0.011306 |  | 0 | 0 | 7800 | 959.9997 | 99.0429
SYL-W.1.RR.675.1 | 24545549150360 | Akhaliya, Noapara, Block-B, H # 61 | 2019-08-29 | NQ1011 | 4.1 | 373 | 4.1 | 374 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.1 | 4.1 | 0.246 | 0.246 | 0.0007168 | 100% | 0% | 0.246 | 0.246 | 0.0011869 | 28 | 0.0049315 | 0.0049315 |  | 0 | 0 | 7800 | 959.9997 | 43.1996
SYL-W.1.RR.676.1 | 24545549150360 | Akhaliya, Noapara, Block-B, H # 60/3 | 2019-08-29 | NQ1011 | 6.6 | 377 | 6.6 | 378 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.6 | 6.6 | 0.396 | 0.396 | 0.0007168 | 100% | 0% | 0.396 | 0.396 | 0.0011869 | 28 | 0.0079384 | 0.0079384 |  | 0 | 0 | 7800 | 959.9997 | 69.5408
SYL-W.1.RR.677.1 | 24550939150294 | Akhalia, Karipara, Block-B, H # 33, Md. Junayed | 2019-08-31 | MP1006 | 12.1 | 387 | 12.1 | 388 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7800 | 959.9997 | 127.4914
SYL-W.1.RR.678.1 | 24550509150261 | Akhalia, Karipara, Block-C, Abdur Rob Mia | 2019-08-31 | MP1006 | 10.6 | 389 | 10.6 | 390 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7800 | 959.9997 | 111.6867
SYL-W.1.RR.679.1 | 24550389150246 | Akhalia, Kholapara, Renasha D-6 | 2019-08-31 | MP1006 | 6.7 | 391 | 6.7 | 392 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.7 | 6.7 | 0.402 | 0.402 | 0.0007168 | 100% | 0% | 0.402 | 0.402 | 0.0011869 | 28 | 0.0080587 | 0.0080587 |  | 0 | 0 | 7800 | 959.9997 | 70.5944
SYL-W.1.RR.680.1 | 24545949150225 | Akhalia, Borobari, 6 No Tuker Bazar Union, Afia Khatun | 2019-08-31 | MP1006 | 11.7 | 393 | 11.7 | 394 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7800 | 959.9997 | 123.2768
SYL-W.1.RR.681.1 | 24545899150211 | Akhalia, Borobari, 6 No Tuker Bazar Union, Nurul Islam | 2019-08-31 | MP1006 | 12.9 | 395 | 12.9 | 396 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.9 | 12.9 | 0.774 | 0.774 | 0.0007168 | 100% | 0% | 0.774 | 0.774 | 0.0011869 | 28 | 0.015516 | 0.015516 |  | 0 | 0 | 7800 | 959.9997 | 135.9206
SYL-W.1.RR.682.1 | 24545629150259 | Akhalia, Chandiala, Block-C, Jalalia-12, Md. Konor Ali | 2019-08-31 | MP1006 | 6.3 | 397 | 6.1 | 398 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7800 | 959.9997 | 64.2725
SYL-W.1.RR.683.1 | 24545699150441 | Akhalia, Nowapara, Block-B, H # 31 | 2019-09-01 | LX1011 | 8.2 | 395 | 8.2 | 396 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7800 | 959.9997 | 86.3991
SYL-W.1.RR.684.1 | 24545629150426 | Akhalia, Nowapara, Block-B, H # 44 | 2019-09-01 | LX1011 | 4.5 | 397 | 4.5 | 398 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.5 | 4.5 | 0.27 | 0.27 | 0.0007168 | 100% | 0% | 0.27 | 0.27 | 0.0011869 | 28 | 0.0054126 | 0.0054126 |  | 0 | 0 | 7800 | 959.9997 | 47.4142
SYL-W.1.RR.685.1 | 24545659150407 | Akhalia, Nowapara, Block-B, H # 41 | 2019-09-01 | LX1011 | 3.3 | 399 | 3.3 | 400 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.3 | 3.3 | 0.198 | 0.198 | 0.0007168 | 100% | 0% | 0.198 | 0.198 | 0.0011869 | 28 | 0.0039692 | 0.0039692 |  | 0 | 0 | 7800 | 959.9997 | 34.7704
SYL-W.1.RR.686.1 | 24545659150407 | Akhalia, Nowapara, Block-B, H # 40 | 2019-09-01 | LX1011 | 12.3 | 401 | 12.1 | 402 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7800 | 959.9997 | 127.4914
SYL-W.1.RR.687.1 | 24545389150334 | Akhalia, Nowapara, Block-C, Munim Mia | 2019-09-01 | LX1011 | 6.5 | 403 | 6.4 | 404 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7800 | 959.9997 | 67.4335
SYL-W.1.RR.688.1 | 24545389150334 | Akhalia, Nowapara, Block-C, H # 3, Lokman | 2019-09-01 | LX1011 | 11.9 | 405 | 11.9 | 406 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7800 | 959.9997 | 125.3841
SYL-W.1.RR.689.1 | 24545389150334 | Akhalia, Nowapara, Block-C, H # 2, Hannan | 2019-09-01 | LX1011 | 12.6 | 407 | 12.2 | 408 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.2 | 12.2 | 0.732 | 0.732 | 0.0007168 | 100% | 0% | 0.732 | 0.732 | 0.0011869 | 28 | 0.014674 | 0.014674 |  | 0 | 0 | 7800 | 959.9997 | 128.5451
SYL-W.1.RR.690.1 | 24545539150313 | Akhalia, Nowapara, Block-C, H # 5, Golav Villa | 2019-09-01 | LX1011 | 11.2 | 409 | 11.2 | 410 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.2 | 11.2 | 0.672 | 0.672 | 0.0007168 | 100% | 0% | 0.672 | 0.672 | 0.0011869 | 28 | 0.013471 | 0.013471 |  | 0 | 0 | 7800 | 959.9997 | 118.0086
SYL-W.1.RR.690.2 | 24545539150313 | Akhalia, Nowapara, Block-C, H # 5, Golav Villa | 2021-02-22 | NQ1007 | 3.5 | 212 | 3.5 | 213 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7800 | 959.9997 | 36.8777
SYL-W.1.RR.691.1 | 24544799150437 | Akhalia, Nowapara, Block - D, H # 13/1, Monira Monjil | 2019-09-02 | LX1011 | 12.4 | 411 | 12.4 | 412 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.4 | 12.4 | 0.744 | 0.744 | 0.0007168 | 100% | 0% | 0.744 | 0.744 | 0.0011869 | 28 | 0.014915 | 0.014915 |  | 0 | 0 | 7800 | 959.9997 | 130.6524
SYL-W.1.RR.692.1 | 24545049150435 | Akhalia, Nowapara, Block - D, Abdur Rahman | 2019-09-02 | LX1011 | 7.6 | 413 | 7.6 | 414 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7800 | 959.9997 | 80.0773
SYL-W.1.RR.693.1 | 24544959150428 | Akhalia, Nowapara, Block - D, H # 14/2 | 2019-09-02 | LX1011 | 5.5 | 415 | 5.5 | 416 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7800 | 959.9997 | 57.9506
SYL-W.1.RR.694.1 | 24544729150539 | Pathantula, Panitula, Block - B, Pallabi R/A, H # 77 | 2019-09-02 | LX1011 | 3.5 | 417 | 3.5 | 418 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7848 | 911.9997 | 36.8777
SYL-W.1.RR.695.1 | 24544869150561 | Pathantula, Panitula, Block - A, Pallabi R/A, H # 47 | 2019-09-02 | LX1011 | 6 | 419 | 6 | 420 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6 | 6 | 0.36 | 0.36 | 0.0007168 | 100% | 0% | 0.36 | 0.36 | 0.0011869 | 28 | 0.0072168 | 0.0072168 |  | 0 | 0 | 7848 | 911.9997 | 63.2189
SYL-W.1.RR.696.1 | 24545009150572 | Pathantula, Panitula, Block - A, Pallabi R/A, Shushil Kumar Ghosh | 2019-09-02 | LX1011 | 10.9 | 421 | 10.9 | 422 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7848 | 911.9997 | 114.8476
SYL-W.1.RR.697.1 | 24550359150425 | Akhalia, Kalibari, Sabujbagicha R/A, H # 11/1 | 2019-09-03 | LX1011 | 7.6 | 439 | 7.6 | 440 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7800 | 959.9997 | 80.0773
SYL-W.1.RR.698.1 | 24550359150425 | Akhalia, Kalibari, Sabujbagicha R/A, H # 13 | 2019-09-03 | LX1011 | 8.1 | 441 | 8.1 | 442 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7800 | 959.9997 | 85.3455
SYL-W.1.RR.699.1 | 24543999151049 | Pathantula, Sunamganj Road, Block-A, Nibash R/A, H # 8 | 2019-09-03 | LX1011 | 10.9 | 443 | 10.9 | 444 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7848 | 911.9997 | 114.8476
SYL-W.1.RR.701.1 | 24550139148520 | Sylhet, Khurumkhola, Shahpur, Tukerbazar, Mazar Road, Atikul Haque | 2019-08-28 | NQ1008 | 8.4 | 187 | 8.4 | 188 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 8.4 | 8.4 | 0.504 | 0.504 | 0.0007168 | 100% | 0% | 0.504 | 0.504 | 0.0011869 | 28 | 0.010103 | 0.010103 |  | 0 | 0 | 7776 | 983.9997 | 88.5064
SYL-W.1.RR.702.1 | 24551839149105 | Sylhet, Jalalabad, Nazirgau, Nazim | 2019-08-29 | NQ1008 | 5.9 | 209 | 5.5 | 210 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7776 | 983.9997 | 57.9506
SYL-W.1.RR.703.1 | 24551899149094 | Sylhet, Jalalabad, Nazirgau, Anwar Ali | 2019-08-29 | NQ1008 | 1.5 | 211 | 1.5 | 212 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 1.5 | 1.5 | 0.09 | 0.09 | 0.0007168 | 100% | 0% | 0.09 | 0.09 | 0.0011869 | 28 | 0.0018042 | 0.0018042 |  | 0 | 0 | 7776 | 983.9997 | 15.8047
SYL-W.1.RR.704.1 | 24552179149133 | Sylhet, Jalalabad, Tukerbazar, Nazirgau, Abdus Sattar | 2019-08-29 | NQ1008 | 3.6 | 213 | 3.6 | 214 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7776 | 983.9997 | 37.9313
SYL-W.1.RR.705.1 | 24552379149146 | Sylhet, Jalalabad, Tukerbazar, Nazirgau, Beside Abdus Sattar | 2019-08-29 | NQ1008 | 7.4 | 215 | 7.4 | 216 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7776 | 983.9997 | 77.97
SYL-W.1.RR.706.1 | 24552229149094 | Sylhet, Jalalabad, Tukerbazar, Nazirgau, Masuk Mia | 2019-08-29 | NQ1008 | 4 | 217 | 4 | 218 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7776 | 983.9997 | 42.1459
SYL-W.1.RR.707.1 | 24551369149130 | Sylhet, Jalalabad, Tukerbazar, Nazirgau, Monu Mia | 2019-08-29 | NQ1008 | 9.6 | 219 | 9.6 | 220 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 9.6 | 9.6 | 0.576 | 0.576 | 0.0007168 | 100% | 0% | 0.576 | 0.576 | 0.0011869 | 28 | 0.011547 | 0.011547 |  | 0 | 0 | 7776 | 983.9997 | 101.1502
SYL-W.1.RR.708.1 | 24543459150007 | Sylhet, Akhalia R/A, Anwara Road, Abdul Hay | 2019-08-29 | NQ1008 | 5.6 | 221 | 5.6 | 222 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.6 | 5.6 | 0.336 | 0.336 | 0.0007168 | 100% | 0% | 0.336 | 0.336 | 0.0011869 | 28 | 0.0067357 | 0.0067357 |  | 0 | 0 | 7824 | 935.9997 | 59.0043
SYL-W.1.RR.709.1 | 24551289150308 | Sylhet, Akhalia, Newbazar, Ujjibon R/A, Abdul Jobbar | 2019-08-31 | NQ1008 | 5.7 | 243 | 5.7 | 244 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7800 | 959.9997 | 60.0579
SYL-W.1.RR.710.1 | 24551379150279 | Sylhet, Akhalia, Newbazar, Ujjibon R/A, Razu Mia | 2019-08-31 | NQ1008 | 5.9 | 245 | 5.9 | 246 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7800 | 959.9997 | 62.1652
SYL-W.1.RR.711.1 | 24551459150258 | Sylhet, Akhalia, Newbazar, Ujjibon R/A, Lalu | 2019-08-31 | NQ1008 | 2.9 | 247 | 2.9 | 248 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7800 | 959.9997 | 30.5558
SYL-W.1.RR.712.1 | 24551509150275 | Sylhet, Akhalia, Newbazar, Ujjibon R/A, Abdur Rohim | 2019-08-31 | NQ1008 | 7.1 | 249 | 7.1 | 250 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7800 | 959.9997 | 74.809
SYL-W.1.RR.713.1 | 24551619150284 | Sylhet, Akhalia, Newbazar, Ujjibon R/A, Nozrul Islam | 2019-08-31 | NQ1008 | 3.6 | 251 | 3.6 | 252 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.6 | 3.6 | 0.216 | 0.216 | 0.0007168 | 100% | 0% | 0.216 | 0.216 | 0.0011869 | 28 | 0.0043301 | 0.0043301 |  | 0 | 0 | 7800 | 959.9997 | 37.9313
SYL-W.1.RR.714.1 | 24551849150217 | Sylhet, Akhalia, Noyabazar, Khadra, Jaher | 2019-08-31 | NQ1008 | 10 | 253 | 10 | 254 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10 | 10 | 0.6 | 0.6 | 0.0007168 | 100% | 0% | 0.6 | 0.6 | 0.0011869 | 28 | 0.012028 | 0.012028 |  | 0 | 0 | 7800 | 959.9997 | 105.3648
SYL-W.1.RR.715.1 | 24551959150218 | Sylhet, Akhalia, Noyabazar, Khadra, Muhibor Rohman | 2019-08-31 | NQ1008 | 13.3 | 255 | 13.3 | 256 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 13.3 | 13.3 | 0.798 | 0.798 | 0.0007168 | 100% | 0% | 0.798 | 0.798 | 0.0011869 | 28 | 0.015997 | 0.015997 |  | 0 | 0 | 7800 | 959.9997 | 140.1352
SYL-W.1.RR.716.1 | 24551619150186 | Sylhet, Akhalia, Sonali R/A, Zihad | 2019-08-31 | NQ1008 | 8.9 | 257 | 8.9 | 258 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7800 | 959.9997 | 93.7747
SYL-W.1.RR.717.1 | 24550059150462 | Sylhet, Brammosason, Kalibari, Kalibari Road, Abul Baset Khan | 2019-09-01 | NQ1008 | 10.9 | 277 | 10.9 | 278 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.9 | 10.9 | 0.654 | 0.654 | 0.0007168 | 100% | 0% | 0.654 | 0.654 | 0.0011869 | 28 | 0.01311 | 0.01311 |  | 0 | 0 | 7800 | 959.9997 | 114.8476
SYL-W.1.RR.718.1 | 24545999150454 | Sylhet, Kalibari, Shahjalal R/A, Block - D, Soiod Goljar Ahmed | 2019-09-01 | NQ1008 | 2.8 | 279 | 2.8 | 280 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 2.8 | 2.8 | 0.168 | 0.168 | 0.0007168 | 100% | 0% | 0.168 | 0.168 | 0.0011869 | 28 | 0.0033678 | 0.0033678 |  | 0 | 0 | 7800 | 959.9997 | 29.5021
SYL-W.1.RR.719.1 | 24550119150418 | Sylhet, Kalibari, Shahjalal R/A, Block - D, H # 16 | 2019-09-01 | NQ1008 | 5.9 | 281 | 5.9 | 282 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7800 | 959.9997 | 62.1652
SYL-W.1.RR.720.1 | 24550099150415 | Sylhet, Kalibari, Shahjalal R/A, Block - D, Shahed Ahmed | 2019-09-01 | NQ1008 | 8.1 | 283 | 8.1 | 284 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.1 | 8.1 | 0.486 | 0.486 | 0.0007168 | 100% | 0% | 0.486 | 0.486 | 0.0011869 | 28 | 0.0097426 | 0.0097426 |  | 0 | 0 | 7800 | 959.9997 | 85.3455
SYL-W.1.RR.721.1 | 24545919150408 | Sylhet, Kalibari, Shahjalal R/A, Block - C, H # 6 | 2019-09-01 | NQ1008 | 5.9 | 285 | 5.9 | 286 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.9 | 5.9 | 0.354 | 0.354 | 0.0007168 | 100% | 0% | 0.354 | 0.354 | 0.0011869 | 28 | 0.0070965 | 0.0070965 |  | 0 | 0 | 7800 | 959.9997 | 62.1652
SYL-W.1.RR.722.1 | 24542849150243 | Sylhet, Akhalia, Purbasha, Block-G, Abdul Malek | 2019-09-03 | NQ1008 | 10.2 | 299 | 10.2 | 300 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.2 | 10.2 | 0.612 | 0.612 | 0.0007168 | 100% | 0% | 0.612 | 0.612 | 0.0011869 | 28 | 0.012269 | 0.012269 |  | 0 | 0 | 7824 | 935.9997 | 107.4721
SYL-W.1.RR.723.1 | 24542789150210 | Sylhet, Akhalia, Purbasha, Block-G, Abdul Mannan | 2019-09-03 | NQ1008 | 6.4 | 301 | 6.4 | 302 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7824 | 935.9997 | 67.4335
SYL-W.1.RR.724.1 | 24542719150251 | Sylhet, Akhalia, Purbasha, Block-G, Aziruddin | 2019-09-03 | NQ1008 | 6.3 | 303 | 6.3 | 304 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7824 | 935.9997 | 66.3798
SYL-W.1.RR.725.1 | 24542139150452 | Sylhet, Uttor Bagbari, Promukto Akota, Rifaqul Islam | 2019-09-03 | NQ1008 | 6.5 | 305 | 6.5 | 306 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7848 | 911.9997 | 68.4871
SYL-W.1.RR.726.1 | 24541939150442 | Sylhet, Uttor Bagbari, Promukto Akota, Md. Golam Mahmud | 2019-09-03 | NQ1008 | 30.5 | 307 | 29.3 | 308 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 29.3 | 29.3 | 1.758 | 1.758 | 0.0007168 | 100% | 0% | 1.758 | 1.758 | 0.0011869 | 28 | 0.035242 | 0.035242 |  | 0 | 0 | 7848 | 911.9997 | 308.7189
SYL-W.1.RR.751.1 | 24545609150224 | Akhalia, Chandiala Boro Bari, Jalalia R/A, H # 20, Ruhul Alom | 2019-09-01 | LX1011 | 11.3 | 373 | 11.3 | 374 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.3 | 11.3 | 0.678 | 0.678 | 0.0007168 | 100% | 0% | 0.678 | 0.678 | 0.0011869 | 28 | 0.013592 | 0.013592 |  | 0 | 0 | 7800 | 959.9997 | 119.0622
SYL-W.1.RR.752.1 | 24545609150224 | Akhalia, Chandiala Boro Bari, Jalalia R/A, Sujon Mia | 2019-09-01 | LX1011 | 3.5 | 375 | 3.5 | 376 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0 | 7800 | 959.9997 | 36.8777
SYL-W.1.RR.753.1 | 24545569150215 | Akhalia, Chandiala Boro Bari, Jalalia R/A, H # B/16, Nuruzzaman | 2019-09-01 | LX1011 | 5 | 377 | 5 | 378 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5 | 5 | 0.3 | 0.3 | 0.0007168 | 100% | 0% | 0.3 | 0.3 | 0.0011869 | 28 | 0.006014 | 0.006014 |  | 0 | 0 | 7800 | 959.9997 | 52.6824
SYL-W.1.RR.754.1 | 24545459150212 | Akhalia, Chandiala, Jalalia R/A, Mostoba | 2019-09-01 | LX1011 | 7.2 | 381 | 7.2 | 382 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7800 | 959.9997 | 75.8627
SYL-W.1.RR.755.1 | 24545699150202 | Akhalia, Chandiala, Jalalia R/A, Sohel | 2019-09-01 | LX1011 | 5.3 | 383 | 5.3 | 384 | 2022-01-01 | [9 empty] | 5.3 | 5.3 | 0.318 | 0.318 | 0.0007168 | 100% | 0% | 0.318 | 0.318 | 0.0011869 | 28 | 0.0063748 | 0.0063748 | 2022-01-24 12:00 | 0 | 0
SYL-W.1.RR.756.1 | 24550449150112 | Akhalia, Dhamalipara, Sonali R/A, H # 79/1, Sahid Ahmed | 2019-09-01 | LX1011 | 6.9 | 385 | 6.9 | 386 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.9 | 6.9 | 0.414 | 0.414 | 0.0007168 | 100% | 0% | 0.414 | 0.414 | 0.0011869 | 28 | 0.0082993 | 0.0082993 |  | 0 | 0 | 7800 | 959.9997 | 72.7017
SYL-W.1.RR.757.1 | 24550219150075 | Akhalia, Dhamalipara, Sonali R/A, H # 103, Abdur Rahman | 2019-09-01 | LX1011 | 3.2 | 387 | 3.2 | 388 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7800 | 959.9997 | 33.7167
SYL-W.1.RR.758.1 | 24550189150094 | Akhalia, Dhamalipara, Sonali R/A, H # 105, Beside Naz Villa | 2019-09-01 | LX1011 | 3.8 | 389 | 3.8 | 390 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.8 | 3.8 | 0.228 | 0.228 | 0.0007168 | 100% | 0% | 0.228 | 0.228 | 0.0011869 | 28 | 0.0045706 | 0.0045706 |  | 0 | 0 | 7800 | 959.9997 | 40.0386
SYL-W.1.RR.759.1 | 24550459150093 | Akhalia, Dhamalipara, Sonali R/A, H # 86, Mosuddor Ali | 2019-09-01 | LX1011 | 4.9 | 391 | 4.9 | 392 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 4.9 | 4.9 | 0.294 | 0.294 | 0.0007168 | 100% | 0% | 0.294 | 0.294 | 0.0011869 | 28 | 0.0058937 | 0.0058937 |  | 0 | 0 | 7800 | 959.9997 | 51.6288
SYL-W.1.RR.760.1 | 24550459150093 | Akhalia, Dhamalipara, Sonali R/A, H # 87, Roshukuddin | 2019-09-01 | LX1011 | 3.2 | 393 | 3.2 | 394 | 2022-01-01 | [9 empty] | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0
SYL-W.1.RR.761.1 | 24544859151026 | West Pathantula, Pallobi R/A, H # C/31, Sritikona | 2019-09-02 | LX1011 | 2.3 | 423 | 2.3 | 424 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 2280 | 0 | 5568 | 911.9997 | 17.9265
SYL-W.1.RR.762.1 | 24544859151026 | West Pathantula, Pallobi R/A, H # C/3 | 2019-09-02 | LX1011 | 4 | 425 | 4 | 426 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4 | 4 | 0.24 | 0.24 | 0.0007168 | 100% | 0% | 0.24 | 0.24 | 0.0011869 | 28 | 0.0048112 | 0.0048112 |  | 0 | 0 | 7848 | 911.9997 | 42.1459
SYL-W.1.RR.763.1 | 24544859151026 | West Pathantula, Pallobi R/A, H # C/27, Hamidul Isalm | 2019-09-02 | LX1011 | 3.5 | 427 | 3.5 | 428 | 2022-01-01 | [9 empty] | 3.5 | 3.5 | 0.21 | 0.21 | 0.0007168 | 100% | 0% | 0.21 | 0.21 | 0.0011869 | 28 | 0.0042098 | 0.0042098 |  | 0 | 0
SYL-W.1.RR.764.1 | 24545069151010 | West Pathantula, Pallobi R/A, H # 12, Shofiq Monjil | 2019-09-02 | LX1011 | 3.7 | 429 | 3.7 | 430 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7848 | 911.9997 | 38.985
SYL-W.1.RR.765.1 | 24545069151010 | West Pathantula, Pallobi R/A, H # 12/1, Kajol Dey | 2019-09-02 | LX1011 | 4.8 | 431 | 4.8 | 432 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 4.8 | 4.8 | 0.288 | 0.288 | 0.0007168 | 100% | 0% | 0.288 | 0.288 | 0.0011869 | 28 | 0.0057734 | 0.0057734 |  | 0 | 0 | 7848 | 911.9997 | 50.5751
SYL-W.1.RR.766.1 | 24545169151014 | West Pathantula, Pallobi R/A, H # 14/2, Pintu | 2019-09-02 | LX1011 | 7.2 | 433 | 7.2 | 434 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7848 | 911.9997 | 75.8627
SYL-W.1.RR.767.1 | 24545479151033 | West Pathantula, Dorjipara, Mohona R/A, H # B/03 | 2019-09-02 | LX1011 | 7.1 | 435 | 7.1 | 436 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 7.1 | 7.1 | 0.426 | 0.426 | 0.0007168 | 100% | 0% | 0.426 | 0.426 | 0.0011869 | 28 | 0.0085398 | 0.0085398 |  | 0 | 0 | 7848 | 911.9997 | 74.809
SYL-W.1.RR.767.2 | 24545479151033 | West Pathantula, Dorjipara, Mohona R/A, H # B/03 | 2021-02-23 | LU1001 | 3.9 | 211 | 3.9 | 212 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 3.9 | 3.9 | 0.234 | 0.234 | 0.0007168 | 100% | 0% | 0.234 | 0.234 | 0.0011869 | 28 | 0.0046909 | 0.0046909 |  | 0 | 0 | 7848 | 911.9997 | 41.0923
SYL-W.1.RR.768.1 | 24544729151017 | West Pathantula, Pallobi R/A, Block - C, Ahammod | 2019-09-02 | LX1011 | 15.7 | 437 | 15.8 | 438 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7848 | 911.9997 | 166.4764
SYL-W.1.RR.769.1 | 24544499150585 | West Pathantula, Pallobi R/A, Block - B, H # 33, Hossain & Iqbal Monjil | 2019-09-03 | LX1011 | 12.1 | 445 | 12.1 | 446 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7848 | 911.9997 | 127.4914
SYL-W.1.RR.770.1 | 24544459150554 | West Pathantula, Pallobi R/A, H # 38/B, Sezina Begum | 2019-09-03 | LX1011 | 1.6 | 447 | 1.6 | 448 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 1.6 | 1.6 | 0.096 | 0.096 | 0.0007168 | 100% | 0% | 0.096 | 0.096 | 0.0011869 | 28 | 0.0019245 | 0.0019245 |  | 0 | 0 | 7848 | 911.9997 | 16.8584
SYL-W.1.RR.771.1 | 24544529150567 | West Pathantula, Pallobi R/A, H # 45, Ahmod Villa | 2019-09-03 | LX1011 | 1.2 | 449 | 1.2 | 450 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 1.2 | 1.2 | 0.072 | 0.072 | 0.0007168 | 100% | 0% | 0.072 | 0.072 | 0.0011869 | 28 | 0.0014434 | 0.0014434 |  | 0 | 0 | 7848 | 911.9997 | 12.6438
SYL-W.1.RR.801.1 | 24544479149137 | Kumargaon, Churugaon,Mirazuddin | 2019-08-28 | MN1032 | 2.3 | 250 | 2.3 | 251 | 2022-01-01 | 2022-11-21 | GS |  |  | 0 |  |  |  |  | 2.3 | 2.3 | 0.138 | 0.138 | 0.0007168 | 100% | 0% | 0.138 | 0.138 | 0.0011869 | 28 | 0.0027664 | 0.0027664 |  | 0 | 0 | 7776 | 983.9997 | 24.2339
SYL-W.1.RR.802.1 | 24544569149207 | Tuker Bazar, Shaheber Gaon, Zahid Hossen | 2019-08-29 | MN1032 | 3 | 252 | 3 | 253 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3 | 3 | 0.18 | 0.18 | 0.0007168 | 100% | 0% | 0.18 | 0.18 | 0.0011869 | 28 | 0.0036084 | 0.0036084 |  | 0 | 0 | 7824 | 935.9997 | 31.6094
SYL-W.1.RR.803.1 | 24544479149216 | Tuker Bazar, Shaheber Gaon, Shaduddin | 2019-08-29 | MN1032 | 5.5 | 255 | 5.5 | 256 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.5 | 5.5 | 0.33 | 0.33 | 0.0007168 | 100% | 0% | 0.33 | 0.33 | 0.0011869 | 28 | 0.0066154 | 0.0066154 |  | 0 | 0 | 7824 | 935.9997 | 57.9506
SYL-W.1.RR.804.1 | 24544199149223 | Tuker Bazar, Shaheber Gaon, Sirazul Haque | 2019-08-29 | MN1032 | 3.4 | 258 | 3.4 | 259 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7824 | 935.9997 | 35.824
SYL-W.1.RR.805.1 | 24544019149229 | Tuker Bazar, Shaheber Gaon, Mesbah | 2019-08-29 | MN1032 | 6.4 | 260 | 6.4 | 261 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.4 | 6.4 | 0.384 | 0.384 | 0.0007168 | 100% | 0% | 0.384 | 0.384 | 0.0011869 | 28 | 0.0076979 | 0.0076979 |  | 0 | 0 | 7824 | 935.9997 | 67.4335
SYL-W.1.RR.806.1 | 24543979149249 | Tuker Bazar, Shaheber Gaon, Md.Babul | 2019-08-29 | MN1032 | 11.9 | 262 | 11.9 | 263 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.9 | 11.9 | 0.714 | 0.714 | 0.0007168 | 100% | 0% | 0.714 | 0.714 | 0.0011869 | 28 | 0.014313 | 0.014313 |  | 0 | 0 | 7824 | 935.9997 | 125.3841
SYL-W.1.RR.807.1 | 24543999149309 | Tuker Bazar, Sheikh Para, Road # 3, Rubel | 2019-08-29 | MN1032 | 13 | 264 | 13 | 265 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 13 | 13 | 0.78 | 0.78 | 0.0007168 | 100% | 0% | 0.78 | 0.78 | 0.0011869 | 28 | 0.015636 | 0.015636 |  | 0 | 0 | 7824 | 935.9997 | 136.9743
SYL-W.1.RR.808.1 | 24543809149312 | Tuker Bazar, Sheikh Para, Road # 3, H # 67, Roich Mia | 2019-08-29 | MN1032 | 11.6 | 266 | 11.6 | 267 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7824 | 935.9997 | 122.2232
SYL-W.1.RR.809.1 | 24543919149295 | Tuker Bazar, Sheikh Para, Road # 3, H # 46, Md.Bodoruddin | 2019-08-29 | MN1032 | 2.9 | 268 | 2.9 | 269 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 2.9 | 2.9 | 0.174 | 0.174 | 0.0007168 | 100% | 0% | 0.174 | 0.174 | 0.0011869 | 28 | 0.0034881 | 0.0034881 |  | 0 | 0 | 7824 | 935.9997 | 30.5558
SYL-W.1.RR.810.1 | 24543919149295 | Tuker Bazar, Sheikh Para, Road # 3, H # 46, Sultan Ahmed | 2019-08-29 | MN1032 | 5.8 | 272 | 5.8 | 273 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7824 | 935.9997 | 61.1116
SYL-W.1.RR.811.1 | 24543919149295 | Tuker Bazar, Sheikh Para, Road # 3, H # 46, Abdul Hannan | 2019-08-29 | MN1032 | 3.7 | 274 | 3.7 | 275 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.7 | 3.7 | 0.222 | 0.222 | 0.0007168 | 100% | 0% | 0.222 | 0.222 | 0.0011869 | 28 | 0.0044503 | 0.0044503 |  | 0 | 0 | 7824 | 935.9997 | 38.985
SYL-W.1.RR.812.1 | 24551099150327 | Akhalia, Brahmman Sashan, Md.Sumon | 2019-08-31 | MN1032 | 12 | 316 | 12 | 317 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12 | 12 | 0.72 | 0.72 | 0.0007168 | 100% | 0% | 0.72 | 0.72 | 0.0011869 | 28 | 0.014434 | 0.014434 |  | 0 | 0 | 7800 | 959.9997 | 126.4378
SYL-W.1.RR.813.1 | 24551289150325 | Akhalia, Notum Bazar, Brahmman Sashan, Md.Mostofa Uddin | 2019-08-31 | MN1032 | 3.4 | 318 | 3.4 | 319 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 3.4 | 3.4 | 0.204 | 0.204 | 0.0007168 | 100% | 0% | 0.204 | 0.204 | 0.0011869 | 28 | 0.0040895 | 0.0040895 |  | 0 | 0 | 7800 | 959.9997 | 35.824
SYL-W.1.RR.814.1 | 24551689150309 | Akhalia, Brahmman Sashan, Babul Ahmed | 2019-08-31 | MN1032 | 13.2 | 320 | 12.7 | 321 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.7 | 12.7 | 0.762 | 0.762 | 0.0007168 | 100% | 0% | 0.762 | 0.762 | 0.0011869 | 28 | 0.015275 | 0.015275 |  | 0 | 0 | 7800 | 959.9997 | 133.8133
SYL-W.1.RR.815.1 | 24552039150273 | Akhalia, Brahmman Sashan, Juber Ahmed | 2019-08-31 | MN1032 | 7 | 324 | 7 | 325 | 2022-01-01 | [9 empty] | 7 | 7 | 0.42 | 0.42 | 0.0007168 | 100% | 0% | 0.42 | 0.42 | 0.0011869 | 28 | 0.0084196 | 0.0084196 |  | 0 | 0
SYL-W.1.RR.816.1 | 24552279150277 | Akhalia, Brahmman Sashan, Mozaffor Ahmed | 2019-08-31 | MN1032 | 14.1 | 326 | 14.1 | 327 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 14.1 | 14.1 | 0.846 | 0.846 | 0.0007168 | 100% | 0% | 0.846 | 0.846 | 0.0011869 | 28 | 0.016959 | 0.016959 |  | 0 | 0 | 7800 | 959.9997 | 148.5644
SYL-W.1.RR.817.1 | 24552279150277 | Akhalia, Brahmman Sashan, Afroz Ali Babul | 2019-08-31 | MN1032 | 5.2 | 330 | 5.2 | 331 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.2 | 5.2 | 0.312 | 0.312 | 0.0007168 | 100% | 0% | 0.312 | 0.312 | 0.0011869 | 28 | 0.0062545 | 0.0062545 |  | 0 | 0 | 7800 | 959.9997 | 54.7897
SYL-W.1.RR.818.1 | 24552969150302 | Akhalia, Brahmman Sashan, Mohammadia R/A, Jamal Ahmed | 2019-08-31 | MN1032 | 11.4 | 332 | 11.1 | 333 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.1 | 11.1 | 0.666 | 0.666 | 0.0007168 | 100% | 0% | 0.666 | 0.666 | 0.0011869 | 28 | 0.013351 | 0.013351 |  | 0 | 0 | 7800 | 959.9997 | 116.9549
SYL-W.1.RR.819.1 | 24551329150444 | Akhalia, Hawladar para, Surma R/A, H # 16/6, Asimuddin | 2019-09-01 | MN1032 | 7.4 | 338 | 7.4 | 339 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.4 | 7.4 | 0.444 | 0.444 | 0.0007168 | 100% | 0% | 0.444 | 0.444 | 0.0011869 | 28 | 0.0089007 | 0.0089007 |  | 0 | 0 | 7800 | 959.9997 | 77.97
SYL-W.1.RR.819.2 | 24551329150444 | Akhalia, Hawladar para, Surma R/A, H # 16/6, Asimuddin | 2021-02-22 | NQ1003 | 6.1 | 274 | 6.1 | 275 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7800 | 959.9997 | 64.2725
SYL-W.1.RR.820.1 | 24551329150444 | Akhalia, Hawladar para, Surma R/A, Ripon Pal | 2019-09-01 | MN1032 | 19 | 340 | 19 | 341 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 19 | 19 | 1.14 | 1.14 | 0.0007168 | 100% | 0% | 1.14 | 1.14 | 0.0011869 | 28 | 0.022853 | 0.022853 |  | 2088 | 0 | 5712 | 959.9997 | 152.4759
SYL-W.1.RR.821.1 | 24551519150439 | Akhalia, Hawladar para, Surma R/A, H # 26, Masum | 2019-09-01 | MN1032 | 12.3 | 342 | 11.6 | 343 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 11.6 | 11.6 | 0.696 | 0.696 | 0.0007168 | 100% | 0% | 0.696 | 0.696 | 0.0011869 | 28 | 0.013952 | 0.013952 |  | 0 | 0 | 7800 | 959.9997 | 122.2232
SYL-W.1.RR.822.1 | 24551449150421 | Akhalia, Hawladar para, Surma R/A, H # 23, Taher Ali | 2019-09-01 | MN1032 | 5.4 | 344 | 5.4 | 345 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7800 | 959.9997 | 56.897
SYL-W.1.RR.823.1 | 24551819150430 | Akhalia, Hawladar para, Surma R/A, H # 32, Shibul Chondro Kopali | 2019-09-02 | MN1032 | 9.9 | 346 | 9.9 | 347 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 9.9 | 9.9 | 0.594 | 0.594 | 0.0007168 | 100% | 0% | 0.594 | 0.594 | 0.0011869 | 28 | 0.011908 | 0.011908 |  | 0 | 0 | 7800 | 959.9997 | 104.3112
SYL-W.1.RR.824.1 | 24551799150454 | Akhalia, Hawladar para, Surma R/A, H # 37/1, Mithun | 2019-09-02 | MN1032 | 10.4 | 348 | 10.4 | 349 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.4 | 10.4 | 0.624 | 0.624 | 0.0007168 | 100% | 0% | 0.624 | 0.624 | 0.0011869 | 28 | 0.012509 | 0.012509 |  | 0 | 0 | 7800 | 959.9997 | 109.5794
SYL-W.1.RR.825.1 | 24545769150473 | Pathantula, Korer para, Dolon | 2019-09-02 | MN1032 | 6.1 | 350 | 6.5 | 351 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7800 | 959.9997 | 68.4871
SYL-W.1.RR.826.1 | 24545729150546 | Pathantula, Korer para, Ruhul Amin | 2019-09-02 | MN1032 | 7.2 | 352 | 7.2 | 353 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7800 | 959.9997 | 75.8627
SYL-W.1.RR.827.1 | 24544639150470 | Akhalia, Noya para, Bondhon-D, H # 12, Anwar Khan | 2019-09-02 | MN1032 | 6 | 355 | 6.1 | 356 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.1 | 6.1 | 0.366 | 0.366 | 0.0007168 | 100% | 0% | 0.366 | 0.366 | 0.0011869 | 28 | 0.007337 | 0.007337 |  | 0 | 0 | 7824 | 935.9997 | 64.2725
SYL-W.1.RR.828.1 | 24544529150479 | Akhalia, Noya para, Bondhon-C, Khaled | 2019-09-02 | MN1032 | 6.3 | 357 | 6.3 | 358 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 6.3 | 6.3 | 0.378 | 0.378 | 0.0007168 | 100% | 0% | 0.378 | 0.378 | 0.0011869 | 28 | 0.0075776 | 0.0075776 |  | 0 | 0 | 7824 | 935.9997 | 66.3798
SYL-W.1.RR.828.2 | 24544529150479 | Akhalia, Noya para, Bondhon-C, Khaled | 2021-10-25 | NQ1007 | 15.8 | 69 | 15.8 | 70 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 15.8 | 15.8 | 0.948 | 0.948 | 0.0007168 | 100% | 0% | 0.948 | 0.948 | 0.0011869 | 28 | 0.019004 | 0.019004 |  | 0 | 0 | 7824 | 935.9997 | 166.4764
SYL-W.1.RR.829.1 | 24544369150456 | Akhalia, Noya para, Bondhon-D, H # 8/3, Khaledur Rahman Chowdhury | 2019-09-02 | MN1032 | 10.3 | 359 | 10.3 | 360 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7824 | 935.9997 | 108.5258
SYL-W.1.RR.830.1 | 24543259150142 | Akhalia, Sunamganj Road, Alahi B-2, British America Tobaco | 2019-09-03 | MN1032 | 21 | 369 | 21 | 370 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 21 | 21 | 1.26 | 1.26 | 0.0007168 | 100% | 0% | 1.26 | 1.26 | 0.0011869 | 28 | 0.025259 | 0.025259 |  | 0 | 0 | 7824 | 935.9997 | 221.2661
SYL-W.1.RR.831.1 | 24544969150377 | Akhalia, Noya para, Bondhon-A, H # 29, Abdul Aziz | 2019-09-03 | MN1032 | 5.4 | 371 | 5.4 | 372 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.4 | 5.4 | 0.324 | 0.324 | 0.0007168 | 100% | 0% | 0.324 | 0.324 | 0.0011869 | 28 | 0.0064951 | 0.0064951 |  | 0 | 0 | 7800 | 959.9997 | 56.897
SYL-W.1.RR.832.1 | 24544969150377 | Akhalia, Noya para, Bondhon-A, H # 29, Rupa Mia | 2019-09-03 | MN1032 | 8.9 | 373 | 8.9 | 374 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 8.9 | 8.9 | 0.534 | 0.534 | 0.0007168 | 100% | 0% | 0.534 | 0.534 | 0.0011869 | 28 | 0.010705 | 0.010705 |  | 0 | 0 | 7800 | 959.9997 | 93.7747
SYL-W.1.RR.833.1 | 24544799150371 | Akhalia, Noya para, Bondhon-A, H # 22, Md.Jogrul Islam | 2019-09-03 | MN1032 | 16.5 | 375 | 16.2 | 376 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 16.2 | 16.2 | 0.972 | 0.972 | 0.0007168 | 100% | 0% | 0.972 | 0.972 | 0.0011869 | 28 | 0.019485 | 0.019485 |  | 0 | 0 | 7800 | 959.9997 | 170.691
SYL-W.1.RR.834.1 | 24544769150388 | Akhalia, Noya para, Bondhon-A, H # 20, Mannan | 2019-09-03 | MN1032 | 10.9 | 377 | 10.5 | 378 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.5 | 10.5 | 0.63 | 0.63 | 0.0007168 | 100% | 0% | 0.63 | 0.63 | 0.0011869 | 28 | 0.012629 | 0.012629 |  | 0 | 0 | 7800 | 959.9997 | 110.6331
SYL-W.1.RR.835.1 | 24544409150365 | Akhalia, Noya para, Bondhon-A, H # 13 | 2019-09-03 | MN1032 | 11.1 | 379 | 10.6 | 380 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7800 | 959.9997 | 111.6867
SYL-W.1.RR.851.1 | 24551659150103 | Akhalia, Sonali R/A, Md. Zakaria | 2019-09-01 | NQ1008 | 12.1 | 259 | 12.1 | 260 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7800 | 959.9997 | 127.4914
SYL-W.1.RR.852.1 | 24551549150094 | Akhalia, Sonali R/A, H # 29 | 2019-09-01 | NQ1008 | 10.6 | 261 | 10.6 | 262 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.6 | 10.6 | 0.636 | 0.636 | 0.0007168 | 100% | 0% | 0.636 | 0.636 | 0.0011869 | 28 | 0.01275 | 0.01275 |  | 0 | 0 | 7800 | 959.9997 | 111.6867
SYL-W.1.RR.852.2 | 24551549150094 | Akhalia, Sonali R/A, H # 29 | 2020-10-28 | MN1032 | 36.6 | 25 | 36.6 | 26 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 36.6 | 36.6 | 2.196 | 2.196 | 0.0007168 | 100% | 0% | 2.196 | 2.196 | 0.0011869 | 28 | 0.044022 | 0.044022 |  | 0 | 0 | 7800 | 959.9997 | 385.6352
SYL-W.1.RR.853.1 | 24551539150091 | Akhalia, Sonali R/A, H # 31 | 2019-09-01 | NQ1008 | 7.2 | 264 | 7.2 | 265 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.2 | 7.2 | 0.432 | 0.432 | 0.0007168 | 100% | 0% | 0.432 | 0.432 | 0.0011869 | 28 | 0.0086601 | 0.0086601 |  | 0 | 0 | 7800 | 959.9997 | 75.8627
SYL-W.1.RR.854.1 | 24551529150086 | Akhalia, Sonali R/A, H # 35 | 2019-09-01 | NQ1008 | 12 | 266 | 12.1 | 267 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 12.1 | 12.1 | 0.726 | 0.726 | 0.0007168 | 100% | 0% | 0.726 | 0.726 | 0.0011869 | 28 | 0.014554 | 0.014554 |  | 0 | 0 | 7800 | 959.9997 | 127.4914
SYL-W.1.RR.855.1 | 24551139150086 | Akhalia, Sonali R/A, H # 45/A | 2019-09-01 | NQ1008 | 8.2 | 268 | 7.6 | 269 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 7.6 | 7.6 | 0.456 | 0.456 | 0.0007168 | 100% | 0% | 0.456 | 0.456 | 0.0011869 | 28 | 0.0091412 | 0.0091412 |  | 0 | 0 | 7800 | 959.9997 | 80.0773
SYL-W.1.RR.856.1 | 24550719150049 | Akhalia, Sonali R/A, H # 115 | 2019-09-01 | NQ1008 | 5.1 | 270 | 5.1 | 271 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.1 | 5.1 | 0.306 | 0.306 | 0.0007168 | 100% | 0% | 0.306 | 0.306 | 0.0011869 | 28 | 0.0061343 | 0.0061343 |  | 0 | 0 | 7800 | 959.9997 | 53.7361
SYL-W.1.RR.857.1 | 24550909150098 | Akhalia, Sonali R/A, H # 62/1 | 2019-09-01 | NQ1008 | 29.9 | 272 | 29.9 | 273 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 29.9 | 29.9 | 1.794 | 1.794 | 0.0007168 | 100% | 0% | 1.794 | 1.794 | 0.0011869 | 28 | 0.035964 | 0.035964 |  | 0 | 0 | 7800 | 959.9997 | 315.0408
SYL-W.1.RR.858.1 | 24550769150152 | Akhalia, Sonali R/A, Maa Manjil, Md. Abdul Hannan | 2019-09-01 | NQ1008 | 5.7 | 275 | 5.7 | 276 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 5.7 | 5.7 | 0.342 | 0.342 | 0.0007168 | 100% | 0% | 0.342 | 0.342 | 0.0011869 | 28 | 0.0068559 | 0.0068559 |  | 0 | 0 | 7800 | 959.9997 | 60.0579
SYL-W.1.RR.859.1 | 24544169150481 | Noapara, Modina Market, Kalibari Road, H # 49 | 2019-09-02 | NQ1008 | 8.2 | 287 | 8.2 | 288 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.2 | 8.2 | 0.492 | 0.492 | 0.0007168 | 100% | 0% | 0.492 | 0.492 | 0.0011869 | 28 | 0.0098629 | 0.0098629 |  | 0 | 0 | 7824 | 935.9997 | 86.3991
SYL-W.1.RR.860.1 | 24544119150469 | Modina Market, Kalibari Road, H # 50, Hazi Suruj Monjil | 2019-09-02 | NQ1008 | 8.8 | 289 | 8.8 | 290 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 8.8 | 8.8 | 0.528 | 0.528 | 0.0007168 | 100% | 0% | 0.528 | 0.528 | 0.0011869 | 28 | 0.010585 | 0.010585 |  | 0 | 0 | 7824 | 935.9997 | 92.721
SYL-W.1.RR.861.1 | 24544009150505 | Modina Market, East Pathantula, Babul Mia | 2019-09-02 | NQ1008 | 3.2 | 291 | 3.2 | 292 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 3.2 | 3.2 | 0.192 | 0.192 | 0.0007168 | 100% | 0% | 0.192 | 0.192 | 0.0011869 | 28 | 0.0038489 | 0.0038489 |  | 0 | 0 | 7824 | 935.9997 | 33.7167
SYL-W.1.RR.862.1 | 24544079150496 | Modina Market, East Pathantula, Rahman Monjil | 2019-09-02 | NQ1008 | 15.1 | 293 | 15.1 | 294 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 15.1 | 15.1 | 0.906 | 0.906 | 0.0007168 | 100% | 0% | 0.906 | 0.906 | 0.0011869 | 28 | 0.018162 | 0.018162 |  | 0 | 0 | 7824 | 935.9997 | 159.1009
SYL-W.1.RR.863.1 | 24544189150528 | Modina Market, East Pathantula, Al-Arafa R/A, H # 25/2 | 2019-09-02 | NQ1008 | 5.8 | 295 | 5.8 | 296 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 5.8 | 5.8 | 0.348 | 0.348 | 0.0007168 | 100% | 0% | 0.348 | 0.348 | 0.0011869 | 28 | 0.0069762 | 0.0069762 |  | 0 | 0 | 7824 | 935.9997 | 61.1116
SYL-W.1.RR.864.1 | 24544259150551 | Modina Market, East Pathantula, Al-Arafa R/A, Khalilur Rahman | 2019-09-02 | NQ1008 | 13.8 | 297 | 13.8 | 298 | 2022-01-01 | 2022-11-23 | GS |  |  | 0 |  |  |  |  | 13.8 | 13.8 | 0.828 | 0.828 | 0.0007168 | 100% | 0% | 0.828 | 0.828 | 0.0011869 | 28 | 0.016599 | 0.016599 |  | 0 | 0 | 7824 | 935.9997 | 145.4034
SYL-W.1.RR.901.1 | 24552089150261 | Akhalia, Nayabazar, Brammon Shashon, Salma Begum Shetu | 2019-09-01 | MN1032 | 10.3 | 334 | 10.3 | 335 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 10.3 | 10.3 | 0.618 | 0.618 | 0.0007168 | 100% | 0% | 0.618 | 0.618 | 0.0011869 | 28 | 0.012389 | 0.012389 |  | 0 | 0 | 7800 | 959.9997 | 108.5258
SYL-W.1.RR.902.1 | 24552109150307 | Akhalia, Nayabazar, Brammon Shashon, Porimul Dash | 2019-09-01 | MN1032 | 22.3 | 336 | 22.3 | 337 | 2022-01-01 | 2022-11-22 | GS |  |  | 0 |  |  |  |  | 22.3 | 22.3 | 1.338 | 1.338 | 0.0007168 | 100% | 0% | 1.338 | 1.338 | 0.0011869 | 28 | 0.026822 | 0.026822 |  | 0 | 0 | 7800 | 959.9997 | 234.9635
SYL-W.1.RR.903.1 | 24543979151026 | West Pathantula, Ragib Rabeya Medical Road, Nibash R/A, H # 14 | 2019-09-02 | MN1032 | 11.7 | 361 | 11.7 | 362 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 11.7 | 11.7 | 0.702 | 0.702 | 0.0007168 | 100% | 0% | 0.702 | 0.702 | 0.0011869 | 28 | 0.014073 | 0.014073 |  | 0 | 0 | 7848 | 911.9997 | 123.2768
SYL-W.1.RR.904.1 | 24544329151089 | West Pathantula, Mohuna R/A, H # 56/14 | 2019-09-02 | MN1032 | 6.5 | 363 | 6.5 | 364 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 6.5 | 6.5 | 0.39 | 0.39 | 0.0007168 | 100% | 0% | 0.39 | 0.39 | 0.0011869 | 28 | 0.0078182 | 0.0078182 |  | 0 | 0 | 7848 | 911.9997 | 68.4871
SYL-W.1.RR.905.1 | 24544049151051 | Pathantula, Ragib Ali Road, Beside Monuara Complex, Omar faruk | 2019-09-02 | MN1032 | 14.3 | 365 | 14.3 | 366 | 2022-01-01 | 2022-11-24 | GS |  |  | 0 |  |  |  |  | 14.3 | 14.3 | 0.858 | 0.858 | 0.0007168 | 100% | 0% | 0.858 | 0.858 | 0.0011869 | 28 | 0.0172 | 0.0172 |  | 0 | 0 | 7848 | 911.9997 | 150.6717
[6 empty] | total | 112804 | l/m | [28 empty] | 1150336.8383
[26 empty] | hrs in monitoring period |  | 8759.9997
[26 empty] | hrs in year |  | 8760
[26 empty] | percentage of Year |  | 100%
[26 empty] | Annual BECAP |  | 1124521
[26 empty] | Comparison BECAP |  | 1124520.9643

## Outage
Leak code | Later of the Date and time when Gas supply to Unit was stopped or start of Monitoring Period | Date and time when Gas supply to Unit was started | Note | Date of monitoring during the 2022 monitoring period | Hours of Shut off for period between the start of the monitoring period through the monitoring date | Hours of Shut off for period from monitoring date through the end of the monitoring period | Start of monitoring period | End of Monitoring Period
[7 empty] | 2022-01-01 | 2022-12-31
HBG-1.RR.9.1 | 2022-08-25 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.17.2 | 2022-03-06 12:00 |  | Cut off |  | 0 | 0
HBG-1.RR.161.1 | 2022-01-01 12:00 | 2022-03-01 12:00 | Outages | 2022-09-27 | 1416 | 0
HBG-1.RR.216.1 | 2022-08-29 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.353.1 | 2022-03-08 12:00 | 2022-09-13 12:00 | Outages | 2022-10-12 | 4536 | 0
HBG-1.RR.356.1 | 2022-01-01 12:00 |  | Cut off |  | 0 | 0
HBG-1.RR.390.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.497.1 | 2022-09-04 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.497.2 | 2022-09-04 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.562.1 | 2022-02-27 12:00 | 2022-09-01 12:00 | Outages | 2022-09-24 | 4464 | 0
HBG-1.RR.739.1 | 2022-01-01 12:00 | 2022-02-28 12:00 | Outages | 2022-10-03 | 1392 | 0
HBG-1.RR.765.1 | 2022-03-10 12:00 |  | Cut off |  | 0 | 0
HBG-1.RR.774.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.805.1 | 2022-01-01 12:00 | 2022-02-27 12:00 | Outages | 2022-09-26 | 1368 | 0
HBG-1.RR.837.1 | 2022-01-01 12:00 | 2022-03-16 12:00 | Outages | 2022-09-28 | 1776 | 0
HBG-1.RR.947.1 | 2022-02-28 12:00 | 2022-09-04 12:00 | Outages | 2022-09-29 | 4512 | 0
HBG-1.RR.1013.1 | 2022-09-28 12:00 | 2022-10-02 12:00 | Outages | 2022-10-08 | 96 | 0
HBG-1.RR.1013.2 | 2022-09-28 12:00 | 2022-10-02 12:00 | Outages | 2022-10-08 | 96 | 0
HBG-1.RR.1048.1 | 2022-03-06 12:00 | 2022-09-15 12:00 | Outages | 2022-10-10 | 4632 | 0
HBG-1.RR.1119.1 | 2022-03-06 12:00 | 2022-09-04 12:00 | Outages | 2022-10-08 | 4368 | 0
HBG-1.RR.1183.1 | 2022-09-12 12:00 |  | Cut off |  | 0 | 0
HBG-1.RR.1226.1 | 2022-01-01 12:00 | 2022-09-14 12:00 | Outages | 2022-10-03 | 6144 | 0
HBG-1.RR.1271.1 | 2022-01-01 12:00 | 2022-03-17 12:00 | Outages | 2022-10-01 | 1800 | 0
HBG-1.RR.1276.1 | 2022-09-14 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.1419.1 | 2022-08-11 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.1471.1 | 2022-02-23 12:00 | 2022-02-28 12:00 | Outages | 2022-10-01 | 120 | 0
HBG-1.RR.1513.1 | 2022-02-24 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.1515.1 | 2022-09-13 12:00 |  | Outages |  | 0 | 0
HBG-1.RR.1521.1 | 2022-02-24 12:00 | 2022-09-11 12:00 | Outages | 2022-10-06 | 4776 | 0
HBG-3.RR.154.1 | 2022-06-16 12:00 |  | Outages |  | 0 | 0
HBG-3.RR.198.1 | 2022-02-28 12:00 |  | Outages |  | 0 | 0
HBG-4.RR.205.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
HBG-4.RR.253.1 | 2022-01-01 12:00 | 2022-09-01 12:00 | Outages | 2022-09-18 | 5832 | 0
MBZ-1.RR.7.1 | 2022-01-01 12:00 | 2022-03-08 12:00 | Outages | 2022-10-15 | 1584 | 0
MBZ-1.RR.14.1 | 2022-10-20 10:00 | 2022-10-20 16:00 | Outages | 2022-10-08 | 0 | 6
MBZ-1.RR.40.1 | 2022-10-20 12:00 |  | Outages |  | 0 | 0
MBZ-1.RR.42.1 | 2022-03-24 12:00 |  | Outages |  | 0 | 0
MBZ-1.RR.89.1 | 2022-03-13 09:00 | 2022-03-13 15:00 | Outages | 2022-10-15 | 6 | 0
MBZ-1.RR.89.2 | 2022-03-13 12:00 | 2022-03-13 16:00 | Outages | 2022-10-15 | 4 | 0
MBZ-1.RR.114.1 | 2022-03-15 12:00 | 2022-03-16 12:00 | Outages | 2022-10-04 | 24 | 0
MBZ-1.RR.147.1 | 2022-01-16 11:00 | 2022-01-16 16:00 | Outages | 2022-10-08 | 5 | 0
MBZ-1.RR.177.1 | 2022-09-18 12:00 |  | Outages |  | 0 | 0
MBZ-1.RR.221.1 | 2022-01-10 12:00 | 2022-01-10 17:00 | Outages | 2022-10-27 | 5 | 0
MBZ-1.RR.274.1 | 2022-01-10 10:00 | 2022-01-10 16:30 | Outages | 2022-10-22 | 6.5 | 0
MBZ-1.RR.303.1 | 2022-10-10 12:00 | 2022-11-06 12:00 | Outages | 2022-10-08 | 0 | 648
MBZ-1.RR.345.1 | 2022-01-17 10:30 | 2022-01-17 15:30 | Outages | 2022-10-22 | 5 | 0
MBZ-1.RR.370.1 | 2022-01-01 12:00 | 2022-03-15 12:00 | Outages | 2022-10-15 | 1752 | 0
MBZ-1.RR.393.1 | 2022-01-16 12:00 | 2022-02-07 12:00 | Outages | 2022-10-13 | 528 | 0
MBZ-1.RR.393.2 | 2022-01-16 12:00 | 2022-02-07 12:00 | Outages | 2022-10-13 | 528 | 0
MBZ-1.RR.417.1 | 2022-04-13 12:00 | 2022-04-13 17:00 | Outages | 2022-10-16 | 5 | 0
MBZ-1.RR.427.1 | 2022-09-19 12:00 |  | Cut off |  | 0 | 0
MBZ-1.RR.433.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
MBZ-1.RR.479.1 | 2022-01-13 11:00 | 2022-01-13 15:00 | Outages | 2022-10-04 | 4 | 0
MBZ-1.RR.481.1 | 2022-03-07 12:00 | 2022-03-09 12:00 | Outages | 2022-10-04 | 48 | 0
MBZ-1.RR.547.1 | 2022-02-08 12:00 | 2022-02-09 12:00 | Outages | 2022-10-19 | 24 | 0
MBZ-1.RR.547.2 | 2022-02-08 12:00 | 2022-02-09 12:00 | Outages | 2022-10-19 | 24 | 0
MBZ-1.RR.565.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
MBZ-1.RR.589.1 | 2022-04-12 12:00 | 2022-04-13 12:00 | Outages | 2022-10-20 | 24 | 0
MBZ-1.RR.589.2 | 2022-04-12 12:00 | 2022-04-13 12:00 | Outages | 2022-10-20 | 24 | 0
MBZ-1.RR.607.1 | 2022-04-12 12:00 | 2022-04-13 12:00 | Outages | 2022-10-17 | 24 | 0
MBZ-1.RR.609.1 | 2022-01-18 09:30 | 2022-01-18 15:00 | Outages | 2022-10-06 | 5.5 | 0
MBZ-1.RR.690.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
MBZ-1.RR.721.1 | 2022-02-08 10:00 | 2022-02-08 16:00 | Outages | 2022-10-13 | 6 | 0
MBZ-1.RR.738.1 | 2022-08-22 10:00 | 2022-08-22 16:30 | Outages | 2022-10-06 | 6.5 | 0
MBZ-1.RR.788.1 | 2022-01-09 09:30 | 2022-01-09 13:00 | Outages | 2022-10-08 | 3.5 | 0
MBZ-1.RR.799.1 | 2022-03-24 12:00 | 2022-03-29 12:00 | Outages | 2022-10-18 | 120 | 0
MBZ-1.RR.821.1 | 2022-03-13 12:00 | 2022-03-15 12:00 | Outages | 2022-10-19 | 48 | 0
MBZ-1.RR.821.2 | 2022-03-13 12:00 | 2022-03-15 12:00 | Outages | 2022-10-19 | 48 | 0
MBZ-1.RR.826.1 | 2022-03-13 12:00 | 2022-03-13 17:00 | Outages | 2022-10-27 | 5 | 0
MBZ-1.RR.830.1 | 2022-06-13 12:00 | 2022-08-22 12:00 | Outages | 2022-10-18 | 1680 | 0
MBZ-1.RR.830.2 | 2022-06-13 12:00 | 2022-08-22 12:00 | Outages | 2022-10-18 | 1680 | 0
MBZ-1.RR.915.1 | 2022-02-17 10:00 | 2022-02-17 16:00 | Outages | 2022-10-18 | 6 | 0
MBZ-1.RR.1004.1 | 2022-02-23 12:00 | 2022-09-28 12:00 | Outages | 2022-10-19 | 5208 | 0
MBZ-1.RR.1011.1 | 2022-01-10 12:00 | 2022-01-12 12:00 | Outages | 2022-10-26 | 48 | 0
MBZ-1.RR.1023.1 | 2022-03-13 09:00 | 2022-03-13 16:30 | Outages | 2022-10-18 | 7.5 | 0
MBZ-1.RR.1179.1 | 2022-03-10 12:30 | 2022-03-10 17:00 | Outages | 2022-10-16 | 4.5 | 0
MBZ-1.RR.1251.1 | 2022-03-10 12:00 | 2022-09-11 12:00 | Outages | 2022-10-16 | 4440 | 0
MBZ-1.RR.1251.2 | 2022-03-10 12:00 | 2022-09-11 12:00 | Outages | 2022-10-16 | 4440 | 0
MBZ-2.RR.35.1 | 2022-02-23 12:00 |  | Outages |  | 0 | 0
MBZ-2.RR.66.1 | 2022-01-01 12:00 | 2022-09-12 12:00 | Outages | 2022-09-14 | 6096 | 0
MBZ-2.RR.137.1 | 2022-09-12 12:00 |  | Cut off |  | 0 | 0
MBZ-2.RR.279.1 | 2022-03-03 12:00 | 2022-08-03 12:00 | Outages | 2022-09-15 | 3672 | 0
MBZ-3.RR.57.1 | 2022-09-11 12:00 |  | Outages |  | 0 | 0
MBZ-3.RR.351.1 | 2022-09-11 12:00 |  | Outages |  | 0 | 0
MBZ-3.RR.62.1 | 2022-02-28 12:00 |  | Cut off |  | 0 | 0
MBZ-4.RR.50.1 | 2022-09-13 12:00 |  | Outages |  | 0 | 0
MBZ-4.RR.116.1 | 2022-01-01 12:00 | 2022-02-28 12:00 | Outages | 2022-09-26 | 1392 | 0
MBZ-4.RR.248.1 | 2022-03-01 12:00 |  | Outages |  | 0 | 0
MBZ-4.RR.256.1 | 2022-03-01 12:00 |  | Outages |  | 0 | 0
SMG-1.RR.37.1 | 2022-01-01 12:00 | 2022-09-14 12:00 | Outages | 2022-10-30 | 6144 | 0
SMG-1.RR.153.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SMG-1.RR.227.1 | 2022-10-04 12:00 |  | Cut off |  | 0 | 0
SMG-1.RR.265.1 | 2022-09-27 12:00 | 2022-09-28 12:00 | Outages | 2022-10-29 | 24 | 0
SMG-1.RR.289.1 | 2022-01-01 12:00 | 2022-02-24 12:00 | Outages | 2022-11-03 | 1296 | 0
SMG-1.RR.370.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SMG-1.RR.406.1 | 2022-01-01 12:00 | 2022-02-27 12:00 | Outages |  | 0 | 0
SMG-1.RR.410.1 | 2022-10-20 12:00 | 2022-10-25 12:00 | Outages | 2022-10-31 | 120 | 0
SMG-1.RR.616.1 | 2022-01-01 12:00 | 2022-02-24 12:00 | Outages | 2022-11-02 | 1296 | 0
SMG-1.RR.742.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SMG-1.RR.760.1 | 2022-02-24 12:00 | 2022-09-12 12:00 | Outages | 2022-11-02 | 4800 | 0
SMG-1.RR.767.1 | 2022-02-24 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.15.1 | 2022-09-20 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.75.1 | 2022-11-02 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.149.1 | 2022-03-15 12:00 | 2022-03-24 12:00 | Outages | 2022-12-01 | 216 | 0
SMG-2.RR.238.1 | 2022-02-01 12:00 | 2022-02-10 12:00 | Outages | 2022-11-27 | 216 | 0
SMG-2.RR.295.1 | 2022-11-01 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.302.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.330.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.330.2 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.371.1 | 2022-01-30 12:00 | 2022-02-03 12:00 | Outages | 2022-11-30 | 96 | 0
SMG-2.RR.378.1 | 2022-08-04 12:00 |  | Outages |  | 0 | 0
SMG-2.RR.385.1 | 2022-01-01 12:00 |  | Cut off |  | 0 | 0
SMG-2.RR.414.1 | 2022-05-25 12:00 | 2022-06-06 12:00 | Outages | 2022-11-27 | 288 | 0
SMG-2.RR.414.2 | 2022-05-25 12:00 | 2022-06-06 12:00 | Outages | 2022-11-27 | 288 | 0
SMG-2.RR.753.1 | 2022-10-04 12:00 |  | Outages |  | 0 | 0
SYL-B.1.CR.4.1 | 2022-08-10 12:00 |  | Cut off |  | 0 | 0
SYL-B.1.RR.10.1 | 2022-01-01 12:00 | 2022-03-01 12:00 | Outages | 2022-10-27 | 1416 | 0
SYL-B.1.RR.64.1 | 2022-03-02 12:00 | 2022-05-18 12:00 | Outages | 2022-10-22 | 1848 | 0
SYL-B.1.RR.69.1 | 2022-03-06 12:00 |  | Outages |  | 0 | 0
SYL-B.1.RR.82.1 | 2022-04-05 12:00 | 2022-09-28 12:00 | Outages | 2022-10-20 | 4224 | 0
SYL-B.1.RR.125.1 | 2022-08-16 12:00 |  | Cut off |  | 0 | 0
SYL-B.1.RR.129.1 | 2022-03-07 12:00 | 2022-08-08 12:00 | Outages | 2022-10-17 | 3696 | 0
SYL-B.1.RR.334.1 | 2022-08-25 12:00 |  | Outages |  | 0 | 0
SYL-B.1.RR.334.2 | 2022-08-25 12:00 |  | Outages |  | 0 | 0
SYL-B.1.RR.421.1 | 2022-01-01 12:00 | 2022-03-22 12:00 | Outages | 2022-10-16 | 1920 | 0
SYL-B.1.RR.451.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.41.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.32.1 | 2022-10-11 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.238.1 | 2022-01-01 12:00 | 2022-04-25 12:00 | Outages | 2022-11-08 | 2736 | 0
SYL-E.1.RR.388.1 | 2022-10-04 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.552.1 | 2022-01-01 12:00 | 2022-05-15 12:00 | Outages | 2022-11-09 | 3216 | 0
SYL-E.1.RR.557.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.564.1 | 2022-01-01 12:00 | 2022-10-19 12:00 | Outages | 2022-11-09 | 6984 | 0
SYL-E.1.RR.571.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.934.1 | 2022-04-20 12:00 | 2022-09-07 12:00 | Outages | 2022-11-13 | 3360 | 0
SYL-E.1.RR.1027.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.1096.1 | 2022-04-15 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.1316.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-E.1.RR.1441.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-F.RR.66.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-F.RR.151.1 | 2022-07-14 12:00 |  | Outages |  | 0 | 0
SYL-F.RR.157.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-F.RR.251.1 | 2022-09-13 12:00 | 2022-09-14 12:00 | Outages | 2022-09-29 | 24 | 0
SYL-F.RR.310.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-F.RR.384.1 | 2022-09-13 12:00 |  | Outages |  | 0 | 0
SYL-G.1.RR.227.1 | 2022-01-01 12:00 |  | Cut off |  | 0 | 0
SYL-G.1.RR.328.1 | 2022-01-01 12:00 | 2022-03-03 12:00 | Outages | 2022-11-02 | 1464 | 0
SYL-G.1.RR.328.2 | 2022-01-01 12:00 | 2022-03-03 12:00 | Outages | 2022-11-02 | 1464 | 0
SYL-G.1.RR.380.1 | 2022-01-01 12:00 | 2022-03-15 12:00 | Outages | 2022-11-05 | 1752 | 0
SYL-G.1.RR.559.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-G.1.RR.569.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-G.1.RR.717.1 | 2022-01-01 12:00 | 2022-09-03 12:00 | Outages | 2022-10-31 | 5880 | 0
SYL-N.1.RR.108.1 | 2022-11-08 12:00 |  | Outages |  | 0 | 0
SYL-N.1.RR.356.1 | 2022-11-02 12:00 |  | Outages |  | 0 | 0
SYL-N.1.RR.430.1 | 2022-01-10 12:00 | 2022-03-08 12:00 | Outages | 2022-12-01 | 1368 | 0
SYL-N.1.RR.507.1 | 2022-01-01 | 2022-03-16 12:00 | Outages | 2022-12-06 | 1788 | 0
SYL-N.1.RR.593.1 | 2022-03-08 12:00 | 2022-06-15 12:00 | Outages | 2022-12-11 | 2376 | 0
SYL-N.1.RR.835.1 | 2022-11-22 12:00 |  | Outages |  | 0 | 0
SYL-N.1.RR.866.1 | 2022-03-23 12:00 |  | Outages |  | 0 | 0
SYL-S.1.RR.301.1 | 2022-01-01 12:00 | 2022-11-09 12:00 | Outages | 2022-11-20 | 7488 | 0
SYL-S.1.RR.301.2 | 2022-01-01 12:00 | 2022-11-09 12:00 | Outages | 2022-11-20 | 7488 | 0
SYL-S.1.RR.339.1 | 2022-01-01 12:00 | 2022-04-28 12:00 | Outages | 2022-11-10 | 2808 | 0
SYL-S.1.RR.357.1 | 2022-01-26 12:00 | 2022-03-02 12:00 | Outages | 2022-11-16 | 840 | 0
SYL-S.1.RR.384.1 | 2022-05-16 12:00 |  | Cut off |  | 0 | 0
SYL-S.1.RR.409.1 | 2022-05-09 12:00 |  | Outages |  | 0 | 0
SYL-S.1.RR.415.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-S.1.RR.419.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-S.1.RR.434.1 | 2022-01-01 12:00 | 2022-02-15 12:00 | Outages | 2022-11-09 | 1080 | 0
SYL-S.1.RR.537.1 | 2022-01-01 12:00 | 2022-05-02 12:00 | Outages | 2022-11-08 | 2904 | 0
SYL-S.1.RR.870.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-W.1.RR.61.1 | 2022-01-01 12:00 | 2022-03-28 12:00 | Outages | 2022-11-23 | 2064 | 0
SYL-W.1.RR.61.2 | 2022-01-01 12:00 | 2022-03-28 12:00 | Outages | 2022-11-23 | 2064 | 0
SYL-W.1.RR.304.1 | 2022-01-01 12:00 |  | Cut off |  | 0 | 0
SYL-W.1.RR.307.1 | 2022-01-01 12:00 | 2022-05-04 12:00 | Outages | 2022-11-24 | 2952 | 0
SYL-W.1.RR.330.1 | 2022-01-01 12:00 |  | Cut off |  | 0 | 0
SYL-W.1.RR.344.1 | 2022-01-01 12:00 | 2022-03-03 12:00 | Outages | 2022-11-30 | 1464 | 0
SYL-W.1.RR.395.1 | 2022-01-01 12:00 | 2022-11-06 12:00 | Outages | 2022-11-27 | 7416 | 0
SYL-W.1.RR.413.1 | 2022-03-22 12:00 |  | Cut off |  | 0 | 0
SYL-W.1.RR.566.1 | 2022-01-01 12:00 |  | Outages |  | 0 | 0
SYL-W.1.RR.755.1 | 2022-01-24 12:00 |  | Cut off |  | 0 | 0
SYL-W.1.RR.761.1 | 2022-01-01 12:00 | 2022-04-06 12:00 | Outages | 2022-11-24 | 2280 | 0
SYL-W.1.RR.815.1 | 2022-03-01 12:00 |  | Outages |  | 0 | 0
SYL-W.1.RR.820.1 | 2022-01-01 12:00 | 2022-03-29 12:00 | Outages | 2022-11-22 | 2088 | 0
HBG-1.RR.1866.1 | 2022-03-02 12:00 | 2022-07-05 12:00 | Outages | 2022-10-10 | 3000 | 0

## Uncertainty
Leak ID | Later of Date of repair and start date of Monitoring Period | Total Leaks l/m (x) | Uncertainty of Each Measurement (Hi-flow sampler ±10%) (U) | (x*U)2 | Monitoring Date | Total Leaks l/m (x) | Uncertainty of Each Measurement (Hi-flow sampler ±10%) (U) | (x*U)2
HBG-1.CR.1.1 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.1.1 | 2022-01-01 | 2.8 | 10% | 0.0784 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.2.1 | 2022-01-01 | 1.1 | 10% | 0.0121 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.3.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.4.1 | 2022-01-01 | 1.9 | 10% | 0.0361 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.5.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.6.1 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.7.1 | 2022-01-01 | 9.2 | 10% | 0.8464 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.8.1 | 2022-01-01 | 1.7 | 10% | 0.0289 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.9.1 | 2022-01-01 | 10.5 | 10% | 1.1025 |  |  | 10%
HBG-1.RR.10.1 | 2022-01-01 | 3.8 | 10% | 0.1444 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.11.1 | 2022-01-01 | 6.6 | 10% | 0.4356 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.12.1 | 2022-01-01 | 16.9 | 10% | 2.8561 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.13.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.14.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.15.1 | 2022-01-01 | 12 | 10% | 1.44 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.17.1 | 2022-01-01 | 63.4 | 10% | 40.1956 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.17.2 | 2022-01-01 | 33.5 | 10% | 11.2225 |  |  | 10%
HBG-1.RR.18.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.19.1 | 2022-01-01 | 9.3 | 10% | 0.8649 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.20.1 | 2022-01-01 | 13.3 | 10% | 1.7689 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.21.1 | 2022-01-01 | 13.7 | 10% | 1.8769 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.22.1 | 2022-01-01 | 9.9 | 10% | 0.9801 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.23.1 | 2022-01-01 | 7.2 | 10% | 0.5184 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.24.1 | 2022-01-01 | 1.2 | 10% | 0.0144 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.25.1 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.26.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.27.1 | 2022-01-01 | 7.8 | 10% | 0.6084 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.28.1 | 2022-01-01 | 3.1 | 10% | 0.0961 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.29.1 | 2022-01-01 | 2.8 | 10% | 0.0784 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.30.1 | 2022-01-01 | 1.2 | 10% | 0.0144 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.31.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.32.1 | 2022-01-01 | 22.5 | 10% | 5.0625 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.33.1 | 2022-01-01 | 25.1 | 10% | 6.3001 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.34.1 | 2022-01-01 | 13.8 | 10% | 1.9044 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.35.1 | 2022-01-01 | 38.1 | 10% | 14.5161 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.36.1 | 2022-01-01 | 20.5 | 10% | 4.2025 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.36.2 | 2022-04-03 | 11.3 | 10% | 1.2769 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.37.1 | 2022-01-01 | 4.9 | 10% | 0.2401 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.38.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.39.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.39.2 | 2022-01-01 | 2.5 | 10% | 0.0625 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.40.1 | 2022-01-01 | 8.1 | 10% | 0.6561 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.41.1 | 2022-01-01 | 4 | 10% | 0.16 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.42.1 | 2022-01-01 | 19.2 | 10% | 3.6864 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.43.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.44.1 | 2022-01-01 | 2.4 | 10% | 0.0576 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.45.1 | 2022-01-01 | 1.5 | 10% | 0.0225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.46.1 | 2022-01-01 | 7.8 | 10% | 0.6084 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.47.1 | 2022-01-01 | 22.4 | 10% | 5.0176 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.48.1 | 2022-01-01 | 18.2 | 10% | 3.3124 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.49.1 | 2022-01-01 | 13.3 | 10% | 1.7689 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.50.1 | 2022-01-01 | 5 | 10% | 0.25 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.51.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.52.1 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.53.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.54.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.55.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.56.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.57.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.58.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.59.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.60.1 | 2022-01-01 | 4.2 | 10% | 0.1764 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.61.1 | 2022-01-01 | 1.2 | 10% | 0.0144 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.62.1 | 2022-01-01 | 2.3 | 10% | 0.0529 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.63.1 | 2022-01-01 | 2.7 | 10% | 0.0729 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.64.1 | 2022-01-01 | 1 | 10% | 0.01 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.65.1 | 2022-01-01 | 3.2 | 10% | 0.1024 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.66.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.67.1 | 2022-01-01 | 1.4 | 10% | 0.0196 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.68.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.69.1 | 2022-01-01 | 13.1 | 10% | 1.7161 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.70.1 | 2022-01-01 | 14.3 | 10% | 2.0449 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.71.1 | 2022-01-01 | 13.9 | 10% | 1.9321 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.71.2 | 2022-04-03 | 2.5 | 10% | 0.0625 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.72.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.73.1 | 2022-01-01 | 5.9 | 10% | 0.3481 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.74.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.75.1 | 2022-01-01 | 12.6 | 10% | 1.5876 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.76.1 | 2022-01-01 | 26.2 | 10% | 6.8644 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.77.1 | 2022-01-01 | 9.2 | 10% | 0.8464 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.78.1 | 2022-01-01 | 23.2 | 10% | 5.3824 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.79.1 | 2022-01-01 | 17.5 | 10% | 3.0625 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.79.2 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.80.1 | 2022-01-01 | 13.1 | 10% | 1.7161 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.81.1 | 2022-01-01 | 14.4 | 10% | 2.0736 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.81.2 | 2022-04-03 | 11.6 | 10% | 1.3456 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.82.1 | 2022-01-01 | 20.6 | 10% | 4.2436 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.83.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.84.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.85.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.86.1 | 2022-01-01 | 13 | 10% | 1.69 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.86.2 | 2022-01-01 | 2.1 | 10% | 0.0441 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.87.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.88.1 | 2022-01-01 | 8 | 10% | 0.64 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.89.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.90.1 | 2022-01-01 | 21.3 | 10% | 4.5369 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.91.1 | 2022-01-01 | 21.3 | 10% | 4.5369 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.92.1 | 2022-01-01 | 6.1 | 10% | 0.3721 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.93.1 | 2022-01-01 | 9.9 | 10% | 0.9801 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.94.1 | 2022-01-01 | 14.3 | 10% | 2.0449 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.95.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.96.1 | 2022-01-01 | 4.7 | 10% | 0.2209 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.97.1 | 2022-01-01 | 24 | 10% | 5.76 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.98.1 | 2022-01-01 | 18.1 | 10% | 3.2761 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.99.1 | 2022-01-01 | 4.1 | 10% | 0.1681 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.100.1 | 2022-01-01 | 94.9 | 10% | 90.0601 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.101.1 | 2022-01-01 | 3.8 | 10% | 0.1444 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.102.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.103.1 | 2022-01-01 | 15.3 | 10% | 2.3409 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.104.1 | 2022-01-01 | 9.4 | 10% | 0.8836 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.105.1 | 2022-01-01 | 2.1 | 10% | 0.0441 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.106.1 | 2022-01-01 | 6.6 | 10% | 0.4356 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.107.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.108.1 | 2022-01-01 | 5 | 10% | 0.25 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.109.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.110.1 | 2022-01-01 | 15.8 | 10% | 2.4964 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.111.1 | 2022-01-01 | 13.5 | 10% | 1.8225 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.112.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.113.1 | 2022-01-01 | 9.7 | 10% | 0.9409 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.114.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.115.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.116.1 | 2022-01-01 | 8.8 | 10% | 0.7744 |  |  | 10%
HBG-1.RR.117.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.118.1 | 2022-01-01 | 16.1 | 10% | 2.5921 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.119.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.120.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.121.1 | 2022-01-01 | 9.3 | 10% | 0.8649 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.122.1 | 2022-01-01 | 15.8 | 10% | 2.4964 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.123.1 | 2022-01-01 | 8.2 | 10% | 0.6724 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.124.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.125.1 | 2022-01-01 | 10 | 10% | 1 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.126.1 | 2022-01-01 | 7.9 | 10% | 0.6241 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.127.1 | 2022-01-01 | 12.5 | 10% | 1.5625 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.128.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.129.1 | 2022-01-01 | 7.9 | 10% | 0.6241 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.130.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.130.2 | 2022-01-01 | 6.4 | 10% | 0.4096 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.131.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.132.1 | 2022-01-01 | 4.2 | 10% | 0.1764 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.133.1 | 2022-01-01 | 19.8 | 10% | 3.9204 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.134.1 | 2022-01-01 | 12.5 | 10% | 1.5625 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.135.1 | 2022-01-01 | 13.4 | 10% | 1.7956 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.135.2 | 2022-09-22 | 5.2 | 10% | 0.2704 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.136.1 | 2022-01-01 | 6.7 | 10% | 0.4489 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.137.1 | 2022-01-01 | 12.4 | 10% | 1.5376 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.138.1 | 2022-01-01 | 12 | 10% | 1.44 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.139.1 | 2022-01-01 | 5 | 10% | 0.25 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.140.1 | 2022-01-01 | 17.5 | 10% | 3.0625 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.141.1 | 2022-01-01 | 3.2 | 10% | 0.1024 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.142.1 | 2022-01-01 | 4.3 | 10% | 0.1849 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.143.1 | 2022-01-01 | 13.2 | 10% | 1.7424 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.143.2 | 2022-09-22 | 3.1 | 10% | 0.0961 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.144.1 | 2022-01-01 | 2.2 | 10% | 0.0484 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.145.1 | 2022-01-01 | 6.7 | 10% | 0.4489 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.146.1 | 2022-01-01 | 34.8 | 10% | 12.1104 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.147.1 | 2022-01-01 | 1.5 | 10% | 0.0225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.148.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.149.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.150.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.150.2 | 2022-01-01 | 7.9 | 10% | 0.6241 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.151.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.152.1 | 2022-01-01 | 3.6 | 10% | 0.1296 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.153.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.154.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.155.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.156.1 | 2022-01-01 | 6 | 10% | 0.36 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.157.1 | 2022-01-01 | 3.5 | 10% | 0.1225 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.158.1 | 2022-01-01 | 16.8 | 10% | 2.8224 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.159.1 | 2022-01-01 | 8 | 10% | 0.64 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.160.1 | 2022-01-01 | 7.5 | 10% | 0.5625 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.161.1 | 2022-01-01 | 10.5 | 10% | 1.1025 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.162.1 | 2022-01-01 | 10 | 10% | 1 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.163.1 | 2022-01-01 | 6 | 10% | 0.36 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.164.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.165.1 | 2022-01-01 | 3.1 | 10% | 0.0961 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.166.1 | 2022-01-01 | 5.5 | 10% | 0.3025 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.167.1 | 2022-01-01 | 8.4 | 10% | 0.7056 |  |  | 10%
HBG-1.RR.168.1 | 2022-01-01 | 54.7 | 10% | 29.9209 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.169.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.170.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.171.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.172.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.173.1 | 2022-01-01 | 4.7 | 10% | 0.2209 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.174.1 | 2022-01-01 | 4.3 | 10% | 0.1849 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.175.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.176.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.177.1 | 2022-01-01 | 12.4 | 10% | 1.5376 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.178.1 | 2022-01-01 | 6.5 | 10% | 0.4225 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.179.1 | 2022-01-01 | 4.1 | 10% | 0.1681 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.180.1 | 2022-01-01 | 5 | 10% | 0.25 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.180.2 | 2022-03-13 | 13.1 | 10% | 1.7161 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.181.1 | 2022-01-01 | 15.2 | 10% | 2.3104 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.181.2 | 2022-03-13 | 7.3 | 10% | 0.5329 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.182.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.182.2 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.183.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.184.1 | 2022-01-01 | 8.6 | 10% | 0.7396 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.185.1 | 2022-01-01 | 15.4 | 10% | 2.3716 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.186.1 | 2022-01-01 | 5.4 | 10% | 0.2916 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.187.1 | 2022-01-01 | 15.6 | 10% | 2.4336 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.188.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.189.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.190.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.191.1 | 2022-01-01 | 13.1 | 10% | 1.7161 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.192.1 | 2022-01-01 | 12.2 | 10% | 1.4884 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.193.1 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.193.2 | 2022-10-11 | 4.7 | 10% | 0.2209 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.194.1 | 2022-01-01 | 2.6 | 10% | 0.0676 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.195.1 | 2022-01-01 | 3.7 | 10% | 0.1369 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.196.1 | 2022-01-01 | 6.1 | 10% | 0.3721 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.197.1 | 2022-01-01 | 9.6 | 10% | 0.9216 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.198.1 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.199.1 | 2022-01-01 | 12.2 | 10% | 1.4884 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.200.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.201.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.202.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.203.1 | 2022-01-01 | 5.5 | 10% | 0.3025 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.204.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.205.1 | 2022-01-01 | 10 | 10% | 1 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.206.1 | 2022-01-01 | 9.7 | 10% | 0.9409 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.207.1 | 2022-01-01 | 13 | 10% | 1.69 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.207.2 | 2022-03-12 | 6.2 | 10% | 0.3844 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.208.1 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.209.1 | 2022-01-01 | 5.6 | 10% | 0.3136 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.210.1 | 2022-01-01 | 3.7 | 10% | 0.1369 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.210.2 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.211.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.212.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.213.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.214.1 | 2022-01-01 | 22 | 10% | 4.84 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.215.1 | 2022-01-01 | 14.7 | 10% | 2.1609 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.215.2 | 2022-03-12 | 10.3 | 10% | 1.0609 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.216.1 | 2022-01-01 | 8.1 | 10% | 0.6561 |  |  | 10%
HBG-1.RR.217.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.218.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.219.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.220.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.221.1 | 2022-01-01 | 7.2 | 10% | 0.5184 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.222.1 | 2022-01-01 | 4.3 | 10% | 0.1849 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.223.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.224.1 | 2022-01-01 | 9.7 | 10% | 0.9409 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.225.1 | 2022-01-01 | 14.8 | 10% | 2.1904 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.226.1 | 2022-01-01 | 7 | 10% | 0.49 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.227.1 | 2022-01-01 | 5 | 10% | 0.25 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.228.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.229.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.230.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.230.2 | 2022-09-21 | 8.9 | 10% | 0.7921 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.231.1 | 2022-01-01 | 58.1 | 10% | 33.7561 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.232.1 | 2022-01-01 | 12.6 | 10% | 1.5876 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.233.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.234.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.235.1 | 2022-01-01 | 13.8 | 10% | 1.9044 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.236.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.237.1 | 2022-01-01 | 8.8 | 10% | 0.7744 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.238.1 | 2022-01-01 | 5.4 | 10% | 0.2916 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.239.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.240.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.241.1 | 2022-01-01 | 9.3 | 10% | 0.8649 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.242.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.243.1 | 2022-01-01 | 27.5 | 10% | 7.5625 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.244.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.245.1 | 2022-01-01 | 9.3 | 10% | 0.8649 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.246.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.247.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.248.1 | 2022-01-01 | 9.6 | 10% | 0.9216 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.249.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.250.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.251.1 | 2022-01-01 | 9.5 | 10% | 0.9025 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.252.1 | 2022-01-01 | 9.9 | 10% | 0.9801 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.253.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.254.1 | 2022-01-01 | 14.7 | 10% | 2.1609 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.255.1 | 2022-01-01 | 9.9 | 10% | 0.9801 | 2022-10-12 | 1.6 | 10% | 0.0256
HBG-1.RR.256.1 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.257.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.258.1 | 2022-01-01 | 9.6 | 10% | 0.9216 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.259.1 | 2022-01-01 | 20.6 | 10% | 4.2436 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.260.1 | 2022-01-01 | 15 | 10% | 2.25 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.261.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.262.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.263.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.264.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.265.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.266.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.267.1 | 2022-01-01 | 9.4 | 10% | 0.8836 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.268.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.269.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.270.1 | 2022-01-01 | 13.1 | 10% | 1.7161 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.271.1 | 2022-01-01 | 9.8 | 10% | 0.9604 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.271.2 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.272.1 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.273.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.274.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.275.1 | 2022-01-01 | 9.5 | 10% | 0.9025 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.276.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.277.1 | 2022-01-01 | 4.9 | 10% | 0.2401 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.278.1 | 2022-01-01 | 10 | 10% | 1 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.279.1 | 2022-01-01 | 12.5 | 10% | 1.5625 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.280.1 | 2022-01-01 | 13.3 | 10% | 1.7689 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.281.1 | 2022-01-01 | 15.1 | 10% | 2.2801 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.282.1 | 2022-01-01 | 12 | 10% | 1.44 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.283.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.284.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.285.1 | 2022-01-01 | 15.7 | 10% | 2.4649 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.286.1 | 2022-01-01 | 11.2 | 10% | 1.2544 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.287.1 | 2022-01-01 | 19.7 | 10% | 3.8809 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.288.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.289.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.290.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.290.2 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.291.1 | 2022-01-01 | 22.9 | 10% | 5.2441 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.292.1 | 2022-01-01 | 4.7 | 10% | 0.2209 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.293.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.294.1 | 2022-01-01 | 9.7 | 10% | 0.9409 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.295.1 | 2022-01-01 | 7.9 | 10% | 0.6241 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.296.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.297.1 | 2022-01-01 | 13.6 | 10% | 1.8496 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.298.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.299.1 | 2022-01-01 | 13 | 10% | 1.69 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.300.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.301.1 | 2022-01-01 | 18.9 | 10% | 3.5721 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.301.2 | 2022-01-01 | 15.1 | 10% | 2.2801 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.302.1 | 2022-01-01 | 10.5 | 10% | 1.1025 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.302.2 | 2022-01-01 | 3 | 10% | 0.09 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.303.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-10-04 | 0 | 10% | 0
HBG-1.RR.304.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.305.1 | 2022-01-01 | 14.9 | 10% | 2.2201 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.306.1 | 2022-01-01 | 21.8 | 10% | 4.7524 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.307.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.308.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.309.1 | 2022-01-01 | 18.6 | 10% | 3.4596 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.310.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.311.1 | 2022-01-01 | 14.7 | 10% | 2.1609 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.312.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.312.2 | 2022-01-01 | 11.2 | 10% | 1.2544 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.313.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.314.1 | 2022-01-01 | 20.9 | 10% | 4.3681 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.315.1 | 2022-01-01 | 17.5 | 10% | 3.0625 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.316.1 | 2022-01-01 | 11.2 | 10% | 1.2544 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.317.1 | 2022-01-01 | 16.4 | 10% | 2.6896 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.318.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.319.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.320.1 | 2022-01-01 | 23.5 | 10% | 5.5225 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.321.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.322.1 | 2022-01-01 | 22.6 | 10% | 5.1076 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.323.1 | 2022-01-01 | 61.3 | 10% | 37.5769 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.324.1 | 2022-01-01 | 13.4 | 10% | 1.7956 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.325.1 | 2022-01-01 | 13.3 | 10% | 1.7689 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.326.1 | 2022-01-01 | 11.2 | 10% | 1.2544 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.327.1 | 2022-01-01 | 13.8 | 10% | 1.9044 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.328.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.329.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.330.1 | 2022-01-01 | 18.7 | 10% | 3.4969 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.330.2 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.331.1 | 2022-01-01 | 14.6 | 10% | 2.1316 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.332.1 | 2022-01-01 | 9.9 | 10% | 0.9801 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.333.1 | 2022-01-01 | 19.3 | 10% | 3.7249 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.334.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.335.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.336.1 | 2022-01-01 | 10 | 10% | 1 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.337.1 | 2022-01-01 | 13.7 | 10% | 1.8769 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.338.1 | 2022-01-01 | 52.7 | 10% | 27.7729 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.339.1 | 2022-01-01 | 17.9 | 10% | 3.2041 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.339.2 | 2022-03-13 | 2.9 | 10% | 0.0841 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.340.1 | 2022-01-01 | 7.2 | 10% | 0.5184 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.341.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.342.1 | 2022-01-01 | 8.1 | 10% | 0.6561 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.343.1 | 2022-01-01 | 8.1 | 10% | 0.6561 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.344.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.345.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.346.1 | 2022-01-01 | 25 | 10% | 6.25 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.346.2 | 2022-01-01 | 107 | 10% | 114.49 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.347.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.347.2 | 2022-03-13 | 11.6 | 10% | 1.3456 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.348.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.349.1 | 2022-01-01 | 18.5 | 10% | 3.4225 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.349.2 | 2022-01-01 | 2.2 | 10% | 0.0484 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.350.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.351.1 | 2022-01-01 | 15.3 | 10% | 2.3409 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.352.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.353.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.354.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.355.1 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.356.1 | 2022-01-01 | 1.5 | 10% | 0.0225 |  |  | 10%
HBG-1.RR.357.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.358.1 | 2022-01-01 | 19.1 | 10% | 3.6481 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.359.1 | 2022-01-01 | 19.9 | 10% | 3.9601 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.360.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.361.1 | 2022-01-01 | 14.6 | 10% | 2.1316 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.362.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.363.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.364.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.365.1 | 2022-01-01 | 13.9 | 10% | 1.9321 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.367.1 | 2022-01-01 | 13.6 | 10% | 1.8496 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.368.1 | 2022-01-01 | 8 | 10% | 0.64 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.369.1 | 2022-01-01 | 9.8 | 10% | 0.9604 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.370.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.371.1 | 2022-01-01 | 3 | 10% | 0.09 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.372.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.373.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.374.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.375.1 | 2022-01-01 | 15.3 | 10% | 2.3409 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.376.1 | 2022-01-01 | 7.8 | 10% | 0.6084 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.377.1 | 2022-01-01 | 14 | 10% | 1.96 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.378.1 | 2022-01-01 | 5.4 | 10% | 0.2916 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.379.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.380.1 | 2022-01-01 | 6.1 | 10% | 0.3721 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.381.1 | 2022-01-01 | 5.4 | 10% | 0.2916 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.382.1 | 2022-01-01 | 4.1 | 10% | 0.1681 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.383.1 | 2022-01-01 | 3.8 | 10% | 0.1444 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.383.2 | 2022-01-01 | 21.4 | 10% | 4.5796 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.384.1 | 2022-01-01 | 2 | 10% | 0.04 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.385.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.386.1 | 2022-01-01 | 7.5 | 10% | 0.5625 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.387.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.388.1 | 2022-01-01 | 23.6 | 10% | 5.5696 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.389.1 | 2022-01-01 | 3.7 | 10% | 0.1369 | 2022-09-21 | 0 | 10% | 0
HBG-1.RR.390.1 | 2022-01-01 | 54.2 | 10% | 29.3764 |  |  | 10%
HBG-1.RR.391.1 | 2022-01-01 | 15.1 | 10% | 2.2801 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.392.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.392.2 | 2022-03-12 | 5.6 | 10% | 0.3136 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.393.1 | 2022-01-01 | 24.7 | 10% | 6.1009 | 2022-09-27 | 0 | 10% | 0
HBG-1.RR.394.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.395.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.396.1 | 2022-01-01 | 14 | 10% | 1.96 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.397.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.398.1 | 2022-01-01 | 8.6 | 10% | 0.7396 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.399.1 | 2022-01-01 | 29.3 | 10% | 8.5849 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.400.1 | 2022-01-01 | 23.2 | 10% | 5.3824 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.401.1 | 2022-01-01 | 3.8 | 10% | 0.1444 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.402.1 | 2022-01-01 | 13.5 | 10% | 1.8225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.403.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.404.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.405.1 | 2022-01-01 | 45.7 | 10% | 20.8849 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.406.1 | 2022-01-01 | 18.8 | 10% | 3.5344 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.407.1 | 2022-01-01 | 6.2 | 10% | 0.3844 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.408.1 | 2022-01-01 | 13.7 | 10% | 1.8769 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.409.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.410.1 | 2022-01-01 | 4.1 | 10% | 0.1681 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.411.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.412.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.413.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.413.2 | 2022-01-01 | 12.2 | 10% | 1.4884 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.414.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.415.1 | 2022-01-01 | 2.4 | 10% | 0.0576 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.416.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.417.1 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.418.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.419.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.420.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.421.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.422.1 | 2022-01-01 | 14 | 10% | 1.96 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.423.1 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.424.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.425.1 | 2022-01-01 | 4.7 | 10% | 0.2209 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.426.1 | 2022-01-01 | 3 | 10% | 0.09 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.427.1 | 2022-01-01 | 30.6 | 10% | 9.3636 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.428.1 | 2022-01-01 | 18.8 | 10% | 3.5344 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.428.2 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.429.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.430.1 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.431.1 | 2022-01-01 | 1.8 | 10% | 0.0324 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.432.1 | 2022-01-01 | 14.3 | 10% | 2.0449 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.433.1 | 2022-01-01 | 8.8 | 10% | 0.7744 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.434.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.435.1 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.435.2 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.436.1 | 2022-01-01 | 21.8 | 10% | 4.7524 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.437.1 | 2022-01-01 | 3.4 | 10% | 0.1156 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.438.1 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.439.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.440.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.441.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.442.1 | 2022-01-01 | 4.8 | 10% | 0.2304 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.443.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.444.1 | 2022-01-01 | 9.8 | 10% | 0.9604 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.445.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.446.1 | 2022-01-01 | 6.9 | 10% | 0.4761 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.447.1 | 2022-01-01 | 3.1 | 10% | 0.0961 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.448.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.449.1 | 2022-01-01 | 7.5 | 10% | 0.5625 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.450.1 | 2022-01-01 | 6.5 | 10% | 0.4225 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.451.1 | 2022-01-01 | 3.7 | 10% | 0.1369 |  |  | 10%
HBG-1.RR.452.1 | 2022-01-01 | 3.3 | 10% | 0.1089 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.453.1 | 2022-01-01 | 13.2 | 10% | 1.7424 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.453.2 | 2022-01-01 | 4 | 10% | 0.16 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.454.1 | 2022-01-01 | 3.5 | 10% | 0.1225 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.455.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.456.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.457.1 | 2022-01-01 | 3 | 10% | 0.09 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.458.1 | 2022-01-01 | 15.4 | 10% | 2.3716 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.459.1 | 2022-01-01 | 11.2 | 10% | 1.2544 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.460.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.461.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.462.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.463.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.464.1 | 2022-01-01 | 5.4 | 10% | 0.2916 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.465.1 | 2022-01-01 | 7.8 | 10% | 0.6084 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.466.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.467.1 | 2022-01-01 | 8.8 | 10% | 0.7744 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.468.1 | 2022-01-01 | 18 | 10% | 3.24 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.469.1 | 2022-01-01 | 5.9 | 10% | 0.3481 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.470.1 | 2022-01-01 | 8.8 | 10% | 0.7744 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.471.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.472.1 | 2022-01-01 | 9.2 | 10% | 0.8464 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.473.1 | 2022-01-01 | 6.1 | 10% | 0.3721 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.474.1 | 2022-01-01 | 12.5 | 10% | 1.5625 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.475.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.476.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.477.1 | 2022-01-01 | 3.8 | 10% | 0.1444 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.478.1 | 2022-01-01 | 15.6 | 10% | 2.4336 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.479.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.480.1 | 2022-01-01 | 5.5 | 10% | 0.3025 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.480.2 | 2022-01-01 | 6.5 | 10% | 0.4225 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.481.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.482.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.483.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.483.2 | 2022-03-22 | 3.8 | 10% | 0.1444 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.484.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.485.1 | 2022-01-01 | 4.7 | 10% | 0.2209 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.485.2 | 2022-03-22 | 12 | 10% | 1.44 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.486.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.487.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.488.1 | 2022-01-01 | 17.3 | 10% | 2.9929 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.489.1 | 2022-01-01 | 1.7 | 10% | 0.0289 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.490.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.491.1 | 2022-01-01 | 4.3 | 10% | 0.1849 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.492.1 | 2022-01-01 | 3 | 10% | 0.09 |  |  | 10%
HBG-1.RR.493.1 | 2022-01-01 | 3.8 | 10% | 0.1444 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.494.1 | 2022-01-01 | 5 | 10% | 0.25 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.495.1 | 2022-01-01 | 3.9 | 10% | 0.1521 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.496.1 | 2022-01-01 | 21.2 | 10% | 4.4944 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.497.1 | 2022-01-01 | 8.4 | 10% | 0.7056 |  |  | 10%
HBG-1.RR.497.2 | 2022-01-01 | 3.2 | 10% | 0.1024 |  |  | 10%
HBG-1.RR.498.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-10-02 | 0 | 10% | 0
HBG-1.RR.499.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-10-02 | 0 | 10% | 0
HBG-1.RR.500.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-10-02 | 0 | 10% | 0
HBG-1.RR.501.1 | 2022-01-01 | 9.9 | 10% | 0.9801 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.502.1 | 2022-01-01 | 6 | 10% | 0.36 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.503.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.504.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.505.1 | 2022-01-01 | 9 | 10% | 0.81 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.506.1 | 2022-01-01 | 10.5 | 10% | 1.1025 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.507.1 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.508.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.509.1 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.510.1 | 2022-01-01 | 7.5 | 10% | 0.5625 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.511.1 | 2022-01-01 | 6.4 | 10% | 0.4096 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.512.1 | 2022-01-01 | 17.6 | 10% | 3.0976 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.513.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.514.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.515.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.516.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.517.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.518.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.519.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.520.1 | 2022-01-01 | 8.2 | 10% | 0.6724 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.521.1 | 2022-01-01 | 6.5 | 10% | 0.4225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.522.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.522.2 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.523.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.524.1 | 2022-01-01 | 8.6 | 10% | 0.7396 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.525.1 | 2022-01-01 | 23.1 | 10% | 5.3361 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.526.1 | 2022-01-01 | 13.7 | 10% | 1.8769 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.527.1 | 2022-01-01 | 14.2 | 10% | 2.0164 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.528.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.529.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.530.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.531.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.532.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.533.1 | 2022-01-01 | 15.1 | 10% | 2.2801 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.534.1 | 2022-01-01 | 18.1 | 10% | 3.2761 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.535.1 | 2022-01-01 | 10.5 | 10% | 1.1025 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.536.1 | 2022-01-01 | 7.5 | 10% | 0.5625 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.537.1 | 2022-01-01 | 7.2 | 10% | 0.5184 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.538.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.539.1 | 2022-01-01 | 7.7 | 10% | 0.5929 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.540.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.541.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.542.1 | 2022-01-01 | 4.8 | 10% | 0.2304 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.543.1 | 2022-01-01 | 9.6 | 10% | 0.9216 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.544.1 | 2022-01-01 | 6.4 | 10% | 0.4096 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.545.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.546.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.547.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.548.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.548.2 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.549.1 | 2022-01-01 | 11.2 | 10% | 1.2544 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.550.1 | 2022-01-01 | 7.5 | 10% | 0.5625 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.551.1 | 2022-01-01 | 7.8 | 10% | 0.6084 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.552.1 | 2022-01-01 | 5.3 | 10% | 0.2809 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.553.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.554.1 | 2022-01-01 | 32.9 | 10% | 10.8241 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.555.1 | 2022-01-01 | 12 | 10% | 1.44 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.556.1 | 2022-01-01 | 14.5 | 10% | 2.1025 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.557.1 | 2022-01-01 | 16 | 10% | 2.56 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.558.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.559.1 | 2022-01-01 | 19.2 | 10% | 3.6864 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.560.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.561.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.562.1 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.563.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.564.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.565.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.566.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.567.1 | 2022-01-01 | 6.4 | 10% | 0.4096 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.568.1 | 2022-01-01 | 14.1 | 10% | 1.9881 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.569.1 | 2022-01-01 | 10 | 10% | 1 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.570.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.571.1 | 2022-01-01 | 9.6 | 10% | 0.9216 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.572.1 | 2022-01-01 | 13.4 | 10% | 1.7956 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.573.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.574.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.575.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.576.1 | 2022-01-01 | 2.3 | 10% | 0.0529 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.577.1 | 2022-01-01 | 8.6 | 10% | 0.7396 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.578.1 | 2022-01-01 | 4.2 | 10% | 0.1764 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.579.1 | 2022-01-01 | 12.2 | 10% | 1.4884 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.580.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.581.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.582.1 | 2022-01-01 | 12 | 10% | 1.44 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.583.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.584.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.585.1 | 2022-01-01 | 4 | 10% | 0.16 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.586.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.586.2 | 2022-01-01 | 21.8 | 10% | 4.7524 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.587.1 | 2022-01-01 | 22.8 | 10% | 5.1984 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.588.1 | 2022-01-01 | 2.4 | 10% | 0.0576 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.589.1 | 2022-01-01 | 6.7 | 10% | 0.4489 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.590.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.591.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.592.1 | 2022-01-01 | 2.8 | 10% | 0.0784 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.593.1 | 2022-01-01 | 20.8 | 10% | 4.3264 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.594.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.595.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.596.1 | 2022-01-01 | 8 | 10% | 0.64 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.597.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.598.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.599.1 | 2022-01-01 | 18.5 | 10% | 3.4225 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.600.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.601.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.602.1 | 2022-01-01 | 34.5 | 10% | 11.9025 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.602.2 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-10-12 | 0 | 10% | 0
HBG-1.RR.603.1 | 2022-01-01 | 27.2 | 10% | 7.3984 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.604.1 | 2022-01-01 | 18.9 | 10% | 3.5721 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.605.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.606.1 | 2022-01-01 | 20.2 | 10% | 4.0804 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.607.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.608.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.609.1 | 2022-01-01 | 14.4 | 10% | 2.0736 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.610.1 | 2022-01-01 | 8.2 | 10% | 0.6724 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.611.1 | 2022-01-01 | 20.8 | 10% | 4.3264 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.612.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.613.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.614.1 | 2022-01-01 | 17.9 | 10% | 3.2041 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.615.1 | 2022-01-01 | 9.9 | 10% | 0.9801 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.616.1 | 2022-01-01 | 20 | 10% | 4 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.617.1 | 2022-01-01 | 13.8 | 10% | 1.9044 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.618.1 | 2022-01-01 | 18.4 | 10% | 3.3856 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.619.1 | 2022-01-01 | 7.7 | 10% | 0.5929 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.620.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.621.1 | 2022-01-01 | 6.9 | 10% | 0.4761 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.621.2 | 2022-09-20 | 11.5 | 10% | 1.3225 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.622.1 | 2022-01-01 | 8.6 | 10% | 0.7396 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.623.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.624.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.625.1 | 2022-01-01 | 13.9 | 10% | 1.9321 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.626.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.627.1 | 2022-01-01 | 20.6 | 10% | 4.2436 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.628.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.629.1 | 2022-01-01 | 5.4 | 10% | 0.2916 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.630.1 | 2022-01-01 | 7.2 | 10% | 0.5184 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.631.1 | 2022-01-01 | 9.2 | 10% | 0.8464 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.632.1 | 2022-01-01 | 17.6 | 10% | 3.0976 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.633.1 | 2022-01-01 | 6.9 | 10% | 0.4761 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.633.2 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.634.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.635.1 | 2022-01-01 | 5.9 | 10% | 0.3481 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.636.1 | 2022-01-01 | 22.2 | 10% | 4.9284 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.637.1 | 2022-01-01 | 13.2 | 10% | 1.7424 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.638.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.639.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.640.1 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.641.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.642.1 | 2022-01-01 | 8.2 | 10% | 0.6724 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.643.1 | 2022-01-01 | 12.5 | 10% | 1.5625 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.644.1 | 2022-01-01 | 12.6 | 10% | 1.5876 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.645.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.646.1 | 2022-01-01 | 8.8 | 10% | 0.7744 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.647.1 | 2022-01-01 | 9.6 | 10% | 0.9216 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.648.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.649.1 | 2022-01-01 | 22.6 | 10% | 5.1076 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.650.1 | 2022-01-01 | 24.1 | 10% | 5.8081 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.651.1 | 2022-01-01 | 8.3 | 10% | 0.6889 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.651.2 | 2022-01-01 | 27.4 | 10% | 7.5076 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.652.1 | 2022-01-01 | 18.9 | 10% | 3.5721 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.653.1 | 2022-01-01 | 6.5 | 10% | 0.4225 | 2022-10-11 | 0 | 10% | 0
HBG-1.RR.654.1 | 2022-01-01 | 58.2 | 10% | 33.8724 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.655.1 | 2022-01-01 | 35.8 | 10% | 12.8164 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.656.1 | 2022-01-01 | 12.2 | 10% | 1.4884 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.657.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.658.1 | 2022-01-01 | 2.9 | 10% | 0.0841 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.659.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.660.1 | 2022-01-01 | 6.4 | 10% | 0.4096 |  |  | 10%
HBG-1.RR.661.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.662.1 | 2022-01-01 | 4.2 | 10% | 0.1764 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.663.1 | 2022-01-01 | 1.4 | 10% | 0.0196 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.664.1 | 2022-01-01 | 4.8 | 10% | 0.2304 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.665.1 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.666.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.667.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.668.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.669.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.670.1 | 2022-01-01 | 8 | 10% | 0.64 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.670.2 | 2022-01-01 | 4.6 | 10% | 0.2116 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.671.1 | 2022-01-01 | 35.8 | 10% | 12.8164 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.672.1 | 2022-01-01 | 8 | 10% | 0.64 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.673.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.674.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.675.1 | 2022-01-01 | 8 | 10% | 0.64 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.676.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.677.1 | 2022-01-01 | 13.2 | 10% | 1.7424 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.678.1 | 2022-01-01 | 8.1 | 10% | 0.6561 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.679.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.679.2 | 2022-01-01 | 6.7 | 10% | 0.4489 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.680.1 | 2022-01-01 | 19.2 | 10% | 3.6864 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.681.1 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.682.1 | 2022-01-01 | 9.5 | 10% | 0.9025 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.683.1 | 2022-01-01 | 7 | 10% | 0.49 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.684.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.685.1 | 2022-01-01 | 4.2 | 10% | 0.1764 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.686.1 | 2022-01-01 | 23.6 | 10% | 5.5696 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.687.1 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.688.1 | 2022-01-01 | 4.3 | 10% | 0.1849 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.689.1 | 2022-01-01 | 17.7 | 10% | 3.1329 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.690.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-24 | 0 | 10% | 0
HBG-1.RR.691.1 | 2022-01-01 | 18.2 | 10% | 3.3124 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.692.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.693.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.694.1 | 2022-01-01 | 19.5 | 10% | 3.8025 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.694.2 | 2022-01-01 | 5.1 | 10% | 0.2601 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.695.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.695.2 | 2022-01-01 | 12.2 | 10% | 1.4884 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.696.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.697.1 | 2022-01-01 | 9.3 | 10% | 0.8649 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.698.1 | 2022-01-01 | 5.6 | 10% | 0.3136 | 2022-09-20 | 0 | 10% | 0
HBG-1.RR.699.1 | 2022-01-01 | 9.2 | 10% | 0.8464 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.700.1 | 2022-01-01 | 13 | 10% | 1.69 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.700.2 | 2022-09-26 | 13.1 | 10% | 1.7161 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.701.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.702.1 | 2022-01-01 | 6.9 | 10% | 0.4761 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.703.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.704.1 | 2022-01-01 | 20.4 | 10% | 4.1616 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.705.1 | 2022-01-01 | 18.1 | 10% | 3.2761 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.706.1 | 2022-01-01 | 14.9 | 10% | 2.2201 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.707.1 | 2022-01-01 | 4.9 | 10% | 0.2401 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.708.1 | 2022-01-01 | 4.9 | 10% | 0.2401 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.709.1 | 2022-01-01 | 14.2 | 10% | 2.0164 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.710.1 | 2022-01-01 | 3.5 | 10% | 0.1225 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.710.2 | 2022-01-01 | 3 | 10% | 0.09 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.711.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.712.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.713.1 | 2022-01-01 | 15.3 | 10% | 2.3409 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.714.1 | 2022-01-01 | 12.4 | 10% | 1.5376 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.715.1 | 2022-01-01 | 5.5 | 10% | 0.3025 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.716.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.717.1 | 2022-01-01 | 3.6 | 10% | 0.1296 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.718.1 | 2022-01-01 | 7.4 | 10% | 0.5476 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.719.1 | 2022-01-01 | 10 | 10% | 1 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.720.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.721.1 | 2022-01-01 | 16 | 10% | 2.56 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.722.1 | 2022-01-01 | 26.6 | 10% | 7.0756 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.723.1 | 2022-01-01 | 14.9 | 10% | 2.2201 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.724.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.725.1 | 2022-01-01 | 8.9 | 10% | 0.7921 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.725.2 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.726.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.727.1 | 2022-01-01 | 9.4 | 10% | 0.8836 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.728.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.728.2 | 2022-01-01 | 6.5 | 10% | 0.4225 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.729.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.730.1 | 2022-01-01 | 2.7 | 10% | 0.0729 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.731.1 | 2022-01-01 | 5.9 | 10% | 0.3481 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.732.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.733.1 | 2022-01-01 | 15.6 | 10% | 2.4336 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.734.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.735.1 | 2022-01-01 | 12.6 | 10% | 1.5876 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.736.1 | 2022-01-01 | 32.3 | 10% | 10.4329 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.737.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.737.2 | 2022-01-01 | 7 | 10% | 0.49 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.738.1 | 2022-01-01 | 5.5 | 10% | 0.3025 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.738.2 | 2022-01-01 | 12.5 | 10% | 1.5625 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.739.1 | 2022-01-01 | 10.7 | 10% | 1.1449 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.740.1 | 2022-01-01 | 11.9 | 10% | 1.4161 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.741.1 | 2022-01-01 | 19.1 | 10% | 3.6481 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.742.1 | 2022-01-01 | 12.7 | 10% | 1.6129 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.743.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.744.1 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.745.1 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-10-08 | 0 | 10% | 0
HBG-1.RR.746.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-10-08 | 0 | 10% | 0
HBG-1.RR.747.1 | 2022-01-01 | 12.6 | 10% | 1.5876 | 2022-10-08 | 0 | 10% | 0
HBG-1.RR.748.1 | 2022-01-01 | 8.2 | 10% | 0.6724 | 2022-10-08 | 0 | 10% | 0
HBG-1.RR.749.1 | 2022-01-01 | 3.6 | 10% | 0.1296 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.750.1 | 2022-01-01 | 7.7 | 10% | 0.5929 | 2022-09-22 | 0 | 10% | 0
HBG-1.RR.751.1 | 2022-01-01 | 13.5 | 10% | 1.8225 | 2022-10-02 | 0 | 10% | 0
HBG-1.RR.751.2 | 2022-01-01 | 1.6 | 10% | 0.0256 | 2022-10-02 | 0 | 10% | 0
HBG-1.RR.752.1 | 2022-01-01 | 13.2 | 10% | 1.7424 | 2022-10-02 | 0 | 10% | 0
HBG-1.RR.753.1 | 2022-01-01 | 12.6 | 10% | 1.5876 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.754.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.755.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.756.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-29 | 0 | 10% | 0
HBG-1.RR.757.1 | 2022-01-01 | 14 | 10% | 1.96 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.758.1 | 2022-01-01 | 13.7 | 10% | 1.8769 |  |  | 10%
HBG-1.RR.759.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.760.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.761.1 | 2022-01-01 | 13.5 | 10% | 1.8225 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.762.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.763.1 | 2022-01-01 | 11 | 10% | 1.21 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.764.1 | 2022-01-01 | 6.5 | 10% | 0.4225 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.765.1 | 2022-01-01 | 5.5 | 10% | 0.3025 |  |  | 10%
HBG-1.RR.766.1 | 2022-01-01 | 7.3 | 10% | 0.5329 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.767.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.768.1 | 2022-01-01 | 21 | 10% | 4.41 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.769.1 | 2022-01-01 | 14.7 | 10% | 2.1609 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.770.1 | 2022-01-01 | 19.1 | 10% | 3.6481 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.771.1 | 2022-01-01 | 10.5 | 10% | 1.1025 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.772.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.773.1 | 2022-01-01 | 11.6 | 10% | 1.3456 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.774.1 | 2022-01-01 | 11.5 | 10% | 1.3225 |  |  | 10%
HBG-1.RR.775.1 | 2022-01-01 | 6.2 | 10% | 0.3844 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.776.1 | 2022-01-01 | 4.9 | 10% | 0.2401 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.777.1 | 2022-01-01 | 12.4 | 10% | 1.5376 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.778.1 | 2022-01-01 | 9 | 10% | 0.81 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.779.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.780.1 | 2022-01-01 | 17.3 | 10% | 2.9929 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.781.1 | 2022-01-01 | 9.6 | 10% | 0.9216 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.782.1 | 2022-01-01 | 6.4 | 10% | 0.4096 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.783.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.784.1 | 2022-01-01 | 3.3 | 10% | 0.1089 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.785.1 | 2022-01-01 | 4.9 | 10% | 0.2401 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.786.1 | 2022-01-01 | 12 | 10% | 1.44 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.787.1 | 2022-01-01 | 6.3 | 10% | 0.3969 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.788.1 | 2022-01-01 | 6.6 | 10% | 0.4356 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.789.1 | 2022-01-01 | 11.5 | 10% | 1.3225 |  |  | 10%
HBG-1.RR.790.1 | 2022-01-01 | 13.1 | 10% | 1.7161 | 2022-10-01 | 0 | 10% | 0
HBG-1.RR.791.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.792.1 | 2022-01-01 | 12.4 | 10% | 1.5376 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.793.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.794.1 | 2022-01-01 | 16.1 | 10% | 2.5921 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.795.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.796.1 | 2022-01-01 | 9 | 10% | 0.81 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.797.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.798.1 | 2022-01-01 | 4.7 | 10% | 0.2209 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.799.1 | 2022-01-01 | 9.8 | 10% | 0.9604 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.800.1 | 2022-01-01 | 9.8 | 10% | 0.9604 | 2022-10-03 | 0 | 10% | 0
HBG-1.RR.801.1 | 2022-01-01 | 13.8 | 10% | 1.9044 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.802.1 | 2022-01-01 | 10.3 | 10% | 1.0609 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.803.1 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.804.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.805.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.806.1 | 2022-01-01 | 11.3 | 10% | 1.2769 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.807.1 | 2022-01-01 | 9.7 | 10% | 0.9409 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.808.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.808.2 | 2022-01-01 | 10.2 | 10% | 1.0404 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.809.1 | 2022-01-01 | 6.9 | 10% | 0.4761 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.810.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.811.1 | 2022-01-01 | 7.6 | 10% | 0.5776 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.811.2 | 2022-03-21 | 7.9 | 10% | 0.6241 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.812.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.813.1 | 2022-01-01 | 9.4 | 10% | 0.8836 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.813.2 | 2022-01-01 | 6.2 | 10% | 0.3844 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.814.1 | 2022-01-01 | 5.5 | 10% | 0.3025 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.815.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.816.1 | 2022-01-01 | 4.9 | 10% | 0.2401 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.817.1 | 2022-01-01 | 2.9 | 10% | 0.0841 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.818.1 | 2022-01-01 | 7.1 | 10% | 0.5041 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.819.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.820.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.821.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.822.1 | 2022-01-01 | 7.8 | 10% | 0.6084 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.823.1 | 2022-01-01 | 4.5 | 10% | 0.2025 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.824.1 | 2022-01-01 | 10 | 10% | 1 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.825.1 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.826.1 | 2022-01-01 | 10.1 | 10% | 1.0201 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.827.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.828.1 | 2022-01-01 | 6.9 | 10% | 0.4761 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.829.1 | 2022-01-01 | 8.7 | 10% | 0.7569 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.830.1 | 2022-01-01 | 5.8 | 10% | 0.3364 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.831.1 | 2022-01-01 | 8.4 | 10% | 0.7056 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.832.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-28 | 2.3 | 10% | 0.0529
HBG-1.RR.833.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.834.1 | 2022-01-01 | 10.5 | 10% | 1.1025 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.835.1 | 2022-01-01 | 2.9 | 10% | 0.0841 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.836.1 | 2022-01-01 | 8.6 | 10% | 0.7396 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.837.1 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.838.1 | 2022-01-01 | 11.1 | 10% | 1.2321 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.839.1 | 2022-01-01 | 12.9 | 10% | 1.6641 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.840.1 | 2022-01-01 | 6 | 10% | 0.36 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.840.2 | 2022-01-01 | 11.7 | 10% | 1.3689 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.841.1 | 2022-01-01 | 5.2 | 10% | 0.2704 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.842.1 | 2022-01-01 | 8.8 | 10% | 0.7744 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.843.1 | 2022-01-01 | 24.3 | 10% | 5.9049 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.844.1 | 2022-01-01 | 13 | 10% | 1.69 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.845.1 | 2022-01-01 | 6.8 | 10% | 0.4624 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.846.1 | 2022-01-01 | 7 | 10% | 0.49 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.847.1 | 2022-01-01 | 13 | 10% | 1.69 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.848.1 | 2022-01-01 | 7.6 | 10% | 0.5776 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.849.1 | 2022-01-01 | 15.6 | 10% | 2.4336 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.850.1 | 2022-01-01 | 12.5 | 10% | 1.5625 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.851.1 | 2022-01-01 | 10.6 | 10% | 1.1236 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.852.1 | 2022-01-01 | 9.4 | 10% | 0.8836 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.853.1 | 2022-01-01 | 10.4 | 10% | 1.0816 |  |  | 10%
HBG-1.RR.854.1 | 2022-01-01 | 7.2 | 10% | 0.5184 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.855.1 | 2022-01-01 | 9.1 | 10% | 0.8281 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.856.1 | 2022-01-01 | 16 | 10% | 2.56 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.857.1 | 2022-01-01 | 11.4 | 10% | 1.2996 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.858.1 | 2022-01-01 | 8.5 | 10% | 0.7225 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.859.1 | 2022-01-01 | 20.4 | 10% | 4.1616 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.860.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.861.1 | 2022-01-01 | 14.9 | 10% | 2.2201 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.862.1 | 2022-01-01 | 9.8 | 10% | 0.9604 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.863.1 | 2022-01-01 | 9.4 | 10% | 0.8836 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.864.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.865.1 | 2022-01-01 | 4.6 | 10% | 0.2116 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.866.1 | 2022-01-01 | 5.7 | 10% | 0.3249 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.867.1 | 2022-01-01 | 30.7 | 10% | 9.4249 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.868.1 | 2022-01-01 | 17 | 10% | 2.89 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.869.1 | 2022-01-01 | 5 | 10% | 0.25 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.870.1 | 2022-01-01 | 10.4 | 10% | 1.0816 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.871.1 | 2022-01-01 | 6 | 10% | 0.36 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.872.1 | 2022-01-01 | 8.8 | 10% | 0.7744 | 2022-09-25 | 0 | 10% | 0
HBG-1.RR.873.1 | 2022-01-01 | 10.8 | 10% | 1.1664 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.874.1 | 2022-01-01 | 3.7 | 10% | 0.1369 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.875.1 | 2022-01-01 | 22.8 | 10% | 5.1984 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.876.1 | 2022-01-01 | 11.2 | 10% | 1.2544 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.877.1 | 2022-01-01 | 9.8 | 10% | 0.9604 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.878.1 | 2022-01-01 | 11.5 | 10% | 1.3225 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.879.1 | 2022-01-01 | 10.9 | 10% | 1.1881 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.880.1 | 2022-01-01 | 12.3 | 10% | 1.5129 | 2022-09-26 | 0 | 10% | 0
HBG-1.RR.881.1 | 2022-01-01 | 12.4 | 10% | 1.5376 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.881.2 | 2022-01-01 | 7.5 | 10% | 0.5625 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.882.1 | 2022-01-01 | 12.1 | 10% | 1.4641 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.883.1 | 2022-01-01 | 25.3 | 10% | 6.4009 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.884.1 | 2022-01-01 | 16.7 | 10% | 2.7889 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.885.1 | 2022-01-01 | 11.8 | 10% | 1.3924 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.886.1 | 2022-01-01 | 12.8 | 10% | 1.6384 | 2022-09-28 | 0 | 10% | 0
HBG-1.RR.887.1 | 2022-01-01 | 14.3 | 10% | 2.0449 | 2022-09-28 | 0 | 10% | 0